## Read Me
DOUBLE CLICK THE IMAGE TO THE LEFT TO READ THE
INSTRUCTIONS FOR THIS WORKBOOK.
The instruction booklet will open in a new Acrobat window.
The main user interface for this workbook is on the Vallve Sizing tab.
Your expereince with this workbook will be significantly enhanced it you read
the INTRODUCTION and USING THE WORKBOOK sections.

## Valve Sizing
CONTROL VALVE SIZING: GAS - Volumetric |  | TAG: | PV123 |  |  |  |  | Available Cv table names |  | Scroll to the right to view the intermediate calculations | Valve sizing per ISA S75.01.01 2012
Flow (at standard conditions) | scfh | Q | 31863 | 93645 | 184894 | 236393 |  | BALL_FP | Full Port Ball Valve |  | DESCRIPTION OF VARIABLE | Eqn. | NAME OF VARIABLE | FORMULA
Inlet pressure | psiA | P_1 | 90 | 88.6 | 83.7 | 80 |  | BALL_RP | Reduced Port Ball Valve |  | CALCULATED IN COLUMN "S" |  | CALCULATED IN COLUMN "S"
Inlet temperature | F | T_1 | 100 | 100 | 100 | 100 |  | BALL_SEG | Segment Ball valve |  | Pressure drop ratio | 9 | x | 0.33333 | 0.3228 | 0.28315 | 0.25
Pressure drop | psi | DELTA_P | 30 | 28.6 | 23.7 | 20 |  | HPBF_150 | High Perf. Buttefly Cl 150 |  | Ratio of specific heats factor | 11 | F_GAMMA | 1 | 1 | 1 | 1
Molecular mass |  | M | 28.97 |  |  |  |  | HPBF_300 | High Perf. Buttefly Cl 300 |  | Absolute temperature |  | T_abs | 559.67 | 559.67 | 559.67 | 559.67
Specific heat ratio |  | GAMMA | 1.4 |  |  |  |  | HPBF_600 | High Perf. Buttefly Cl 600
Compressibility factor |  | Z | 1 | 1 | 1 | 1 |  | GC_EQ | Globe Cage Guided =% |  | WITHOUT REDUCERS
Choked press drop ratio factor |  | x_T | 0.64 | 0.62307 | 0.55446 | 0.44972 | 4 | GC_LIN | Globe Cage Guided linear |  | Expansion factor | 12 | Y | 0.82639 | 0.82731 | 0.82977 | 0.8147
Liquid press. Recovery factor |  | F_L | 0.92464 | 0.89311 | 0.83223 | 0.77714 | 1, 3 | GP_EQ | Globe Parabolic Plug =% |  | C Non choked | 7 | C_NonCh | 12.9077 | 39.1153 | 87.0274 | 126.1844
Valve style modifier |  | F_D | 0.77395 | 0.84824 | 0.92141 | 0.95597 | 1, 3 | GP_LIN | Globe Parabolic Plug Linear |  | C Choked | 7 | C_Ch | 11.5414 | 34.9209 | 77.3686 | 114.9146
Valve correction - accoustic efficiency, Ah |  | A_ETA | -3.6 |  |  |  | 1, 3 | ROT_PLUG | Eccentric Rotary Plug |  | Choked pressure drop ratio (xchoked) | 10 | CH_x | 0.64 | 0.62307 | 0.55446 | 0.44972
Strouhal number (peak) |  | St_P | 0.3 |  |  |  | 1, 3 |  |  |  | Select C Non choked or C choked |  | Select_C_Non_or_C_Ch | 12.9077 | 39.1153 | 87.0274 | 126.1844
Inlet pipe diameter | inch | D_1 | 6 | [7 empty] | (This is the initial guess for
Outlet pipe diameter | inch | D_2 | 6
Valve size | inch | d | 3 |  |  |  | 5
Valve Cv table |  | Cv_Table | BALL_SEG |  |  |  | 6
Outlet pipe wall thickness | inch | T_S | 0.28 |  |  |  | 1 |  |  |  | Reducer velocity head coefficients | 18 | ZETA_1 | 0.28125 | ======> | ======> | ======>
Contraction coeff. for valve outlet |  | BETA | 0.75 |  |  |  | 1, 2 |  |  |  |  | 17 | ZETA_B1 | 0.9375 | ======> | ======> | ======>
Atmospheric pressure outside pipe | psiA | p_a | 14.696 |  |  |  | 1 |  |  |  |  | 19 | ZETA_2 | 0.5625 | ======> | ======> | ======>
Required flow coef. (Cv or Kv) | Cv | C_ | 12.9194 | 39.4405 | 90.6476 | 136.9874 | 1 = This entry is only used in the IEC noise calculation. |  |  |  |  | 17 | ZETA_B2 | 0.9375 | ======> | ======> | ======>
Flow calculated from C_ above | scfh |  | 31863 | 93645 | 184894 | 236393 | 2 = Beta is used when valve outlet exceeds Mach 0.3, 0.75 is typical. |  |  |  | Sum of velocity head coefficients | 16 | SIGMA_ZETA | 0.84375 | ======> | ======> | ======>
Outlet velocity | Mach |  | 0.0411 | 0.12079 | 0.2385 | 0.30493 | Consult valve manufacturer. |  |  |  | Sum of upstream velocity head coef |  | SIGMA_ZETA_1 | 1.2188 | ======> | ======> | ======>
Sound pressure level | dB(A) |  | 78.1748 | 84.616 | 87.3885 | 87.6799 | 3 = Values automatically copied from the "xT, FL, Fd, Aeta, Stp" tab. Can be overridden manually.
Travel | % |  | 21.1574 | 40.0187 | 60.7462 | 73.6335 | 4 = See "xT, FL, Fd, Aeta, Stp" tab for typical values. |  |  |  | Beginning of iterative calculation |  | Total 60 iterations
[5 empty] | Data input | Calculated values | 5 = See "Valve Travel" tab for supported valve sizes. |  |  |  | Assumed C for iterative purposes |  | C_i | 12.9077 | 39.1153 | 87.0274 | 126.1844
Unit selection: | 1 | 1 = US; 2 = SI (Cv, bar); 3 = SI (Cv, kPa); 4 = SI (Kv, bar); 5 = SI (Kv, kPa) |  |  |  |  | 6 = A valid "Cv table" name must be entered for SPL and Travel results. |  |  |  | Piping geometry factor | 15 | F_P | 0.99903 | 0.99116 | 0.95842 | 0.9181
Valve & pipe dia., wall thickness: | 1 | 1 = inch & Cv 2 = mm & Cv 3 = mm & Kv | [8 empty] | Choked Pres drop ratio factor with reducers | 22 | x_TP | 0.64022 | 0.62526 | 0.56774 | 0.48164
Standard cond. temp. reference: | 1 | 1 = 15C / 60F; 2 = 0C / 32F | [8 empty] | Expansion factor | 12 | Y_W_Reducers | 0.82645 | 0.82791 | 0.83375 | 0.82698
[11 empty] | C Non choked w/ reducers | 7 | C_NonCh_W_Reducers | 12.9194 | 39.4352 | 90.3692 | 135.3994
[11 empty] | C Choked w/ reducers | 7 | C_Ch_W_Reducers | 11.5506 | 35.1704 | 79.7754 | 120.9469
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 | CH_x_W_Reducers | 0.64022 | 0.62526 | 0.56774 | 0.48164
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4352 | 90.3692 | 135.3994
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4352 | 90.3692 | 135.3994
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95538 | 0.90738
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.56871 | 0.48594
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83404 | 0.82851
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4404 | 90.6258 | 136.7468
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1745 | 79.9607 | 121.8341
| The cells below (Rows 44 & 46) detrmine if any input data is missing. | [9 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.56871 | 0.48594
| If it is, error messages are blanked out of the calculated results. | [9 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4404 | 90.6258 | 136.7468
| DATA1 | DATA2 | DATA3 | DATA4
For sizing calculations | 2.4117e+13 | 6.4762e+13 | 8.9078e+13 | 7.4508e+13 | [6 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4404 | 90.6258 | 136.7468
| N_DAT1 | N_DAT2 | N_DAT3 | N_DAT4 | [6 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95515 | 0.90578
For noise calculations | -2.3852 | -2.525 | -2.5559 | -2.4762 | [6 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.56879 | 0.48658
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82874
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6459 | 136.9508
These Numerical constants are set by the units choises set by the user below the user interface | [10 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9752 | 121.9685
which incllude all the options supported by the ISA Standard | [10 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.56879 | 0.48658
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6459 | 136.9508
Numerical constants
N_2 | 890 |  |  | The formula in Column C returns values of N_9 depending on Unit selection codes for a Standard temp Reference of 15C (60F) | [6 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6459 | 136.9508
N_5 | 1000 |  |  | The formula in Column D returns values of N_9 depending on Unit selection codes in B27 for a Standard temp Reference of 0C (32F) | [6 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90554
N_9 | 7320 | 7320 | 6940 | The actual value of N_9 in Column B used in the calculations is selected from the value entered for "Standard cond. temp." | [6 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.56879 | 0.48668
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82877
FLAG_A | 1 | 1= Inlet Temp entered in F is converted to R in T_abs field | [8 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6474 | 136.9818
|  | 2= Inlet Temp entered in C is coverted to K in T_abs field | [8 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9764 | 121.9889
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.56879 | 0.48668
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6474 | 136.9818
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6474 | 136.9818
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.9055
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.48669
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9865
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.992
Sizing Gas 3.5 | [10 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.48669
Noise 1a | [10 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9865
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9865
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9872
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9925
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9872
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9872
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9873
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9873
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9873
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Assumed C for iterative purposes |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 |  | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 |  | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | C Non choked w/ reducers | 7 |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | C Choked w/ reducers | 7 |  | 11.5506 | 35.1746 | 79.9765 | 121.9926
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select C Non choked or C choked |  |  | 12.9194 | 39.4405 | 90.6476 | 136.9874
Confirmation that the calculated C will produce the given flow rate
[11 empty] | Final C calculated above |  | Final_Calculated_C | 12.9194 | 39.4405 | 90.6476 | 136.9874
[11 empty] | Piping geometry factor | 15 | Final_F_P | 0.99902 | 0.99102 | 0.95513 | 0.90549
[11 empty] | Presssure drop ratio factor w/reducers | 22 | Final_x_TP | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Expansion factor | 12 | Final_Y_W_Reducers | 0.82645 | 0.82792 | 0.83406 | 0.82878
[11 empty] | Flow Non choked w/ reducers | 7 | Final_Flow_NonCh_W_Reducers | 31863 | 93645 | 184894 | 236393
[11 empty] | Flow Choked w/ reducers | 7 | Final_Flow_Ch_W_Reducers | 35638.7258 | 105002.0803 | 209564.0593 | 265449.321
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 | Final_CH_x_W_Reducers | 0.64022 | 0.6253 | 0.5688 | 0.4867
[11 empty] | Select flow Non choked or flow choked |  | Calc_Flow_From_Final_ Calc_C | 31863 | 93645 | 184894 | 236393

## Installed Flow
Intermediate Calculations
VALVE DATA | [11 empty] | Scroll to the right to see the | DESCRIPTION OF VARIABLE | Eqn. | NAME OF VARIABLE | FORMULA
Valve Cv table | BALL_SEG | [10 empty] | intermediate calculations | CALCULATED IN COLUMN "P" |  | CALCULATED IN COLUMN "P"
Valve size, Inch, from Valve Travell tab | 3
Relative travel, h | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 |  | NO USER INPUT IS REQUIRED FOR THIS TAB. | CALCULATE PARAMETERS FOR UPSTREAM AND DOWNSTREAM PROCESS PRESSURE MODEL
Cv from tables on Valve Travel tab | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420 |  |  | Minimum design flow (From Col D of Valve Sizing tab) |  | Q_min | 31863
xT | 0.64 | 0.64 | 0.63341 | 0.6231 | 0.60075 | 0.55873 | 0.50449 | 0.42327 | 0.34677 | 0.18243 |  |  | Maximum design flow (From Col F of Valve Sizing tab) |  | Q_max | 236393
[13 empty] | Valve inlet pressure at minimum des. Flow |  | P_1_minQ | 90
[12 empty] | Scroll down for instructions for the Installed flow and gain graphs and | Valve inlet pressure at maximum des. flow |  | P_1_maxQ | 80
[12 empty] | the calculation of the fully open flow, Qf. The accuracy of the calculations | Pressure drop at minimum des. flow |  | DELTA_P_minQ | 30
| 3 0.7: BALL_SEG |  | on this and the Installed Gain tab depend on the accuracy of the process | Pressure drop at maximum des. flow |  | DELTA_P_maxQ | 20
| 3 0.7: 3 |  | data. | Valve outlet pressure at minimum des. Flow |  | P_2_minQ | 60
| 3 0.7: PV123 |  |  | Valve outlet pressure at maximum des. flow |  | P_2_maxQ | 60
[13 empty] | Upstream system drop |  | dp_up | 10
| 3 0.7: Fully open Flow, Qf |  | INSTALED FLOW AND GAIN ERRORS | Upstream system resistance factor |  | R_up | 1.8226e-10
| 3 0.7: Qf=; 3 0.8: 328229.9007 |  | If there are any error messages below, the graphs and Qf are not valid | Downstream system drop |  | dp_dn | 0
[13 empty] | Downstream system resistance factor |  | R_dn | 0 | ` | 0.1 |  |  | 0.2 |  |  | 0.3 |  |  | 0.4 |  |  | 0.5 |  |  | 0.6 |  |  | 0.7 |  |  | 0.8 |  |  | 0.9 |  |  | 1
[13 empty] | Upstream system press drop an min flow |  | dpup_minQ | 0.18504 | Min C_h - Ci | 0.00059933 |  |  | 0.015885 |  |  | 0.10968 |  |  | 0.068214 |  |  | 0.29767 |  |  | 0.17793 |  |  | 0.055026 |  |  | 0.63105 |  |  | 1.3663 |  |  | 2.2591
[13 empty] | Downstream system press drop an min flow |  | dpdn_minQ | 0 | Flow at C_h | 11708.9493 |  |  | 28670.9158 |  |  | 55843.6258 |  |  | 93688.2323 |  |  | 136740.5267 |  |  | 182480.763 |  |  | 222661.2095 |  |  | 258502.7518 |  |  | 303114.8064 |  |  | 328229.9007
| 3 0.7: Qmax = maximum | [6 empty] | Values found on Line | 2591 |  |  | 1303 |  |  | 981 |  |  | 771 |  |  | 575 |  |  | 449 |  |  | 323 |  |  | 253 |  |  | 267 |  |  | 155
[8 empty] | design flow = | 236393
[11 empty] | Scroll down for instructions |  | CALCULATE FLOW AT EACH INCREMENT OF h
[13 empty] | Valve C at travel h (Cv or Kv) |  | C_h | 4.73 |  |  | 11.6 |  | ` | 23 |  |  | 39.4 |  |  | 61 |  |  | 88.2 |  |  | 121 |  |  | 165 |  |  | 246 |  |  | 420
C_h is Cv or Kv depending on the
| 3 0.7: Qmin = minimum |  |  |  |  | "Unit Selection" made on the
| 3 0.8: design flow =; 3 0.9: 31863 |  |  | Caculation of flow conditions |  | Valve Sizing tab.
[13 empty] | Piping geometry factor at relative travel, h | 15 | F_P_h | 0.99987 |  |  | 0.99921 |  |  | 0.99692 |  |  | 0.99104 |  |  | 0.97891 |  |  | 0.95737 |  |  | 0.92396 |  |  | 0.87084 |  |  | 0.7651 |  |  | 0.57123
| 3 0.8: Flow units are; 3 0.9: scfh |  |  | Reducer corrected pressure drop ratio factor at choked flow | 21 | x_TP_h | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | First iteration flow rate |  | Q_i | 318.63 | Abs Value of | Flow this | 11708.9493 | Abs Value of | Flow this | 28670.9158 | Abs Value of | Flow this | 55843.6258 | Abs Value of | Flow this | 93688.2323 | Abs Value of | Flow this | 136740.5267 | Abs Value of | Flow this | 182480.763 | Abs Value of | Flow this | 222661.2095 | Abs Value of | Flow this | 258502.7518 | Abs Value of | Flow this | 303114.8064 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  | P1_Qi | 90.185 |  |  | 90.1601 |  |  | 90.0352 |  |  | 89.6167 |  |  | 88.5852 |  |  | 86.7771 |  |  | 84.1159 |  |  | 81.1489 |  |  | 78.0057 |  |  | 73.4392
Valve relative travel, h | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 |  | P2 at this iteration flow rate |  | P2_Qi | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
Relative Flow Q/Qf | 0 | 0.035673 | 0.08735 | 0.17014 | 0.28543 | 0.4166 | 0.55595 | 0.67837 | 0.78757 | 0.92348 | 1 |  | Delta P at this iteration flow rate |  | DELTA_P_Qi | 30.185 |  |  | 30.1601 |  |  | 30.0352 |  |  | 29.6167 |  |  | 28.5852 |  |  | 26.7771 |  |  | 24.1159 |  |  | 21.1489 |  |  | 18.0057 |  |  | 13.4392
Minimum Flow | 0.097075 | 0.097075 | 0.097075 | 0.097075 | 0.097075 | 0.097075 | 0.097075 | 0.097075 | 0.097075 | 0.097075 | 0.097075 |  | Press drop ratio this iteration |  | x_Qi | 0.3347 |  |  | 0.33452 |  |  | 0.33359 |  |  | 0.33048 |  |  | 0.32269 |  |  | 0.30857 |  |  | 0.2867 |  |  | 0.26062 |  |  | 0.23083 |  |  | 0.183
Maximum Flow | 0.72021 | 0.72021 | 0.72021 | 0.72021 | 0.72021 | 0.72021 | 0.72021 | 0.72021 | 0.72021 | 0.72021 | 0.72021 |  | Expansion factor | 12 | Y_C_h | 0.82568 |  |  | 0.82582 |  |  | 0.82465 |  |  | 0.82383 |  |  | 0.82266 |  |  | 0.82023 |  |  | 0.82031 |  |  | 0.81737 |  |  | 0.86971 |  |  | 0.83807
[13 empty] | C Non choked w/ reducers | 7 | C_N_Ch | 0.12868 |  |  | 4.7335 |  |  | 11.666 |  |  | 23.0946 |  |  | 40.2163 |  |  | 62.8385 |  |  | 92.9873 |  |  | 131.3518 |  |  | 180.3152 |  |  | 350.5869
[13 empty] | C Choked w/ reducers | 7 | C_Ch | 0.11519 |  |  | 4.2364 |  |  | 10.4612 |  |  | 20.737 |  |  | 36.1796 |  |  | 56.7481 |  |  | 83.9653 |  |  | 119.1457 |  |  | 146.9932 |  |  | 307.0281
INSTRUCTIONS FOR THE OPTIONAL INSTALLED FLOW AND GAIN GRAPHS AND FULLY OPEN FLOW CALCULATION The process pressure model is a curve fit based on the Flow, P1 and Delta P in Columns D and G on the Valve Sizing tab. The curve fit is based on the principle that piping pressure losses are approximately proportional to flow squared. The Temperature and Compressibility Factor used in the installed flow calculation are the values entered in Column G on the Valve Sizing tab. To calculate the fully open flow, Qf, the installed flow and the installed gain, on the Valve Sizing tab, enter the minimum design flow along with its associated values of P1 and Delta P in Column D and the maximum design flow along with its associated values of P1 and Delta P in Column G. The accuracy of these calculations depends on the accuracy of the process data that is used. Any process conditions entered in Columns E and F are not used in the calculation of the fully open flow, the installed flow and the installed gain. The process model, Qf, and the graphs are only valid if: 1. The flow in G2 on the Valve Sizing tab is greater than the flow in D2 2. P1 is either constant or decreasing with increasing flow 3. P2 is either constant or increasing with increasing flow NOTE: Extrapolating curve-fit data beyond the limits for which the curve fit was established can be uncertain. The farther beyond the limits, the greater is the potential for uncertainty. As such, the fully open flow, the Installed Flow and the Installed Gain should be treated as approximations. | [12 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 | CH_x_W_Reducers | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  | C_i | 0.12868 |  |  | 4.7335 |  |  | 11.666 |  |  | 23.0946 |  |  | 40.2163 |  |  | 62.8385 |  |  | 92.9873 |  |  | 131.3518 |  |  | 180.3152 |  |  | 350.5869
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.6013 | 318.63 |  | 6.8665 | 11708.9493 |  | 11.334 | 28670.9158 |  | 16.3054 | 55843.6258 |  | 20.7837 | 93688.2323 |  | 25.3615 | 136740.5267 |  | 28.0127 | 182480.763 |  | 33.6482 | 222661.2095 |  | 65.6848 | 258502.7518 |  | 69.4131 | 303114.8064
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 325.0026 | C_100 - C this iteration | iteration | 11826.0388 | C_100 - C this iteration | iteration | 28957.6249 | C_100 - C this iteration | iteration | 56402.062 | C_100 - C this iteration | iteration | 94625.1146 | C_100 - C this iteration | iteration | 138107.932 | C_100 - C this iteration | iteration | 184305.5707 | C_100 - C this iteration | iteration | 224887.8216 | C_100 - C this iteration | iteration | 261087.7793 | C_100 - C this iteration | iteration | 306145.9545 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1596 |  |  | 90.0322 |  |  | 89.6052 |  |  | 88.5531 |  |  | 86.7086 |  |  | 83.9939 |  |  | 80.9673 |  |  | 77.7609 |  |  | 73.1026
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1596 |  |  | 30.0322 |  |  | 29.6052 |  |  | 28.5531 |  |  | 26.7086 |  |  | 23.9939 |  |  | 20.9673 |  |  | 17.7609 |  |  | 13.1026
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33451 |  |  | 0.33357 |  |  | 0.3304 |  |  | 0.32244 |  |  | 0.30803 |  |  | 0.28566 |  |  | 0.25896 |  |  | 0.2284 |  |  | 0.17924
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82582 |  |  | 0.82466 |  |  | 0.82388 |  |  | 0.82279 |  |  | 0.82055 |  |  | 0.82096 |  |  | 0.81853 |  |  | 0.87108 |  |  | 0.84139
[13 empty] | C Non choked w/ reducers | 7 |  | 0.13125 |  |  | 4.7808 |  |  | 11.7833 |  |  | 23.3302 |  |  | 40.642 |  |  | 63.5486 |  |  | 94.1495 |  |  | 133.1986 |  |  | 183.3693 |  |  | 358.0147
[13 empty] | C Choked w/ reducers | 7 |  | 0.11749 |  |  | 4.2788 |  |  | 10.5661 |  |  | 20.947 |  |  | 36.5546 |  |  | 57.3609 |  |  | 84.9282 |  |  | 120.6071 |  |  | 148.9305 |  |  | 311.5262
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.13125 |  |  | 4.7808 |  |  | 11.7833 |  |  | 23.3302 |  |  | 40.642 |  |  | 63.5486 |  |  | 94.1495 |  |  | 133.1986 |  |  | 183.3693 |  |  | 358.0147
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5988 | 325.0026 |  | 6.8192 | 11826.0388 |  | 11.2167 | 28957.6249 |  | 16.0698 | 56402.062 |  | 20.358 | 94625.1146 |  | 24.6514 | 138107.932 |  | 26.8505 | 184305.5707 |  | 31.8014 | 224887.8216 |  | 62.6307 | 261087.7793 |  | 61.9853 | 306145.9545
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 331.5027 | C_100 - C this iteration | iteration | 11944.2991 | C_100 - C this iteration | iteration | 29247.2012 | C_100 - C this iteration | iteration | 56966.0827 | C_100 - C this iteration | iteration | 95571.3658 | C_100 - C this iteration | iteration | 139489.0113 | C_100 - C this iteration | iteration | 186148.6264 | C_100 - C this iteration | iteration | 227136.6998 | C_100 - C this iteration | iteration | 263698.6571 | C_100 - C this iteration | iteration | 309207.4141 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.159 |  |  | 90.0291 |  |  | 89.5936 |  |  | 88.5203 |  |  | 86.6388 |  |  | 83.8695 |  |  | 80.782 |  |  | 77.5112 |  |  | 72.7592
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.159 |  |  | 30.0291 |  |  | 29.5936 |  |  | 28.5203 |  |  | 26.6388 |  |  | 23.8695 |  |  | 20.782 |  |  | 17.5112 |  |  | 12.7592
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33451 |  |  | 0.33355 |  |  | 0.33031 |  |  | 0.32219 |  |  | 0.30747 |  |  | 0.2846 |  |  | 0.25726 |  |  | 0.22592 |  |  | 0.17536
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82582 |  |  | 0.82467 |  |  | 0.82393 |  |  | 0.82293 |  |  | 0.82088 |  |  | 0.82162 |  |  | 0.81972 |  |  | 0.87248 |  |  | 0.84482
[13 empty] | C Non choked w/ reducers | 7 |  | 0.13387 |  |  | 4.8287 |  |  | 11.9017 |  |  | 23.5684 |  |  | 41.0727 |  |  | 64.2687 |  |  | 95.3321 |  |  | 135.0873 |  |  | 186.5187 |  |  | 365.8014
[13 empty] | C Choked w/ reducers | 7 |  | 0.11984 |  |  | 4.3216 |  |  | 10.6722 |  |  | 21.1592 |  |  | 36.9339 |  |  | 57.9812 |  |  | 85.9047 |  |  | 122.0926 |  |  | 150.9045 |  |  | 316.1263
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.13387 |  |  | 4.8287 |  |  | 11.9017 |  |  | 23.5684 |  |  | 41.0727 |  |  | 64.2687 |  |  | 95.3321 |  |  | 135.0873 |  |  | 186.5187 |  |  | 365.8014
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5961 | 331.5027 |  | 6.7713 | 11944.2991 |  | 11.0983 | 29247.2012 |  | 15.8316 | 56966.0827 |  | 19.9273 | 95571.3658 |  | 23.9313 | 139489.0113 |  | 25.6679 | 186148.6264 |  | 29.9127 | 227136.6998 |  | 59.4813 | 263698.6571 |  | 54.1986 | 309207.4141
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
xT for characteritics calculation | [12 empty] | Next iteration flow rate |  |  | 338.1327 | C_100 - C this iteration | iteration | 12063.7421 | C_100 - C this iteration | iteration | 29539.6732 | C_100 - C this iteration | iteration | 57535.7435 | C_100 - C this iteration | iteration | 96527.0794 | C_100 - C this iteration | iteration | 140883.9014 | C_100 - C this iteration | iteration | 188010.1126 | C_100 - C this iteration | iteration | 229408.0668 | C_100 - C this iteration | iteration | 266335.6437 | C_100 - C this iteration | iteration | 312299.4882 | C_100 - C this iteration | iteration
Globe, cage | 0.74 | 0.73391 | 0.7245 | 0.72088 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1585 |  |  | 90.026 |  |  | 89.5817 |  |  | 88.4868 |  |  | 86.5675 |  |  | 83.7425 |  |  | 80.593 |  |  | 77.2564 |  |  | 72.409
Globe Parabolic | 0.61655 | 0.60846 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
Rotary plug | 0.62 | 0.62 | 0.62 | 0.62 | 0.60431 | 0.55623 | 0.45298 | 0.399 | 0.399 | 0.399 |  |  | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1585 |  |  | 30.026 |  |  | 29.5817 |  |  | 28.4868 |  |  | 26.5675 |  |  | 23.7425 |  |  | 20.593 |  |  | 17.2564 |  |  | 12.409
Segment ball | 0.64 | 0.64 | 0.63341 | 0.6231 | 0.60075 | 0.55873 | 0.50449 | 0.42327 | 0.34677 | 0.18243 |  |  | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33451 |  |  | 0.33353 |  |  | 0.33022 |  |  | 0.32193 |  |  | 0.3069 |  |  | 0.28352 |  |  | 0.25552 |  |  | 0.22337 |  |  | 0.17137
Butterfly | 0.693 | 0.693 | 0.69101 | 0.6622 | 0.62425 | 0.57647 | 0.51885 | 0.44156 | 0.37887 | 0.15395 |  |  | Expansion factor | 12 |  | 0.82568 |  |  | 0.82583 |  |  | 0.82468 |  |  | 0.82397 |  |  | 0.82307 |  |  | 0.82121 |  |  | 0.8223 |  |  | 0.82094 |  |  | 0.87392 |  |  | 0.84835
Full ball (Full and reduced port | 0.82 | 0.82 | 0.80951 | 0.75917 | 0.69747 | 0.62685 | 0.55156 | 0.46607 | 0.34881 | 0.21951 |  |  | C Non choked w/ reducers | 7 |  | 0.13655 |  |  | 4.877 |  |  | 12.0214 |  |  | 23.8091 |  |  | 41.5085 |  |  | 64.9989 |  |  | 96.5358 |  |  | 137.0194 |  |  | 189.7685 |  |  | 373.9798
[13 empty] | C Choked w/ reducers | 7 |  | 0.12224 |  |  | 4.3649 |  |  | 10.7793 |  |  | 21.3737 |  |  | 37.3173 |  |  | 58.6092 |  |  | 86.8953 |  |  | 123.6027 |  |  | 152.9161 |  |  | 320.832
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.13655 |  |  | 4.877 |  |  | 12.0214 |  |  | 23.8091 |  |  | 41.5085 |  |  | 64.9989 |  |  | 96.5358 |  |  | 137.0194 |  |  | 189.7685 |  |  | 373.9798
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5934 | 338.1327 |  | 6.723 | 12063.7421 |  | 10.9786 | 29539.6732 |  | 15.5909 | 57535.7435 |  | 19.4915 | 96527.0794 |  | 23.2011 | 140883.9014 |  | 24.4642 | 188010.1126 |  | 27.9806 | 229408.0668 |  | 56.2315 | 266335.6437 |  | 46.0202 | 312299.4882
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 344.8954 | C_100 - C this iteration | iteration | 12184.3796 | C_100 - C this iteration | iteration | 29835.0699 | C_100 - C this iteration | iteration | 58111.1009 | C_100 - C this iteration | iteration | 97492.3502 | C_100 - C this iteration | iteration | 142292.7405 | C_100 - C this iteration | iteration | 189890.2138 | C_100 - C this iteration | iteration | 231702.1475 | C_100 - C this iteration | iteration | 268999.0001 | C_100 - C this iteration | iteration | 315422.4831 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.158 |  |  | 90.0228 |  |  | 89.5696 |  |  | 88.4527 |  |  | 86.4948 |  |  | 83.613 |  |  | 80.4002 |  |  | 76.9966 |  |  | 72.0517
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.158 |  |  | 30.0228 |  |  | 29.5696 |  |  | 28.4527 |  |  | 26.4948 |  |  | 23.613 |  |  | 20.4002 |  |  | 16.9966 |  |  | 12.0517
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.3345 |  |  | 0.3335 |  |  | 0.33013 |  |  | 0.32167 |  |  | 0.30632 |  |  | 0.28241 |  |  | 0.25373 |  |  | 0.22074 |  |  | 0.16726
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82583 |  |  | 0.8247 |  |  | 0.82402 |  |  | 0.82321 |  |  | 0.82155 |  |  | 0.823 |  |  | 0.82219 |  |  | 0.8754 |  |  | 0.85199
[13 empty] | C Non choked w/ reducers | 7 |  | 0.13928 |  |  | 4.9258 |  |  | 12.1423 |  |  | 24.0523 |  |  | 41.9495 |  |  | 65.7393 |  |  | 97.7611 |  |  | 138.9968 |  |  | 193.1246 |  |  | 382.5872
[13 empty] | C Choked w/ reducers | 7 |  | 0.12468 |  |  | 4.4085 |  |  | 10.8874 |  |  | 21.5903 |  |  | 37.705 |  |  | 59.2451 |  |  | 87.9002 |  |  | 125.1381 |  |  | 154.9665 |  |  | 325.6472
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.13928 |  |  | 4.9258 |  |  | 12.1423 |  |  | 24.0523 |  |  | 41.9495 |  |  | 65.7393 |  |  | 97.7611 |  |  | 138.9968 |  |  | 193.1246 |  |  | 382.5872
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5907 | 344.8954 |  | 6.6742 | 12184.3796 |  | 10.8577 | 29835.0699 |  | 15.3477 | 58111.1009 |  | 19.0505 | 97492.3502 |  | 22.4607 | 142292.7405 |  | 23.2389 | 189890.2138 |  | 26.0032 | 231702.1475 |  | 52.8754 | 268999.0001 |  | 37.4128 | 315422.4831
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 351.7933 | C_100 - C this iteration | iteration | 12306.2234 | C_100 - C this iteration | iteration | 30133.4206 | C_100 - C this iteration | iteration | 58692.2119 | C_100 - C this iteration | iteration | 98467.2737 | C_100 - C this iteration | iteration | 143715.6679 | C_100 - C this iteration | iteration | 191789.1159 | C_100 - C this iteration | iteration | 234019.169 | C_100 - C this iteration | iteration | 271688.9901 | C_100 - C this iteration | iteration | 318576.7079 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1574 |  |  | 90.0195 |  |  | 89.5572 |  |  | 88.4179 |  |  | 86.4206 |  |  | 83.4809 |  |  | 80.2035 |  |  | 76.7315 |  |  | 71.6872
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1574 |  |  | 30.0195 |  |  | 29.5572 |  |  | 28.4179 |  |  | 26.4206 |  |  | 23.4809 |  |  | 20.2035 |  |  | 16.7315 |  |  | 11.6872
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.3345 |  |  | 0.33348 |  |  | 0.33004 |  |  | 0.3214 |  |  | 0.30572 |  |  | 0.28127 |  |  | 0.2519 |  |  | 0.21805 |  |  | 0.16303
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82583 |  |  | 0.82471 |  |  | 0.82407 |  |  | 0.82336 |  |  | 0.8219 |  |  | 0.82371 |  |  | 0.82347 |  |  | 0.87692 |  |  | 0.85573
[13 empty] | C Non choked w/ reducers | 7 |  | 0.14207 |  |  | 4.9752 |  |  | 12.2644 |  |  | 24.2981 |  |  | 42.3958 |  |  | 66.4903 |  |  | 99.0088 |  |  | 141.0213 |  |  | 196.593 |  |  | 391.6662
[13 empty] | C Choked w/ reducers | 7 |  | 0.12718 |  |  | 4.4526 |  |  | 10.9967 |  |  | 21.8092 |  |  | 38.0971 |  |  | 59.8889 |  |  | 88.9196 |  |  | 126.6994 |  |  | 157.0569 |  |  | 330.5759
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.14207 |  |  | 4.9752 |  |  | 12.2644 |  |  | 24.2981 |  |  | 42.3958 |  |  | 66.4903 |  |  | 99.0088 |  |  | 141.0213 |  |  | 196.593 |  |  | 391.6662
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5879 | 351.7933 |  | 6.6248 | 12306.2234 |  | 10.7356 | 30133.4206 |  | 15.1019 | 58692.2119 |  | 18.6042 | 98467.2737 |  | 21.7097 | 143715.6679 |  | 21.9912 | 191789.1159 |  | 23.9787 | 234019.169 |  | 49.407 | 271688.9901 |  | 28.3338 | 318576.7079
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 358.8291 | C_100 - C this iteration | iteration | 12429.2856 | C_100 - C this iteration | iteration | 30434.7548 | C_100 - C this iteration | iteration | 59279.134 | C_100 - C this iteration | iteration | 99451.9465 | C_100 - C this iteration | iteration | 145152.8245 | C_100 - C this iteration | iteration | 193707.0071 | C_100 - C this iteration | iteration | 236359.3607 | C_100 - C this iteration | iteration | 274405.8801 | C_100 - C this iteration | iteration | 321762.475 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1569 |  |  | 90.0162 |  |  | 89.5446 |  |  | 88.3824 |  |  | 86.3449 |  |  | 83.3462 |  |  | 80.0029 |  |  | 76.4611 |  |  | 71.3154
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1569 |  |  | 30.0162 |  |  | 29.5446 |  |  | 28.3824 |  |  | 26.3449 |  |  | 23.3462 |  |  | 20.0029 |  |  | 16.4611 |  |  | 11.3154
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33449 |  |  | 0.33345 |  |  | 0.32994 |  |  | 0.32113 |  |  | 0.30511 |  |  | 0.28011 |  |  | 0.25003 |  |  | 0.21529 |  |  | 0.15867
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82583 |  |  | 0.82472 |  |  | 0.82412 |  |  | 0.82351 |  |  | 0.82225 |  |  | 0.82444 |  |  | 0.82479 |  |  | 0.87848 |  |  | 0.8596
[13 empty] | C Non choked w/ reducers | 7 |  | 0.14491 |  |  | 5.025 |  |  | 12.3878 |  |  | 24.5466 |  |  | 42.8473 |  |  | 67.252 |  |  | 100.2794 |  |  | 143.095 |  |  | 200.1805 |  |  | 401.2654
[13 empty] | C Choked w/ reducers | 7 |  | 0.12972 |  |  | 4.4972 |  |  | 11.1071 |  |  | 22.0304 |  |  | 38.4935 |  |  | 60.5408 |  |  | 89.954 |  |  | 128.2873 |  |  | 159.1885 |  |  | 335.6224
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.14491 |  |  | 5.025 |  |  | 12.3878 |  |  | 24.5466 |  |  | 42.8473 |  |  | 67.252 |  |  | 100.2794 |  |  | 143.095 |  |  | 200.1805 |  |  | 401.2654
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5851 | 358.8291 |  | 6.575 | 12429.2856 |  | 10.6122 | 30434.7548 |  | 14.8534 | 59279.134 |  | 18.1527 | 99451.9465 |  | 20.948 | 145152.8245 |  | 20.7206 | 193707.0071 |  | 21.905 | 236359.3607 |  | 45.8195 | 274405.8801 |  | 18.7346 | 321762.475
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 366.0057 | C_100 - C this iteration | iteration | 12553.5784 | C_100 - C this iteration | iteration | 30739.1024 | C_100 - C this iteration | iteration | 59871.9254 | C_100 - C this iteration | iteration | 100446.4659 | C_100 - C this iteration | iteration | 146604.3528 | C_100 - C this iteration | iteration | 195644.0771 | C_100 - C this iteration | iteration | 238722.9543 | C_100 - C this iteration | iteration | 277149.9389 | C_100 - C this iteration | iteration | 324980.0997 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1563 |  |  | 90.0128 |  |  | 89.5317 |  |  | 88.3461 |  |  | 86.2677 |  |  | 83.2087 |  |  | 79.7982 |  |  | 76.1852 |  |  | 70.9361
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1563 |  |  | 30.0128 |  |  | 29.5317 |  |  | 28.3461 |  |  | 26.2677 |  |  | 23.2087 |  |  | 19.7982 |  |  | 16.1852 |  |  | 10.9361
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33449 |  |  | 0.33343 |  |  | 0.32985 |  |  | 0.32085 |  |  | 0.30449 |  |  | 0.27892 |  |  | 0.2481 |  |  | 0.21245 |  |  | 0.15417
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82584 |  |  | 0.82473 |  |  | 0.82417 |  |  | 0.82366 |  |  | 0.82261 |  |  | 0.82518 |  |  | 0.82614 |  |  | 0.88008 |  |  | 0.86358
[13 empty] | C Non choked w/ reducers | 7 |  | 0.14781 |  |  | 5.0753 |  |  | 12.5124 |  |  | 24.7977 |  |  | 43.3043 |  |  | 68.0247 |  |  | 101.5737 |  |  | 145.2199 |  |  | 203.8946 |  |  | 411.4413
[13 empty] | C Choked w/ reducers | 7 |  | 0.13232 |  |  | 4.5422 |  |  | 11.2186 |  |  | 22.2539 |  |  | 38.8944 |  |  | 61.2009 |  |  | 91.0037 |  |  | 129.9025 |  |  | 161.3625 |  |  | 340.7911
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.14781 |  |  | 5.0753 |  |  | 12.5124 |  |  | 24.7977 |  |  | 43.3043 |  |  | 68.0247 |  |  | 101.5737 |  |  | 145.2199 |  |  | 203.8946 |  |  | 411.4413
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5822 | 366.0057 |  | 6.5247 | 12553.5784 |  | 10.4876 | 30739.1024 |  | 14.6023 | 59871.9254 |  | 17.6957 | 100446.4659 |  | 20.1753 | 146604.3528 |  | 19.4263 | 195644.0771 |  | 19.7801 | 238722.9543 |  | 42.1054 | 277149.9389 |  | 8.5587 | 324980.0997
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 373.3258 | C_100 - C this iteration | iteration | 12679.1142 | C_100 - C this iteration | iteration | 31046.4934 | C_100 - C this iteration | iteration | 60470.6446 | C_100 - C this iteration | iteration | 101450.9306 | C_100 - C this iteration | iteration | 148070.3963 | C_100 - C this iteration | iteration | 197600.5179 | C_100 - C this iteration | iteration | 241110.1838 | C_100 - C this iteration | iteration | 279921.4382 | C_100 - C this iteration | iteration | 328229.9007 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1557 |  |  | 90.0094 |  |  | 89.5186 |  |  | 88.3092 |  |  | 86.189 |  |  | 83.0685 |  |  | 79.5895 |  |  | 75.9038 |  |  | 70.5492
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1557 |  |  | 30.0094 |  |  | 29.5186 |  |  | 28.3092 |  |  | 26.189 |  |  | 23.0685 |  |  | 19.5895 |  |  | 15.9038 |  |  | 10.5492
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33448 |  |  | 0.3334 |  |  | 0.32975 |  |  | 0.32057 |  |  | 0.30386 |  |  | 0.2777 |  |  | 0.24613 |  |  | 0.20953 |  |  | 0.14953
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82584 |  |  | 0.82475 |  |  | 0.82423 |  |  | 0.82382 |  |  | 0.82298 |  |  | 0.82595 |  |  | 0.82752 |  |  | 0.88173 |  |  | 0.86768
[13 empty] | C Non choked w/ reducers | 7 |  | 0.15076 |  |  | 5.1261 |  |  | 12.6383 |  |  | 25.0515 |  |  | 43.7667 |  |  | 68.8087 |  |  | 102.8925 |  |  | 147.3982 |  |  | 207.7431 |  |  | 422.2591
[13 empty] | C Choked w/ reducers | 7 |  | 0.13496 |  |  | 4.5876 |  |  | 11.3312 |  |  | 22.4798 |  |  | 39.2998 |  |  | 61.8694 |  |  | 92.0689 |  |  | 131.5457 |  |  | 163.5803 |  |  | 346.0866
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.15076 |  |  | 5.1261 |  |  | 12.6383 |  |  | 25.0515 |  |  | 43.7667 |  |  | 68.8087 |  |  | 102.8925 |  |  | 147.3982 |  |  | 207.7431 |  |  | 422.2591
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5792 | 373.3258 |  | 6.4739 | 12679.1142 |  | 10.3617 | 31046.4934 |  | 14.3485 | 60470.6446 |  | 17.2333 | 101450.9306 |  | 19.3913 | 148070.3963 |  | 18.1075 | 197600.5179 |  | 17.6018 | 241110.1838 |  | 38.2569 | 279921.4382 |  | 2.2591 | 328229.9007
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 380.7923 | C_100 - C this iteration | iteration | 12805.9054 | C_100 - C this iteration | iteration | 31356.9583 | C_100 - C this iteration | iteration | 61075.3511 | C_100 - C this iteration | iteration | 102465.4399 | C_100 - C this iteration | iteration | 149551.1003 | C_100 - C this iteration | iteration | 199576.5231 | C_100 - C this iteration | iteration | 243521.2857 | C_100 - C this iteration | iteration | 282720.6526 | C_100 - C this iteration | iteration | 331512.1997 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1552 |  |  | 90.0058 |  |  | 89.5052 |  |  | 88.2715 |  |  | 86.1087 |  |  | 82.9254 |  |  | 79.3765 |  |  | 75.6167 |  |  | 70.1545
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1552 |  |  | 30.0058 |  |  | 29.5052 |  |  | 28.2715 |  |  | 26.1087 |  |  | 22.9254 |  |  | 19.3765 |  |  | 15.6167 |  |  | 10.1545
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33448 |  |  | 0.33338 |  |  | 0.32965 |  |  | 0.32028 |  |  | 0.30321 |  |  | 0.27646 |  |  | 0.24411 |  |  | 0.20653 |  |  | 0.14474
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82584 |  |  | 0.82476 |  |  | 0.82428 |  |  | 0.82398 |  |  | 0.82336 |  |  | 0.82673 |  |  | 0.82894 |  |  | 0.88343 |  |  | 0.87192
[13 empty] | C Non choked w/ reducers | 7 |  | 0.15378 |  |  | 5.1774 |  |  | 12.7655 |  |  | 25.308 |  |  | 44.2347 |  |  | 69.604 |  |  | 104.2364 |  |  | 149.6325 |  |  | 211.7349 |  |  | 433.7952
[13 empty] | C Choked w/ reducers | 7 |  | 0.13766 |  |  | 4.6336 |  |  | 11.445 |  |  | 22.708 |  |  | 39.7097 |  |  | 62.5464 |  |  | 93.1499 |  |  | 133.2176 |  |  | 165.8433 |  |  | 351.514
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.15378 |  |  | 5.1774 |  |  | 12.7655 |  |  | 25.308 |  |  | 44.2347 |  |  | 69.604 |  |  | 104.2364 |  |  | 149.6325 |  |  | 211.7349 |  |  | 433.7952
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5762 | 380.7923 |  | 6.4226 | 12805.9054 |  | 10.2345 | 31356.9583 |  | 14.092 | 61075.3511 |  | 16.7653 | 102465.4399 |  | 18.596 | 149551.1003 |  | 16.7636 | 199576.5231 |  | 15.3675 | 243521.2857 |  | 34.2651 | 282720.6526 |  | 13.7952 | 331512.1997
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 388.4082 | C_100 - C this iteration | iteration | 12933.9644 | C_100 - C this iteration | iteration | 31670.5279 | C_100 - C this iteration | iteration | 61686.1046 | C_100 - C this iteration | iteration | 103490.0943 | C_100 - C this iteration | iteration | 151046.6113 | C_100 - C this iteration | iteration | 201572.2883 | C_100 - C this iteration | iteration | 245956.4985 | C_100 - C this iteration | iteration | 285547.8591 | C_100 - C this iteration | iteration | 334827.3217 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1546 |  |  | 90.0022 |  |  | 89.4915 |  |  | 88.233 |  |  | 86.0267 |  |  | 82.7795 |  |  | 79.1592 |  |  | 75.3239 |  |  | 69.7519
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1546 |  |  | 30.0022 |  |  | 29.4915 |  |  | 28.233 |  |  | 26.0267 |  |  | 22.7795 |  |  | 19.1592 |  |  | 15.3239 |  |  | 9.7519
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33448 |  |  | 0.33335 |  |  | 0.32955 |  |  | 0.31998 |  |  | 0.30254 |  |  | 0.27518 |  |  | 0.24203 |  |  | 0.20344 |  |  | 0.13981
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82584 |  |  | 0.82478 |  |  | 0.82433 |  |  | 0.82414 |  |  | 0.82375 |  |  | 0.82753 |  |  | 0.83039 |  |  | 0.88517 |  |  | 0.87628
[13 empty] | C Non choked w/ reducers | 7 |  | 0.15685 |  |  | 5.2292 |  |  | 12.8939 |  |  | 25.5673 |  |  | 44.7084 |  |  | 70.4111 |  |  | 105.6064 |  |  | 151.9252 |  |  | 215.8796 |  |  | 446.1392
[13 empty] | C Choked w/ reducers | 7 |  | 0.14042 |  |  | 4.6799 |  |  | 11.5599 |  |  | 22.9386 |  |  | 40.1243 |  |  | 63.232 |  |  | 94.2473 |  |  | 134.919 |  |  | 168.1529 |  |  | 357.0784
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.15685 |  |  | 5.2292 |  |  | 12.8939 |  |  | 25.5673 |  |  | 44.7084 |  |  | 70.4111 |  |  | 105.6064 |  |  | 151.9252 |  |  | 215.8796 |  |  | 446.1392
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5731 | 388.4082 |  | 6.3708 | 12933.9644 |  | 10.1061 | 31670.5279 |  | 13.8327 | 61686.1046 |  | 16.2916 | 103490.0943 |  | 17.7889 | 151046.6113 |  | 15.3936 | 201572.2883 |  | 13.0748 | 245956.4985 |  | 30.1204 | 285547.8591 |  | 26.1392 | 334827.3217
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 396.1764 | C_100 - C this iteration | iteration | 13063.3041 | C_100 - C this iteration | iteration | 31987.2332 | C_100 - C this iteration | iteration | 62302.9656 | C_100 - C this iteration | iteration | 104524.9952 | C_100 - C this iteration | iteration | 152557.0774 | C_100 - C this iteration | iteration | 203588.0112 | C_100 - C this iteration | iteration | 248416.0635 | C_100 - C this iteration | iteration | 288403.3377 | C_100 - C this iteration | iteration | 338175.595 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1539 |  |  | 89.9986 |  |  | 89.4776 |  |  | 88.1938 |  |  | 85.9432 |  |  | 82.6307 |  |  | 78.9376 |  |  | 75.0252 |  |  | 69.3412
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1539 |  |  | 29.9986 |  |  | 29.4776 |  |  | 28.1938 |  |  | 25.9432 |  |  | 22.6307 |  |  | 18.9376 |  |  | 15.0252 |  |  | 9.3412
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33447 |  |  | 0.33332 |  |  | 0.32944 |  |  | 0.31968 |  |  | 0.30186 |  |  | 0.27388 |  |  | 0.23991 |  |  | 0.20027 |  |  | 0.13471
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82584 |  |  | 0.82479 |  |  | 0.82439 |  |  | 0.82431 |  |  | 0.82414 |  |  | 0.82834 |  |  | 0.83188 |  |  | 0.88696 |  |  | 0.88079
[13 empty] | C Non choked w/ reducers | 7 |  | 0.15999 |  |  | 5.2815 |  |  | 13.0237 |  |  | 25.8293 |  |  | 45.1878 |  |  | 71.2301 |  |  | 107.0032 |  |  | 154.2791 |  |  | 220.1877 |  |  | 459.3977
[13 empty] | C Choked w/ reducers | 7 |  | 0.14322 |  |  | 4.7268 |  |  | 11.676 |  |  | 23.1716 |  |  | 40.5436 |  |  | 63.9264 |  |  | 95.3612 |  |  | 136.6508 |  |  | 170.5106 |  |  | 362.7853
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.15999 |  |  | 5.2815 |  |  | 13.0237 |  |  | 25.8293 |  |  | 45.1878 |  |  | 71.2301 |  |  | 107.0032 |  |  | 154.2791 |  |  | 220.1877 |  |  | 459.3977
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.57 | 396.1764 |  | 6.3185 | 13063.3041 |  | 9.9763 | 31987.2332 |  | 13.5707 | 62302.9656 |  | 15.8122 | 104524.9952 |  | 16.9699 | 152557.0774 |  | 13.9968 | 203588.0112 |  | 10.7209 | 248416.0635 |  | 25.8123 | 288403.3377 |  | 39.3977 | 338175.595
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 404.0999 | C_100 - C this iteration | iteration | 13193.9371 | C_100 - C this iteration | iteration | 32307.1055 | C_100 - C this iteration | iteration | 62925.9953 | C_100 - C this iteration | iteration | 105570.2452 | C_100 - C this iteration | iteration | 154082.6482 | C_100 - C this iteration | iteration | 205623.8913 | C_100 - C this iteration | iteration | 250900.2241 | C_100 - C this iteration | iteration | 291287.3711 | C_100 - C this iteration | iteration | 341557.3509 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1533 |  |  | 89.9948 |  |  | 89.4633 |  |  | 88.1537 |  |  | 85.8579 |  |  | 82.4788 |  |  | 78.7115 |  |  | 74.7205 |  |  | 68.9222
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1533 |  |  | 29.9948 |  |  | 29.4633 |  |  | 28.1537 |  |  | 25.8579 |  |  | 22.4788 |  |  | 18.7115 |  |  | 14.7205 |  |  | 8.9222
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33447 |  |  | 0.33329 |  |  | 0.32933 |  |  | 0.31937 |  |  | 0.30117 |  |  | 0.27254 |  |  | 0.23772 |  |  | 0.19701 |  |  | 0.12945
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82585 |  |  | 0.8248 |  |  | 0.82445 |  |  | 0.82448 |  |  | 0.82455 |  |  | 0.82918 |  |  | 0.83341 |  |  | 0.8888 |  |  | 0.88545
[13 empty] | C Non choked w/ reducers | 7 |  | 0.16319 |  |  | 5.3344 |  |  | 13.1548 |  |  | 26.0942 |  |  | 45.6731 |  |  | 72.0614 |  |  | 108.4277 |  |  | 156.6972 |  |  | 224.6708 |  |  | 473.6982
[13 empty] | C Choked w/ reducers | 7 |  | 0.14609 |  |  | 4.7741 |  |  | 11.7932 |  |  | 23.407 |  |  | 40.9676 |  |  | 64.6298 |  |  | 96.4922 |  |  | 138.4137 |  |  | 172.918 |  |  | 368.6405
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.16319 |  |  | 5.3344 |  |  | 13.1548 |  |  | 26.0942 |  |  | 45.6731 |  |  | 72.0614 |  |  | 108.4277 |  |  | 156.6972 |  |  | 224.6708 |  |  | 473.6982
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5668 | 404.0999 |  | 6.2656 | 13193.9371 |  | 9.8452 | 32307.1055 |  | 13.3058 | 62925.9953 |  | 15.3269 | 105570.2452 |  | 16.1386 | 154082.6482 |  | 12.5723 | 205623.8913 |  | 8.3028 | 250900.2241 |  | 21.3292 | 291287.3711 |  | 53.6982 | 341557.3509
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 412.1819 | C_100 - C this iteration | iteration | 13325.8765 | C_100 - C this iteration | iteration | 32630.1766 | C_100 - C this iteration | iteration | 63555.2553 | C_100 - C this iteration | iteration | 106625.9476 | C_100 - C this iteration | iteration | 155623.4747 | C_100 - C this iteration | iteration | 207680.1302 | C_100 - C this iteration | iteration | 253409.2264 | C_100 - C this iteration | iteration | 294200.2448 | C_100 - C this iteration | iteration | 344972.9244 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1527 |  |  | 89.991 |  |  | 89.4488 |  |  | 88.1129 |  |  | 85.7709 |  |  | 82.3239 |  |  | 78.4809 |  |  | 74.4097 |  |  | 68.4948
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1527 |  |  | 29.991 |  |  | 29.4488 |  |  | 28.1129 |  |  | 25.7709 |  |  | 22.3239 |  |  | 18.4809 |  |  | 14.4097 |  |  | 8.4948
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33446 |  |  | 0.33327 |  |  | 0.32923 |  |  | 0.31906 |  |  | 0.30046 |  |  | 0.27117 |  |  | 0.23548 |  |  | 0.19365 |  |  | 0.12402
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82585 |  |  | 0.82482 |  |  | 0.8245 |  |  | 0.82465 |  |  | 0.82496 |  |  | 0.83004 |  |  | 0.83498 |  |  | 0.89069 |  |  | 0.89025
[13 empty] | C Non choked w/ reducers | 7 |  | 0.16646 |  |  | 5.3878 |  |  | 13.2873 |  |  | 26.3619 |  |  | 46.1643 |  |  | 72.9052 |  |  | 109.8809 |  |  | 159.1826 |  |  | 229.3419 |  |  | 489.1944
[13 empty] | C Choked w/ reducers | 7 |  | 0.14901 |  |  | 4.8218 |  |  | 11.9117 |  |  | 23.6449 |  |  | 41.3965 |  |  | 65.3423 |  |  | 97.6405 |  |  | 140.2087 |  |  | 175.3768 |  |  | 374.6501
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.16646 |  |  | 5.3878 |  |  | 13.2873 |  |  | 26.3619 |  |  | 46.1643 |  |  | 72.9052 |  |  | 109.8809 |  |  | 159.1826 |  |  | 229.3419 |  |  | 489.1944
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5635 | 412.1819 |  | 6.2122 | 13325.8765 |  | 9.7127 | 32630.1766 |  | 13.0381 | 63555.2553 |  | 14.8357 | 106625.9476 |  | 15.2948 | 155623.4747 |  | 11.1191 | 207680.1302 |  | 5.8174 | 253409.2264 |  | 16.6581 | 294200.2448 |  | 69.1944 | 344972.9244
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 420.4255 | C_100 - C this iteration | iteration | 13459.1352 | C_100 - C this iteration | iteration | 32956.4783 | C_100 - C this iteration | iteration | 64190.8078 | C_100 - C this iteration | iteration | 107692.2071 | C_100 - C this iteration | iteration | 157179.7094 | C_100 - C this iteration | iteration | 209756.9315 | C_100 - C this iteration | iteration | 255943.3186 | C_100 - C this iteration | iteration | 297142.2473 | C_100 - C this iteration | iteration | 348422.6537 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.152 |  |  | 89.9871 |  |  | 89.434 |  |  | 88.0712 |  |  | 85.6822 |  |  | 82.1659 |  |  | 78.2457 |  |  | 74.0926 |  |  | 68.0589
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.152 |  |  | 29.9871 |  |  | 29.434 |  |  | 28.0712 |  |  | 25.6822 |  |  | 22.1659 |  |  | 18.2457 |  |  | 14.0926 |  |  | 8.0589
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33446 |  |  | 0.33324 |  |  | 0.32911 |  |  | 0.31873 |  |  | 0.29974 |  |  | 0.26977 |  |  | 0.23318 |  |  | 0.1902 |  |  | 0.11841
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82585 |  |  | 0.82483 |  |  | 0.82456 |  |  | 0.82483 |  |  | 0.82538 |  |  | 0.83092 |  |  | 0.83659 |  |  | 0.89264 |  |  | 0.89522
[13 empty] | C Non choked w/ reducers | 7 |  | 0.16978 |  |  | 5.4418 |  |  | 13.421 |  |  | 26.6325 |  |  | 46.6616 |  |  | 73.7618 |  |  | 111.3637 |  |  | 161.7386 |  |  | 234.2152 |  |  | 506.0745
[13 empty] | C Choked w/ reducers | 7 |  | 0.15199 |  |  | 4.8701 |  |  | 12.0313 |  |  | 23.8853 |  |  | 41.8302 |  |  | 66.0641 |  |  | 98.8065 |  |  | 142.0365 |  |  | 177.8886 |  |  | 380.8205
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.16978 |  |  | 5.4418 |  |  | 13.421 |  |  | 26.6325 |  |  | 46.6616 |  |  | 73.7618 |  |  | 111.3637 |  |  | 161.7386 |  |  | 234.2152 |  |  | 506.0745
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5602 | 420.4255 |  | 6.1582 | 13459.1352 |  | 9.579 | 32956.4783 |  | 12.7675 | 64190.8078 |  | 14.3384 | 107692.2071 |  | 14.4382 | 157179.7094 |  | 9.6363 | 209756.9315 |  | 3.2614 | 255943.3186 |  | 11.7848 | 297142.2473 |  | 86.0745 | 348422.6537
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 428.834 | C_100 - C this iteration | iteration | 13593.7266 | C_100 - C this iteration | iteration | 33286.0431 | C_100 - C this iteration | iteration | 64832.7159 | C_100 - C this iteration | iteration | 108769.1292 | C_100 - C this iteration | iteration | 158751.5065 | C_100 - C this iteration | iteration | 211854.5008 | C_100 - C this iteration | iteration | 258502.7518 | C_100 - C this iteration | iteration | 300113.6697 | C_100 - C this iteration | iteration | 351906.8802 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1514 |  |  | 89.9831 |  |  | 89.4189 |  |  | 88.0288 |  |  | 85.5917 |  |  | 82.0047 |  |  | 78.0057 |  |  | 73.7691 |  |  | 67.6141
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1514 |  |  | 29.9831 |  |  | 29.4189 |  |  | 28.0288 |  |  | 25.5917 |  |  | 22.0047 |  |  | 18.0057 |  |  | 13.7691 |  |  | 7.6141
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33445 |  |  | 0.33321 |  |  | 0.329 |  |  | 0.3184 |  |  | 0.299 |  |  | 0.26834 |  |  | 0.23083 |  |  | 0.18665 |  |  | 0.11261
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82585 |  |  | 0.82485 |  |  | 0.82462 |  |  | 0.82501 |  |  | 0.82581 |  |  | 0.83182 |  |  | 0.83824 |  |  | 0.89464 |  |  | 0.90035
[13 empty] | C Non choked w/ reducers | 7 |  | 0.17318 |  |  | 5.4962 |  |  | 13.5562 |  |  | 26.906 |  |  | 47.1649 |  |  | 74.6314 |  |  | 112.8772 |  |  | 164.369 |  |  | 239.3066 |  |  | 524.5707
[13 empty] | C Choked w/ reducers | 7 |  | 0.15503 |  |  | 4.9188 |  |  | 12.1521 |  |  | 24.1282 |  |  | 42.2689 |  |  | 66.7953 |  |  | 99.9907 |  |  | 143.8982 |  |  | 180.4553 |  |  | 387.1587
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.17318 |  |  | 5.4962 |  |  | 13.5562 |  |  | 26.906 |  |  | 47.1649 |  |  | 74.6314 |  |  | 112.8772 |  |  | 164.369 |  |  | 239.3066 |  |  | 524.5707
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5568 | 428.834 |  | 6.1038 | 13593.7266 |  | 9.4438 | 33286.0431 |  | 12.494 | 64832.7159 |  | 13.8351 | 108769.1292 |  | 13.5686 | 158751.5065 |  | 8.1228 | 211854.5008 |  | 0.63105 | 258502.7518 |  | 6.6934 | 300113.6697 |  | 104.5707 | 351906.8802
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 437.4107 | C_100 - C this iteration | iteration | 13729.6639 | C_100 - C this iteration | iteration | 33618.9035 | C_100 - C this iteration | iteration | 65481.043 | C_100 - C this iteration | iteration | 109856.8205 | C_100 - C this iteration | iteration | 160339.0216 | C_100 - C this iteration | iteration | 213973.0458 | C_100 - C this iteration | iteration | 261087.7793 | C_100 - C this iteration | iteration | 303114.8064 | C_100 - C this iteration | iteration | 355425.949 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1507 |  |  | 89.979 |  |  | 89.4035 |  |  | 87.9854 |  |  | 85.4994 |  |  | 81.8403 |  |  | 77.7609 |  |  | 73.4392 |  |  | 67.1605
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1507 |  |  | 29.979 |  |  | 29.4035 |  |  | 27.9854 |  |  | 25.4994 |  |  | 21.8403 |  |  | 17.7609 |  |  | 13.4392 |  |  | 7.1605
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33445 |  |  | 0.33318 |  |  | 0.32889 |  |  | 0.31807 |  |  | 0.29824 |  |  | 0.26687 |  |  | 0.2284 |  |  | 0.183 |  |  | 0.10662
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82586 |  |  | 0.82487 |  |  | 0.82469 |  |  | 0.82519 |  |  | 0.82625 |  |  | 0.83274 |  |  | 0.83994 |  |  | 0.89671 |  |  | 0.90565
[13 empty] | C Non choked w/ reducers | 7 |  | 0.17664 |  |  | 5.5513 |  |  | 13.6927 |  |  | 27.1825 |  |  | 47.6745 |  |  | 75.5145 |  |  | 114.4225 |  |  | 167.0775 |  |  | 244.6337 |  |  | 544.9743
[13 empty] | C Choked w/ reducers | 7 |  | 0.15813 |  |  | 4.968 |  |  | 12.2742 |  |  | 24.3737 |  |  | 42.7126 |  |  | 67.5361 |  |  | 101.1935 |  |  | 145.7948 |  |  | 183.0787 |  |  | 393.6717
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.17664 |  |  | 5.5513 |  |  | 13.6927 |  |  | 27.1825 |  |  | 47.6745 |  |  | 75.5145 |  |  | 114.4225 |  |  | 167.0775 |  |  | 244.6337 |  |  | 544.9743
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5534 | 437.4107 |  | 6.0487 | 13729.6639 |  | 9.3073 | 33618.9035 |  | 12.2175 | 65481.043 |  | 13.3255 | 109856.8205 |  | 12.6855 | 160339.0216 |  | 6.5775 | 213973.0458 |  | 2.0775 | 261087.7793 |  | 1.3663 | 303114.8064 |  | 124.9743 | 355425.949
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 446.1589 | C_100 - C this iteration | iteration | 13866.9605 | C_100 - C this iteration | iteration | 33955.0926 | C_100 - C this iteration | iteration | 66135.8535 | C_100 - C this iteration | iteration | 110955.3887 | C_100 - C this iteration | iteration | 161942.4118 | C_100 - C this iteration | iteration | 216112.7763 | C_100 - C this iteration | iteration | 263698.6571 | C_100 - C this iteration | iteration | 306145.9545 | C_100 - C this iteration | iteration | 358980.2085 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.15 |  |  | 89.9749 |  |  | 89.3878 |  |  | 87.9412 |  |  | 85.4052 |  |  | 81.6726 |  |  | 77.5112 |  |  | 73.1026 |  |  | 66.6977
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.15 |  |  | 29.9749 |  |  | 29.3878 |  |  | 27.9412 |  |  | 25.4052 |  |  | 21.6726 |  |  | 17.5112 |  |  | 13.1026 |  |  | 6.6977
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33444 |  |  | 0.33315 |  |  | 0.32877 |  |  | 0.31773 |  |  | 0.29747 |  |  | 0.26536 |  |  | 0.22592 |  |  | 0.17924 |  |  | 0.10042
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82586 |  |  | 0.82488 |  |  | 0.82475 |  |  | 0.82538 |  |  | 0.82671 |  |  | 0.83368 |  |  | 0.84168 |  |  | 0.89883 |  |  | 0.91114
[13 empty] | C Non choked w/ reducers | 7 |  | 0.18018 |  |  | 5.6069 |  |  | 13.8307 |  |  | 27.462 |  |  | 48.1905 |  |  | 76.4113 |  |  | 116.0007 |  |  | 169.8685 |  |  | 250.2165 |  |  | 567.6559
[13 empty] | C Choked w/ reducers | 7 |  | 0.16129 |  |  | 5.0178 |  |  | 12.3975 |  |  | 24.6218 |  |  | 43.1614 |  |  | 68.2866 |  |  | 102.4154 |  |  | 147.7271 |  |  | 185.7609 |  |  | 400.3673
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.18018 |  |  | 5.6069 |  |  | 13.8307 |  |  | 27.462 |  |  | 48.1905 |  |  | 76.4113 |  |  | 116.0007 |  |  | 169.8685 |  |  | 250.2165 |  |  | 567.6559
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5498 | 446.1589 |  | 5.9931 | 13866.9605 |  | 9.1693 | 33955.0926 |  | 11.938 | 66135.8535 |  | 12.8095 | 110955.3887 |  | 11.7887 | 161942.4118 |  | 4.9993 | 216112.7763 |  | 4.8685 | 263698.6571 |  | 4.2165 | 306145.9545 |  | 147.6559 | 358980.2085
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 455.0821 | C_100 - C this iteration | iteration | 14005.6301 | C_100 - C this iteration | iteration | 34294.6435 | C_100 - C this iteration | iteration | 66797.212 | C_100 - C this iteration | iteration | 112064.9426 | C_100 - C this iteration | iteration | 163561.8359 | C_100 - C this iteration | iteration | 218273.9041 | C_100 - C this iteration | iteration | 266335.6437 | C_100 - C this iteration | iteration | 309207.4141 | C_100 - C this iteration | iteration | 362570.0106 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1493 |  |  | 89.9707 |  |  | 89.3718 |  |  | 87.8961 |  |  | 85.3091 |  |  | 81.5015 |  |  | 77.2564 |  |  | 72.7592 |  |  | 66.2256
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1493 |  |  | 29.9707 |  |  | 29.3718 |  |  | 27.8961 |  |  | 25.3091 |  |  | 21.5015 |  |  | 17.2564 |  |  | 12.7592 |  |  | 6.2256
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33444 |  |  | 0.33312 |  |  | 0.32865 |  |  | 0.31738 |  |  | 0.29668 |  |  | 0.26382 |  |  | 0.22337 |  |  | 0.17536 |  |  | 0.094005
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82586 |  |  | 0.8249 |  |  | 0.82481 |  |  | 0.82557 |  |  | 0.82717 |  |  | 0.83465 |  |  | 0.84347 |  |  | 0.90102 |  |  | 0.91681
[13 empty] | C Non choked w/ reducers | 7 |  | 0.18378 |  |  | 5.663 |  |  | 13.97 |  |  | 27.7445 |  |  | 48.7128 |  |  | 77.3222 |  |  | 117.613 |  |  | 172.7465 |  |  | 256.0772 |  |  | 593.0956
[13 empty] | C Choked w/ reducers | 7 |  | 0.16452 |  |  | 5.068 |  |  | 12.5221 |  |  | 24.8724 |  |  | 43.6154 |  |  | 69.0472 |  |  | 103.6567 |  |  | 149.6964 |  |  | 188.5039 |  |  | 407.2536
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.18378 |  |  | 5.663 |  |  | 13.97 |  |  | 27.7445 |  |  | 48.7128 |  |  | 77.3222 |  |  | 117.613 |  |  | 172.7465 |  |  | 256.0772 |  |  | 593.0956
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5462 | 455.0821 |  | 5.937 | 14005.6301 |  | 9.03 | 34294.6435 |  | 11.6555 | 66797.212 |  | 12.2872 | 112064.9426 |  | 10.8778 | 163561.8359 |  | 3.387 | 218273.9041 |  | 7.7465 | 266335.6437 |  | 10.0772 | 309207.4141 |  | 173.0956 | 362570.0106
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 464.1837 | C_100 - C this iteration | iteration | 14145.6864 | C_100 - C this iteration | iteration | 34637.5899 | C_100 - C this iteration | iteration | 67465.1841 | C_100 - C this iteration | iteration | 113185.592 | C_100 - C this iteration | iteration | 165197.4543 | C_100 - C this iteration | iteration | 220456.6431 | C_100 - C this iteration | iteration | 268999.0001 | C_100 - C this iteration | iteration | 312299.4882 | C_100 - C this iteration | iteration | 366195.7107 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1486 |  |  | 89.9664 |  |  | 89.3555 |  |  | 87.8501 |  |  | 85.2111 |  |  | 81.327 |  |  | 76.9966 |  |  | 72.409 |  |  | 65.744
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1486 |  |  | 29.9664 |  |  | 29.3555 |  |  | 27.8501 |  |  | 25.2111 |  |  | 21.327 |  |  | 16.9966 |  |  | 12.409 |  |  | 5.744
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33443 |  |  | 0.33308 |  |  | 0.32852 |  |  | 0.31702 |  |  | 0.29587 |  |  | 0.26224 |  |  | 0.22074 |  |  | 0.17137 |  |  | 0.087369
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82587 |  |  | 0.82492 |  |  | 0.82488 |  |  | 0.82577 |  |  | 0.82764 |  |  | 0.83564 |  |  | 0.84531 |  |  | 0.90327 |  |  | 0.92269
[13 empty] | C Non choked w/ reducers | 7 |  | 0.18746 |  |  | 5.7197 |  |  | 14.1108 |  |  | 28.0301 |  |  | 49.2418 |  |  | 78.2475 |  |  | 119.2606 |  |  | 175.7165 |  |  | 262.241 |  |  | 621.9291
[13 empty] | C Choked w/ reducers | 7 |  | 0.16781 |  |  | 5.1187 |  |  | 12.6479 |  |  | 25.1258 |  |  | 44.0746 |  |  | 69.8179 |  |  | 104.9179 |  |  | 151.7036 |  |  | 191.3099 |  |  | 414.3391
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.18746 |  |  | 5.7197 |  |  | 14.1108 |  |  | 28.0301 |  |  | 49.2418 |  |  | 78.2475 |  |  | 119.2606 |  |  | 175.7165 |  |  | 262.241 |  |  | 621.9291
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5425 | 464.1837 |  | 5.8803 | 14145.6864 |  | 8.8892 | 34637.5899 |  | 11.3699 | 67465.1841 |  | 11.7582 | 113185.592 |  | 9.9525 | 165197.4543 |  | 1.7394 | 220456.6431 |  | 10.7165 | 268999.0001 |  | 16.241 | 312299.4882 |  | 201.9291 | 366195.7107
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 473.4674 | C_100 - C this iteration | iteration | 14287.1433 | C_100 - C this iteration | iteration | 34983.9658 | C_100 - C this iteration | iteration | 68139.836 | C_100 - C this iteration | iteration | 114317.4479 | C_100 - C this iteration | iteration | 166849.4288 | C_100 - C this iteration | iteration | 222661.2095 | C_100 - C this iteration | iteration | 271688.9901 | C_100 - C this iteration | iteration | 315422.4831 | C_100 - C this iteration | iteration | 369857.6678 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1478 |  |  | 89.962 |  |  | 89.3388 |  |  | 87.8032 |  |  | 85.1111 |  |  | 81.1489 |  |  | 76.7315 |  |  | 72.0517 |  |  | 65.2527
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1478 |  |  | 29.962 |  |  | 29.3388 |  |  | 27.8032 |  |  | 25.1111 |  |  | 21.1489 |  |  | 16.7315 |  |  | 12.0517 |  |  | 5.2527
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33443 |  |  | 0.33305 |  |  | 0.3284 |  |  | 0.31665 |  |  | 0.29504 |  |  | 0.26062 |  |  | 0.21805 |  |  | 0.16726 |  |  | 0.080498
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82587 |  |  | 0.82493 |  |  | 0.82494 |  |  | 0.82597 |  |  | 0.82812 |  |  | 0.83665 |  |  | 0.84719 |  |  | 0.90559 |  |  | 0.92877
[13 empty] | C Non choked w/ reducers | 7 |  | 0.1912 |  |  | 5.777 |  |  | 14.253 |  |  | 28.3188 |  |  | 49.7773 |  |  | 79.1875 |  |  | 120.945 |  |  | 178.7837 |  |  | 268.7364 |  |  | 655.0178
[13 empty] | C Choked w/ reducers | 7 |  | 0.17117 |  |  | 5.1699 |  |  | 12.775 |  |  | 25.3818 |  |  | 44.5392 |  |  | 70.5989 |  |  | 106.1996 |  |  | 153.75 |  |  | 194.1812 |  |  | 421.6331
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.1912 |  |  | 5.777 |  |  | 14.253 |  |  | 28.3188 |  |  | 49.7773 |  |  | 79.1875 |  |  | 120.945 |  |  | 178.7837 |  |  | 268.7364 |  |  | 655.0178
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5388 | 473.4674 |  | 5.823 | 14287.1433 |  | 8.747 | 34983.9658 |  | 11.0812 | 68139.836 |  | 11.2227 | 114317.4479 |  | 9.0125 | 166849.4288 |  | 0.055026 | 222661.2095 |  | 13.7837 | 271688.9901 |  | 22.7364 | 315422.4831 |  | 235.0178 | 369857.6678
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 482.9368 | C_100 - C this iteration | iteration | 14430.0147 | C_100 - C this iteration | iteration | 35333.8055 | C_100 - C this iteration | iteration | 68821.2343 | C_100 - C this iteration | iteration | 115460.6224 | C_100 - C this iteration | iteration | 168517.9231 | C_100 - C this iteration | iteration | 224887.8216 | C_100 - C this iteration | iteration | 274405.8801 | C_100 - C this iteration | iteration | 318576.7079 | C_100 - C this iteration | iteration | 373556.2445 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1471 |  |  | 89.9575 |  |  | 89.3218 |  |  | 87.7553 |  |  | 85.0091 |  |  | 80.9673 |  |  | 76.4611 |  |  | 71.6872 |  |  | 64.7516
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1471 |  |  | 29.9575 |  |  | 29.3218 |  |  | 27.7553 |  |  | 25.0091 |  |  | 20.9673 |  |  | 16.4611 |  |  | 11.6872 |  |  | 4.7516
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33442 |  |  | 0.33302 |  |  | 0.32827 |  |  | 0.31628 |  |  | 0.29419 |  |  | 0.25896 |  |  | 0.21529 |  |  | 0.16303 |  |  | 0.073382
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82587 |  |  | 0.82495 |  |  | 0.82501 |  |  | 0.82618 |  |  | 0.82861 |  |  | 0.83769 |  |  | 0.84913 |  |  | 0.90798 |  |  | 0.93506
[13 empty] | C Non choked w/ reducers | 7 |  | 0.19503 |  |  | 5.8348 |  |  | 14.3966 |  |  | 28.6106 |  |  | 50.3197 |  |  | 80.1427 |  |  | 122.6675 |  |  | 181.9541 |  |  | 275.5962 |  |  | 693.5647
[13 empty] | C Choked w/ reducers | 7 |  | 0.17459 |  |  | 5.2217 |  |  | 12.9034 |  |  | 25.6405 |  |  | 45.0091 |  |  | 71.3904 |  |  | 107.5022 |  |  | 155.8367 |  |  | 197.1201 |  |  | 429.1453
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.19503 |  |  | 5.8348 |  |  | 14.3966 |  |  | 28.6106 |  |  | 50.3197 |  |  | 80.1427 |  |  | 122.6675 |  |  | 181.9541 |  |  | 275.5962 |  |  | 693.5647
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.535 | 482.9368 |  | 5.7652 | 14430.0147 |  | 8.6034 | 35333.8055 |  | 10.7894 | 68821.2343 |  | 10.6803 | 115460.6224 |  | 8.0573 | 168517.9231 |  | 1.6675 | 224887.8216 |  | 16.9541 | 274405.8801 |  | 29.5962 | 318576.7079 |  | 273.5647 | 373556.2445
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 492.5955 | C_100 - C this iteration | iteration | 14574.3149 | C_100 - C this iteration | iteration | 35687.1436 | C_100 - C this iteration | iteration | 69509.4467 | C_100 - C this iteration | iteration | 116615.2286 | C_100 - C this iteration | iteration | 170203.1023 | C_100 - C this iteration | iteration | 227136.6998 | C_100 - C this iteration | iteration | 277149.9389 | C_100 - C this iteration | iteration | 321762.475 | C_100 - C this iteration | iteration | 377291.8069 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1463 |  |  | 89.9529 |  |  | 89.3044 |  |  | 87.7065 |  |  | 84.9051 |  |  | 80.782 |  |  | 76.1852 |  |  | 71.3154 |  |  | 64.2404
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1463 |  |  | 29.9529 |  |  | 29.3044 |  |  | 27.7065 |  |  | 24.9051 |  |  | 20.782 |  |  | 16.1852 |  |  | 11.3154 |  |  | 4.2404
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33442 |  |  | 0.33298 |  |  | 0.32814 |  |  | 0.3159 |  |  | 0.29333 |  |  | 0.25726 |  |  | 0.21245 |  |  | 0.15867 |  |  | 0.066008
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82587 |  |  | 0.82497 |  |  | 0.82508 |  |  | 0.82638 |  |  | 0.82912 |  |  | 0.83876 |  |  | 0.85112 |  |  | 0.91044 |  |  | 0.94159
[13 empty] | C Non choked w/ reducers | 7 |  | 0.19893 |  |  | 5.8932 |  |  | 14.5418 |  |  | 28.9056 |  |  | 50.8689 |  |  | 81.1134 |  |  | 124.4296 |  |  | 185.234 |  |  | 282.8575 |  |  | 739.3103
[13 empty] | C Choked w/ reducers | 7 |  | 0.17808 |  |  | 5.2739 |  |  | 13.0331 |  |  | 25.9019 |  |  | 45.4845 |  |  | 72.1927 |  |  | 108.8263 |  |  | 157.965 |  |  | 200.1293 |  |  | 436.886
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.19893 |  |  | 5.8932 |  |  | 14.5418 |  |  | 28.9056 |  |  | 50.8689 |  |  | 81.1134 |  |  | 124.4296 |  |  | 185.234 |  |  | 282.8575 |  |  | 739.3103
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5311 | 492.5955 |  | 5.7068 | 14574.3149 |  | 8.4582 | 35687.1436 |  | 10.4944 | 69509.4467 |  | 10.1311 | 116615.2286 |  | 7.0866 | 170203.1023 |  | 3.4296 | 227136.6998 |  | 20.234 | 277149.9389 |  | 36.8575 | 321762.475 |  | 319.3103 | 377291.8069
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 502.4474 | C_100 - C this iteration | iteration | 14720.058 | C_100 - C this iteration | iteration | 36044.015 | C_100 - C this iteration | iteration | 70204.5411 | C_100 - C this iteration | iteration | 117781.3809 | C_100 - C this iteration | iteration | 171905.1333 | C_100 - C this iteration | iteration | 229408.0668 | C_100 - C this iteration | iteration | 279921.4382 | C_100 - C this iteration | iteration | 324980.0997 | C_100 - C this iteration | iteration | 381064.725 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1455 |  |  | 89.9483 |  |  | 89.2867 |  |  | 87.6566 |  |  | 84.799 |  |  | 80.593 |  |  | 75.9038 |  |  | 70.9361 |  |  | 63.7189
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1455 |  |  | 29.9483 |  |  | 29.2867 |  |  | 27.6566 |  |  | 24.799 |  |  | 20.593 |  |  | 15.9038 |  |  | 10.9361 |  |  | 3.7189
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33441 |  |  | 0.33295 |  |  | 0.32801 |  |  | 0.31551 |  |  | 0.29244 |  |  | 0.25552 |  |  | 0.20953 |  |  | 0.15417 |  |  | 0.058364
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82588 |  |  | 0.82499 |  |  | 0.82515 |  |  | 0.8266 |  |  | 0.82963 |  |  | 0.83985 |  |  | 0.85317 |  |  | 0.91298 |  |  | 0.94835
[13 empty] | C Non choked w/ reducers | 7 |  | 0.20291 |  |  | 5.9523 |  |  | 14.6884 |  |  | 29.2039 |  |  | 51.4252 |  |  | 82.0999 |  |  | 126.2329 |  |  | 188.6303 |  |  | 290.5633 |  |  | 794.8865
[13 empty] | C Choked w/ reducers | 7 |  | 0.18164 |  |  | 5.3267 |  |  | 13.1641 |  |  | 26.1661 |  |  | 45.9655 |  |  | 73.0058 |  |  | 110.1723 |  |  | 160.1361 |  |  | 203.2114 |  |  | 444.8661
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.20291 |  |  | 5.9523 |  |  | 14.6884 |  |  | 29.2039 |  |  | 51.4252 |  |  | 82.0999 |  |  | 126.2329 |  |  | 188.6303 |  |  | 290.5633 |  |  | 794.8865
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5271 | 502.4474 |  | 5.6477 | 14720.058 |  | 8.3116 | 36044.015 |  | 10.1961 | 70204.5411 |  | 9.5748 | 117781.3809 |  | 6.1001 | 171905.1333 |  | 5.2329 | 229408.0668 |  | 23.6303 | 279921.4382 |  | 44.5633 | 324980.0997 |  | 374.8865 | 381064.725
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 512.4964 | C_100 - C this iteration | iteration | 14867.2586 | C_100 - C this iteration | iteration | 36404.4551 | C_100 - C this iteration | iteration | 70906.5865 | C_100 - C this iteration | iteration | 118959.1947 | C_100 - C this iteration | iteration | 173624.1847 | C_100 - C this iteration | iteration | 231702.1475 | C_100 - C this iteration | iteration | 282720.6526 | C_100 - C this iteration | iteration | 328229.9007 | C_100 - C this iteration | iteration | 384875.3722 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1448 |  |  | 89.9435 |  |  | 89.2687 |  |  | 87.6058 |  |  | 84.6907 |  |  | 80.4002 |  |  | 75.6167 |  |  | 70.5492 |  |  | 63.1869
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1448 |  |  | 29.9435 |  |  | 29.2687 |  |  | 27.6058 |  |  | 24.6907 |  |  | 20.4002 |  |  | 15.6167 |  |  | 10.5492 |  |  | 3.1869
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.3344 |  |  | 0.33291 |  |  | 0.32787 |  |  | 0.31511 |  |  | 0.29154 |  |  | 0.25373 |  |  | 0.20653 |  |  | 0.14953 |  |  | 0.050436
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82588 |  |  | 0.825 |  |  | 0.82523 |  |  | 0.82682 |  |  | 0.83016 |  |  | 0.84097 |  |  | 0.85527 |  |  | 0.9156 |  |  | 0.95537
[13 empty] | C Non choked w/ reducers | 7 |  | 0.20697 |  |  | 6.0119 |  |  | 14.8365 |  |  | 29.5054 |  |  | 51.9886 |  |  | 83.1028 |  |  | 128.0792 |  |  | 192.1505 |  |  | 298.7635 |  |  | 864.5049
[13 empty] | C Choked w/ reducers | 7 |  | 0.18527 |  |  | 5.38 |  |  | 13.2965 |  |  | 26.4331 |  |  | 46.4521 |  |  | 73.8302 |  |  | 111.5408 |  |  | 162.3514 |  |  | 206.3691 |  |  | 453.0976
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.20697 |  |  | 6.0119 |  |  | 14.8365 |  |  | 29.5054 |  |  | 51.9886 |  |  | 83.1028 |  |  | 128.0792 |  |  | 192.1505 |  |  | 298.7635 |  |  | 864.5049
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.523 | 512.4964 |  | 5.5881 | 14867.2586 |  | 8.1635 | 36404.4551 |  | 9.8946 | 70906.5865 |  | 9.0114 | 118959.1947 |  | 5.0972 | 173624.1847 |  | 7.0792 | 231702.1475 |  | 27.1505 | 282720.6526 |  | 52.7635 | 328229.9007 |  | 444.5049 | 384875.3722
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 522.7463 | C_100 - C this iteration | iteration | 15015.9312 | C_100 - C this iteration | iteration | 36768.4997 | C_100 - C this iteration | iteration | 71615.6524 | C_100 - C this iteration | iteration | 120148.7867 | C_100 - C this iteration | iteration | 175360.4265 | C_100 - C this iteration | iteration | 234019.169 | C_100 - C this iteration | iteration | 285547.8591 | C_100 - C this iteration | iteration | 331512.1997 | C_100 - C this iteration | iteration | 388724.126 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1439 |  |  | 89.9386 |  |  | 89.2503 |  |  | 87.554 |  |  | 84.5803 |  |  | 80.2035 |  |  | 75.3239 |  |  | 70.1545 |  |  | 62.6442
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1439 |  |  | 29.9386 |  |  | 29.2503 |  |  | 27.554 |  |  | 24.5803 |  |  | 20.2035 |  |  | 15.3239 |  |  | 10.1545 |  |  | 2.6442
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.3344 |  |  | 0.33288 |  |  | 0.32773 |  |  | 0.31471 |  |  | 0.29061 |  |  | 0.2519 |  |  | 0.20344 |  |  | 0.14474 |  |  | 0.04221
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82588 |  |  | 0.82502 |  |  | 0.8253 |  |  | 0.82704 |  |  | 0.8307 |  |  | 0.84212 |  |  | 0.85743 |  |  | 0.9183 |  |  | 0.96265
[13 empty] | C Non choked w/ reducers | 7 |  | 0.21111 |  |  | 6.0721 |  |  | 14.9861 |  |  | 29.8103 |  |  | 52.5592 |  |  | 84.1225 |  |  | 129.9701 |  |  | 195.8031 |  |  | 307.5163 |  |  | 955.4312
[13 empty] | C Choked w/ reducers | 7 |  | 0.18898 |  |  | 5.4339 |  |  | 13.4302 |  |  | 26.7029 |  |  | 46.9444 |  |  | 74.6658 |  |  | 112.9325 |  |  | 164.6124 |  |  | 209.6054 |  |  | 461.5928
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.21111 |  |  | 6.0721 |  |  | 14.9861 |  |  | 29.8103 |  |  | 52.5592 |  |  | 84.1225 |  |  | 129.9701 |  |  | 195.8031 |  |  | 307.5163 |  |  | 955.4312
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5189 | 522.7463 |  | 5.5279 | 15015.9312 |  | 8.0139 | 36768.4997 |  | 9.5897 | 71615.6524 |  | 8.4408 | 120148.7867 |  | 4.0775 | 175360.4265 |  | 8.9701 | 234019.169 |  | 30.8031 | 285547.8591 |  | 61.5163 | 331512.1997 |  | 535.4312 | 388724.126
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 533.2012 | C_100 - C this iteration | iteration | 15166.0905 | C_100 - C this iteration | iteration | 37136.1847 | C_100 - C this iteration | iteration | 72331.8089 | C_100 - C this iteration | iteration | 121350.2745 | C_100 - C this iteration | iteration | 177114.0308 | C_100 - C this iteration | iteration | 236359.3607 | C_100 - C this iteration | iteration | 288403.3377 | C_100 - C this iteration | iteration | 334827.3217 | C_100 - C this iteration | iteration | 392611.3672 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1431 |  |  | 89.9337 |  |  | 89.2315 |  |  | 87.5011 |  |  | 84.4676 |  |  | 80.0029 |  |  | 75.0252 |  |  | 69.7519 |  |  | 62.0907
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1431 |  |  | 29.9337 |  |  | 29.2315 |  |  | 27.5011 |  |  | 24.4676 |  |  | 20.0029 |  |  | 15.0252 |  |  | 9.7519 |  |  | 2.0907
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33439 |  |  | 0.33284 |  |  | 0.32759 |  |  | 0.31429 |  |  | 0.28967 |  |  | 0.25003 |  |  | 0.20027 |  |  | 0.13981 |  |  | 0.033671
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82589 |  |  | 0.82504 |  |  | 0.82538 |  |  | 0.82727 |  |  | 0.83125 |  |  | 0.84329 |  |  | 0.85966 |  |  | 0.92108 |  |  | 0.9702
[13 empty] | C Non choked w/ reducers | 7 |  | 0.21533 |  |  | 6.1329 |  |  | 15.1373 |  |  | 30.1185 |  |  | 53.1373 |  |  | 85.1594 |  |  | 131.9076 |  |  | 199.5971 |  |  | 316.8899 |  |  | 1081.5837
[13 empty] | C Choked w/ reducers | 7 |  | 0.19276 |  |  | 5.4883 |  |  | 13.5652 |  |  | 26.9757 |  |  | 47.4425 |  |  | 75.5131 |  |  | 114.3479 |  |  | 166.9205 |  |  | 212.9234 |  |  | 470.3652
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.21533 |  |  | 6.1329 |  |  | 15.1373 |  |  | 30.1185 |  |  | 53.1373 |  |  | 85.1594 |  |  | 131.9076 |  |  | 199.5971 |  |  | 316.8899 |  |  | 1081.5837
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5147 | 533.2012 |  | 5.4671 | 15166.0905 |  | 7.8627 | 37136.1847 |  | 9.2815 | 72331.8089 |  | 7.8627 | 121350.2745 |  | 3.0406 | 177114.0308 |  | 10.9076 | 236359.3607 |  | 34.5971 | 288403.3377 |  | 70.8899 | 334827.3217 |  | 661.5837 | 392611.3672
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 543.8652 | C_100 - C this iteration | iteration | 15317.7514 | C_100 - C this iteration | iteration | 37507.5465 | C_100 - C this iteration | iteration | 73055.127 | C_100 - C this iteration | iteration | 122563.7773 | C_100 - C this iteration | iteration | 178885.1711 | C_100 - C this iteration | iteration | 238722.9543 | C_100 - C this iteration | iteration | 291287.3711 | C_100 - C this iteration | iteration | 338175.595 | C_100 - C this iteration | iteration | 396537.4809 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1423 |  |  | 89.9286 |  |  | 89.2123 |  |  | 87.4471 |  |  | 84.3527 |  |  | 79.7982 |  |  | 74.7205 |  |  | 69.3412 |  |  | 61.526
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1423 |  |  | 29.9286 |  |  | 29.2123 |  |  | 27.4471 |  |  | 24.3527 |  |  | 19.7982 |  |  | 14.7205 |  |  | 9.3412 |  |  | 1.526
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33439 |  |  | 0.3328 |  |  | 0.32745 |  |  | 0.31387 |  |  | 0.2887 |  |  | 0.2481 |  |  | 0.19701 |  |  | 0.13471 |  |  | 0.024802
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82589 |  |  | 0.82506 |  |  | 0.82545 |  |  | 0.8275 |  |  | 0.83181 |  |  | 0.8445 |  |  | 0.86194 |  |  | 0.92396 |  |  | 0.97805
[13 empty] | C Non choked w/ reducers | 7 |  | 0.21963 |  |  | 6.1943 |  |  | 15.2901 |  |  | 30.43 |  |  | 53.7228 |  |  | 86.2139 |  |  | 133.8937 |  |  | 203.5426 |  |  | 326.9654 |  |  | 1274.1942
[13 empty] | C Choked w/ reducers | 7 |  | 0.19662 |  |  | 5.5432 |  |  | 13.7016 |  |  | 27.2513 |  |  | 47.9464 |  |  | 76.3721 |  |  | 115.7875 |  |  | 169.2772 |  |  | 216.3264 |  |  | 479.4292
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.21963 |  |  | 6.1943 |  |  | 15.2901 |  |  | 30.43 |  |  | 53.7228 |  |  | 86.2139 |  |  | 133.8937 |  |  | 203.5426 |  |  | 326.9654 |  |  | 1274.1942
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5104 | 543.8652 |  | 5.4057 | 15317.7514 |  | 7.7099 | 37507.5465 |  | 8.97 | 73055.127 |  | 7.2772 | 122563.7773 |  | 1.9861 | 178885.1711 |  | 12.8937 | 238722.9543 |  | 38.5426 | 291287.3711 |  | 80.9654 | 338175.595 |  | 854.1942 | 396537.4809
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 554.7425 | C_100 - C this iteration | iteration | 15470.9289 | C_100 - C this iteration | iteration | 37882.622 | C_100 - C this iteration | iteration | 73785.6783 | C_100 - C this iteration | iteration | 123789.415 | C_100 - C this iteration | iteration | 180674.0228 | C_100 - C this iteration | iteration | 241110.1838 | C_100 - C this iteration | iteration | 294200.2448 | C_100 - C this iteration | iteration | 341557.3509 | C_100 - C this iteration | iteration | 400502.8557 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1414 |  |  | 89.9235 |  |  | 89.1928 |  |  | 87.3921 |  |  | 84.2355 |  |  | 79.5895 |  |  | 74.4097 |  |  | 68.9222 |  |  | 60.9499
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1414 |  |  | 29.9235 |  |  | 29.1928 |  |  | 27.3921 |  |  | 24.2355 |  |  | 19.5895 |  |  | 14.4097 |  |  | 8.9222 |  |  | 0.94993
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33438 |  |  | 0.33277 |  |  | 0.3273 |  |  | 0.31344 |  |  | 0.28771 |  |  | 0.24613 |  |  | 0.19365 |  |  | 0.12945 |  |  | 0.015585
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82589 |  |  | 0.82508 |  |  | 0.82553 |  |  | 0.82774 |  |  | 0.83239 |  |  | 0.84573 |  |  | 0.86429 |  |  | 0.92693 |  |  | 0.98621
[13 empty] | C Non choked w/ reducers | 7 |  | 0.22403 |  |  | 6.2563 |  |  | 15.4443 |  |  | 30.7451 |  |  | 54.3161 |  |  | 87.2866 |  |  | 135.9306 |  |  | 207.6507 |  |  | 337.8394 |  |  | 1625.255
[13 empty] | C Choked w/ reducers | 7 |  | 0.20055 |  |  | 5.5987 |  |  | 13.8394 |  |  | 27.5298 |  |  | 48.4564 |  |  | 77.2432 |  |  | 117.2522 |  |  | 171.6842 |  |  | 219.8178 |  |  | 488.7999
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.22403 |  |  | 6.2563 |  |  | 15.4443 |  |  | 30.7451 |  |  | 54.3161 |  |  | 87.2866 |  |  | 135.9306 |  |  | 207.6507 |  |  | 337.8394 |  |  | 1625.255
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.506 | 554.7425 |  | 5.3437 | 15470.9289 |  | 7.5557 | 37882.622 |  | 8.6549 | 73785.6783 |  | 6.6839 | 123789.415 |  | 0.91341 | 180674.0228 |  | 14.9306 | 241110.1838 |  | 42.6507 | 294200.2448 |  | 91.8394 | 341557.3509 |  | 1205.255 | 400502.8557
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 565.8374 | C_100 - C this iteration | iteration | 15625.6382 | C_100 - C this iteration | iteration | 38261.4482 | C_100 - C this iteration | iteration | 74523.5351 | C_100 - C this iteration | iteration | 125027.3092 | C_100 - C this iteration | iteration | 182480.763 | C_100 - C this iteration | iteration | 243521.2857 | C_100 - C this iteration | iteration | 297142.2473 | C_100 - C this iteration | iteration | 344972.9244 | C_100 - C this iteration | iteration | 404507.8842 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1405 |  |  | 89.9182 |  |  | 89.1728 |  |  | 87.336 |  |  | 84.1159 |  |  | 79.3765 |  |  | 74.0926 |  |  | 68.4948 |  |  | 60.3623
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1405 |  |  | 29.9182 |  |  | 29.1728 |  |  | 27.336 |  |  | 24.1159 |  |  | 19.3765 |  |  | 14.0926 |  |  | 8.4948 |  |  | 0.3623
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33437 |  |  | 0.33273 |  |  | 0.32715 |  |  | 0.313 |  |  | 0.2867 |  |  | 0.24411 |  |  | 0.1902 |  |  | 0.12402 |  |  | 0.0060021
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.8259 |  |  | 0.8251 |  |  | 0.82561 |  |  | 0.82798 |  |  | 0.83298 |  |  | 0.847 |  |  | 0.86671 |  |  | 0.93 |  |  | 0.99469
[13 empty] | C Non choked w/ reducers | 7 |  | 0.22851 |  |  | 6.319 |  |  | 15.6002 |  |  | 31.0636 |  |  | 54.9171 |  |  | 88.3779 |  |  | 138.0205 |  |  | 211.9339 |  |  | 349.6287 |  |  | 2648.1221
[13 empty] | C Choked w/ reducers | 7 |  | 0.20456 |  |  | 5.6547 |  |  | 13.9786 |  |  | 27.8113 |  |  | 48.9724 |  |  | 78.1265 |  |  | 118.7425 |  |  | 174.1431 |  |  | 223.4013 |  |  | 498.494
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.22851 |  |  | 6.319 |  |  | 15.6002 |  |  | 31.0636 |  |  | 54.9171 |  |  | 88.3779 |  |  | 138.0205 |  |  | 211.9339 |  |  | 349.6287 |  |  | 2648.1221
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5015 | 565.8374 |  | 5.281 | 15625.6382 |  | 7.3998 | 38261.4482 |  | 8.3364 | 74523.5351 |  | 6.0829 | 125027.3092 |  | 0.17793 | 182480.763 |  | 17.0205 | 243521.2857 |  | 46.9339 | 297142.2473 |  | 103.6287 | 344972.9244 |  | 2228.1221 | 404507.8842
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 577.1541 | C_100 - C this iteration | iteration | 15781.8946 | C_100 - C this iteration | iteration | 38644.0627 | C_100 - C this iteration | iteration | 75268.7704 | C_100 - C this iteration | iteration | 126277.5823 | C_100 - C this iteration | iteration | 184305.5707 | C_100 - C this iteration | iteration | 245956.4985 | C_100 - C this iteration | iteration | 300113.6697 | C_100 - C this iteration | iteration | 348422.6537 | C_100 - C this iteration | iteration | 408552.9631 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1396 |  |  | 89.9129 |  |  | 89.1525 |  |  | 87.2787 |  |  | 83.9939 |  |  | 79.1592 |  |  | 73.7691 |  |  | 68.0589 |  |  | 59.7629
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1396 |  |  | 29.9129 |  |  | 29.1525 |  |  | 27.2787 |  |  | 23.9939 |  |  | 19.1592 |  |  | 13.7691 |  |  | 8.0589 |  |  | -0.23713
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33437 |  |  | 0.33269 |  |  | 0.327 |  |  | 0.31255 |  |  | 0.28566 |  |  | 0.24203 |  |  | 0.18665 |  |  | 0.11841 |  |  | -0.0039679
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.8259 |  |  | 0.82512 |  |  | 0.82569 |  |  | 0.82823 |  |  | 0.83358 |  |  | 0.8483 |  |  | 0.8692 |  |  | 0.93316 |  |  | 1.0035
[13 empty] | C Non choked w/ reducers | 7 |  | 0.23308 |  |  | 6.3823 |  |  | 15.7577 |  |  | 31.3857 |  |  | 55.526 |  |  | 89.4885 |  |  | 140.1659 |  |  | 216.4058 |  |  | 362.4759 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.20865 |  |  | 5.7113 |  |  | 14.1193 |  |  | 28.0958 |  |  | 49.4946 |  |  | 79.0224 |  |  | 120.259 |  |  | 176.6557 |  |  | 227.0806 |  |  | 508.5289
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.23308 |  |  | 6.3823 |  |  | 15.7577 |  |  | 31.3857 |  |  | 55.526 |  |  | 89.4885 |  |  | 140.1659 |  |  | 216.4058 |  |  | 362.4759 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4969 | 577.1541 |  | 5.2177 | 15781.8946 |  | 7.2423 | 38644.0627 |  | 8.0143 | 75268.7704 |  | 5.474 | 126277.5823 |  | 1.2885 | 184305.5707 |  | 19.1659 | 245956.4985 |  | 51.4058 | 300113.6697 |  | 116.4759 | 348422.6537 |  | 236393 | 408552.9631
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 588.6972 | C_100 - C this iteration | iteration | 15939.7135 | C_100 - C this iteration | iteration | 39030.5033 | C_100 - C this iteration | iteration | 76021.4581 | C_100 - C this iteration | iteration | 127540.3581 | C_100 - C this iteration | iteration | 186148.6264 | C_100 - C this iteration | iteration | 248416.0635 | C_100 - C this iteration | iteration | 303114.8064 | C_100 - C this iteration | iteration | 351906.8802 | C_100 - C this iteration | iteration | 412638.4927 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1387 |  |  | 89.9074 |  |  | 89.1317 |  |  | 87.2203 |  |  | 83.8695 |  |  | 78.9376 |  |  | 73.4392 |  |  | 67.6141 |  |  | 59.1514
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1387 |  |  | 29.9074 |  |  | 29.1317 |  |  | 27.2203 |  |  | 23.8695 |  |  | 18.9376 |  |  | 13.4392 |  |  | 7.6141 |  |  | -0.84862
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33436 |  |  | 0.33265 |  |  | 0.32684 |  |  | 0.31209 |  |  | 0.2846 |  |  | 0.23991 |  |  | 0.183 |  |  | 0.11261 |  |  | -0.014347
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.8259 |  |  | 0.82515 |  |  | 0.82578 |  |  | 0.82848 |  |  | 0.8342 |  |  | 0.84964 |  |  | 0.87176 |  |  | 0.93644 |  |  | 1.0127
[13 empty] | C Non choked w/ reducers | 7 |  | 0.23774 |  |  | 6.4462 |  |  | 15.9168 |  |  | 31.7113 |  |  | 56.1431 |  |  | 90.6187 |  |  | 142.3694 |  |  | 221.0818 |  |  | 376.5566 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.21282 |  |  | 5.7685 |  |  | 14.2613 |  |  | 28.3834 |  |  | 50.023 |  |  | 79.931 |  |  | 121.8026 |  |  | 179.2239 |  |  | 230.86 |  |  | 518.9238
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.23774 |  |  | 6.4462 |  |  | 15.9168 |  |  | 31.7113 |  |  | 56.1431 |  |  | 90.6187 |  |  | 142.3694 |  |  | 221.0818 |  |  | 376.5566 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4923 | 588.6972 |  | 5.1538 | 15939.7135 |  | 7.0832 | 39030.5033 |  | 7.6887 | 76021.4581 |  | 4.8569 | 127540.3581 |  | 2.4187 | 186148.6264 |  | 21.3694 | 248416.0635 |  | 56.0818 | 303114.8064 |  | 130.5566 | 351906.8802 |  | 236393 | 412638.4927
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 600.4712 | C_100 - C this iteration | iteration | 16099.1106 | C_100 - C this iteration | iteration | 39420.8084 | C_100 - C this iteration | iteration | 76781.6727 | C_100 - C this iteration | iteration | 128815.7617 | C_100 - C this iteration | iteration | 188010.1126 | C_100 - C this iteration | iteration | 250900.2241 | C_100 - C this iteration | iteration | 306145.9545 | C_100 - C this iteration | iteration | 355425.949 | C_100 - C this iteration | iteration | 416764.8776 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1378 |  |  | 89.9018 |  |  | 89.1105 |  |  | 87.1607 |  |  | 83.7425 |  |  | 78.7115 |  |  | 73.1026 |  |  | 67.1605 |  |  | 58.5276
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1378 |  |  | 29.9018 |  |  | 29.1105 |  |  | 27.1607 |  |  | 23.7425 |  |  | 18.7115 |  |  | 13.1026 |  |  | 7.1605 |  |  | -1.4724
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33435 |  |  | 0.33261 |  |  | 0.32668 |  |  | 0.31162 |  |  | 0.28352 |  |  | 0.23772 |  |  | 0.17924 |  |  | 0.10662 |  |  | -0.025157
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82591 |  |  | 0.82517 |  |  | 0.82586 |  |  | 0.82874 |  |  | 0.83483 |  |  | 0.851 |  |  | 0.8744 |  |  | 0.93982 |  |  | 1.0223
[13 empty] | C Non choked w/ reducers | 7 |  | 0.24249 |  |  | 6.5108 |  |  | 16.0776 |  |  | 32.0405 |  |  | 56.7684 |  |  | 91.7693 |  |  | 144.6338 |  |  | 225.9792 |  |  | 392.0911 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.21708 |  |  | 5.8263 |  |  | 14.4048 |  |  | 28.6741 |  |  | 50.5578 |  |  | 80.8527 |  |  | 123.374 |  |  | 181.8496 |  |  | 234.7437 |  |  | 529.6989
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.24249 |  |  | 6.5108 |  |  | 16.0776 |  |  | 32.0405 |  |  | 56.7684 |  |  | 91.7693 |  |  | 144.6338 |  |  | 225.9792 |  |  | 392.0911 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4875 | 600.4712 |  | 5.0892 | 16099.1106 |  | 6.9224 | 39420.8084 |  | 7.3595 | 76781.6727 |  | 4.2316 | 128815.7617 |  | 3.5693 | 188010.1126 |  | 23.6338 | 250900.2241 |  | 60.9792 | 306145.9545 |  | 146.0911 | 355425.949 |  | 236393 | 416764.8776
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 612.4806 | C_100 - C this iteration | iteration | 16260.1018 | C_100 - C this iteration | iteration | 39815.0164 | C_100 - C this iteration | iteration | 77549.4894 | C_100 - C this iteration | iteration | 130103.9193 | C_100 - C this iteration | iteration | 189890.2138 | C_100 - C this iteration | iteration | 253409.2264 | C_100 - C this iteration | iteration | 309207.4141 | C_100 - C this iteration | iteration | 358980.2085 | C_100 - C this iteration | iteration | 420932.5264 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1369 |  |  | 89.8961 |  |  | 89.0889 |  |  | 87.0999 |  |  | 83.613 |  |  | 78.4809 |  |  | 72.7592 |  |  | 66.6977 |  |  | 57.8913
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1369 |  |  | 29.8961 |  |  | 29.0889 |  |  | 27.0999 |  |  | 23.613 |  |  | 18.4809 |  |  | 12.7592 |  |  | 6.6977 |  |  | -2.1087
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33435 |  |  | 0.33256 |  |  | 0.32652 |  |  | 0.31114 |  |  | 0.28241 |  |  | 0.23548 |  |  | 0.17536 |  |  | 0.10042 |  |  | -0.036425
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82591 |  |  | 0.82519 |  |  | 0.82595 |  |  | 0.829 |  |  | 0.83548 |  |  | 0.85241 |  |  | 0.87711 |  |  | 0.94332 |  |  | 1.0322
[13 empty] | C Non choked w/ reducers | 7 |  | 0.24734 |  |  | 6.576 |  |  | 16.24 |  |  | 32.3735 |  |  | 57.4021 |  |  | 92.9408 |  |  | 146.9621 |  |  | 231.1173 |  |  | 409.3594 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.22142 |  |  | 5.8846 |  |  | 14.5498 |  |  | 28.9678 |  |  | 51.099 |  |  | 81.7877 |  |  | 124.9739 |  |  | 184.5349 |  |  | 238.7362 |  |  | 540.8763
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.24734 |  |  | 6.576 |  |  | 16.24 |  |  | 32.3735 |  |  | 57.4021 |  |  | 92.9408 |  |  | 146.9621 |  |  | 231.1173 |  |  | 409.3594 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4827 | 612.4806 |  | 5.024 | 16260.1018 |  | 6.76 | 39815.0164 |  | 7.0265 | 77549.4894 |  | 3.5979 | 130103.9193 |  | 4.7408 | 189890.2138 |  | 25.9621 | 253409.2264 |  | 66.1173 | 309207.4141 |  | 163.3594 | 358980.2085 |  | 236393 | 420932.5264
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 624.7302 | C_100 - C this iteration | iteration | 16422.7028 | C_100 - C this iteration | iteration | 40213.1666 | C_100 - C this iteration | iteration | 78324.9843 | C_100 - C this iteration | iteration | 131404.9585 | C_100 - C this iteration | iteration | 191789.1159 | C_100 - C this iteration | iteration | 255943.3186 | C_100 - C this iteration | iteration | 312299.4882 | C_100 - C this iteration | iteration | 362570.0106 | C_100 - C this iteration | iteration | 425141.8517 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1359 |  |  | 89.8903 |  |  | 89.0669 |  |  | 87.0379 |  |  | 83.4809 |  |  | 78.2457 |  |  | 72.409 |  |  | 66.2256 |  |  | 57.2422
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1359 |  |  | 29.8903 |  |  | 29.0669 |  |  | 27.0379 |  |  | 23.4809 |  |  | 18.2457 |  |  | 12.409 |  |  | 6.2256 |  |  | -2.7578
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33434 |  |  | 0.33252 |  |  | 0.32635 |  |  | 0.31065 |  |  | 0.28127 |  |  | 0.23318 |  |  | 0.17137 |  |  | 0.094005 |  |  | -0.048178
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82591 |  |  | 0.82521 |  |  | 0.82604 |  |  | 0.82927 |  |  | 0.83614 |  |  | 0.85385 |  |  | 0.87991 |  |  | 0.94694 |  |  | 1.0426
[13 empty] | C Non choked w/ reducers | 7 |  | 0.25229 |  |  | 6.6419 |  |  | 16.404 |  |  | 32.7101 |  |  | 58.0443 |  |  | 94.1338 |  |  | 149.3575 |  |  | 236.518 |  |  | 428.7237 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.22585 |  |  | 5.9435 |  |  | 14.6963 |  |  | 29.2647 |  |  | 51.6468 |  |  | 82.7363 |  |  | 126.6031 |  |  | 187.2818 |  |  | 242.8425 |  |  | 552.4798
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.25229 |  |  | 6.6419 |  |  | 16.404 |  |  | 32.7101 |  |  | 58.0443 |  |  | 94.1338 |  |  | 149.3575 |  |  | 236.518 |  |  | 428.7237 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4777 | 624.7302 |  | 4.9581 | 16422.7028 |  | 6.596 | 40213.1666 |  | 6.6899 | 78324.9843 |  | 2.9557 | 131404.9585 |  | 5.9338 | 191789.1159 |  | 28.3575 | 255943.3186 |  | 71.518 | 312299.4882 |  | 182.7237 | 362570.0106 |  | 236393 | 425141.8517
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 637.2248 | C_100 - C this iteration | iteration | 16586.9298 | C_100 - C this iteration | iteration | 40615.2983 | C_100 - C this iteration | iteration | 79108.2342 | C_100 - C this iteration | iteration | 132719.0081 | C_100 - C this iteration | iteration | 193707.0071 | C_100 - C this iteration | iteration | 258502.7518 | C_100 - C this iteration | iteration | 315422.4831 | C_100 - C this iteration | iteration | 366195.7107 | C_100 - C this iteration | iteration | 429393.2702 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1349 |  |  | 89.8844 |  |  | 89.0444 |  |  | 86.9746 |  |  | 83.3462 |  |  | 78.0057 |  |  | 72.0517 |  |  | 65.744 |  |  | 56.58
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1349 |  |  | 29.8844 |  |  | 29.0444 |  |  | 26.9746 |  |  | 23.3462 |  |  | 18.0057 |  |  | 12.0517 |  |  | 5.744 |  |  | -3.42
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33433 |  |  | 0.33248 |  |  | 0.32618 |  |  | 0.31014 |  |  | 0.28011 |  |  | 0.23083 |  |  | 0.16726 |  |  | 0.087369 |  |  | -0.060445
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82592 |  |  | 0.82523 |  |  | 0.82613 |  |  | 0.82955 |  |  | 0.83682 |  |  | 0.85533 |  |  | 0.88279 |  |  | 0.95068 |  |  | 1.0535
[13 empty] | C Non choked w/ reducers | 7 |  | 0.25734 |  |  | 6.7084 |  |  | 16.5698 |  |  | 33.0505 |  |  | 58.6953 |  |  | 95.3489 |  |  | 151.8236 |  |  | 242.2061 |  |  | 450.6631 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.23037 |  |  | 6.003 |  |  | 14.8442 |  |  | 29.5648 |  |  | 52.2012 |  |  | 83.6988 |  |  | 128.2625 |  |  | 190.0926 |  |  | 247.0676 |  |  | 564.5348
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.25734 |  |  | 6.7084 |  |  | 16.5698 |  |  | 33.0505 |  |  | 58.6953 |  |  | 95.3489 |  |  | 151.8236 |  |  | 242.2061 |  |  | 450.6631 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4727 | 637.2248 |  | 4.8916 | 16586.9298 |  | 6.4302 | 40615.2983 |  | 6.3495 | 79108.2342 |  | 2.3047 | 132719.0081 |  | 7.1489 | 193707.0071 |  | 30.8236 | 258502.7518 |  | 77.2061 | 315422.4831 |  | 204.6631 | 366195.7107 |  | 236393 | 429393.2702
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 649.9693 | C_100 - C this iteration | iteration | 16752.7991 | C_100 - C this iteration | iteration | 41021.4513 | C_100 - C this iteration | iteration | 79899.3165 | C_100 - C this iteration | iteration | 134046.1982 | C_100 - C this iteration | iteration | 195644.0771 | C_100 - C this iteration | iteration | 261087.7793 | C_100 - C this iteration | iteration | 318576.7079 | C_100 - C this iteration | iteration | 369857.6678 | C_100 - C this iteration | iteration | 433687.2029 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1339 |  |  | 89.8783 |  |  | 89.0215 |  |  | 86.9101 |  |  | 83.2087 |  |  | 77.7609 |  |  | 71.6872 |  |  | 65.2527 |  |  | 55.9046
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1339 |  |  | 29.8783 |  |  | 29.0215 |  |  | 26.9101 |  |  | 23.2087 |  |  | 17.7609 |  |  | 11.6872 |  |  | 5.2527 |  |  | -4.0954
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33432 |  |  | 0.33243 |  |  | 0.32601 |  |  | 0.30963 |  |  | 0.27892 |  |  | 0.2284 |  |  | 0.16303 |  |  | 0.080498 |  |  | -0.073257
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82592 |  |  | 0.82526 |  |  | 0.82622 |  |  | 0.82983 |  |  | 0.83751 |  |  | 0.85684 |  |  | 0.88575 |  |  | 0.95456 |  |  | 1.0648
[13 empty] | C Non choked w/ reducers | 7 |  | 0.26248 |  |  | 6.7756 |  |  | 16.7373 |  |  | 33.3948 |  |  | 59.3552 |  |  | 96.587 |  |  | 154.3639 |  |  | 248.2099 |  |  | 475.8264 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.23497 |  |  | 6.0631 |  |  | 14.9937 |  |  | 29.8682 |  |  | 52.7624 |  |  | 84.6754 |  |  | 129.953 |  |  | 192.9697 |  |  | 251.4169 |  |  | 577.0693
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.26248 |  |  | 6.7756 |  |  | 16.7373 |  |  | 33.3948 |  |  | 59.3552 |  |  | 96.587 |  |  | 154.3639 |  |  | 248.2099 |  |  | 475.8264 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4675 | 649.9693 |  | 4.8244 | 16752.7991 |  | 6.2627 | 41021.4513 |  | 6.0052 | 79899.3165 |  | 1.6448 | 134046.1982 |  | 8.387 | 195644.0771 |  | 33.3639 | 261087.7793 |  | 83.2099 | 318576.7079 |  | 229.8264 | 369857.6678 |  | 236393 | 433687.2029
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 662.9687 | C_100 - C this iteration | iteration | 16920.3271 | C_100 - C this iteration | iteration | 41431.6658 | C_100 - C this iteration | iteration | 80698.3097 | C_100 - C this iteration | iteration | 135386.6601 | C_100 - C this iteration | iteration | 197600.5179 | C_100 - C this iteration | iteration | 263698.6571 | C_100 - C this iteration | iteration | 321762.475 | C_100 - C this iteration | iteration | 373556.2445 | C_100 - C this iteration | iteration | 438024.0749 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1329 |  |  | 89.8722 |  |  | 88.9981 |  |  | 86.8443 |  |  | 83.0685 |  |  | 77.5112 |  |  | 71.3154 |  |  | 64.7516 |  |  | 55.2155
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1329 |  |  | 29.8722 |  |  | 28.9981 |  |  | 26.8443 |  |  | 23.0685 |  |  | 17.5112 |  |  | 11.3154 |  |  | 4.7516 |  |  | -4.7845
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33432 |  |  | 0.33239 |  |  | 0.32583 |  |  | 0.30911 |  |  | 0.2777 |  |  | 0.22592 |  |  | 0.15867 |  |  | 0.073382 |  |  | -0.086651
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82593 |  |  | 0.82528 |  |  | 0.82631 |  |  | 0.83012 |  |  | 0.83822 |  |  | 0.8584 |  |  | 0.88881 |  |  | 0.95858 |  |  | 1.0767
[13 empty] | C Non choked w/ reducers | 7 |  | 0.26773 |  |  | 6.8435 |  |  | 16.9065 |  |  | 33.7429 |  |  | 60.0241 |  |  | 97.8486 |  |  | 156.9826 |  |  | 254.5618 |  |  | 505.1187 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.23967 |  |  | 6.1238 |  |  | 15.1446 |  |  | 30.1748 |  |  | 53.3304 |  |  | 85.6665 |  |  | 131.6754 |  |  | 195.9155 |  |  | 255.8964 |  |  | 590.1133
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.26773 |  |  | 6.8435 |  |  | 16.9065 |  |  | 33.7429 |  |  | 60.0241 |  |  | 97.8486 |  |  | 156.9826 |  |  | 254.5618 |  |  | 505.1187 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4623 | 662.9687 |  | 4.7565 | 16920.3271 |  | 6.0935 | 41431.6658 |  | 5.6571 | 80698.3097 |  | 0.97587 | 135386.6601 |  | 9.6486 | 197600.5179 |  | 35.9826 | 263698.6571 |  | 89.5618 | 321762.475 |  | 259.1187 | 373556.2445 |  | 236393 | 438024.0749
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 676.2281 | C_100 - C this iteration | iteration | 17089.5304 | C_100 - C this iteration | iteration | 41845.9824 | C_100 - C this iteration | iteration | 81505.2928 | C_100 - C this iteration | iteration | 136740.5267 | C_100 - C this iteration | iteration | 199576.5231 | C_100 - C this iteration | iteration | 266335.6437 | C_100 - C this iteration | iteration | 324980.0997 | C_100 - C this iteration | iteration | 377291.8069 | C_100 - C this iteration | iteration | 442404.3157 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1318 |  |  | 89.8659 |  |  | 88.9743 |  |  | 86.7771 |  |  | 82.9254 |  |  | 77.2564 |  |  | 70.9361 |  |  | 64.2404 |  |  | 54.5126
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1318 |  |  | 29.8659 |  |  | 28.9743 |  |  | 26.7771 |  |  | 22.9254 |  |  | 17.2564 |  |  | 10.9361 |  |  | 4.2404 |  |  | -5.4874
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33431 |  |  | 0.33234 |  |  | 0.32565 |  |  | 0.30857 |  |  | 0.27646 |  |  | 0.22337 |  |  | 0.15417 |  |  | 0.066008 |  |  | -0.10066
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82593 |  |  | 0.82531 |  |  | 0.82641 |  |  | 0.83041 |  |  | 0.83894 |  |  | 0.86 |  |  | 0.89196 |  |  | 0.96274 |  |  | 1.0891
[13 empty] | C Non choked w/ reducers | 7 |  | 0.27309 |  |  | 6.912 |  |  | 17.0774 |  |  | 34.095 |  |  | 60.7023 |  |  | 99.1345 |  |  | 159.6839 |  |  | 261.2993 |  |  | 539.8482 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.24447 |  |  | 6.1851 |  |  | 15.2971 |  |  | 30.4847 |  |  | 53.9054 |  |  | 86.6725 |  |  | 133.4307 |  |  | 198.9327 |  |  | 260.5121 |  |  | 603.6995
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.27309 |  |  | 6.912 |  |  | 17.0774 |  |  | 34.095 |  |  | 60.7023 |  |  | 99.1345 |  |  | 159.6839 |  |  | 261.2993 |  |  | 539.8482 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4569 | 676.2281 |  | 4.688 | 17089.5304 |  | 5.9226 | 41845.9824 |  | 5.305 | 81505.2928 |  | 0.29767 | 136740.5267 |  | 10.9345 | 199576.5231 |  | 38.6839 | 266335.6437 |  | 96.2993 | 324980.0997 |  | 293.8482 | 377291.8069 |  | 236393 | 442404.3157
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 689.7526 | C_100 - C this iteration | iteration | 17260.4257 | C_100 - C this iteration | iteration | 42264.4423 | C_100 - C this iteration | iteration | 82320.3457 | C_100 - C this iteration | iteration | 138107.932 | C_100 - C this iteration | iteration | 201572.2883 | C_100 - C this iteration | iteration | 268999.0001 | C_100 - C this iteration | iteration | 328229.9007 | C_100 - C this iteration | iteration | 381064.725 | C_100 - C this iteration | iteration | 446828.3588 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1307 |  |  | 89.8595 |  |  | 88.9499 |  |  | 86.7086 |  |  | 82.7795 |  |  | 76.9966 |  |  | 70.5492 |  |  | 63.7189 |  |  | 53.7956
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1307 |  |  | 29.8595 |  |  | 28.9499 |  |  | 26.7086 |  |  | 22.7795 |  |  | 16.9966 |  |  | 10.5492 |  |  | 3.7189 |  |  | -6.2044
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.3343 |  |  | 0.33229 |  |  | 0.32546 |  |  | 0.30803 |  |  | 0.27518 |  |  | 0.22074 |  |  | 0.14953 |  |  | 0.058364 |  |  | -0.11533
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82593 |  |  | 0.82533 |  |  | 0.82651 |  |  | 0.83071 |  |  | 0.83969 |  |  | 0.86165 |  |  | 0.89521 |  |  | 0.96706 |  |  | 1.1021
[13 empty] | C Non choked w/ reducers | 7 |  | 0.27855 |  |  | 6.9813 |  |  | 17.2501 |  |  | 34.451 |  |  | 61.39 |  |  | 100.4456 |  |  | 162.4727 |  |  | 268.4658 |  |  | 581.9916 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.24936 |  |  | 6.247 |  |  | 15.4512 |  |  | 30.798 |  |  | 54.4874 |  |  | 87.6935 |  |  | 135.2198 |  |  | 202.0239 |  |  | 265.2706 |  |  | 617.8633
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.27855 |  |  | 6.9813 |  |  | 17.2501 |  |  | 34.451 |  |  | 61.39 |  |  | 100.4456 |  |  | 162.4727 |  |  | 268.4658 |  |  | 581.9916 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4515 | 689.7526 |  | 4.6187 | 17260.4257 |  | 5.7499 | 42264.4423 |  | 4.949 | 82320.3457 |  | 0.38997 | 138107.932 |  | 12.2456 | 201572.2883 |  | 41.4727 | 268999.0001 |  | 103.4658 | 328229.9007 |  | 335.9916 | 381064.725 |  | 236393 | 446828.3588
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 703.5477 | C_100 - C this iteration | iteration | 17433.0299 | C_100 - C this iteration | iteration | 42687.0867 | C_100 - C this iteration | iteration | 83143.5492 | C_100 - C this iteration | iteration | 139489.0113 | C_100 - C this iteration | iteration | 203588.0112 | C_100 - C this iteration | iteration | 271688.9901 | C_100 - C this iteration | iteration | 331512.1997 | C_100 - C this iteration | iteration | 384875.3722 | C_100 - C this iteration | iteration | 451296.6424 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.185 |  |  | 90.1296 |  |  | 89.8529 |  |  | 88.9251 |  |  | 86.6388 |  |  | 82.6307 |  |  | 76.7315 |  |  | 70.1545 |  |  | 63.1869 |  |  | 53.0642
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.185 |  |  | 30.1296 |  |  | 29.8529 |  |  | 28.9251 |  |  | 26.6388 |  |  | 22.6307 |  |  | 16.7315 |  |  | 10.1545 |  |  | 3.1869 |  |  | -6.9358
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33429 |  |  | 0.33224 |  |  | 0.32527 |  |  | 0.30747 |  |  | 0.27388 |  |  | 0.21805 |  |  | 0.14474 |  |  | 0.050436 |  |  | -0.13071
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82594 |  |  | 0.82536 |  |  | 0.82661 |  |  | 0.83102 |  |  | 0.84045 |  |  | 0.86333 |  |  | 0.89857 |  |  | 0.97153 |  |  | 1.1157
[13 empty] | C Non choked w/ reducers | 7 |  | 0.28412 |  |  | 7.0512 |  |  | 17.4247 |  |  | 34.8111 |  |  | 62.0872 |  |  | 101.7826 |  |  | 165.3539 |  |  | 276.1119 |  |  | 634.7093 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.25434 |  |  | 6.3096 |  |  | 15.6069 |  |  | 31.1146 |  |  | 55.0767 |  |  | 88.73 |  |  | 137.0438 |  |  | 205.1921 |  |  | 270.1789 |  |  | 632.6436
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.28412 |  |  | 7.0512 |  |  | 17.4247 |  |  | 34.8111 |  |  | 62.0872 |  |  | 101.7826 |  |  | 165.3539 |  |  | 276.1119 |  |  | 634.7093 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4459 | 703.5477 |  | 4.5488 | 17433.0299 |  | 5.5753 | 42687.0867 |  | 4.5889 | 83143.5492 |  | 1.0872 | 139489.0113 |  | 13.5826 | 203588.0112 |  | 44.3539 | 271688.9901 |  | 111.1119 | 331512.1997 |  | 388.7093 | 384875.3722 |  | 236393 | 451296.6424
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 717.6186 | C_100 - C this iteration | iteration | 17607.3602 | C_100 - C this iteration | iteration | 43113.9575 | C_100 - C this iteration | iteration | 83974.9847 | C_100 - C this iteration | iteration | 140883.9014 | C_100 - C this iteration | iteration | 205623.8913 | C_100 - C this iteration | iteration | 274405.8801 | C_100 - C this iteration | iteration | 334827.3217 | C_100 - C this iteration | iteration | 388724.126 | C_100 - C this iteration | iteration | 455809.6089 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1285 |  |  | 89.8463 |  |  | 88.8998 |  |  | 86.5675 |  |  | 82.4788 |  |  | 76.4611 |  |  | 69.7519 |  |  | 62.6442 |  |  | 52.3181
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1285 |  |  | 29.8463 |  |  | 28.8998 |  |  | 26.5675 |  |  | 22.4788 |  |  | 16.4611 |  |  | 9.7519 |  |  | 2.6442 |  |  | -7.6819
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33428 |  |  | 0.33219 |  |  | 0.32508 |  |  | 0.3069 |  |  | 0.27254 |  |  | 0.21529 |  |  | 0.13981 |  |  | 0.04221 |  |  | -0.14683
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82594 |  |  | 0.82538 |  |  | 0.82671 |  |  | 0.83133 |  |  | 0.84123 |  |  | 0.86507 |  |  | 0.90203 |  |  | 0.97617 |  |  | 1.1299
[13 empty] | C Non choked w/ reducers | 7 |  | 0.2898 |  |  | 7.1219 |  |  | 17.601 |  |  | 35.1752 |  |  | 62.7944 |  |  | 103.1463 |  |  | 168.3331 |  |  | 284.2971 |  |  | 703.4489 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.25943 |  |  | 6.3727 |  |  | 15.7641 |  |  | 31.4347 |  |  | 55.6732 |  |  | 89.7823 |  |  | 138.9038 |  |  | 208.4402 |  |  | 275.2446 |  |  | 648.0827
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.2898 |  |  | 7.1219 |  |  | 17.601 |  |  | 35.1752 |  |  | 62.7944 |  |  | 103.1463 |  |  | 168.3331 |  |  | 284.2971 |  |  | 703.4489 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4402 | 717.6186 |  | 4.4781 | 17607.3602 |  | 5.399 | 43113.9575 |  | 4.2248 | 83974.9847 |  | 1.7944 | 140883.9014 |  | 14.9463 | 205623.8913 |  | 47.3331 | 274405.8801 |  | 119.2971 | 334827.3217 |  | 457.4489 | 388724.126 |  | 236393 | 455809.6089
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 731.971 | C_100 - C this iteration | iteration | 17783.4338 | C_100 - C this iteration | iteration | 43545.0971 | C_100 - C this iteration | iteration | 84814.7345 | C_100 - C this iteration | iteration | 142292.7405 | C_100 - C this iteration | iteration | 207680.1302 | C_100 - C this iteration | iteration | 277149.9389 | C_100 - C this iteration | iteration | 338175.595 | C_100 - C this iteration | iteration | 392611.3672 | C_100 - C this iteration | iteration | 460367.7049 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1274 |  |  | 89.8394 |  |  | 88.8739 |  |  | 86.4948 |  |  | 82.3239 |  |  | 76.1852 |  |  | 69.3412 |  |  | 62.0907 |  |  | 51.557
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1274 |  |  | 29.8394 |  |  | 28.8739 |  |  | 26.4948 |  |  | 22.3239 |  |  | 16.1852 |  |  | 9.3412 |  |  | 2.0907 |  |  | -8.443
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33428 |  |  | 0.33214 |  |  | 0.32489 |  |  | 0.30632 |  |  | 0.27117 |  |  | 0.21245 |  |  | 0.13471 |  |  | 0.033671 |  |  | -0.16376
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82595 |  |  | 0.82541 |  |  | 0.82682 |  |  | 0.83165 |  |  | 0.84202 |  |  | 0.86685 |  |  | 0.9056 |  |  | 0.98099 |  |  | 1.1449
[13 empty] | C Non choked w/ reducers | 7 |  | 0.2956 |  |  | 7.1933 |  |  | 17.7791 |  |  | 35.5435 |  |  | 63.5115 |  |  | 104.5378 |  |  | 171.4164 |  |  | 293.092 |  |  | 798.6378 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.26462 |  |  | 6.4366 |  |  | 15.923 |  |  | 31.7583 |  |  | 56.2772 |  |  | 90.8507 |  |  | 140.8008 |  |  | 211.7715 |  |  | 280.4755 |  |  | 664.2267
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.2956 |  |  | 7.1933 |  |  | 17.7791 |  |  | 35.5435 |  |  | 63.5115 |  |  | 104.5378 |  |  | 171.4164 |  |  | 293.092 |  |  | 798.6378 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4344 | 731.971 |  | 4.4067 | 17783.4338 |  | 5.2209 | 43545.0971 |  | 3.8565 | 84814.7345 |  | 2.5115 | 142292.7405 |  | 16.3378 | 207680.1302 |  | 50.4164 | 277149.9389 |  | 128.092 | 338175.595 |  | 552.6378 | 392611.3672 |  | 236393 | 460367.7049
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 746.6104 | C_100 - C this iteration | iteration | 17961.2682 | C_100 - C this iteration | iteration | 43980.5481 | C_100 - C this iteration | iteration | 85662.8819 | C_100 - C this iteration | iteration | 143715.6679 | C_100 - C this iteration | iteration | 209756.9315 | C_100 - C this iteration | iteration | 279921.4382 | C_100 - C this iteration | iteration | 341557.3509 | C_100 - C this iteration | iteration | 396537.4809 | C_100 - C this iteration | iteration | 464971.382 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1262 |  |  | 89.8325 |  |  | 88.8476 |  |  | 86.4206 |  |  | 82.1659 |  |  | 75.9038 |  |  | 68.9222 |  |  | 61.526 |  |  | 50.7805
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1262 |  |  | 29.8325 |  |  | 28.8476 |  |  | 26.4206 |  |  | 22.1659 |  |  | 15.9038 |  |  | 8.9222 |  |  | 1.526 |  |  | -9.2195
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33427 |  |  | 0.33209 |  |  | 0.32469 |  |  | 0.30572 |  |  | 0.26977 |  |  | 0.20953 |  |  | 0.12945 |  |  | 0.024802 |  |  | -0.18156
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82595 |  |  | 0.82544 |  |  | 0.82692 |  |  | 0.83198 |  |  | 0.84284 |  |  | 0.86868 |  |  | 0.90928 |  |  | 0.986 |  |  | 1.1607
[13 empty] | C Non choked w/ reducers | 7 |  | 0.30151 |  |  | 7.2653 |  |  | 17.9591 |  |  | 35.9161 |  |  | 64.2389 |  |  | 105.9579 |  |  | 174.6104 |  |  | 302.581 |  |  | 943.6561 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.26991 |  |  | 6.501 |  |  | 16.0834 |  |  | 32.0854 |  |  | 56.8888 |  |  | 91.9357 |  |  | 142.736 |  |  | 215.1894 |  |  | 285.8803 |  |  | 681.1264
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.30151 |  |  | 7.2653 |  |  | 17.9591 |  |  | 35.9161 |  |  | 64.2389 |  |  | 105.9579 |  |  | 174.6104 |  |  | 302.581 |  |  | 943.6561 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4285 | 746.6104 |  | 4.3347 | 17961.2682 |  | 5.0409 | 43980.5481 |  | 3.4839 | 85662.8819 |  | 3.2389 | 143715.6679 |  | 17.7579 | 209756.9315 |  | 53.6104 | 279921.4382 |  | 137.581 | 341557.3509 |  | 697.6561 | 396537.4809 |  | 236393 | 464971.382
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 761.5426 | C_100 - C this iteration | iteration | 18140.8808 | C_100 - C this iteration | iteration | 44420.3536 | C_100 - C this iteration | iteration | 86519.5107 | C_100 - C this iteration | iteration | 145152.8245 | C_100 - C this iteration | iteration | 211854.5008 | C_100 - C this iteration | iteration | 282720.6526 | C_100 - C this iteration | iteration | 344972.9244 | C_100 - C this iteration | iteration | 400502.8557 | C_100 - C this iteration | iteration | 469621.0958 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1251 |  |  | 89.8254 |  |  | 88.8207 |  |  | 86.3449 |  |  | 82.0047 |  |  | 75.6167 |  |  | 68.4948 |  |  | 60.9499 |  |  | 49.9885
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1251 |  |  | 29.8254 |  |  | 28.8207 |  |  | 26.3449 |  |  | 22.0047 |  |  | 15.6167 |  |  | 8.4948 |  |  | 0.94993 |  |  | -10.0115
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33426 |  |  | 0.33204 |  |  | 0.32448 |  |  | 0.30511 |  |  | 0.26834 |  |  | 0.20653 |  |  | 0.12402 |  |  | 0.015585 |  |  | -0.20028
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82596 |  |  | 0.82547 |  |  | 0.82703 |  |  | 0.83231 |  |  | 0.84368 |  |  | 0.87056 |  |  | 0.91309 |  |  | 0.9912 |  |  | 1.1772
[13 empty] | C Non choked w/ reducers | 7 |  | 0.30754 |  |  | 7.3381 |  |  | 18.1409 |  |  | 36.2929 |  |  | 64.9767 |  |  | 107.4077 |  |  | 177.9222 |  |  | 312.866 |  |  | 1207.3154 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.27531 |  |  | 6.5661 |  |  | 16.2455 |  |  | 32.4161 |  |  | 57.508 |  |  | 93.0375 |  |  | 144.7107 |  |  | 218.6975 |  |  | 291.468 |  |  | 698.8376
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.30754 |  |  | 7.3381 |  |  | 18.1409 |  |  | 36.2929 |  |  | 64.9767 |  |  | 107.4077 |  |  | 177.9222 |  |  | 312.866 |  |  | 1207.3154 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4225 | 761.5426 |  | 4.2619 | 18140.8808 |  | 4.8591 | 44420.3536 |  | 3.1071 | 86519.5107 |  | 3.9767 | 145152.8245 |  | 19.2077 | 211854.5008 |  | 56.9222 | 282720.6526 |  | 147.866 | 344972.9244 |  | 961.3154 | 400502.8557 |  | 236393 | 469621.0958
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 776.7735 | C_100 - C this iteration | iteration | 18322.2896 | C_100 - C this iteration | iteration | 44864.5571 | C_100 - C this iteration | iteration | 87384.7058 | C_100 - C this iteration | iteration | 146604.3528 | C_100 - C this iteration | iteration | 213973.0458 | C_100 - C this iteration | iteration | 285547.8591 | C_100 - C this iteration | iteration | 348422.6537 | C_100 - C this iteration | iteration | 404507.8842 | C_100 - C this iteration | iteration | 474317.3068 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1239 |  |  | 89.8182 |  |  | 88.7933 |  |  | 86.2677 |  |  | 81.8403 |  |  | 75.3239 |  |  | 68.0589 |  |  | 60.3623 |  |  | 49.1805
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1239 |  |  | 29.8182 |  |  | 28.7933 |  |  | 26.2677 |  |  | 21.8403 |  |  | 15.3239 |  |  | 8.0589 |  |  | 0.3623 |  |  | -10.8195
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33425 |  |  | 0.33198 |  |  | 0.32427 |  |  | 0.30449 |  |  | 0.26687 |  |  | 0.20344 |  |  | 0.11841 |  |  | 0.0060021 |  |  | -0.21999
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82596 |  |  | 0.82549 |  |  | 0.82714 |  |  | 0.83266 |  |  | 0.84453 |  |  | 0.87249 |  |  | 0.91702 |  |  | 0.99661 |  |  | 1.1947
[13 empty] | C Non choked w/ reducers | 7 |  | 0.31369 |  |  | 7.4117 |  |  | 18.3247 |  |  | 36.674 |  |  | 65.7252 |  |  | 108.8881 |  |  | 181.3597 |  |  | 324.0714 |  |  | 1973.2951 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.28082 |  |  | 6.6318 |  |  | 16.4093 |  |  | 32.7504 |  |  | 58.1351 |  |  | 94.1567 |  |  | 146.726 |  |  | 222.2994 |  |  | 297.2485 |  |  | 717.4214
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.31369 |  |  | 7.4117 |  |  | 18.3247 |  |  | 36.674 |  |  | 65.7252 |  |  | 108.8881 |  |  | 181.3597 |  |  | 324.0714 |  |  | 1973.2951 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4163 | 776.7735 |  | 4.1883 | 18322.2896 |  | 4.6753 | 44864.5571 |  | 2.726 | 87384.7058 |  | 4.7252 | 146604.3528 |  | 20.6881 | 213973.0458 |  | 60.3597 | 285547.8591 |  | 159.0714 | 348422.6537 |  | 1727.2951 | 404507.8842 |  | 236393 | 474317.3068
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 792.309 | C_100 - C this iteration | iteration | 18505.5125 | C_100 - C this iteration | iteration | 45313.2027 | C_100 - C this iteration | iteration | 88258.5528 | C_100 - C this iteration | iteration | 148070.3963 | C_100 - C this iteration | iteration | 216112.7763 | C_100 - C this iteration | iteration | 288403.3377 | C_100 - C this iteration | iteration | 351906.8802 | C_100 - C this iteration | iteration | 408552.9631 | C_100 - C this iteration | iteration | 479060.4798 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1226 |  |  | 89.8108 |  |  | 88.7653 |  |  | 86.189 |  |  | 81.6726 |  |  | 75.0252 |  |  | 67.6141 |  |  | 59.7629 |  |  | 48.3564
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1226 |  |  | 29.8108 |  |  | 28.7653 |  |  | 26.189 |  |  | 21.6726 |  |  | 15.0252 |  |  | 7.6141 |  |  | -0.23713 |  |  | -11.6436
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33424 |  |  | 0.33193 |  |  | 0.32406 |  |  | 0.30386 |  |  | 0.26536 |  |  | 0.20027 |  |  | 0.11261 |  |  | -0.0039679 |  |  | -0.24079
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82596 |  |  | 0.82552 |  |  | 0.82726 |  |  | 0.833 |  |  | 0.84541 |  |  | 0.87448 |  |  | 0.92108 |  |  | 1.0022 |  |  | 1.2131
[13 empty] | C Non choked w/ reducers | 7 |  | 0.31997 |  |  | 7.486 |  |  | 18.5103 |  |  | 37.0595 |  |  | 66.4847 |  |  | 110.4004 |  |  | 184.9317 |  |  | 336.3506 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.28643 |  |  | 6.6983 |  |  | 16.5748 |  |  | 33.0883 |  |  | 58.7701 |  |  | 95.2936 |  |  | 148.7832 |  |  | 225.9992 |  |  | 303.2323 |  |  | 736.9457
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.31997 |  |  | 7.486 |  |  | 18.5103 |  |  | 37.0595 |  |  | 66.4847 |  |  | 110.4004 |  |  | 184.9317 |  |  | 336.3506 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.41 | 792.309 |  | 4.114 | 18505.5125 |  | 4.4897 | 45313.2027 |  | 2.3405 | 88258.5528 |  | 5.4847 | 148070.3963 |  | 22.2004 | 216112.7763 |  | 63.9317 | 288403.3377 |  | 171.3506 | 351906.8802 |  | 236393 | 408552.9631 |  | 236393 | 479060.4798
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 808.1551 | C_100 - C this iteration | iteration | 18690.5677 | C_100 - C this iteration | iteration | 45766.3347 | C_100 - C this iteration | iteration | 89141.1384 | C_100 - C this iteration | iteration | 149551.1003 | C_100 - C this iteration | iteration | 218273.9041 | C_100 - C this iteration | iteration | 291287.3711 | C_100 - C this iteration | iteration | 355425.949 | C_100 - C this iteration | iteration | 412638.4927 | C_100 - C this iteration | iteration | 483851.0846 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1214 |  |  | 89.8033 |  |  | 88.7368 |  |  | 86.1087 |  |  | 81.5015 |  |  | 74.7205 |  |  | 67.1605 |  |  | 59.1514 |  |  | 47.5156
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1214 |  |  | 29.8033 |  |  | 28.7368 |  |  | 26.1087 |  |  | 21.5015 |  |  | 14.7205 |  |  | 7.1605 |  |  | -0.84862 |  |  | -12.4844
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33423 |  |  | 0.33187 |  |  | 0.32384 |  |  | 0.30321 |  |  | 0.26382 |  |  | 0.19701 |  |  | 0.10662 |  |  | -0.014347 |  |  | -0.26274
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82597 |  |  | 0.82555 |  |  | 0.82737 |  |  | 0.83336 |  |  | 0.84631 |  |  | 0.87652 |  |  | 0.92529 |  |  | 1.0081 |  |  | 1.2325
[13 empty] | C Non choked w/ reducers | 7 |  | 0.32637 |  |  | 7.561 |  |  | 18.6979 |  |  | 37.4494 |  |  | 67.2553 |  |  | 111.9457 |  |  | 188.6477 |  |  | 349.8962 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.29216 |  |  | 6.7653 |  |  | 16.7419 |  |  | 33.4299 |  |  | 59.4132 |  |  | 96.4485 |  |  | 150.8839 |  |  | 229.8011 |  |  | 309.4306 |  |  | 757.4853
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.32637 |  |  | 7.561 |  |  | 18.6979 |  |  | 37.4494 |  |  | 67.2553 |  |  | 111.9457 |  |  | 188.6477 |  |  | 349.8962 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4036 | 808.1551 |  | 4.039 | 18690.5677 |  | 4.3021 | 45766.3347 |  | 1.9506 | 89141.1384 |  | 6.2553 | 149551.1003 |  | 23.7457 | 218273.9041 |  | 67.6477 | 291287.3711 |  | 184.8962 | 355425.949 |  | 236393 | 412638.4927 |  | 236393 | 483851.0846
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 824.3182 | C_100 - C this iteration | iteration | 18877.4733 | C_100 - C this iteration | iteration | 46223.9981 | C_100 - C this iteration | iteration | 90032.5497 | C_100 - C this iteration | iteration | 151046.6113 | C_100 - C this iteration | iteration | 220456.6431 | C_100 - C this iteration | iteration | 294200.2448 | C_100 - C this iteration | iteration | 358980.2085 | C_100 - C this iteration | iteration | 416764.8776 | C_100 - C this iteration | iteration | 488689.5955 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1201 |  |  | 89.7956 |  |  | 88.7077 |  |  | 86.0267 |  |  | 81.327 |  |  | 74.4097 |  |  | 66.6977 |  |  | 58.5276 |  |  | 46.6579
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1201 |  |  | 29.7956 |  |  | 28.7077 |  |  | 26.0267 |  |  | 21.327 |  |  | 14.4097 |  |  | 6.6977 |  |  | -1.4724 |  |  | -13.3421
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33422 |  |  | 0.33182 |  |  | 0.32362 |  |  | 0.30254 |  |  | 0.26224 |  |  | 0.19365 |  |  | 0.10042 |  |  | -0.025157 |  |  | -0.28595
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82597 |  |  | 0.82558 |  |  | 0.82749 |  |  | 0.83373 |  |  | 0.84723 |  |  | 0.87863 |  |  | 0.92963 |  |  | 1.0142 |  |  | 1.253
[13 empty] | C Non choked w/ reducers | 7 |  | 0.33289 |  |  | 7.6368 |  |  | 18.8874 |  |  | 37.8439 |  |  | 68.0373 |  |  | 113.5251 |  |  | 192.5183 |  |  | 364.9528 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.298 |  |  | 6.8331 |  |  | 16.9108 |  |  | 33.7753 |  |  | 60.0644 |  |  | 97.6221 |  |  | 153.0293 |  |  | 233.7096 |  |  | 315.8558 |  |  | 779.1234
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.33289 |  |  | 7.6368 |  |  | 18.8874 |  |  | 37.8439 |  |  | 68.0373 |  |  | 113.5251 |  |  | 192.5183 |  |  | 364.9528 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3971 | 824.3182 |  | 3.9632 | 18877.4733 |  | 4.1126 | 46223.9981 |  | 1.5561 | 90032.5497 |  | 7.0373 | 151046.6113 |  | 25.3251 | 220456.6431 |  | 71.5183 | 294200.2448 |  | 199.9528 | 358980.2085 |  | 236393 | 416764.8776 |  | 236393 | 488689.5955
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 840.8046 | C_100 - C this iteration | iteration | 19066.2481 | C_100 - C this iteration | iteration | 46686.238 | C_100 - C this iteration | iteration | 90932.8752 | C_100 - C this iteration | iteration | 152557.0774 | C_100 - C this iteration | iteration | 222661.2095 | C_100 - C this iteration | iteration | 297142.2473 | C_100 - C this iteration | iteration | 362570.0106 | C_100 - C this iteration | iteration | 420932.5264 | C_100 - C this iteration | iteration | 493576.4914 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1188 |  |  | 89.7878 |  |  | 88.678 |  |  | 85.9432 |  |  | 81.1489 |  |  | 74.0926 |  |  | 66.2256 |  |  | 57.8913 |  |  | 45.783
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1188 |  |  | 29.7878 |  |  | 28.678 |  |  | 25.9432 |  |  | 21.1489 |  |  | 14.0926 |  |  | 6.2256 |  |  | -2.1087 |  |  | -14.217
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33421 |  |  | 0.33176 |  |  | 0.32339 |  |  | 0.30186 |  |  | 0.26062 |  |  | 0.1902 |  |  | 0.094005 |  |  | -0.036425 |  |  | -0.31053
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82598 |  |  | 0.82561 |  |  | 0.82761 |  |  | 0.8341 |  |  | 0.84817 |  |  | 0.88079 |  |  | 0.93412 |  |  | 1.0206 |  |  | 1.2748
[13 empty] | C Non choked w/ reducers | 7 |  | 0.33955 |  |  | 7.7133 |  |  | 19.0789 |  |  | 38.2429 |  |  | 68.831 |  |  | 115.1401 |  |  | 196.5552 |  |  | 381.8374 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.30396 |  |  | 6.9015 |  |  | 17.0814 |  |  | 34.1245 |  |  | 60.7241 |  |  | 98.8146 |  |  | 155.2211 |  |  | 237.7293 |  |  | 322.5208 |  |  | 801.9522
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.33955 |  |  | 7.7133 |  |  | 19.0789 |  |  | 38.2429 |  |  | 68.831 |  |  | 115.1401 |  |  | 196.5552 |  |  | 381.8374 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3904 | 840.8046 |  | 3.8867 | 19066.2481 |  | 3.9211 | 46686.238 |  | 1.1571 | 90932.8752 |  | 7.831 | 152557.0774 |  | 26.9401 | 222661.2095 |  | 75.5552 | 297142.2473 |  | 216.8374 | 362570.0106 |  | 236393 | 420932.5264 |  | 236393 | 493576.4914
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 857.6207 | C_100 - C this iteration | iteration | 19256.9106 | C_100 - C this iteration | iteration | 47153.1004 | C_100 - C this iteration | iteration | 91842.204 | C_100 - C this iteration | iteration | 154082.6482 | C_100 - C this iteration | iteration | 224887.8216 | C_100 - C this iteration | iteration | 300113.6697 | C_100 - C this iteration | iteration | 366195.7107 | C_100 - C this iteration | iteration | 425141.8517 | C_100 - C this iteration | iteration | 498512.2564 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1175 |  |  | 89.7798 |  |  | 88.6477 |  |  | 85.8579 |  |  | 80.9673 |  |  | 73.7691 |  |  | 65.744 |  |  | 57.2422 |  |  | 44.8906
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1175 |  |  | 29.7798 |  |  | 28.6477 |  |  | 25.8579 |  |  | 20.9673 |  |  | 13.7691 |  |  | 5.744 |  |  | -2.7578 |  |  | -15.1094
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.3342 |  |  | 0.3317 |  |  | 0.32316 |  |  | 0.30117 |  |  | 0.25896 |  |  | 0.18665 |  |  | 0.087369 |  |  | -0.048178 |  |  | -0.33658
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82598 |  |  | 0.82564 |  |  | 0.82774 |  |  | 0.83448 |  |  | 0.84914 |  |  | 0.88301 |  |  | 0.93877 |  |  | 1.0272 |  |  | 1.2978
[13 empty] | C Non choked w/ reducers | 7 |  | 0.34634 |  |  | 7.7906 |  |  | 19.2724 |  |  | 38.6466 |  |  | 69.6365 |  |  | 116.792 |  |  | 200.7716 |  |  | 400.9689 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.31004 |  |  | 6.9706 |  |  | 17.2537 |  |  | 34.4775 |  |  | 61.3922 |  |  | 100.0267 |  |  | 157.4607 |  |  | 241.8655 |  |  | 329.4398 |  |  | 826.075
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.34634 |  |  | 7.7906 |  |  | 19.2724 |  |  | 38.6466 |  |  | 69.6365 |  |  | 116.792 |  |  | 200.7716 |  |  | 400.9689 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3837 | 857.6207 |  | 3.8094 | 19256.9106 |  | 3.7276 | 47153.1004 |  | 0.75339 | 91842.204 |  | 8.6365 | 154082.6482 |  | 28.592 | 224887.8216 |  | 79.7716 | 300113.6697 |  | 235.9689 | 366195.7107 |  | 236393 | 425141.8517 |  | 236393 | 498512.2564
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 874.7731 | C_100 - C this iteration | iteration | 19449.4797 | C_100 - C this iteration | iteration | 47624.6314 | C_100 - C this iteration | iteration | 92760.626 | C_100 - C this iteration | iteration | 155623.4747 | C_100 - C this iteration | iteration | 227136.6998 | C_100 - C this iteration | iteration | 303114.8064 | C_100 - C this iteration | iteration | 369857.6678 | C_100 - C this iteration | iteration | 429393.2702 | C_100 - C this iteration | iteration | 503497.3789 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1161 |  |  | 89.7717 |  |  | 88.6168 |  |  | 85.7709 |  |  | 80.782 |  |  | 73.4392 |  |  | 65.2527 |  |  | 56.58 |  |  | 43.9801
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1161 |  |  | 29.7717 |  |  | 28.6168 |  |  | 25.7709 |  |  | 20.782 |  |  | 13.4392 |  |  | 5.2527 |  |  | -3.42 |  |  | -16.0199
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33419 |  |  | 0.33164 |  |  | 0.32293 |  |  | 0.30046 |  |  | 0.25726 |  |  | 0.183 |  |  | 0.080498 |  |  | -0.060445 |  |  | -0.36425
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82599 |  |  | 0.82568 |  |  | 0.82786 |  |  | 0.83487 |  |  | 0.85013 |  |  | 0.8853 |  |  | 0.94359 |  |  | 1.0341 |  |  | 1.3223
[13 empty] | C Non choked w/ reducers | 7 |  | 0.35327 |  |  | 7.8687 |  |  | 19.468 |  |  | 39.055 |  |  | 70.4543 |  |  | 118.4822 |  |  | 205.1819 |  |  | 422.9155 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.31624 |  |  | 7.0404 |  |  | 17.4279 |  |  | 34.8344 |  |  | 62.069 |  |  | 101.2586 |  |  | 159.7498 |  |  | 246.1232 |  |  | 336.6282 |  |  | 851.607
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.35327 |  |  | 7.8687 |  |  | 19.468 |  |  | 39.055 |  |  | 70.4543 |  |  | 118.4822 |  |  | 205.1819 |  |  | 422.9155 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3767 | 874.7731 |  | 3.7313 | 19449.4797 |  | 3.532 | 47624.6314 |  | 0.34498 | 92760.626 |  | 9.4543 | 155623.4747 |  | 30.2822 | 227136.6998 |  | 84.1819 | 303114.8064 |  | 257.9155 | 369857.6678 |  | 236393 | 429393.2702 |  | 236393 | 503497.3789
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 892.2686 | C_100 - C this iteration | iteration | 19643.9745 | C_100 - C this iteration | iteration | 48100.8777 | C_100 - C this iteration | iteration | 93688.2323 | C_100 - C this iteration | iteration | 157179.7094 | C_100 - C this iteration | iteration | 229408.0668 | C_100 - C this iteration | iteration | 306145.9545 | C_100 - C this iteration | iteration | 373556.2445 | C_100 - C this iteration | iteration | 433687.2029 | C_100 - C this iteration | iteration | 508532.3527 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1147 |  |  | 89.7633 |  |  | 88.5852 |  |  | 85.6822 |  |  | 80.593 |  |  | 73.1026 |  |  | 64.7516 |  |  | 55.9046 |  |  | 43.0514
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1147 |  |  | 29.7633 |  |  | 28.5852 |  |  | 25.6822 |  |  | 20.593 |  |  | 13.1026 |  |  | 4.7516 |  |  | -4.0954 |  |  | -16.9486
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33418 |  |  | 0.33158 |  |  | 0.32269 |  |  | 0.29974 |  |  | 0.25552 |  |  | 0.17924 |  |  | 0.073382 |  |  | -0.073257 |  |  | -0.39368
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.826 |  |  | 0.82571 |  |  | 0.82799 |  |  | 0.83527 |  |  | 0.85114 |  |  | 0.88766 |  |  | 0.94858 |  |  | 1.0414 |  |  | 1.3484
[13 empty] | C Non choked w/ reducers | 7 |  | 0.36033 |  |  | 7.9476 |  |  | 19.6655 |  |  | 39.4682 |  |  | 71.2846 |  |  | 120.2123 |  |  | 209.8025 |  |  | 448.4695 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.32257 |  |  | 7.111 |  |  | 17.6038 |  |  | 35.1953 |  |  | 62.7546 |  |  | 102.5111 |  |  | 162.0902 |  |  | 250.5084 |  |  | 344.1024 |  |  | 878.6779
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.36033 |  |  | 7.9476 |  |  | 19.6655 |  |  | 39.4682 |  |  | 71.2846 |  |  | 120.2123 |  |  | 209.8025 |  |  | 448.4695 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3697 | 892.2686 |  | 3.6524 | 19643.9745 |  | 3.3345 | 48100.8777 |  | 0.068214 | 93688.2323 |  | 10.2846 | 157179.7094 |  | 32.0123 | 229408.0668 |  | 88.8025 | 306145.9545 |  | 283.4695 | 373556.2445 |  | 236393 | 433687.2029 |  | 236393 | 508532.3527
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 910.1139 | C_100 - C this iteration | iteration | 19840.4142 | C_100 - C this iteration | iteration | 48581.8865 | C_100 - C this iteration | iteration | 94625.1146 | C_100 - C this iteration | iteration | 158751.5065 | C_100 - C this iteration | iteration | 231702.1475 | C_100 - C this iteration | iteration | 309207.4141 | C_100 - C this iteration | iteration | 377291.8069 | C_100 - C this iteration | iteration | 438024.0749 | C_100 - C this iteration | iteration | 513617.6762 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1133 |  |  | 89.7549 |  |  | 88.5531 |  |  | 85.5917 |  |  | 80.4002 |  |  | 72.7592 |  |  | 64.2404 |  |  | 55.2155 |  |  | 42.104
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1133 |  |  | 29.7549 |  |  | 28.5531 |  |  | 25.5917 |  |  | 20.4002 |  |  | 12.7592 |  |  | 4.2404 |  |  | -4.7845 |  |  | -17.896
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33417 |  |  | 0.33151 |  |  | 0.32244 |  |  | 0.299 |  |  | 0.25373 |  |  | 0.17536 |  |  | 0.066008 |  |  | -0.086651 |  |  | -0.42504
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.826 |  |  | 0.82574 |  |  | 0.82812 |  |  | 0.83567 |  |  | 0.85218 |  |  | 0.89009 |  |  | 0.95374 |  |  | 1.0489 |  |  | 1.3761
[13 empty] | C Non choked w/ reducers | 7 |  | 0.36754 |  |  | 8.0273 |  |  | 19.8651 |  |  | 39.8863 |  |  | 72.1276 |  |  | 121.9839 |  |  | 214.6519 |  |  | 478.7771 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.32902 |  |  | 7.1822 |  |  | 17.7815 |  |  | 35.5601 |  |  | 63.4492 |  |  | 103.7845 |  |  | 164.4837 |  |  | 255.0269 |  |  | 351.8805 |  |  | 907.4336
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.36754 |  |  | 8.0273 |  |  | 19.8651 |  |  | 39.8863 |  |  | 72.1276 |  |  | 121.9839 |  |  | 214.6519 |  |  | 478.7771 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3625 | 910.1139 |  | 3.5727 | 19840.4142 |  | 3.1349 | 48581.8865 |  | 0.48626 | 94625.1146 |  | 11.1276 | 158751.5065 |  | 33.7839 | 231702.1475 |  | 93.6519 | 309207.4141 |  | 313.7771 | 377291.8069 |  | 236393 | 438024.0749 |  | 236393 | 513617.6762
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 928.3162 | C_100 - C this iteration | iteration | 20038.8184 | C_100 - C this iteration | iteration | 49067.7054 | C_100 - C this iteration | iteration | 95571.3658 | C_100 - C this iteration | iteration | 160339.0216 | C_100 - C this iteration | iteration | 234019.169 | C_100 - C this iteration | iteration | 312299.4882 | C_100 - C this iteration | iteration | 381064.725 | C_100 - C this iteration | iteration | 442404.3157 | C_100 - C this iteration | iteration | 518753.853 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1119 |  |  | 89.7462 |  |  | 88.5203 |  |  | 85.4994 |  |  | 80.2035 |  |  | 72.409 |  |  | 63.7189 |  |  | 54.5126 |  |  | 41.1376
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1119 |  |  | 29.7462 |  |  | 28.5203 |  |  | 25.4994 |  |  | 20.2035 |  |  | 12.409 |  |  | 3.7189 |  |  | -5.4874 |  |  | -18.8624
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33416 |  |  | 0.33145 |  |  | 0.32219 |  |  | 0.29824 |  |  | 0.2519 |  |  | 0.17137 |  |  | 0.058364 |  |  | -0.10066 |  |  | -0.45852
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82601 |  |  | 0.82578 |  |  | 0.82825 |  |  | 0.83609 |  |  | 0.85325 |  |  | 0.89259 |  |  | 0.9591 |  |  | 1.0568 |  |  | 1.4057
[13 empty] | C Non choked w/ reducers | 7 |  | 0.37489 |  |  | 8.1077 |  |  | 20.0669 |  |  | 40.3092 |  |  | 72.9837 |  |  | 123.7988 |  |  | 219.7506 |  |  | 515.5704 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.3356 |  |  | 7.2541 |  |  | 17.961 |  |  | 35.929 |  |  | 64.1529 |  |  | 105.0794 |  |  | 166.9321 |  |  | 259.6852 |  |  | 359.9818 |  |  | 938.0391
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.37489 |  |  | 8.1077 |  |  | 20.0669 |  |  | 40.3092 |  |  | 72.9837 |  |  | 123.7988 |  |  | 219.7506 |  |  | 515.5704 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3551 | 928.3162 |  | 3.4923 | 20038.8184 |  | 2.9331 | 49067.7054 |  | 0.90924 | 95571.3658 |  | 11.9837 | 160339.0216 |  | 35.5988 | 234019.169 |  | 98.7506 | 312299.4882 |  | 350.5704 | 381064.725 |  | 236393 | 442404.3157 |  | 236393 | 518753.853
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 946.8825 | C_100 - C this iteration | iteration | 20239.2065 | C_100 - C this iteration | iteration | 49558.3824 | C_100 - C this iteration | iteration | 96527.0794 | C_100 - C this iteration | iteration | 161942.4118 | C_100 - C this iteration | iteration | 236359.3607 | C_100 - C this iteration | iteration | 315422.4831 | C_100 - C this iteration | iteration | 384875.3722 | C_100 - C this iteration | iteration | 446828.3588 | C_100 - C this iteration | iteration | 523941.3915 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1104 |  |  | 89.7374 |  |  | 88.4868 |  |  | 85.4052 |  |  | 80.0029 |  |  | 72.0517 |  |  | 63.1869 |  |  | 53.7956 |  |  | 40.1518
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1104 |  |  | 29.7374 |  |  | 28.4868 |  |  | 25.4052 |  |  | 20.0029 |  |  | 12.0517 |  |  | 3.1869 |  |  | -6.2044 |  |  | -19.8482
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33415 |  |  | 0.33138 |  |  | 0.32193 |  |  | 0.29747 |  |  | 0.25003 |  |  | 0.16726 |  |  | 0.050436 |  |  | -0.11533 |  |  | -0.49433
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82601 |  |  | 0.82581 |  |  | 0.82839 |  |  | 0.83652 |  |  | 0.85434 |  |  | 0.89516 |  |  | 0.96466 |  |  | 1.0651 |  |  | 1.4374
[13 empty] | C Non choked w/ reducers | 7 |  | 0.38239 |  |  | 8.189 |  |  | 20.2707 |  |  | 40.7372 |  |  | 73.8532 |  |  | 125.6588 |  |  | 225.1223 |  |  | 561.6203 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.34231 |  |  | 7.3268 |  |  | 18.1424 |  |  | 36.3021 |  |  | 64.8659 |  |  | 106.3963 |  |  | 169.4375 |  |  | 264.4902 |  |  | 368.4276 |  |  | 970.6816
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.38239 |  |  | 8.189 |  |  | 20.2707 |  |  | 40.7372 |  |  | 73.8532 |  |  | 125.6588 |  |  | 225.1223 |  |  | 561.6203 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3476 | 946.8825 |  | 3.411 | 20239.2065 |  | 2.7293 | 49558.3824 |  | 1.3372 | 96527.0794 |  | 12.8532 | 161942.4118 |  | 37.4588 | 236359.3607 |  | 104.1223 | 315422.4831 |  | 396.6203 | 384875.3722 |  | 236393 | 446828.3588 |  | 236393 | 523941.3915
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 965.8202 | C_100 - C this iteration | iteration | 20441.5986 | C_100 - C this iteration | iteration | 50053.9663 | C_100 - C this iteration | iteration | 97492.3502 | C_100 - C this iteration | iteration | 163561.8359 | C_100 - C this iteration | iteration | 238722.9543 | C_100 - C this iteration | iteration | 318576.7079 | C_100 - C this iteration | iteration | 388724.126 | C_100 - C this iteration | iteration | 451296.6424 | C_100 - C this iteration | iteration | 529180.8054 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1089 |  |  | 89.7284 |  |  | 88.4527 |  |  | 85.3091 |  |  | 79.7982 |  |  | 71.6872 |  |  | 62.6442 |  |  | 53.0642 |  |  | 39.1461
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1089 |  |  | 29.7284 |  |  | 28.4527 |  |  | 25.3091 |  |  | 19.7982 |  |  | 11.6872 |  |  | 2.6442 |  |  | -6.9358 |  |  | -20.8539
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33414 |  |  | 0.33132 |  |  | 0.32167 |  |  | 0.29668 |  |  | 0.2481 |  |  | 0.16303 |  |  | 0.04221 |  |  | -0.13071 |  |  | -0.53272
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82602 |  |  | 0.82584 |  |  | 0.82853 |  |  | 0.83695 |  |  | 0.85546 |  |  | 0.89782 |  |  | 0.97042 |  |  | 1.0738 |  |  | 1.4714
[13 empty] | C Non choked w/ reducers | 7 |  | 0.39004 |  |  | 8.2711 |  |  | 20.4766 |  |  | 41.1703 |  |  | 74.7364 |  |  | 127.5659 |  |  | 230.7939 |  |  | 621.704 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.34916 |  |  | 7.4002 |  |  | 18.3257 |  |  | 36.6792 |  |  | 65.5883 |  |  | 107.7359 |  |  | 172.002 |  |  | 269.4492 |  |  | 377.241 |  |  | 1005.5747
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.39004 |  |  | 8.2711 |  |  | 20.4766 |  |  | 41.1703 |  |  | 74.7364 |  |  | 127.5659 |  |  | 230.7939 |  |  | 621.704 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.34 | 965.8202 |  | 3.3289 | 20441.5986 |  | 2.5234 | 50053.9663 |  | 1.7703 | 97492.3502 |  | 13.7364 | 163561.8359 |  | 39.3659 | 238722.9543 |  | 109.7939 | 318576.7079 |  | 456.704 | 388724.126 |  | 236393 | 451296.6424 |  | 236393 | 529180.8054
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 985.1366 | C_100 - C this iteration | iteration | 20646.0146 | C_100 - C this iteration | iteration | 50554.5059 | C_100 - C this iteration | iteration | 98467.2737 | C_100 - C this iteration | iteration | 165197.4543 | C_100 - C this iteration | iteration | 241110.1838 | C_100 - C this iteration | iteration | 321762.475 | C_100 - C this iteration | iteration | 392611.3672 | C_100 - C this iteration | iteration | 455809.6089 | C_100 - C this iteration | iteration | 534472.6135 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1074 |  |  | 89.7192 |  |  | 88.4179 |  |  | 85.2111 |  |  | 79.5895 |  |  | 71.3154 |  |  | 62.0907 |  |  | 52.3181 |  |  | 38.1202
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1074 |  |  | 29.7192 |  |  | 28.4179 |  |  | 25.2111 |  |  | 19.5895 |  |  | 11.3154 |  |  | 2.0907 |  |  | -7.6819 |  |  | -21.8798
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33413 |  |  | 0.33125 |  |  | 0.3214 |  |  | 0.29587 |  |  | 0.24613 |  |  | 0.15867 |  |  | 0.033671 |  |  | -0.14683 |  |  | -0.57397
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82602 |  |  | 0.82588 |  |  | 0.82867 |  |  | 0.8374 |  |  | 0.85661 |  |  | 0.90055 |  |  | 0.9764 |  |  | 1.0829 |  |  | 1.5079
[13 empty] | C Non choked w/ reducers | 7 |  | 0.39784 |  |  | 8.3541 |  |  | 20.6848 |  |  | 41.6085 |  |  | 75.6336 |  |  | 129.5221 |  |  | 236.796 |  |  | 704.9693 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.35614 |  |  | 7.4743 |  |  | 18.5108 |  |  | 37.0606 |  |  | 66.3204 |  |  | 109.0987 |  |  | 174.6277 |  |  | 274.57 |  |  | 386.4472 |  |  | 1042.9629
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.39784 |  |  | 8.3541 |  |  | 20.6848 |  |  | 41.6085 |  |  | 75.6336 |  |  | 129.5221 |  |  | 236.796 |  |  | 704.9693 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3322 | 985.1366 |  | 3.2459 | 20646.0146 |  | 2.3152 | 50554.5059 |  | 2.2085 | 98467.2737 |  | 14.6336 | 165197.4543 |  | 41.3221 | 241110.1838 |  | 115.796 | 321762.475 |  | 539.9693 | 392611.3672 |  | 236393 | 455809.6089 |  | 236393 | 534472.6135
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1004.8393 | C_100 - C this iteration | iteration | 20852.4747 | C_100 - C this iteration | iteration | 51060.051 | C_100 - C this iteration | iteration | 99451.9465 | C_100 - C this iteration | iteration | 166849.4288 | C_100 - C this iteration | iteration | 243521.2857 | C_100 - C this iteration | iteration | 324980.0997 | C_100 - C this iteration | iteration | 396537.4809 | C_100 - C this iteration | iteration | 460367.7049 | C_100 - C this iteration | iteration | 539817.3396 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1849 |  |  | 90.1058 |  |  | 89.7099 |  |  | 88.3824 |  |  | 85.1111 |  |  | 79.3765 |  |  | 70.9361 |  |  | 61.526 |  |  | 51.557 |  |  | 37.0737
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1849 |  |  | 30.1058 |  |  | 29.7099 |  |  | 28.3824 |  |  | 25.1111 |  |  | 19.3765 |  |  | 10.9361 |  |  | 1.526 |  |  | -8.443 |  |  | -22.9263
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33412 |  |  | 0.33118 |  |  | 0.32113 |  |  | 0.29504 |  |  | 0.24411 |  |  | 0.15417 |  |  | 0.024802 |  |  | -0.16376 |  |  | -0.6184
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82603 |  |  | 0.82592 |  |  | 0.82882 |  |  | 0.83785 |  |  | 0.85779 |  |  | 0.90337 |  |  | 0.98262 |  |  | 1.0924 |  |  | 1.5472
[13 empty] | C Non choked w/ reducers | 7 |  | 0.4058 |  |  | 8.4378 |  |  | 20.8951 |  |  | 42.0519 |  |  | 76.5453 |  |  | 131.5297 |  |  | 243.1641 |  |  | 831.9343 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.36326 |  |  | 7.5492 |  |  | 18.6979 |  |  | 37.4463 |  |  | 67.0623 |  |  | 110.4853 |  |  | 177.3171 |  |  | 279.861 |  |  | 396.0738 |  |  | 1083.1273
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.4058 |  |  | 8.4378 |  |  | 20.8951 |  |  | 42.0519 |  |  | 76.5453 |  |  | 131.5297 |  |  | 243.1641 |  |  | 831.9343 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3242 | 1004.8393 |  | 3.1622 | 20852.4747 |  | 2.1049 | 51060.051 |  | 2.6519 | 99451.9465 |  | 15.5453 | 166849.4288 |  | 43.3297 | 243521.2857 |  | 122.1641 | 324980.0997 |  | 666.9343 | 396537.4809 |  | 236393 | 460367.7049 |  | 236393 | 539817.3396
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1024.9361 | C_100 - C this iteration | iteration | 21060.9995 | C_100 - C this iteration | iteration | 51570.6515 | C_100 - C this iteration | iteration | 100446.4659 | C_100 - C this iteration | iteration | 168517.9231 | C_100 - C this iteration | iteration | 245956.4985 | C_100 - C this iteration | iteration | 328229.9007 | C_100 - C this iteration | iteration | 400502.8557 | C_100 - C this iteration | iteration | 464971.382 | C_100 - C this iteration | iteration | 545215.513 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1848 |  |  | 90.1042 |  |  | 89.7003 |  |  | 88.3461 |  |  | 85.0091 |  |  | 79.1592 |  |  | 70.5492 |  |  | 60.9499 |  |  | 50.7805 |  |  | 36.0062
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1848 |  |  | 30.1042 |  |  | 29.7003 |  |  | 28.3461 |  |  | 25.0091 |  |  | 19.1592 |  |  | 10.5492 |  |  | 0.94993 |  |  | -9.2195 |  |  | -23.9938
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.3341 |  |  | 0.33111 |  |  | 0.32085 |  |  | 0.29419 |  |  | 0.24203 |  |  | 0.14953 |  |  | 0.015585 |  |  | -0.18156 |  |  | -0.66638
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82604 |  |  | 0.82596 |  |  | 0.82897 |  |  | 0.83831 |  |  | 0.859 |  |  | 0.90628 |  |  | 0.98908 |  |  | 1.1025 |  |  | 1.5897
[13 empty] | C Non choked w/ reducers | 7 |  | 0.41391 |  |  | 8.5225 |  |  | 21.1076 |  |  | 42.5007 |  |  | 77.4717 |  |  | 133.591 |  |  | 249.9393 |  |  | 1063.0071 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.37053 |  |  | 7.6248 |  |  | 18.8869 |  |  | 37.8362 |  |  | 67.8142 |  |  | 111.8964 |  |  | 180.0724 |  |  | 285.331 |  |  | 406.151 |  |  | 1126.3931
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.41391 |  |  | 8.5225 |  |  | 21.1076 |  |  | 42.5007 |  |  | 77.4717 |  |  | 133.591 |  |  | 249.9393 |  |  | 1063.0071 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3161 | 1024.9361 |  | 3.0775 | 21060.9995 |  | 1.8924 | 51570.6515 |  | 3.1007 | 100446.4659 |  | 16.4717 | 168517.9231 |  | 45.391 | 245956.4985 |  | 128.9393 | 328229.9007 |  | 898.0071 | 400502.8557 |  | 236393 | 464971.382 |  | 236393 | 545215.513
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1045.4348 | C_100 - C this iteration | iteration | 21271.6095 | C_100 - C this iteration | iteration | 52086.358 | C_100 - C this iteration | iteration | 101450.9306 | C_100 - C this iteration | iteration | 170203.1023 | C_100 - C this iteration | iteration | 248416.0635 | C_100 - C this iteration | iteration | 331512.1997 | C_100 - C this iteration | iteration | 404507.8842 | C_100 - C this iteration | iteration | 469621.0958 | C_100 - C this iteration | iteration | 550667.6682 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1848 |  |  | 90.1026 |  |  | 89.6906 |  |  | 88.3092 |  |  | 84.9051 |  |  | 78.9376 |  |  | 70.1545 |  |  | 60.3623 |  |  | 49.9885 |  |  | 34.9172
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1848 |  |  | 30.1026 |  |  | 29.6906 |  |  | 28.3092 |  |  | 24.9051 |  |  | 18.9376 |  |  | 10.1545 |  |  | 0.3623 |  |  | -10.0115 |  |  | -25.0828
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33409 |  |  | 0.33103 |  |  | 0.32057 |  |  | 0.29333 |  |  | 0.23991 |  |  | 0.14474 |  |  | 0.0060021 |  |  | -0.20028 |  |  | -0.71835
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82604 |  |  | 0.82599 |  |  | 0.82912 |  |  | 0.83879 |  |  | 0.86024 |  |  | 0.90928 |  |  | 0.99579 |  |  | 1.113 |  |  | 1.6357
[13 empty] | C Non choked w/ reducers | 7 |  | 0.42219 |  |  | 8.6079 |  |  | 21.3223 |  |  | 42.9548 |  |  | 78.4132 |  |  | 135.7086 |  |  | 257.1695 |  |  | 1735.131 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.37794 |  |  | 7.7012 |  |  | 19.0778 |  |  | 38.2306 |  |  | 68.5762 |  |  | 113.3327 |  |  | 182.8963 |  |  | 290.9898 |  |  | 416.712 |  |  | 1173.1382
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.42219 |  |  | 8.6079 |  |  | 21.3223 |  |  | 42.9548 |  |  | 78.4132 |  |  | 135.7086 |  |  | 257.1695 |  |  | 1735.131 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3078 | 1045.4348 |  | 2.9921 | 21271.6095 |  | 1.6777 | 52086.358 |  | 3.5548 | 101450.9306 |  | 17.4132 | 170203.1023 |  | 47.5086 | 248416.0635 |  | 136.1695 | 331512.1997 |  | 1570.131 | 404507.8842 |  | 236393 | 469621.0958 |  | 236393 | 550667.6682
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1066.3435 | C_100 - C this iteration | iteration | 21484.3256 | C_100 - C this iteration | iteration | 52607.2216 | C_100 - C this iteration | iteration | 102465.4399 | C_100 - C this iteration | iteration | 171905.1333 | C_100 - C this iteration | iteration | 250900.2241 | C_100 - C this iteration | iteration | 334827.3217 | C_100 - C this iteration | iteration | 408552.9631 | C_100 - C this iteration | iteration | 474317.3068 | C_100 - C this iteration | iteration | 556174.3448 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1848 |  |  | 90.1009 |  |  | 89.6806 |  |  | 88.2715 |  |  | 84.799 |  |  | 78.7115 |  |  | 69.7519 |  |  | 59.7629 |  |  | 49.1805 |  |  | 33.8063
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1848 |  |  | 30.1009 |  |  | 29.6806 |  |  | 28.2715 |  |  | 24.799 |  |  | 18.7115 |  |  | 9.7519 |  |  | -0.23713 |  |  | -10.8195 |  |  | -26.1937
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33408 |  |  | 0.33096 |  |  | 0.32028 |  |  | 0.29244 |  |  | 0.23772 |  |  | 0.13981 |  |  | -0.0039679 |  |  | -0.21999 |  |  | -0.77482
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82605 |  |  | 0.82603 |  |  | 0.82927 |  |  | 0.83928 |  |  | 0.86151 |  |  | 0.91237 |  |  | 1.0028 |  |  | 1.1242 |  |  | 1.6856
[13 empty] | C Non choked w/ reducers | 7 |  | 0.43063 |  |  | 8.6943 |  |  | 21.5393 |  |  | 43.4145 |  |  | 79.3703 |  |  | 137.8853 |  |  | 264.9112 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.3855 |  |  | 7.7783 |  |  | 19.2707 |  |  | 38.6294 |  |  | 69.3487 |  |  | 114.7948 |  |  | 185.7915 |  |  | 296.8476 |  |  | 427.7934 |  |  | 1223.8047
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.43063 |  |  | 8.6943 |  |  | 21.5393 |  |  | 43.4145 |  |  | 79.3703 |  |  | 137.8853 |  |  | 264.9112 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2994 | 1066.3435 |  | 2.9057 | 21484.3256 |  | 1.4607 | 52607.2216 |  | 4.0145 | 102465.4399 |  | 18.3703 | 171905.1333 |  | 49.6853 | 250900.2241 |  | 143.9112 | 334827.3217 |  | 236393 | 408552.9631 |  | 236393 | 474317.3068 |  | 236393 | 556174.3448
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1087.6704 | C_100 - C this iteration | iteration | 21699.1688 | C_100 - C this iteration | iteration | 53133.2938 | C_100 - C this iteration | iteration | 103490.0943 | C_100 - C this iteration | iteration | 173624.1847 | C_100 - C this iteration | iteration | 253409.2264 | C_100 - C this iteration | iteration | 338175.595 | C_100 - C this iteration | iteration | 412638.4927 | C_100 - C this iteration | iteration | 479060.4798 | C_100 - C this iteration | iteration | 561736.0883 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1848 |  |  | 90.0992 |  |  | 89.6705 |  |  | 88.233 |  |  | 84.6907 |  |  | 78.4809 |  |  | 69.3412 |  |  | 59.1514 |  |  | 48.3564 |  |  | 32.6731
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1848 |  |  | 30.0992 |  |  | 29.6705 |  |  | 28.233 |  |  | 24.6907 |  |  | 18.4809 |  |  | 9.3412 |  |  | -0.84862 |  |  | -11.6436 |  |  | -27.3269
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33407 |  |  | 0.33088 |  |  | 0.31998 |  |  | 0.29154 |  |  | 0.23548 |  |  | 0.13471 |  |  | -0.014347 |  |  | -0.24079 |  |  | -0.83637
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82606 |  |  | 0.82607 |  |  | 0.82943 |  |  | 0.83977 |  |  | 0.86282 |  |  | 0.91557 |  |  | 1.0101 |  |  | 1.1359 |  |  | 1.7401
[13 empty] | C Non choked w/ reducers | 7 |  | 0.43925 |  |  | 8.7815 |  |  | 21.7586 |  |  | 43.8797 |  |  | 80.3433 |  |  | 140.1238 |  |  | 273.2311 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.39321 |  |  | 7.8563 |  |  | 19.4656 |  |  | 39.0327 |  |  | 70.1317 |  |  | 116.2834 |  |  | 188.7609 |  |  | 302.9155 |  |  | 439.4356 |  |  | 1278.9129
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.43925 |  |  | 8.7815 |  |  | 21.7586 |  |  | 43.8797 |  |  | 80.3433 |  |  | 140.1238 |  |  | 273.2311 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2908 | 1087.6704 |  | 2.8185 | 21699.1688 |  | 1.2414 | 53133.2938 |  | 4.4797 | 103490.0943 |  | 19.3433 | 173624.1847 |  | 51.9238 | 253409.2264 |  | 152.2311 | 338175.595 |  | 236393 | 412638.4927 |  | 236393 | 479060.4798 |  | 236393 | 561736.0883
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1109.4238 | C_100 - C this iteration | iteration | 21916.1605 | C_100 - C this iteration | iteration | 53664.6267 | C_100 - C this iteration | iteration | 104524.9952 | C_100 - C this iteration | iteration | 175360.4265 | C_100 - C this iteration | iteration | 255943.3186 | C_100 - C this iteration | iteration | 341557.3509 | C_100 - C this iteration | iteration | 416764.8776 | C_100 - C this iteration | iteration | 483851.0846 | C_100 - C this iteration | iteration | 567353.4492 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1848 |  |  | 90.0975 |  |  | 89.6601 |  |  | 88.1938 |  |  | 84.5803 |  |  | 78.2457 |  |  | 68.9222 |  |  | 58.5276 |  |  | 47.5156 |  |  | 31.5171
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1848 |  |  | 30.0975 |  |  | 29.6601 |  |  | 28.1938 |  |  | 24.5803 |  |  | 18.2457 |  |  | 8.9222 |  |  | -1.4724 |  |  | -12.4844 |  |  | -28.4829
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33405 |  |  | 0.33081 |  |  | 0.31968 |  |  | 0.29061 |  |  | 0.23318 |  |  | 0.12945 |  |  | -0.025157 |  |  | -0.26274 |  |  | -0.90373
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82606 |  |  | 0.82611 |  |  | 0.82959 |  |  | 0.84028 |  |  | 0.86415 |  |  | 0.91886 |  |  | 1.0176 |  |  | 1.1483 |  |  | 1.7997
[13 empty] | C Non choked w/ reducers | 7 |  | 0.44803 |  |  | 8.8695 |  |  | 21.9802 |  |  | 44.3506 |  |  | 81.3327 |  |  | 142.4275 |  |  | 282.2091 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.40107 |  |  | 7.935 |  |  | 19.6626 |  |  | 39.4406 |  |  | 70.9255 |  |  | 117.7993 |  |  | 191.8074 |  |  | 309.2053 |  |  | 451.6833 |  |  | 1339.0794
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.44803 |  |  | 8.8695 |  |  | 21.9802 |  |  | 44.3506 |  |  | 81.3327 |  |  | 142.4275 |  |  | 282.2091 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.282 | 1109.4238 |  | 2.7305 | 21916.1605 |  | 1.0198 | 53664.6267 |  | 4.9506 | 104524.9952 |  | 20.3327 | 175360.4265 |  | 54.2275 | 255943.3186 |  | 161.2091 | 341557.3509 |  | 236393 | 416764.8776 |  | 236393 | 483851.0846 |  | 236393 | 567353.4492
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1131.6123 | C_100 - C this iteration | iteration | 22135.3221 | C_100 - C this iteration | iteration | 54201.273 | C_100 - C this iteration | iteration | 105570.2452 | C_100 - C this iteration | iteration | 177114.0308 | C_100 - C this iteration | iteration | 258502.7518 | C_100 - C this iteration | iteration | 344972.9244 | C_100 - C this iteration | iteration | 420932.5264 | C_100 - C this iteration | iteration | 488689.5955 | C_100 - C this iteration | iteration | 573026.9837 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1848 |  |  | 90.0957 |  |  | 89.6496 |  |  | 88.1537 |  |  | 84.4676 |  |  | 78.0057 |  |  | 68.4948 |  |  | 57.8913 |  |  | 46.6579 |  |  | 30.3379
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1848 |  |  | 30.0957 |  |  | 29.6496 |  |  | 28.1537 |  |  | 24.4676 |  |  | 18.0057 |  |  | 8.4948 |  |  | -2.1087 |  |  | -13.3421 |  |  | -29.6621
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33404 |  |  | 0.33073 |  |  | 0.31937 |  |  | 0.28967 |  |  | 0.23083 |  |  | 0.12402 |  |  | -0.036425 |  |  | -0.28595 |  |  | -0.97773
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82607 |  |  | 0.82615 |  |  | 0.82976 |  |  | 0.8408 |  |  | 0.86553 |  |  | 0.92227 |  |  | 1.0255 |  |  | 1.1614 |  |  | 1.8652
[13 empty] | C Non choked w/ reducers | 7 |  | 0.45699 |  |  | 8.9585 |  |  | 22.2042 |  |  | 44.8272 |  |  | 82.3388 |  |  | 144.7995 |  |  | 291.9415 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.4091 |  |  | 8.0145 |  |  | 19.8615 |  |  | 39.853 |  |  | 71.7303 |  |  | 119.3434 |  |  | 194.9342 |  |  | 315.73 |  |  | 464.5859 |  |  | 1405.0404
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.45699 |  |  | 8.9585 |  |  | 22.2042 |  |  | 44.8272 |  |  | 82.3388 |  |  | 144.7995 |  |  | 291.9415 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.273 | 1131.6123 |  | 2.6415 | 22135.3221 |  | 0.79584 | 54201.273 |  | 5.4272 | 105570.2452 |  | 21.3388 | 177114.0308 |  | 56.5995 | 258502.7518 |  | 170.9415 | 344972.9244 |  | 236393 | 420932.5264 |  | 236393 | 488689.5955 |  | 236393 | 573026.9837
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1154.2445 | C_100 - C this iteration | iteration | 22356.6753 | C_100 - C this iteration | iteration | 54743.2857 | C_100 - C this iteration | iteration | 106625.9476 | C_100 - C this iteration | iteration | 178885.1711 | C_100 - C this iteration | iteration | 261087.7793 | C_100 - C this iteration | iteration | 348422.6537 | C_100 - C this iteration | iteration | 425141.8517 | C_100 - C this iteration | iteration | 493576.4914 | C_100 - C this iteration | iteration | 578757.2535 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1848 |  |  | 90.0939 |  |  | 89.6388 |  |  | 88.1129 |  |  | 84.3527 |  |  | 77.7609 |  |  | 68.0589 |  |  | 57.2422 |  |  | 45.783 |  |  | 29.1349
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1848 |  |  | 30.0939 |  |  | 29.6388 |  |  | 28.1129 |  |  | 24.3527 |  |  | 17.7609 |  |  | 8.0589 |  |  | -2.7578 |  |  | -14.217 |  |  | -30.8651
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33403 |  |  | 0.33065 |  |  | 0.31906 |  |  | 0.2887 |  |  | 0.2284 |  |  | 0.11841 |  |  | -0.048178 |  |  | -0.31053 |  |  | -1.0594
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82608 |  |  | 0.8262 |  |  | 0.82993 |  |  | 0.84133 |  |  | 0.86694 |  |  | 0.92578 |  |  | 1.0338 |  |  | 1.1753 |  |  | 1.9374
[13 empty] | C Non choked w/ reducers | 7 |  | 0.46613 |  |  | 9.0484 |  |  | 22.4305 |  |  | 45.3096 |  |  | 83.3622 |  |  | 147.2435 |  |  | 302.546 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.41728 |  |  | 8.0948 |  |  | 20.0626 |  |  | 40.2702 |  |  | 72.5463 |  |  | 120.9163 |  |  | 198.1448 |  |  | 322.5034 |  |  | 478.1985 |  |  | 1477.6825
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.46613 |  |  | 9.0484 |  |  | 22.4305 |  |  | 45.3096 |  |  | 83.3622 |  |  | 147.2435 |  |  | 302.546 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2639 | 1154.2445 |  | 2.5516 | 22356.6753 |  | 0.56952 | 54743.2857 |  | 5.9096 | 106625.9476 |  | 22.3622 | 178885.1711 |  | 59.0435 | 261087.7793 |  | 181.546 | 348422.6537 |  | 236393 | 425141.8517 |  | 236393 | 493576.4914 |  | 236393 | 578757.2535
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1177.3294 | C_100 - C this iteration | iteration | 22580.2421 | C_100 - C this iteration | iteration | 55290.7186 | C_100 - C this iteration | iteration | 107692.2071 | C_100 - C this iteration | iteration | 180674.0228 | C_100 - C this iteration | iteration | 263698.6571 | C_100 - C this iteration | iteration | 351906.8802 | C_100 - C this iteration | iteration | 429393.2702 | C_100 - C this iteration | iteration | 498512.2564 | C_100 - C this iteration | iteration | 584544.826 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1848 |  |  | 90.0921 |  |  | 89.6279 |  |  | 88.0712 |  |  | 84.2355 |  |  | 77.5112 |  |  | 67.6141 |  |  | 56.58 |  |  | 44.8906 |  |  | 27.9078
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1848 |  |  | 30.0921 |  |  | 29.6279 |  |  | 28.0712 |  |  | 24.2355 |  |  | 17.5112 |  |  | 7.6141 |  |  | -3.42 |  |  | -15.1094 |  |  | -32.0922
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33401 |  |  | 0.33057 |  |  | 0.31873 |  |  | 0.28771 |  |  | 0.22592 |  |  | 0.11261 |  |  | -0.060445 |  |  | -0.33658 |  |  | -1.1499
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82608 |  |  | 0.82624 |  |  | 0.8301 |  |  | 0.84188 |  |  | 0.86839 |  |  | 0.92942 |  |  | 1.0424 |  |  | 1.19 |  |  | 2.0176
[13 empty] | C Non choked w/ reducers | 7 |  | 0.47545 |  |  | 9.1392 |  |  | 22.6592 |  |  | 45.798 |  |  | 84.4034 |  |  | 149.7635 |  |  | 314.1677 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.42562 |  |  | 8.1759 |  |  | 20.2657 |  |  | 40.6922 |  |  | 73.3737 |  |  | 122.5189 |  |  | 201.4426 |  |  | 329.5404 |  |  | 492.5828 |  |  | 1558.0827
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.47545 |  |  | 9.1392 |  |  | 22.6592 |  |  | 45.798 |  |  | 84.4034 |  |  | 149.7635 |  |  | 314.1677 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2545 | 1177.3294 |  | 2.4608 | 22580.2421 |  | 0.34082 | 55290.7186 |  | 6.398 | 107692.2071 |  | 23.4034 | 180674.0228 |  | 61.5635 | 263698.6571 |  | 193.1677 | 351906.8802 |  | 236393 | 429393.2702 |  | 236393 | 498512.2564 |  | 236393 | 584544.826
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1200.876 | C_100 - C this iteration | iteration | 22806.0445 | C_100 - C this iteration | iteration | 55843.6258 | C_100 - C this iteration | iteration | 108769.1292 | C_100 - C this iteration | iteration | 182480.763 | C_100 - C this iteration | iteration | 266335.6437 | C_100 - C this iteration | iteration | 355425.949 | C_100 - C this iteration | iteration | 433687.2029 | C_100 - C this iteration | iteration | 503497.3789 | C_100 - C this iteration | iteration | 590390.2743 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1848 |  |  | 90.0902 |  |  | 89.6167 |  |  | 88.0288 |  |  | 84.1159 |  |  | 77.2564 |  |  | 67.1605 |  |  | 55.9046 |  |  | 43.9801 |  |  | 26.6561
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1848 |  |  | 30.0902 |  |  | 29.6167 |  |  | 28.0288 |  |  | 24.1159 |  |  | 17.2564 |  |  | 7.1605 |  |  | -4.0954 |  |  | -16.0199 |  |  | -33.3439
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.334 |  |  | 0.33048 |  |  | 0.3184 |  |  | 0.2867 |  |  | 0.22337 |  |  | 0.10662 |  |  | -0.073257 |  |  | -0.36425 |  |  | -1.2509
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82609 |  |  | 0.82628 |  |  | 0.83027 |  |  | 0.84243 |  |  | 0.86987 |  |  | 0.93318 |  |  | 1.0513 |  |  | 1.2056 |  |  | 2.1069
[13 empty] | C Non choked w/ reducers | 7 |  | 0.48496 |  |  | 9.2309 |  |  | 22.8903 |  |  | 46.2924 |  |  | 85.4627 |  |  | 152.3637 |  |  | 326.9886 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.43414 |  |  | 8.2578 |  |  | 20.4709 |  |  | 41.1189 |  |  | 74.2128 |  |  | 124.1521 |  |  | 204.8314 |  |  | 336.8572 |  |  | 507.8074 |  |  | 1647.563
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.48496 |  |  | 9.2309 |  |  | 22.8903 |  |  | 46.2924 |  |  | 85.4627 |  |  | 152.3637 |  |  | 326.9886 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.245 | 1200.876 |  | 2.3691 | 22806.0445 |  | 0.10968 | 55843.6258 |  | 6.8924 | 108769.1292 |  | 24.4627 | 182480.763 |  | 64.1637 | 266335.6437 |  | 205.9886 | 355425.949 |  | 236393 | 433687.2029 |  | 236393 | 503497.3789 |  | 236393 | 590390.2743
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1224.8935 | C_100 - C this iteration | iteration | 23034.105 | C_100 - C this iteration | iteration | 56402.062 | C_100 - C this iteration | iteration | 109856.8205 | C_100 - C this iteration | iteration | 184305.5707 | C_100 - C this iteration | iteration | 268999.0001 | C_100 - C this iteration | iteration | 358980.2085 | C_100 - C this iteration | iteration | 438024.0749 | C_100 - C this iteration | iteration | 508532.3527 | C_100 - C this iteration | iteration | 596294.177 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1848 |  |  | 90.0883 |  |  | 89.6052 |  |  | 87.9854 |  |  | 83.9939 |  |  | 76.9966 |  |  | 66.6977 |  |  | 55.2155 |  |  | 43.0514 |  |  | 25.3791
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1848 |  |  | 30.0883 |  |  | 29.6052 |  |  | 27.9854 |  |  | 23.9939 |  |  | 16.9966 |  |  | 6.6977 |  |  | -4.7845 |  |  | -16.9486 |  |  | -34.6209
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33399 |  |  | 0.3304 |  |  | 0.31807 |  |  | 0.28566 |  |  | 0.22074 |  |  | 0.10042 |  |  | -0.086651 |  |  | -0.39368 |  |  | -1.3641
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.8261 |  |  | 0.82633 |  |  | 0.83045 |  |  | 0.843 |  |  | 0.8714 |  |  | 0.93706 |  |  | 1.0607 |  |  | 1.2222 |  |  | 2.2071
[13 empty] | C Non choked w/ reducers | 7 |  | 0.49466 |  |  | 9.3235 |  |  | 23.1239 |  |  | 46.793 |  |  | 86.5408 |  |  | 155.0485 |  |  | 341.2399 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.44282 |  |  | 8.3406 |  |  | 20.6782 |  |  | 41.5506 |  |  | 75.0638 |  |  | 125.8168 |  |  | 208.3152 |  |  | 344.4715 |  |  | 523.9496 |  |  | 1747.7636
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.49466 |  |  | 9.3235 |  |  | 23.1239 |  |  | 46.793 |  |  | 86.5408 |  |  | 155.0485 |  |  | 341.2399 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2353 | 1224.8935 |  | 2.2765 | 23034.105 |  | 0.1239 | 56402.062 |  | 7.393 | 109856.8205 |  | 25.5408 | 184305.5707 |  | 66.8485 | 268999.0001 |  | 220.2399 | 358980.2085 |  | 236393 | 438024.0749 |  | 236393 | 508532.3527 |  | 236393 | 596294.177
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1249.3914 | C_100 - C this iteration | iteration | 23264.446 | C_100 - C this iteration | iteration | 56966.0827 | C_100 - C this iteration | iteration | 110955.3887 | C_100 - C this iteration | iteration | 186148.6264 | C_100 - C this iteration | iteration | 271688.9901 | C_100 - C this iteration | iteration | 362570.0106 | C_100 - C this iteration | iteration | 442404.3157 | C_100 - C this iteration | iteration | 513617.6762 | C_100 - C this iteration | iteration | 602257.1188 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1848 |  |  | 90.0864 |  |  | 89.5936 |  |  | 87.9412 |  |  | 83.8695 |  |  | 76.7315 |  |  | 66.2256 |  |  | 54.5126 |  |  | 42.104 |  |  | 24.0765
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1848 |  |  | 30.0864 |  |  | 29.5936 |  |  | 27.9412 |  |  | 23.8695 |  |  | 16.7315 |  |  | 6.2256 |  |  | -5.4874 |  |  | -17.896 |  |  | -35.9235
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33397 |  |  | 0.33031 |  |  | 0.31773 |  |  | 0.2846 |  |  | 0.21805 |  |  | 0.094005 |  |  | -0.10066 |  |  | -0.42504 |  |  | -1.4921
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.8261 |  |  | 0.82637 |  |  | 0.83063 |  |  | 0.84359 |  |  | 0.87297 |  |  | 0.94108 |  |  | 1.0705 |  |  | 1.2399 |  |  | 2.3203
[13 empty] | C Non choked w/ reducers | 7 |  | 0.50456 |  |  | 9.417 |  |  | 23.36 |  |  | 47.2998 |  |  | 87.6382 |  |  | 157.823 |  |  | 357.2211 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.45167 |  |  | 8.4242 |  |  | 20.8877 |  |  | 41.9872 |  |  | 75.9269 |  |  | 127.514 |  |  | 211.8982 |  |  | 352.4022 |  |  | 541.0964 |  |  | 1860.7451
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.50456 |  |  | 9.417 |  |  | 23.36 |  |  | 47.2998 |  |  | 87.6382 |  |  | 157.823 |  |  | 357.2211 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2254 | 1249.3914 |  | 2.183 | 23264.446 |  | 0.35996 | 56966.0827 |  | 7.8998 | 110955.3887 |  | 26.6382 | 186148.6264 |  | 69.623 | 271688.9901 |  | 236.2211 | 362570.0106 |  | 236393 | 442404.3157 |  | 236393 | 513617.6762 |  | 236393 | 602257.1188
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1274.3792 | C_100 - C this iteration | iteration | 23497.0905 | C_100 - C this iteration | iteration | 57535.7435 | C_100 - C this iteration | iteration | 112064.9426 | C_100 - C this iteration | iteration | 188010.1126 | C_100 - C this iteration | iteration | 274405.8801 | C_100 - C this iteration | iteration | 366195.7107 | C_100 - C this iteration | iteration | 446828.3588 | C_100 - C this iteration | iteration | 518753.853 | C_100 - C this iteration | iteration | 608279.69 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1847 |  |  | 90.0844 |  |  | 89.5817 |  |  | 87.8961 |  |  | 83.7425 |  |  | 76.4611 |  |  | 65.744 |  |  | 53.7956 |  |  | 41.1376 |  |  | 22.7477
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1847 |  |  | 30.0844 |  |  | 29.5817 |  |  | 27.8961 |  |  | 23.7425 |  |  | 16.4611 |  |  | 5.744 |  |  | -6.2044 |  |  | -18.8624 |  |  | -37.2523
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33396 |  |  | 0.33022 |  |  | 0.31738 |  |  | 0.28352 |  |  | 0.21529 |  |  | 0.087369 |  |  | -0.11533 |  |  | -0.45852 |  |  | -1.6376
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82611 |  |  | 0.82642 |  |  | 0.83082 |  |  | 0.84418 |  |  | 0.87458 |  |  | 0.94524 |  |  | 1.0808 |  |  | 1.2588 |  |  | 2.4491
[13 empty] | C Non choked w/ reducers | 7 |  | 0.51465 |  |  | 9.5115 |  |  | 23.5985 |  |  | 47.8129 |  |  | 88.7554 |  |  | 160.6926 |  |  | 375.328 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.46071 |  |  | 8.5086 |  |  | 21.0994 |  |  | 42.4288 |  |  | 76.8025 |  |  | 129.2447 |  |  | 215.5848 |  |  | 360.6702 |  |  | 559.3462 |  |  | 1989.1326
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.51465 |  |  | 9.5115 |  |  | 23.5985 |  |  | 47.8129 |  |  | 88.7554 |  |  | 160.6926 |  |  | 375.328 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2154 | 1274.3792 |  | 2.0885 | 23497.0905 |  | 0.59853 | 57535.7435 |  | 8.4129 | 112064.9426 |  | 27.7554 | 188010.1126 |  | 72.4926 | 274405.8801 |  | 254.328 | 366195.7107 |  | 236393 | 446828.3588 |  | 236393 | 518753.853 |  | 236393 | 608279.69
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1299.8668 | C_100 - C this iteration | iteration | 23732.0614 | C_100 - C this iteration | iteration | 58111.1009 | C_100 - C this iteration | iteration | 113185.592 | C_100 - C this iteration | iteration | 189890.2138 | C_100 - C this iteration | iteration | 277149.9389 | C_100 - C this iteration | iteration | 369857.6678 | C_100 - C this iteration | iteration | 451296.6424 | C_100 - C this iteration | iteration | 523941.3915 | C_100 - C this iteration | iteration | 614362.4869 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1847 |  |  | 90.0824 |  |  | 89.5696 |  |  | 87.8501 |  |  | 83.613 |  |  | 76.1852 |  |  | 65.2527 |  |  | 53.0642 |  |  | 40.1518 |  |  | 21.3923
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1847 |  |  | 30.0824 |  |  | 29.5696 |  |  | 27.8501 |  |  | 23.613 |  |  | 16.1852 |  |  | 5.2527 |  |  | -6.9358 |  |  | -19.8482 |  |  | -38.6077
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33394 |  |  | 0.33013 |  |  | 0.31702 |  |  | 0.28241 |  |  | 0.21245 |  |  | 0.080498 |  |  | -0.13071 |  |  | -0.49433 |  |  | -1.8048
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82612 |  |  | 0.82647 |  |  | 0.83101 |  |  | 0.84479 |  |  | 0.87624 |  |  | 0.94955 |  |  | 1.0916 |  |  | 1.279 |  |  | 2.597
[13 empty] | C Non choked w/ reducers | 7 |  | 0.52494 |  |  | 9.607 |  |  | 23.8396 |  |  | 48.3325 |  |  | 89.8931 |  |  | 163.6631 |  |  | 396.0969 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.46992 |  |  | 8.5939 |  |  | 21.3133 |  |  | 42.8755 |  |  | 77.6906 |  |  | 131.0097 |  |  | 219.38 |  |  | 369.2981 |  |  | 578.8107 |  |  | 2136.3229
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.52494 |  |  | 9.607 |  |  | 23.8396 |  |  | 48.3325 |  |  | 89.8931 |  |  | 163.6631 |  |  | 396.0969 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2051 | 1299.8668 |  | 1.993 | 23732.0614 |  | 0.83964 | 58111.1009 |  | 8.9325 | 113185.592 |  | 28.8931 | 189890.2138 |  | 75.4631 | 277149.9389 |  | 275.0969 | 369857.6678 |  | 236393 | 451296.6424 |  | 236393 | 523941.3915 |  | 236393 | 614362.4869
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1325.8642 | C_100 - C this iteration | iteration | 23969.382 | C_100 - C this iteration | iteration | 58692.2119 | C_100 - C this iteration | iteration | 114317.4479 | C_100 - C this iteration | iteration | 191789.1159 | C_100 - C this iteration | iteration | 279921.4382 | C_100 - C this iteration | iteration | 373556.2445 | C_100 - C this iteration | iteration | 455809.6089 | C_100 - C this iteration | iteration | 529180.8054 | C_100 - C this iteration | iteration | 620506.1118 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1847 |  |  | 90.0803 |  |  | 89.5572 |  |  | 87.8032 |  |  | 83.4809 |  |  | 75.9038 |  |  | 64.7516 |  |  | 52.3181 |  |  | 39.1461 |  |  | 20.0095
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1847 |  |  | 30.0803 |  |  | 29.5572 |  |  | 27.8032 |  |  | 23.4809 |  |  | 15.9038 |  |  | 4.7516 |  |  | -7.6819 |  |  | -20.8539 |  |  | -39.9905
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33393 |  |  | 0.33004 |  |  | 0.31665 |  |  | 0.28127 |  |  | 0.20953 |  |  | 0.073382 |  |  | -0.14683 |  |  | -0.53272 |  |  | -1.9986
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82613 |  |  | 0.82652 |  |  | 0.83121 |  |  | 0.84542 |  |  | 0.87794 |  |  | 0.95401 |  |  | 1.1029 |  |  | 1.3007 |  |  | 2.7685
[13 empty] | C Non choked w/ reducers | 7 |  | 0.53544 |  |  | 9.7034 |  |  | 24.0833 |  |  | 48.8586 |  |  | 91.0518 |  |  | 166.7408 |  |  | 420.2762 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.47932 |  |  | 8.68 |  |  | 21.5294 |  |  | 43.3274 |  |  | 78.5917 |  |  | 132.8104 |  |  | 223.2886 |  |  | 378.3104 |  |  | 599.6172 |  |  | 2306.7906
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.53544 |  |  | 9.7034 |  |  | 24.0833 |  |  | 48.8586 |  |  | 91.0518 |  |  | 166.7408 |  |  | 420.2762 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1946 | 1325.8642 |  | 1.8966 | 23969.382 |  | 1.0833 | 58692.2119 |  | 9.4586 | 114317.4479 |  | 30.0518 | 191789.1159 |  | 78.5408 | 279921.4382 |  | 299.2762 | 373556.2445 |  | 236393 | 455809.6089 |  | 236393 | 529180.8054 |  | 236393 | 620506.1118
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1352.3814 | C_100 - C this iteration | iteration | 24209.0758 | C_100 - C this iteration | iteration | 59279.134 | C_100 - C this iteration | iteration | 115460.6224 | C_100 - C this iteration | iteration | 193707.0071 | C_100 - C this iteration | iteration | 282720.6526 | C_100 - C this iteration | iteration | 377291.8069 | C_100 - C this iteration | iteration | 460367.7049 | C_100 - C this iteration | iteration | 534472.6135 | C_100 - C this iteration | iteration | 626711.1729 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1847 |  |  | 90.0782 |  |  | 89.5446 |  |  | 87.7553 |  |  | 83.3462 |  |  | 75.6167 |  |  | 64.2404 |  |  | 51.557 |  |  | 38.1202 |  |  | 18.599
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1847 |  |  | 30.0782 |  |  | 29.5446 |  |  | 27.7553 |  |  | 23.3462 |  |  | 15.6167 |  |  | 4.2404 |  |  | -8.443 |  |  | -21.8798 |  |  | -41.401
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33391 |  |  | 0.32994 |  |  | 0.31628 |  |  | 0.28011 |  |  | 0.20653 |  |  | 0.066008 |  |  | -0.16376 |  |  | -0.57397 |  |  | -2.226
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82614 |  |  | 0.82657 |  |  | 0.8314 |  |  | 0.84605 |  |  | 0.87969 |  |  | 0.95863 |  |  | 1.1148 |  |  | 1.324 |  |  | 2.9698
[13 empty] | C Non choked w/ reducers | 7 |  | 0.54615 |  |  | 9.8008 |  |  | 24.3296 |  |  | 49.3914 |  |  | 92.2322 |  |  | 169.9328 |  |  | 448.9478 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.48891 |  |  | 8.767 |  |  | 21.7477 |  |  | 43.7846 |  |  | 79.5059 |  |  | 134.6477 |  |  | 227.3162 |  |  | 387.7343 |  |  | 621.9115 |  |  | 2506.5526
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.54615 |  |  | 9.8008 |  |  | 24.3296 |  |  | 49.3914 |  |  | 92.2322 |  |  | 169.9328 |  |  | 448.9478 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1839 | 1352.3814 |  | 1.7992 | 24209.0758 |  | 1.3296 | 59279.134 |  | 9.9914 | 115460.6224 |  | 31.2322 | 193707.0071 |  | 81.7328 | 282720.6526 |  | 327.9478 | 377291.8069 |  | 236393 | 460367.7049 |  | 236393 | 534472.6135 |  | 236393 | 626711.1729
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1379.4291 | C_100 - C this iteration | iteration | 24451.1666 | C_100 - C this iteration | iteration | 59871.9254 | C_100 - C this iteration | iteration | 116615.2286 | C_100 - C this iteration | iteration | 195644.0771 | C_100 - C this iteration | iteration | 285547.8591 | C_100 - C this iteration | iteration | 381064.725 | C_100 - C this iteration | iteration | 464971.382 | C_100 - C this iteration | iteration | 539817.3396 | C_100 - C this iteration | iteration | 632978.2846 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1847 |  |  | 90.0761 |  |  | 89.5317 |  |  | 87.7065 |  |  | 83.2087 |  |  | 75.3239 |  |  | 63.7189 |  |  | 50.7805 |  |  | 37.0737 |  |  | 17.1601
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1847 |  |  | 30.0761 |  |  | 29.5317 |  |  | 27.7065 |  |  | 23.2087 |  |  | 15.3239 |  |  | 3.7189 |  |  | -9.2195 |  |  | -22.9263 |  |  | -42.8399
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.3339 |  |  | 0.32985 |  |  | 0.3159 |  |  | 0.27892 |  |  | 0.20344 |  |  | 0.058364 |  |  | -0.18156 |  |  | -0.6184 |  |  | -2.4965
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82614 |  |  | 0.82662 |  |  | 0.83161 |  |  | 0.84671 |  |  | 0.88148 |  |  | 0.96342 |  |  | 1.1272 |  |  | 1.3491 |  |  | 3.2091
[13 empty] | C Non choked w/ reducers | 7 |  | 0.55707 |  |  | 9.8992 |  |  | 24.5785 |  |  | 49.9309 |  |  | 93.4349 |  |  | 173.2468 |  |  | 483.7464 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.49869 |  |  | 8.8549 |  |  | 21.9684 |  |  | 44.2471 |  |  | 80.4337 |  |  | 136.5229 |  |  | 231.4684 |  |  | 397.5993 |  |  | 645.8613 |  |  | 2743.8949
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.55707 |  |  | 9.8992 |  |  | 24.5785 |  |  | 49.9309 |  |  | 93.4349 |  |  | 173.2468 |  |  | 483.7464 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1729 | 1379.4291 |  | 1.7008 | 24451.1666 |  | 1.5785 | 59871.9254 |  | 10.5309 | 116615.2286 |  | 32.4349 | 195644.0771 |  | 85.0468 | 285547.8591 |  | 362.7464 | 381064.725 |  | 236393 | 464971.382 |  | 236393 | 539817.3396 |  | 236393 | 632978.2846
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1407.0177 | C_100 - C this iteration | iteration | 24695.6782 | C_100 - C this iteration | iteration | 60470.6446 | C_100 - C this iteration | iteration | 117781.3809 | C_100 - C this iteration | iteration | 197600.5179 | C_100 - C this iteration | iteration | 288403.3377 | C_100 - C this iteration | iteration | 384875.3722 | C_100 - C this iteration | iteration | 469621.0958 | C_100 - C this iteration | iteration | 545215.513 | C_100 - C this iteration | iteration | 639308.0675 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1847 |  |  | 90.0739 |  |  | 89.5186 |  |  | 87.6566 |  |  | 83.0685 |  |  | 75.0252 |  |  | 63.1869 |  |  | 49.9885 |  |  | 36.0062 |  |  | 15.6923
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1847 |  |  | 30.0739 |  |  | 29.5186 |  |  | 27.6566 |  |  | 23.0685 |  |  | 15.0252 |  |  | 3.1869 |  |  | -10.0115 |  |  | -23.9938 |  |  | -44.3077
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33388 |  |  | 0.32975 |  |  | 0.31551 |  |  | 0.2777 |  |  | 0.20027 |  |  | 0.050436 |  |  | -0.20028 |  |  | -0.66638 |  |  | -2.8235
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82615 |  |  | 0.82667 |  |  | 0.83181 |  |  | 0.84738 |  |  | 0.88333 |  |  | 0.96839 |  |  | 1.1403 |  |  | 1.3761 |  |  | 3.4985
[13 empty] | C Non choked w/ reducers | 7 |  | 0.56821 |  |  | 9.9986 |  |  | 24.8301 |  |  | 50.4774 |  |  | 94.6607 |  |  | 176.6911 |  |  | 527.2867 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.50866 |  |  | 8.9437 |  |  | 22.1913 |  |  | 44.7149 |  |  | 81.3751 |  |  | 138.4371 |  |  | 235.7513 |  |  | 407.938 |  |  | 671.6604 |  |  | 3030.5543
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.56821 |  |  | 9.9986 |  |  | 24.8301 |  |  | 50.4774 |  |  | 94.6607 |  |  | 176.6911 |  |  | 527.2867 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1618 | 1407.0177 |  | 1.6014 | 24695.6782 |  | 1.8301 | 60470.6446 |  | 11.0774 | 117781.3809 |  | 33.6607 | 197600.5179 |  | 88.4911 | 288403.3377 |  | 406.2867 | 384875.3722 |  | 236393 | 469621.0958 |  | 236393 | 545215.513 |  | 236393 | 639308.0675
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1435.158 | C_100 - C this iteration | iteration | 24942.635 | C_100 - C this iteration | iteration | 61075.3511 | C_100 - C this iteration | iteration | 118959.1947 | C_100 - C this iteration | iteration | 199576.5231 | C_100 - C this iteration | iteration | 291287.3711 | C_100 - C this iteration | iteration | 388724.126 | C_100 - C this iteration | iteration | 474317.3068 | C_100 - C this iteration | iteration | 550667.6682 | C_100 - C this iteration | iteration | 645701.1481 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1847 |  |  | 90.0716 |  |  | 89.5052 |  |  | 87.6058 |  |  | 82.9254 |  |  | 74.7205 |  |  | 62.6442 |  |  | 49.1805 |  |  | 34.9172 |  |  | 14.195
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1847 |  |  | 30.0716 |  |  | 29.5052 |  |  | 27.6058 |  |  | 22.9254 |  |  | 14.7205 |  |  | 2.6442 |  |  | -10.8195 |  |  | -25.0828 |  |  | -45.805
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33386 |  |  | 0.32965 |  |  | 0.31511 |  |  | 0.27646 |  |  | 0.19701 |  |  | 0.04221 |  |  | -0.21999 |  |  | -0.71835 |  |  | -3.2268
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82616 |  |  | 0.82672 |  |  | 0.83203 |  |  | 0.84806 |  |  | 0.88523 |  |  | 0.97354 |  |  | 1.1542 |  |  | 1.4055 |  |  | 3.8554
[13 empty] | C Non choked w/ reducers | 7 |  | 0.57958 |  |  | 10.0989 |  |  | 25.0844 |  |  | 51.0309 |  |  | 95.9103 |  |  | 180.2751 |  |  | 584.0756 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.51883 |  |  | 9.0333 |  |  | 22.4166 |  |  | 45.1883 |  |  | 82.3307 |  |  | 140.3917 |  |  | 240.1714 |  |  | 418.7861 |  |  | 699.5342 |  |  | 3383.7226
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.57958 |  |  | 10.0989 |  |  | 25.0844 |  |  | 51.0309 |  |  | 95.9103 |  |  | 180.2751 |  |  | 584.0756 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1504 | 1435.158 |  | 1.5011 | 24942.635 |  | 2.0844 | 61075.3511 |  | 11.6309 | 118959.1947 |  | 34.9103 | 199576.5231 |  | 92.0751 | 291287.3711 |  | 463.0756 | 388724.126 |  | 236393 | 474317.3068 |  | 236393 | 550667.6682 |  | 236393 | 645701.1481
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1463.8612 | C_100 - C this iteration | iteration | 25192.0614 | C_100 - C this iteration | iteration | 61686.1046 | C_100 - C this iteration | iteration | 120148.7867 | C_100 - C this iteration | iteration | 201572.2883 | C_100 - C this iteration | iteration | 294200.2448 | C_100 - C this iteration | iteration | 392611.3672 | C_100 - C this iteration | iteration | 479060.4798 | C_100 - C this iteration | iteration | 556174.3448 | C_100 - C this iteration | iteration | 652158.1596 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1846 |  |  | 90.0694 |  |  | 89.4915 |  |  | 87.554 |  |  | 82.7795 |  |  | 74.4097 |  |  | 62.0907 |  |  | 48.3564 |  |  | 33.8063 |  |  | 12.6676
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1846 |  |  | 30.0694 |  |  | 29.4915 |  |  | 27.554 |  |  | 22.7795 |  |  | 14.4097 |  |  | 2.0907 |  |  | -11.6436 |  |  | -26.1937 |  |  | -47.3324
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33385 |  |  | 0.32955 |  |  | 0.31471 |  |  | 0.27518 |  |  | 0.19365 |  |  | 0.033671 |  |  | -0.24079 |  |  | -0.77482 |  |  | -3.7365
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82617 |  |  | 0.82678 |  |  | 0.83224 |  |  | 0.84876 |  |  | 0.88718 |  |  | 0.9789 |  |  | 1.1687 |  |  | 1.4373 |  |  | 4.3064
[13 empty] | C Non choked w/ reducers | 7 |  | 0.59117 |  |  | 10.2003 |  |  | 25.3414 |  |  | 51.5916 |  |  | 97.1845 |  |  | 184.009 |  |  | 662.7421 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.52921 |  |  | 9.1239 |  |  | 22.6442 |  |  | 45.6672 |  |  | 83.3005 |  |  | 142.3879 |  |  | 244.7358 |  |  | 430.1831 |  |  | 729.7463 |  |  | 3829.633
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.59117 |  |  | 10.2003 |  |  | 25.3414 |  |  | 51.5916 |  |  | 97.1845 |  |  | 184.009 |  |  | 662.7421 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1388 | 1463.8612 |  | 1.3997 | 25192.0614 |  | 2.3414 | 61686.1046 |  | 12.1916 | 120148.7867 |  | 36.1845 | 201572.2883 |  | 95.809 | 294200.2448 |  | 541.7421 | 392611.3672 |  | 236393 | 479060.4798 |  | 236393 | 556174.3448 |  | 236393 | 652158.1596
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1493.1384 | C_100 - C this iteration | iteration | 25443.982 | C_100 - C this iteration | iteration | 62302.9656 | C_100 - C this iteration | iteration | 121350.2745 | C_100 - C this iteration | iteration | 203588.0112 | C_100 - C this iteration | iteration | 297142.2473 | C_100 - C this iteration | iteration | 396537.4809 | C_100 - C this iteration | iteration | 483851.0846 | C_100 - C this iteration | iteration | 561736.0883 | C_100 - C this iteration | iteration | 658679.7412 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1846 |  |  | 90.067 |  |  | 89.4776 |  |  | 87.5011 |  |  | 82.6307 |  |  | 74.0926 |  |  | 61.526 |  |  | 47.5156 |  |  | 32.6731 |  |  | 11.1095
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1846 |  |  | 30.067 |  |  | 29.4776 |  |  | 27.5011 |  |  | 22.6307 |  |  | 14.0926 |  |  | 1.526 |  |  | -12.4844 |  |  | -27.3269 |  |  | -48.8905
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33383 |  |  | 0.32944 |  |  | 0.31429 |  |  | 0.27388 |  |  | 0.1902 |  |  | 0.024802 |  |  | -0.26274 |  |  | -0.83637 |  |  | -4.4008
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82618 |  |  | 0.82683 |  |  | 0.83246 |  |  | 0.84948 |  |  | 0.88919 |  |  | 0.98445 |  |  | 1.1841 |  |  | 1.4721 |  |  | 4.8943
[13 empty] | C Non choked w/ reducers | 7 |  | 0.60299 |  |  | 10.3028 |  |  | 25.6011 |  |  | 52.1595 |  |  | 98.484 |  |  | 187.9042 |  |  | 782.636 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.53979 |  |  | 9.2154 |  |  | 22.8742 |  |  | 46.1517 |  |  | 84.2851 |  |  | 144.4272 |  |  | 249.4518 |  |  | 442.1729 |  |  | 762.6069 |  |  | 4410.4038
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.60299 |  |  | 10.3028 |  |  | 25.6011 |  |  | 52.1595 |  |  | 98.484 |  |  | 187.9042 |  |  | 782.636 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.127 | 1493.1384 |  | 1.2972 | 25443.982 |  | 2.6011 | 62302.9656 |  | 12.7595 | 121350.2745 |  | 37.484 | 203588.0112 |  | 99.7042 | 297142.2473 |  | 661.636 | 396537.4809 |  | 236393 | 483851.0846 |  | 236393 | 561736.0883 |  | 236393 | 658679.7412
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1523.0012 | C_100 - C this iteration | iteration | 25698.4218 | C_100 - C this iteration | iteration | 62925.9953 | C_100 - C this iteration | iteration | 122563.7773 | C_100 - C this iteration | iteration | 205623.8913 | C_100 - C this iteration | iteration | 300113.6697 | C_100 - C this iteration | iteration | 400502.8557 | C_100 - C this iteration | iteration | 488689.5955 | C_100 - C this iteration | iteration | 567353.4492 | C_100 - C this iteration | iteration | 665266.5386 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1846 |  |  | 90.0647 |  |  | 89.4633 |  |  | 87.4471 |  |  | 82.4788 |  |  | 73.7691 |  |  | 60.9499 |  |  | 46.6579 |  |  | 31.5171 |  |  | 9.5201
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1846 |  |  | 30.0647 |  |  | 29.4633 |  |  | 27.4471 |  |  | 22.4788 |  |  | 13.7691 |  |  | 0.94993 |  |  | -13.3421 |  |  | -28.4829 |  |  | -50.4799
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33381 |  |  | 0.32933 |  |  | 0.31387 |  |  | 0.27254 |  |  | 0.18665 |  |  | 0.015585 |  |  | -0.28595 |  |  | -0.90373 |  |  | -5.3025
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82619 |  |  | 0.82689 |  |  | 0.83269 |  |  | 0.85021 |  |  | 0.89126 |  |  | 0.99023 |  |  | 1.2004 |  |  | 1.5101 |  |  | 5.6922
[13 empty] | C Non choked w/ reducers | 7 |  | 0.61505 |  |  | 10.4062 |  |  | 25.8637 |  |  | 52.7348 |  |  | 99.8097 |  |  | 191.9733 |  |  | 1000.717 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.55059 |  |  | 9.3078 |  |  | 23.1066 |  |  | 46.642 |  |  | 85.2847 |  |  | 146.5111 |  |  | 254.3275 |  |  | 454.8038 |  |  | 798.4838 |  |  | 5198.2067
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.61505 |  |  | 10.4062 |  |  | 25.8637 |  |  | 52.7348 |  |  | 99.8097 |  |  | 191.9733 |  |  | 1000.717 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1149 | 1523.0012 |  | 1.1938 | 25698.4218 |  | 2.8637 | 62925.9953 |  | 13.3348 | 122563.7773 |  | 38.8097 | 205623.8913 |  | 103.7733 | 300113.6697 |  | 879.717 | 400502.8557 |  | 236393 | 488689.5955 |  | 236393 | 567353.4492 |  | 236393 | 665266.5386
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1553.4612 | C_100 - C this iteration | iteration | 25955.406 | C_100 - C this iteration | iteration | 63555.2553 | C_100 - C this iteration | iteration | 123789.415 | C_100 - C this iteration | iteration | 207680.1302 | C_100 - C this iteration | iteration | 303114.8064 | C_100 - C this iteration | iteration | 404507.8842 | C_100 - C this iteration | iteration | 493576.4914 | C_100 - C this iteration | iteration | 573026.9837 | C_100 - C this iteration | iteration | 671919.204 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1846 |  |  | 90.0623 |  |  | 89.4488 |  |  | 87.3921 |  |  | 82.3239 |  |  | 73.4392 |  |  | 60.3623 |  |  | 45.783 |  |  | 30.3379 |  |  | 7.8987
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1846 |  |  | 30.0623 |  |  | 29.4488 |  |  | 27.3921 |  |  | 22.3239 |  |  | 13.4392 |  |  | 0.3623 |  |  | -14.217 |  |  | -29.6621 |  |  | -52.1013
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33379 |  |  | 0.32923 |  |  | 0.31344 |  |  | 0.27117 |  |  | 0.183 |  |  | 0.0060021 |  |  | -0.31053 |  |  | -0.97773 |  |  | -6.5962
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.8262 |  |  | 0.82694 |  |  | 0.83292 |  |  | 0.85097 |  |  | 0.89339 |  |  | 0.99624 |  |  | 1.2176 |  |  | 1.5519 |  |  | 6.837
[13 empty] | C Non choked w/ reducers | 7 |  | 0.62735 |  |  | 10.5107 |  |  | 26.1291 |  |  | 53.3176 |  |  | 101.1626 |  |  | 196.2305 |  |  | 1634.6316 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.5616 |  |  | 9.4011 |  |  | 23.3415 |  |  | 47.1381 |  |  | 86.2996 |  |  | 148.6411 |  |  | 259.3715 |  |  | 468.1299 |  |  | 837.8158 |  |  | 6327.8919
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.62735 |  |  | 10.5107 |  |  | 26.1291 |  |  | 53.3176 |  |  | 101.1626 |  |  | 196.2305 |  |  | 1634.6316 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1026 | 1553.4612 |  | 1.0893 | 25955.406 |  | 3.1291 | 63555.2553 |  | 13.9176 | 123789.415 |  | 40.1626 | 207680.1302 |  | 108.0305 | 303114.8064 |  | 1513.6316 | 404507.8842 |  | 236393 | 493576.4914 |  | 236393 | 573026.9837 |  | 236393 | 671919.204
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1584.5304 | C_100 - C this iteration | iteration | 26214.9601 | C_100 - C this iteration | iteration | 64190.8078 | C_100 - C this iteration | iteration | 125027.3092 | C_100 - C this iteration | iteration | 209756.9315 | C_100 - C this iteration | iteration | 306145.9545 | C_100 - C this iteration | iteration | 408552.9631 | C_100 - C this iteration | iteration | 498512.2564 | C_100 - C this iteration | iteration | 578757.2535 | C_100 - C this iteration | iteration | 678638.396 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1846 |  |  | 90.0598 |  |  | 89.434 |  |  | 87.336 |  |  | 82.1659 |  |  | 73.1026 |  |  | 59.7629 |  |  | 44.8906 |  |  | 29.1349 |  |  | 6.2448
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1846 |  |  | 30.0598 |  |  | 29.434 |  |  | 27.336 |  |  | 22.1659 |  |  | 13.1026 |  |  | -0.23713 |  |  | -15.1094 |  |  | -30.8651 |  |  | -53.7552
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33378 |  |  | 0.32911 |  |  | 0.313 |  |  | 0.26977 |  |  | 0.17924 |  |  | -0.0039679 |  |  | -0.33658 |  |  | -1.0594 |  |  | -8.608
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82621 |  |  | 0.827 |  |  | 0.83315 |  |  | 0.85174 |  |  | 0.89558 |  |  | 1.0025 |  |  | 1.2359 |  |  | 1.598 |  |  | 8.6173
[13 empty] | C Non choked w/ reducers | 7 |  | 0.6399 |  |  | 10.6163 |  |  | 26.3973 |  |  | 53.9082 |  |  | 102.5434 |  |  | 200.6917 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.57283 |  |  | 9.4954 |  |  | 23.5788 |  |  | 47.6401 |  |  | 87.3302 |  |  | 150.8187 |  |  | 264.5927 |  |  | 482.2112 |  |  | 881.1318 |  |  | 8083.9023
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.6399 |  |  | 10.6163 |  |  | 26.3973 |  |  | 53.9082 |  |  | 102.5434 |  |  | 200.6917 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0901 | 1584.5304 |  | 0.98371 | 26214.9601 |  | 3.3973 | 64190.8078 |  | 14.5082 | 125027.3092 |  | 41.5434 | 209756.9315 |  | 112.4917 | 306145.9545 |  | 236393 | 408552.9631 |  | 236393 | 498512.2564 |  | 236393 | 578757.2535 |  | 236393 | 678638.396
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1616.221 | C_100 - C this iteration | iteration | 26477.1097 | C_100 - C this iteration | iteration | 64832.7159 | C_100 - C this iteration | iteration | 126277.5823 | C_100 - C this iteration | iteration | 211854.5008 | C_100 - C this iteration | iteration | 309207.4141 | C_100 - C this iteration | iteration | 412638.4927 | C_100 - C this iteration | iteration | 503497.3789 | C_100 - C this iteration | iteration | 584544.826 | C_100 - C this iteration | iteration | 685424.78 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1846 |  |  | 90.0573 |  |  | 89.4189 |  |  | 87.2787 |  |  | 82.0047 |  |  | 72.7592 |  |  | 59.1514 |  |  | 43.9801 |  |  | 27.9078 |  |  | 4.5576
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1846 |  |  | 30.0573 |  |  | 29.4189 |  |  | 27.2787 |  |  | 22.0047 |  |  | 12.7592 |  |  | -0.84862 |  |  | -16.0199 |  |  | -32.0922 |  |  | -55.4424
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33376 |  |  | 0.329 |  |  | 0.31255 |  |  | 0.26834 |  |  | 0.17536 |  |  | -0.014347 |  |  | -0.36425 |  |  | -1.1499 |  |  | -12.1649
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82622 |  |  | 0.82706 |  |  | 0.83339 |  |  | 0.85253 |  |  | 0.89784 |  |  | 1.009 |  |  | 1.2553 |  |  | 1.6491 |  |  | 11.7648
[13 empty] | C Non choked w/ reducers | 7 |  | 0.6527 |  |  | 10.7229 |  |  | 26.6684 |  |  | 54.5065 |  |  | 103.9533 |  |  | 205.3745 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.58429 |  |  | 9.5906 |  |  | 23.8186 |  |  | 48.148 |  |  | 88.3769 |  |  | 153.0458 |  |  | 270.0013 |  |  | 497.1153 |  |  | 929.0739 |  |  | 11187.3087
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.6527 |  |  | 10.7229 |  |  | 26.6684 |  |  | 54.5065 |  |  | 103.9533 |  |  | 205.3745 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0773 | 1616.221 |  | 0.87707 | 26477.1097 |  | 3.6684 | 64832.7159 |  | 15.1065 | 126277.5823 |  | 42.9533 | 211854.5008 |  | 117.1745 | 309207.4141 |  | 236393 | 412638.4927 |  | 236393 | 503497.3789 |  | 236393 | 584544.826 |  | 236393 | 685424.78
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1648.5454 | C_100 - C this iteration | iteration | 26741.8808 | C_100 - C this iteration | iteration | 65481.043 | C_100 - C this iteration | iteration | 127540.3581 | C_100 - C this iteration | iteration | 213973.0458 | C_100 - C this iteration | iteration | 312299.4882 | C_100 - C this iteration | iteration | 416764.8776 | C_100 - C this iteration | iteration | 508532.3527 | C_100 - C this iteration | iteration | 590390.2743 | C_100 - C this iteration | iteration | 692279.0278 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1845 |  |  | 90.0547 |  |  | 89.4035 |  |  | 87.2203 |  |  | 81.8403 |  |  | 72.409 |  |  | 58.5276 |  |  | 43.0514 |  |  | 26.6561 |  |  | 2.8365
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1845 |  |  | 30.0547 |  |  | 29.4035 |  |  | 27.2203 |  |  | 21.8403 |  |  | 12.409 |  |  | -1.4724 |  |  | -16.9486 |  |  | -33.3439 |  |  | -57.1635
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33374 |  |  | 0.32889 |  |  | 0.31209 |  |  | 0.26687 |  |  | 0.17137 |  |  | -0.025157 |  |  | -0.39368 |  |  | -1.2509 |  |  | -20.1532
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82623 |  |  | 0.82712 |  |  | 0.83364 |  |  | 0.85333 |  |  | 0.90016 |  |  | 1.0158 |  |  | 1.2759 |  |  | 1.7061 |  |  | 18.8336
[13 empty] | C Non choked w/ reducers | 7 |  | 0.66575 |  |  | 10.8306 |  |  | 26.9425 |  |  | 55.1129 |  |  | 105.3933 |  |  | 210.2991 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.59598 |  |  | 9.6868 |  |  | 24.0609 |  |  | 48.6621 |  |  | 89.44 |  |  | 155.3239 |  |  | 275.6077 |  |  | 512.9176 |  |  | 982.4304 |  |  | 18155.3368
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.66575 |  |  | 10.8306 |  |  | 26.9425 |  |  | 55.1129 |  |  | 105.3933 |  |  | 210.2991 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0642 | 1648.5454 |  | 0.76935 | 26741.8808 |  | 3.9425 | 65481.043 |  | 15.7129 | 127540.3581 |  | 44.3933 | 213973.0458 |  | 122.0991 | 312299.4882 |  | 236393 | 416764.8776 |  | 236393 | 508532.3527 |  | 236393 | 590390.2743 |  | 236393 | 692279.0278
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1681.5163 | C_100 - C this iteration | iteration | 27009.2996 | C_100 - C this iteration | iteration | 66135.8535 | C_100 - C this iteration | iteration | 128815.7617 | C_100 - C this iteration | iteration | 216112.7763 | C_100 - C this iteration | iteration | 315422.4831 | C_100 - C this iteration | iteration | 420932.5264 | C_100 - C this iteration | iteration | 513617.6762 | C_100 - C this iteration | iteration | 596294.177 | C_100 - C this iteration | iteration | 699201.8181 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1845 |  |  | 90.0521 |  |  | 89.3878 |  |  | 87.1607 |  |  | 81.6726 |  |  | 72.0517 |  |  | 57.8913 |  |  | 42.104 |  |  | 25.3791 |  |  | 1.0807
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1845 |  |  | 30.0521 |  |  | 29.3878 |  |  | 27.1607 |  |  | 21.6726 |  |  | 12.0517 |  |  | -2.1087 |  |  | -17.896 |  |  | -34.6209 |  |  | -58.9193
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33372 |  |  | 0.32877 |  |  | 0.31162 |  |  | 0.26536 |  |  | 0.16726 |  |  | -0.036425 |  |  | -0.42504 |  |  | -1.3641 |  |  | -54.5172
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82624 |  |  | 0.82718 |  |  | 0.83389 |  |  | 0.85416 |  |  | 0.90256 |  |  | 1.0228 |  |  | 1.2979 |  |  | 1.77 |  |  | 49.2423
[13 empty] | C Non choked w/ reducers | 7 |  | 0.67907 |  |  | 10.9395 |  |  | 27.2196 |  |  | 55.7273 |  |  | 106.8644 |  |  | 215.4884 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.6079 |  |  | 9.7839 |  |  | 24.3058 |  |  | 49.1823 |  |  | 90.5199 |  |  | 157.6551 |  |  | 281.4234 |  |  | 529.7034 |  |  | 1042.1793 |  |  | 48125.7512
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.67907 |  |  | 10.9395 |  |  | 27.2196 |  |  | 55.7273 |  |  | 106.8644 |  |  | 215.4884 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0509 | 1681.5163 |  | 0.66055 | 27009.2996 |  | 4.2196 | 66135.8535 |  | 16.3273 | 128815.7617 |  | 45.8644 | 216112.7763 |  | 127.2884 | 315422.4831 |  | 236393 | 420932.5264 |  | 236393 | 513617.6762 |  | 236393 | 596294.177 |  | 236393 | 699201.8181
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1715.1467 | C_100 - C this iteration | iteration | 27279.3926 | C_100 - C this iteration | iteration | 66797.212 | C_100 - C this iteration | iteration | 130103.9193 | C_100 - C this iteration | iteration | 218273.9041 | C_100 - C this iteration | iteration | 318576.7079 | C_100 - C this iteration | iteration | 425141.8517 | C_100 - C this iteration | iteration | 518753.853 | C_100 - C this iteration | iteration | 602257.1188 | C_100 - C this iteration | iteration | 706193.8363 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1845 |  |  | 90.0494 |  |  | 89.3718 |  |  | 87.0999 |  |  | 81.5015 |  |  | 71.6872 |  |  | 57.2422 |  |  | 41.1376 |  |  | 24.0765 |  |  | -0.71025
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1845 |  |  | 30.0494 |  |  | 29.3718 |  |  | 27.0999 |  |  | 21.5015 |  |  | 11.6872 |  |  | -2.7578 |  |  | -18.8624 |  |  | -35.9235 |  |  | -60.7103
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.3337 |  |  | 0.32865 |  |  | 0.31114 |  |  | 0.26382 |  |  | 0.16303 |  |  | -0.048178 |  |  | -0.45852 |  |  | -1.4921 |  |  | 85.4773
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82625 |  |  | 0.82725 |  |  | 0.83415 |  |  | 0.85501 |  |  | 0.90502 |  |  | 1.0302 |  |  | 1.3213 |  |  | 1.8422 |  |  | -74.6389
[13 empty] | C Non choked w/ reducers | 7 |  | 0.69265 |  |  | 11.0494 |  |  | 27.4996 |  |  | 56.35 |  |  | 108.3678 |  |  | 220.9682 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 43.8771
[13 empty] | C Choked w/ reducers | 7 |  | 0.62005 |  |  | 9.8821 |  |  | 24.5533 |  |  | 49.7088 |  |  | 91.617 |  |  | 160.0413 |  |  | 287.4608 |  |  | 547.5689 |  |  | 1109.5494 |  |  | -73962.4575
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.69265 |  |  | 11.0494 |  |  | 27.4996 |  |  | 56.35 |  |  | 108.3678 |  |  | 220.9682 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -73962.4575
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0373 | 1715.1467 |  | 0.55063 | 27279.3926 |  | 4.4996 | 66797.212 |  | 16.95 | 130103.9193 |  | 47.3678 | 218273.9041 |  | 132.7682 | 318576.7079 |  | 236393 | 425141.8517 |  | 236393 | 518753.853 |  | 236393 | 602257.1188 |  | 236393 | 706193.8363
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1749.4496 | C_100 - C this iteration | iteration | 27552.1865 | C_100 - C this iteration | iteration | 67465.1841 | C_100 - C this iteration | iteration | 131404.9585 | C_100 - C this iteration | iteration | 220456.6431 | C_100 - C this iteration | iteration | 321762.475 | C_100 - C this iteration | iteration | 429393.2702 | C_100 - C this iteration | iteration | 523941.3915 | C_100 - C this iteration | iteration | 608279.69 | C_100 - C this iteration | iteration | 713255.7746 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1845 |  |  | 90.0467 |  |  | 89.3555 |  |  | 87.0379 |  |  | 81.327 |  |  | 71.3154 |  |  | 56.58 |  |  | 40.1518 |  |  | 22.7477 |  |  | -2.5372
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1845 |  |  | 30.0467 |  |  | 29.3555 |  |  | 27.0379 |  |  | 21.327 |  |  | 11.3154 |  |  | -3.42 |  |  | -19.8482 |  |  | -37.2523 |  |  | -62.5372
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33368 |  |  | 0.32852 |  |  | 0.31065 |  |  | 0.26224 |  |  | 0.15867 |  |  | -0.060445 |  |  | -0.49433 |  |  | -1.6376 |  |  | 24.6477
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82626 |  |  | 0.82731 |  |  | 0.83441 |  |  | 0.85588 |  |  | 0.90757 |  |  | 1.0379 |  |  | 1.3464 |  |  | 1.9244 |  |  | -20.8108
[13 empty] | C Non choked w/ reducers | 7 |  | 0.7065 |  |  | 11.1604 |  |  | 27.7827 |  |  | 56.9812 |  |  | 109.9046 |  |  | 226.7684 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 82.8558
[13 empty] | C Choked w/ reducers | 7 |  | 0.63246 |  |  | 9.9812 |  |  | 24.8033 |  |  | 50.2417 |  |  | 92.7318 |  |  | 162.4844 |  |  | 293.7332 |  |  | 566.6236 |  |  | 1186.106 |  |  | -20911.3235
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.7065 |  |  | 11.1604 |  |  | 27.7827 |  |  | 56.9812 |  |  | 109.9046 |  |  | 226.7684 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -20911.3235
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0235 | 1749.4496 |  | 0.43961 | 27552.1865 |  | 4.7827 | 67465.1841 |  | 17.5812 | 131404.9585 |  | 48.9046 | 220456.6431 |  | 138.5684 | 321762.475 |  | 236393 | 429393.2702 |  | 236393 | 523941.3915 |  | 236393 | 608279.69 |  | 236393 | 713255.7746
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1784.4386 | C_100 - C this iteration | iteration | 27827.7084 | C_100 - C this iteration | iteration | 68139.836 | C_100 - C this iteration | iteration | 132719.0081 | C_100 - C this iteration | iteration | 222661.2095 | C_100 - C this iteration | iteration | 324980.0997 | C_100 - C this iteration | iteration | 433687.2029 | C_100 - C this iteration | iteration | 529180.8054 | C_100 - C this iteration | iteration | 614362.4869 | C_100 - C this iteration | iteration | 720388.3324 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1845 |  |  | 90.0439 |  |  | 89.3388 |  |  | 86.9746 |  |  | 81.1489 |  |  | 70.9361 |  |  | 55.9046 |  |  | 39.1461 |  |  | 21.3923 |  |  | -4.401
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1845 |  |  | 30.0439 |  |  | 29.3388 |  |  | 26.9746 |  |  | 21.1489 |  |  | 10.9361 |  |  | -4.0954 |  |  | -20.8539 |  |  | -38.6077 |  |  | -64.401
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33366 |  |  | 0.3284 |  |  | 0.31014 |  |  | 0.26062 |  |  | 0.15417 |  |  | -0.073257 |  |  | -0.53272 |  |  | -1.8048 |  |  | 14.6334
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82627 |  |  | 0.82738 |  |  | 0.83468 |  |  | 0.85677 |  |  | 0.91019 |  |  | 1.0459 |  |  | 1.3733 |  |  | 2.0187 |  |  | -11.9491
[13 empty] | C Non choked w/ reducers | 7 |  | 0.72063 |  |  | 11.2725 |  |  | 28.0689 |  |  | 57.6209 |  |  | 111.4763 |  |  | 232.9234 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 109.0507
[13 empty] | C Choked w/ reducers | 7 |  | 0.6451 |  |  | 10.0813 |  |  | 25.056 |  |  | 50.781 |  |  | 93.8646 |  |  | 164.9867 |  |  | 300.255 |  |  | 586.9921 |  |  | 1273.8745 |  |  | -12176.3639
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.72063 |  |  | 11.2725 |  |  | 28.0689 |  |  | 57.6209 |  |  | 111.4763 |  |  | 232.9234 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -12176.3639
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0094 | 1784.4386 |  | 0.32745 | 27827.7084 |  | 5.0689 | 68139.836 |  | 18.2209 | 132719.0081 |  | 50.4763 | 222661.2095 |  | 144.7234 | 324980.0997 |  | 236393 | 433687.2029 |  | 236393 | 529180.8054 |  | 236393 | 614362.4869 |  | 236393 | 720388.3324
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1820.1274 | C_100 - C this iteration | iteration | 28105.9855 | C_100 - C this iteration | iteration | 68821.2343 | C_100 - C this iteration | iteration | 134046.1982 | C_100 - C this iteration | iteration | 224887.8216 | C_100 - C this iteration | iteration | 328229.9007 | C_100 - C this iteration | iteration | 438024.0749 | C_100 - C this iteration | iteration | 534472.6135 | C_100 - C this iteration | iteration | 620506.1118 | C_100 - C this iteration | iteration | 727592.2157 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1844 |  |  | 90.0411 |  |  | 89.3218 |  |  | 86.9101 |  |  | 80.9673 |  |  | 70.5492 |  |  | 55.2155 |  |  | 38.1202 |  |  | 20.0095 |  |  | -6.3021
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1844 |  |  | 30.0411 |  |  | 29.3218 |  |  | 26.9101 |  |  | 20.9673 |  |  | 10.5492 |  |  | -4.7845 |  |  | -21.8798 |  |  | -39.9905 |  |  | -66.3021
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33364 |  |  | 0.32827 |  |  | 0.30963 |  |  | 0.25896 |  |  | 0.14953 |  |  | -0.086651 |  |  | -0.57397 |  |  | -1.9986 |  |  | 10.5206
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82628 |  |  | 0.82745 |  |  | 0.83495 |  |  | 0.85768 |  |  | 0.91289 |  |  | 1.0543 |  |  | 1.4022 |  |  | 2.1281 |  |  | -8.3097
[13 empty] | C Non choked w/ reducers | 7 |  | 0.73505 |  |  | 11.3858 |  |  | 28.3582 |  |  | 58.2695 |  |  | 113.0841 |  |  | 239.4727 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 130.4407
[13 empty] | C Choked w/ reducers | 7 |  | 0.65801 |  |  | 10.1825 |  |  | 25.3114 |  |  | 51.3269 |  |  | 95.0159 |  |  | 167.5504 |  |  | 307.0419 |  |  | 608.817 |  |  | 1375.5232 |  |  | -8588.129
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.73505 |  |  | 11.3858 |  |  | 28.3582 |  |  | 58.2695 |  |  | 113.0841 |  |  | 239.4727 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -8588.129
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.995 | 1820.1274 |  | 0.21416 | 28105.9855 |  | 5.3582 | 68821.2343 |  | 18.8695 | 134046.1982 |  | 52.0841 | 224887.8216 |  | 151.2727 | 328229.9007 |  | 236393 | 438024.0749 |  | 236393 | 534472.6135 |  | 236393 | 620506.1118 |  | 236393 | 727592.2157
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1856.5299 | C_100 - C this iteration | iteration | 28387.0453 | C_100 - C this iteration | iteration | 69509.4467 | C_100 - C this iteration | iteration | 135386.6601 | C_100 - C this iteration | iteration | 227136.6998 | C_100 - C this iteration | iteration | 331512.1997 | C_100 - C this iteration | iteration | 442404.3157 | C_100 - C this iteration | iteration | 539817.3396 | C_100 - C this iteration | iteration | 626711.1729 | C_100 - C this iteration | iteration | 734868.1379 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1844 |  |  | 90.0382 |  |  | 89.3044 |  |  | 86.8443 |  |  | 80.782 |  |  | 70.1545 |  |  | 54.5126 |  |  | 37.0737 |  |  | 18.599 |  |  | -8.2415
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1844 |  |  | 30.0382 |  |  | 29.3044 |  |  | 26.8443 |  |  | 20.782 |  |  | 10.1545 |  |  | -5.4874 |  |  | -22.9263 |  |  | -41.401 |  |  | -68.2415
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33362 |  |  | 0.32814 |  |  | 0.30911 |  |  | 0.25726 |  |  | 0.14474 |  |  | -0.10066 |  |  | -0.6184 |  |  | -2.226 |  |  | 8.2802
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82629 |  |  | 0.82751 |  |  | 0.83523 |  |  | 0.85861 |  |  | 0.91568 |  |  | 1.0631 |  |  | 1.4334 |  |  | 2.2565 |  |  | -6.3272
[13 empty] | C Non choked w/ reducers | 7 |  | 0.74975 |  |  | 11.5003 |  |  | 28.6507 |  |  | 58.9269 |  |  | 114.7295 |  |  | 246.463 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 149.1382
[13 empty] | C Choked w/ reducers | 7 |  | 0.67117 |  |  | 10.2846 |  |  | 25.5695 |  |  | 51.8794 |  |  | 96.1862 |  |  | 170.178 |  |  | 314.1109 |  |  | 632.2624 |  |  | 1494.6399 |  |  | -6632.848
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.74975 |  |  | 11.5003 |  |  | 28.6507 |  |  | 58.9269 |  |  | 114.7295 |  |  | 246.463 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -6632.848
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.9803 | 1856.5299 |  | 0.099719 | 28387.0453 |  | 5.6507 | 69509.4467 |  | 19.5269 | 135386.6601 |  | 53.7295 | 227136.6998 |  | 158.263 | 331512.1997 |  | 236393 | 442404.3157 |  | 236393 | 539817.3396 |  | 236393 | 626711.1729 |  | 236393 | 734868.1379
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1893.6605 | C_100 - C this iteration | iteration | 28670.9158 | C_100 - C this iteration | iteration | 70204.5411 | C_100 - C this iteration | iteration | 136740.5267 | C_100 - C this iteration | iteration | 229408.0668 | C_100 - C this iteration | iteration | 334827.3217 | C_100 - C this iteration | iteration | 446828.3588 | C_100 - C this iteration | iteration | 545215.513 | C_100 - C this iteration | iteration | 632978.2846 | C_100 - C this iteration | iteration | 742216.8192 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1844 |  |  | 90.0352 |  |  | 89.2867 |  |  | 86.7771 |  |  | 80.593 |  |  | 69.7519 |  |  | 53.7956 |  |  | 36.0062 |  |  | 17.1601 |  |  | -10.2199
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1844 |  |  | 30.0352 |  |  | 29.2867 |  |  | 26.7771 |  |  | 20.593 |  |  | 9.7519 |  |  | -6.2044 |  |  | -23.9938 |  |  | -42.8399 |  |  | -70.2199
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33359 |  |  | 0.32801 |  |  | 0.30857 |  |  | 0.25552 |  |  | 0.13981 |  |  | -0.11533 |  |  | -0.66638 |  |  | -2.4965 |  |  | 6.8709
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.8263 |  |  | 0.82758 |  |  | 0.83551 |  |  | 0.85957 |  |  | 0.91855 |  |  | 1.0723 |  |  | 1.467 |  |  | 2.4091 |  |  | -5.0801
[13 empty] | C Non choked w/ reducers | 7 |  | 0.76474 |  |  | 11.6159 |  |  | 28.9464 |  |  | 59.5935 |  |  | 116.414 |  |  | 253.9487 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 166.0828
[13 empty] | C Choked w/ reducers | 7 |  | 0.68459 |  |  | 10.3878 |  |  | 25.8303 |  |  | 52.4388 |  |  | 97.3759 |  |  | 172.8719 |  |  | 321.4805 |  |  | 657.5183 |  |  | 1636.1655 |  |  | -5402.3471
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.76474 |  |  | 11.6159 |  |  | 28.9464 |  |  | 59.5935 |  |  | 116.414 |  |  | 253.9487 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -5402.3471
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.9653 | 1893.6605 |  | 0.015885 | 28670.9158 |  | 5.9464 | 70204.5411 |  | 20.1935 | 136740.5267 |  | 55.414 | 229408.0668 |  | 165.7487 | 334827.3217 |  | 236393 | 446828.3588 |  | 236393 | 545215.513 |  | 236393 | 632978.2846 |  | 236393 | 742216.8192
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1931.5337 | C_100 - C this iteration | iteration | 28957.6249 | C_100 - C this iteration | iteration | 70906.5865 | C_100 - C this iteration | iteration | 138107.932 | C_100 - C this iteration | iteration | 231702.1475 | C_100 - C this iteration | iteration | 338175.595 | C_100 - C this iteration | iteration | 451296.6424 | C_100 - C this iteration | iteration | 550667.6682 | C_100 - C this iteration | iteration | 639308.0675 | C_100 - C this iteration | iteration | 749638.9874 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1844 |  |  | 90.0322 |  |  | 89.2687 |  |  | 86.7086 |  |  | 80.4002 |  |  | 69.3412 |  |  | 53.0642 |  |  | 34.9172 |  |  | 15.6923 |  |  | -12.238
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1844 |  |  | 30.0322 |  |  | 29.2687 |  |  | 26.7086 |  |  | 20.4002 |  |  | 9.3412 |  |  | -6.9358 |  |  | -25.0828 |  |  | -44.3077 |  |  | -72.238
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33357 |  |  | 0.32787 |  |  | 0.30803 |  |  | 0.25373 |  |  | 0.13471 |  |  | -0.13071 |  |  | -0.71835 |  |  | -2.8235 |  |  | 5.9027
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82631 |  |  | 0.82766 |  |  | 0.8358 |  |  | 0.86055 |  |  | 0.92152 |  |  | 1.0819 |  |  | 1.5034 |  |  | 2.5938 |  |  | -4.2233
[13 empty] | C Non choked w/ reducers | 7 |  | 0.78004 |  |  | 11.7327 |  |  | 29.2453 |  |  | 60.2693 |  |  | 118.1391 |  |  | 261.9944 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 181.7914
[13 empty] | C Choked w/ reducers | 7 |  | 0.69828 |  |  | 10.492 |  |  | 26.0939 |  |  | 53.005 |  |  | 98.5855 |  |  | 175.6347 |  |  | 329.1709 |  |  | 684.8052 |  |  | 1807.0985 |  |  | -4556.577
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.78004 |  |  | 11.7327 |  |  | 29.2453 |  |  | 60.2693 |  |  | 118.1391 |  |  | 261.9944 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -4556.577
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.95 | 1931.5337 |  | 0.13266 | 28957.6249 |  | 6.2453 | 70906.5865 |  | 20.8693 | 138107.932 |  | 57.1391 | 231702.1475 |  | 173.7944 | 338175.595 |  | 236393 | 451296.6424 |  | 236393 | 550667.6682 |  | 236393 | 639308.0675 |  | 236393 | 749638.9874
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 1970.1644 | C_100 - C this iteration | iteration | 29247.2012 | C_100 - C this iteration | iteration | 71615.6524 | C_100 - C this iteration | iteration | 139489.0113 | C_100 - C this iteration | iteration | 234019.169 | C_100 - C this iteration | iteration | 341557.3509 | C_100 - C this iteration | iteration | 455809.6089 | C_100 - C this iteration | iteration | 556174.3448 | C_100 - C this iteration | iteration | 645701.1481 | C_100 - C this iteration | iteration | 757135.3773 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1843 |  |  | 90.0291 |  |  | 89.2503 |  |  | 86.6388 |  |  | 80.2035 |  |  | 68.9222 |  |  | 52.3181 |  |  | 33.8063 |  |  | 14.195 |  |  | -14.2968
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1843 |  |  | 30.0291 |  |  | 29.2503 |  |  | 26.6388 |  |  | 20.2035 |  |  | 8.9222 |  |  | -7.6819 |  |  | -26.1937 |  |  | -45.805 |  |  | -74.2968
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33355 |  |  | 0.32773 |  |  | 0.30747 |  |  | 0.2519 |  |  | 0.12945 |  |  | -0.14683 |  |  | -0.77482 |  |  | -3.2268 |  |  | 5.1968
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82632 |  |  | 0.82773 |  |  | 0.8361 |  |  | 0.86156 |  |  | 0.92458 |  |  | 1.092 |  |  | 1.543 |  |  | 2.8214 |  |  | -3.5986
[13 empty] | C Non choked w/ reducers | 7 |  | 0.79564 |  |  | 11.8506 |  |  | 29.5475 |  |  | 60.9547 |  |  | 119.9066 |  |  | 270.6775 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 196.5853
[13 empty] | C Choked w/ reducers | 7 |  | 0.71225 |  |  | 10.5973 |  |  | 26.3603 |  |  | 53.5782 |  |  | 99.8155 |  |  | 178.4694 |  |  | 337.204 |  |  | 714.3812 |  |  | 2017.6903 |  |  | -3939.4433
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.79564 |  |  | 11.8506 |  |  | 29.5475 |  |  | 60.9547 |  |  | 119.9066 |  |  | 270.6775 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -3939.4433
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.9344 | 1970.1644 |  | 0.25063 | 29247.2012 |  | 6.5475 | 71615.6524 |  | 21.5547 | 139489.0113 |  | 58.9066 | 234019.169 |  | 182.4775 | 341557.3509 |  | 236393 | 455809.6089 |  | 236393 | 556174.3448 |  | 236393 | 645701.1481 |  | 236393 | 757135.3773
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2009.5677 | C_100 - C this iteration | iteration | 29539.6732 | C_100 - C this iteration | iteration | 72331.8089 | C_100 - C this iteration | iteration | 140883.9014 | C_100 - C this iteration | iteration | 236359.3607 | C_100 - C this iteration | iteration | 344972.9244 | C_100 - C this iteration | iteration | 460367.7049 | C_100 - C this iteration | iteration | 561736.0883 | C_100 - C this iteration | iteration | 652158.1596 | C_100 - C this iteration | iteration | 764706.7311 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1843 |  |  | 90.026 |  |  | 89.2315 |  |  | 86.5675 |  |  | 80.0029 |  |  | 68.4948 |  |  | 51.557 |  |  | 32.6731 |  |  | 12.6676 |  |  | -16.3968
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1843 |  |  | 30.026 |  |  | 29.2315 |  |  | 26.5675 |  |  | 20.0029 |  |  | 8.4948 |  |  | -8.443 |  |  | -27.3269 |  |  | -47.3324 |  |  | -76.3968
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33353 |  |  | 0.32759 |  |  | 0.3069 |  |  | 0.25003 |  |  | 0.12402 |  |  | -0.16376 |  |  | -0.83637 |  |  | -3.7365 |  |  | 4.6592
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82634 |  |  | 0.8278 |  |  | 0.83641 |  |  | 0.86259 |  |  | 0.92775 |  |  | 1.1026 |  |  | 1.5861 |  |  | 3.1091 |  |  | -3.123
[13 empty] | C Non choked w/ reducers | 7 |  | 0.81155 |  |  | 11.9698 |  |  | 29.853 |  |  | 61.6497 |  |  | 121.7184 |  |  | 280.0911 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 210.6814
[13 empty] | C Choked w/ reducers | 7 |  | 0.72649 |  |  | 10.7037 |  |  | 26.6295 |  |  | 54.1586 |  |  | 101.0664 |  |  | 181.3788 |  |  | 345.6039 |  |  | 746.5499 |  |  | 2283.5836 |  |  | -3469.2337
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.81155 |  |  | 11.9698 |  |  | 29.853 |  |  | 61.6497 |  |  | 121.7184 |  |  | 280.0911 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -3469.2337
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.9184 | 2009.5677 |  | 0.36979 | 29539.6732 |  | 6.853 | 72331.8089 |  | 22.2497 | 140883.9014 |  | 60.7184 | 236359.3607 |  | 191.8911 | 344972.9244 |  | 236393 | 460367.7049 |  | 236393 | 561736.0883 |  | 236393 | 652158.1596 |  | 236393 | 764706.7311
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2049.759 | C_100 - C this iteration | iteration | 29835.0699 | C_100 - C this iteration | iteration | 73055.127 | C_100 - C this iteration | iteration | 142292.7405 | C_100 - C this iteration | iteration | 238722.9543 | C_100 - C this iteration | iteration | 348422.6537 | C_100 - C this iteration | iteration | 464971.382 | C_100 - C this iteration | iteration | 567353.4492 | C_100 - C this iteration | iteration | 658679.7412 | C_100 - C this iteration | iteration | 772353.7984 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1843 |  |  | 90.0228 |  |  | 89.2123 |  |  | 86.4948 |  |  | 79.7982 |  |  | 68.0589 |  |  | 50.7805 |  |  | 31.5171 |  |  | 11.1095 |  |  | -18.5391
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1843 |  |  | 30.0228 |  |  | 29.2123 |  |  | 26.4948 |  |  | 19.7982 |  |  | 8.0589 |  |  | -9.2195 |  |  | -28.4829 |  |  | -48.8905 |  |  | -78.5391
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.3335 |  |  | 0.32745 |  |  | 0.30632 |  |  | 0.2481 |  |  | 0.11841 |  |  | -0.18156 |  |  | -0.90373 |  |  | -4.4008 |  |  | 4.2364
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82635 |  |  | 0.82788 |  |  | 0.83672 |  |  | 0.86364 |  |  | 0.93102 |  |  | 1.1138 |  |  | 1.6333 |  |  | 3.484 |  |  | -2.7488
[13 empty] | C Non choked w/ reducers | 7 |  | 0.82778 |  |  | 12.0902 |  |  | 30.1619 |  |  | 62.3547 |  |  | 123.5763 |  |  | 290.349 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 224.2349
[13 empty] | C Choked w/ reducers | 7 |  | 0.74102 |  |  | 10.8111 |  |  | 26.9016 |  |  | 54.7462 |  |  | 102.3389 |  |  | 184.3661 |  |  | 354.397 |  |  | 781.6714 |  |  | 2629.8932 |  |  | -3099.0287
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.82778 |  |  | 12.0902 |  |  | 30.1619 |  |  | 62.3547 |  |  | 123.5763 |  |  | 290.349 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -3099.0287
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.9022 | 2049.759 |  | 0.49017 | 29835.0699 |  | 7.1619 | 73055.127 |  | 22.9547 | 142292.7405 |  | 62.5763 | 238722.9543 |  | 202.149 | 348422.6537 |  | 236393 | 464971.382 |  | 236393 | 567353.4492 |  | 236393 | 658679.7412 |  | 236393 | 772353.7984
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2090.7542 | C_100 - C this iteration | iteration | 30133.4206 | C_100 - C this iteration | iteration | 73785.6783 | C_100 - C this iteration | iteration | 143715.6679 | C_100 - C this iteration | iteration | 241110.1838 | C_100 - C this iteration | iteration | 351906.8802 | C_100 - C this iteration | iteration | 469621.0958 | C_100 - C this iteration | iteration | 573026.9837 | C_100 - C this iteration | iteration | 665266.5386 | C_100 - C this iteration | iteration | 780077.3364 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1842 |  |  | 90.0195 |  |  | 89.1928 |  |  | 86.4206 |  |  | 79.5895 |  |  | 67.6141 |  |  | 49.9885 |  |  | 30.3379 |  |  | 9.5201 |  |  | -20.7245
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1842 |  |  | 30.0195 |  |  | 29.1928 |  |  | 26.4206 |  |  | 19.5895 |  |  | 7.6141 |  |  | -10.0115 |  |  | -29.6621 |  |  | -50.4799 |  |  | -80.7245
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33348 |  |  | 0.3273 |  |  | 0.30572 |  |  | 0.24613 |  |  | 0.11261 |  |  | -0.20028 |  |  | -0.97773 |  |  | -5.3025 |  |  | 3.8951
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82636 |  |  | 0.82796 |  |  | 0.83703 |  |  | 0.86473 |  |  | 0.9344 |  |  | 1.1255 |  |  | 1.6852 |  |  | 3.993 |  |  | -2.4468
[13 empty] | C Non choked w/ reducers | 7 |  | 0.84434 |  |  | 12.2118 |  |  | 30.4742 |  |  | 63.0697 |  |  | 125.4823 |  |  | 301.5915 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 237.3619
[13 empty] | C Choked w/ reducers | 7 |  | 0.75584 |  |  | 10.9196 |  |  | 27.1765 |  |  | 55.3411 |  |  | 103.6334 |  |  | 187.4346 |  |  | 363.6123 |  |  | 820.1753 |  |  | 3099.6546 |  |  | -2799.9647
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.84434 |  |  | 12.2118 |  |  | 30.4742 |  |  | 63.0697 |  |  | 125.4823 |  |  | 301.5915 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -2799.9647
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.8857 | 2090.7542 |  | 0.61177 | 30133.4206 |  | 7.4742 | 73785.6783 |  | 23.6697 | 143715.6679 |  | 64.4823 | 241110.1838 |  | 213.3915 | 351906.8802 |  | 236393 | 469621.0958 |  | 236393 | 573026.9837 |  | 236393 | 665266.5386 |  | 236393 | 780077.3364
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2132.5693 | C_100 - C this iteration | iteration | 30434.7548 | C_100 - C this iteration | iteration | 74523.5351 | C_100 - C this iteration | iteration | 145152.8245 | C_100 - C this iteration | iteration | 243521.2857 | C_100 - C this iteration | iteration | 355425.949 | C_100 - C this iteration | iteration | 474317.3068 | C_100 - C this iteration | iteration | 578757.2535 | C_100 - C this iteration | iteration | 671919.204 | C_100 - C this iteration | iteration | 787878.1097 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1842 |  |  | 90.0162 |  |  | 89.1728 |  |  | 86.3449 |  |  | 79.3765 |  |  | 67.1605 |  |  | 49.1805 |  |  | 29.1349 |  |  | 7.8987 |  |  | -22.9538
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1842 |  |  | 30.0162 |  |  | 29.1728 |  |  | 26.3449 |  |  | 19.3765 |  |  | 7.1605 |  |  | -10.8195 |  |  | -30.8651 |  |  | -52.1013 |  |  | -82.9538
[13 empty] | Press drop ratio this iteration |  |  | 0.3347 |  |  | 0.33345 |  |  | 0.32715 |  |  | 0.30511 |  |  | 0.24411 |  |  | 0.10662 |  |  | -0.21999 |  |  | -1.0594 |  |  | -6.5962 |  |  | 3.6139
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82637 |  |  | 0.82803 |  |  | 0.83736 |  |  | 0.86584 |  |  | 0.93789 |  |  | 1.1379 |  |  | 1.7424 |  |  | 4.7232 |  |  | -2.198
[13 empty] | C Non choked w/ reducers | 7 |  | 0.86123 |  |  | 12.3346 |  |  | 30.7899 |  |  | 63.795 |  |  | 127.4388 |  |  | 313.9946 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 250.1527
[13 empty] | C Choked w/ reducers | 7 |  | 0.77096 |  |  | 11.0292 |  |  | 27.4544 |  |  | 55.9435 |  |  | 104.9506 |  |  | 190.5877 |  |  | 373.2816 |  |  | 862.5792 |  |  | 3773.2781 |  |  | -2553.3111
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.86123 |  |  | 12.3346 |  |  | 30.7899 |  |  | 63.795 |  |  | 127.4388 |  |  | 313.9946 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -2553.3111
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.8688 | 2132.5693 |  | 0.73461 | 30434.7548 |  | 7.7899 | 74523.5351 |  | 24.395 | 145152.8245 |  | 66.4388 | 243521.2857 |  | 225.7946 | 355425.949 |  | 236393 | 474317.3068 |  | 236393 | 578757.2535 |  | 236393 | 671919.204 |  | 236393 | 787878.1097
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2175.2207 | C_100 - C this iteration | iteration | 30739.1024 | C_100 - C this iteration | iteration | 75268.7704 | C_100 - C this iteration | iteration | 146604.3528 | C_100 - C this iteration | iteration | 245956.4985 | C_100 - C this iteration | iteration | 358980.2085 | C_100 - C this iteration | iteration | 479060.4798 | C_100 - C this iteration | iteration | 584544.826 | C_100 - C this iteration | iteration | 678638.396 | C_100 - C this iteration | iteration | 795756.8908 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1842 |  |  | 90.0128 |  |  | 89.1525 |  |  | 86.2677 |  |  | 79.1592 |  |  | 66.6977 |  |  | 48.3564 |  |  | 27.9078 |  |  | 6.2448 |  |  | -25.2279
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1842 |  |  | 30.0128 |  |  | 29.1525 |  |  | 26.2677 |  |  | 19.1592 |  |  | 6.6977 |  |  | -11.6436 |  |  | -32.0922 |  |  | -53.7552 |  |  | -85.2279
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33343 |  |  | 0.327 |  |  | 0.30449 |  |  | 0.24203 |  |  | 0.10042 |  |  | -0.24079 |  |  | -1.1499 |  |  | -8.608 |  |  | 3.3783
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82639 |  |  | 0.82812 |  |  | 0.83769 |  |  | 0.86698 |  |  | 0.9415 |  |  | 1.1509 |  |  | 1.8058 |  |  | 5.8588 |  |  | -1.9895
[13 empty] | C Non choked w/ reducers | 7 |  | 0.87845 |  |  | 12.4587 |  |  | 31.1092 |  |  | 64.5309 |  |  | 129.4479 |  |  | 327.7818 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 262.6794
[13 empty] | C Choked w/ reducers | 7 |  | 0.78638 |  |  | 11.1399 |  |  | 27.7353 |  |  | 56.5535 |  |  | 106.291 |  |  | 193.8293 |  |  | 383.4403 |  |  | 909.5119 |  |  | 4820.3749 |  |  | -2346.382
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.87845 |  |  | 12.4587 |  |  | 31.1092 |  |  | 64.5309 |  |  | 129.4479 |  |  | 327.7818 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -2346.382
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.8515 | 2175.2207 |  | 0.85869 | 30739.1024 |  | 8.1092 | 75268.7704 |  | 25.1309 | 146604.3528 |  | 68.4479 | 245956.4985 |  | 239.5818 | 358980.2085 |  | 236393 | 479060.4798 |  | 236393 | 584544.826 |  | 236393 | 678638.396 |  | 236393 | 795756.8908
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2218.7251 | C_100 - C this iteration | iteration | 31046.4934 | C_100 - C this iteration | iteration | 76021.4581 | C_100 - C this iteration | iteration | 148070.3963 | C_100 - C this iteration | iteration | 248416.0635 | C_100 - C this iteration | iteration | 362570.0106 | C_100 - C this iteration | iteration | 483851.0846 | C_100 - C this iteration | iteration | 590390.2743 | C_100 - C this iteration | iteration | 685424.78 | C_100 - C this iteration | iteration | 803714.4597 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1841 |  |  | 90.0094 |  |  | 89.1317 |  |  | 86.189 |  |  | 78.9376 |  |  | 66.2256 |  |  | 47.5156 |  |  | 26.6561 |  |  | 4.5576 |  |  | -27.5477
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1841 |  |  | 30.0094 |  |  | 29.1317 |  |  | 26.189 |  |  | 18.9376 |  |  | 6.2256 |  |  | -12.4844 |  |  | -33.3439 |  |  | -55.4424 |  |  | -87.5477
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.3334 |  |  | 0.32684 |  |  | 0.30386 |  |  | 0.23991 |  |  | 0.094005 |  |  | -0.26274 |  |  | -1.2509 |  |  | -12.1649 |  |  | 3.178
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.8264 |  |  | 0.8282 |  |  | 0.83803 |  |  | 0.86815 |  |  | 0.94524 |  |  | 1.1647 |  |  | 1.8766 |  |  | 7.8665 |  |  | -1.8123
[13 empty] | C Non choked w/ reducers | 7 |  | 0.89602 |  |  | 12.584 |  |  | 31.432 |  |  | 65.2775 |  |  | 131.5122 |  |  | 343.2424 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 275.0012
[13 empty] | C Choked w/ reducers | 7 |  | 0.80211 |  |  | 11.2517 |  |  | 28.0192 |  |  | 57.1712 |  |  | 107.6553 |  |  | 197.1631 |  |  | 394.1273 |  |  | 961.745 |  |  | 6670.9146 |  |  | -2170.2801
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.89602 |  |  | 12.584 |  |  | 31.432 |  |  | 65.2775 |  |  | 131.5122 |  |  | 343.2424 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -2170.2801
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.834 | 2218.7251 |  | 0.98405 | 31046.4934 |  | 8.432 | 76021.4581 |  | 25.8775 | 148070.3963 |  | 70.5122 | 248416.0635 |  | 255.0424 | 362570.0106 |  | 236393 | 483851.0846 |  | 236393 | 590390.2743 |  | 236393 | 685424.78 |  | 236393 | 803714.4597
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2263.0996 | C_100 - C this iteration | iteration | 31356.9583 | C_100 - C this iteration | iteration | 76781.6727 | C_100 - C this iteration | iteration | 149551.1003 | C_100 - C this iteration | iteration | 250900.2241 | C_100 - C this iteration | iteration | 366195.7107 | C_100 - C this iteration | iteration | 488689.5955 | C_100 - C this iteration | iteration | 596294.177 | C_100 - C this iteration | iteration | 692279.0278 | C_100 - C this iteration | iteration | 811751.6043 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1841 |  |  | 90.0058 |  |  | 89.1105 |  |  | 86.1087 |  |  | 78.7115 |  |  | 65.744 |  |  | 46.6579 |  |  | 25.3791 |  |  | 2.8365 |  |  | -29.9141
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1841 |  |  | 30.0058 |  |  | 29.1105 |  |  | 26.1087 |  |  | 18.7115 |  |  | 5.744 |  |  | -13.3421 |  |  | -34.6209 |  |  | -57.1635 |  |  | -89.9141
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33338 |  |  | 0.32668 |  |  | 0.30321 |  |  | 0.23772 |  |  | 0.087369 |  |  | -0.28595 |  |  | -1.3641 |  |  | -20.1532 |  |  | 3.0057
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82641 |  |  | 0.82828 |  |  | 0.83837 |  |  | 0.86935 |  |  | 0.9491 |  |  | 1.1792 |  |  | 1.956 |  |  | 12.3755 |  |  | -1.6598
[13 empty] | C Non choked w/ reducers | 7 |  | 0.91394 |  |  | 12.7107 |  |  | 31.7584 |  |  | 66.0351 |  |  | 133.6344 |  |  | 360.7592 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 287.1679
[13 empty] | C Choked w/ reducers | 7 |  | 0.81815 |  |  | 11.3647 |  |  | 28.3061 |  |  | 57.7967 |  |  | 109.0442 |  |  | 200.5934 |  |  | 405.3858 |  |  | 1020.2358 |  |  | 10825.9014 |  |  | -2018.5807
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.91394 |  |  | 12.7107 |  |  | 31.7584 |  |  | 66.0351 |  |  | 133.6344 |  |  | 360.7592 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -2018.5807
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.8161 | 2263.0996 |  | 1.1107 | 31356.9583 |  | 8.7584 | 76781.6727 |  | 26.6351 | 149551.1003 |  | 72.6344 | 250900.2241 |  | 272.5592 | 366195.7107 |  | 236393 | 488689.5955 |  | 236393 | 596294.177 |  | 236393 | 692279.0278 |  | 236393 | 811751.6043
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2308.3616 | C_100 - C this iteration | iteration | 31670.5279 | C_100 - C this iteration | iteration | 77549.4894 | C_100 - C this iteration | iteration | 151046.6113 | C_100 - C this iteration | iteration | 253409.2264 | C_100 - C this iteration | iteration | 369857.6678 | C_100 - C this iteration | iteration | 493576.4914 | C_100 - C this iteration | iteration | 602257.1188 | C_100 - C this iteration | iteration | 699201.8181 | C_100 - C this iteration | iteration | 819869.1204 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1841 |  |  | 90.0022 |  |  | 89.0889 |  |  | 86.0267 |  |  | 78.4809 |  |  | 65.2527 |  |  | 45.783 |  |  | 24.0765 |  |  | 1.0807 |  |  | -32.3281
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1841 |  |  | 30.0022 |  |  | 29.0889 |  |  | 26.0267 |  |  | 18.4809 |  |  | 5.2527 |  |  | -14.217 |  |  | -35.9235 |  |  | -58.9193 |  |  | -92.3281
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33335 |  |  | 0.32652 |  |  | 0.30254 |  |  | 0.23548 |  |  | 0.080498 |  |  | -0.31053 |  |  | -1.4921 |  |  | -54.5172 |  |  | 2.856
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82643 |  |  | 0.82837 |  |  | 0.83873 |  |  | 0.87058 |  |  | 0.9531 |  |  | 1.1946 |  |  | 2.0456 |  |  | 31.7724 |  |  | -1.5273
[13 empty] | C Non choked w/ reducers | 7 |  | 0.93222 |  |  | 12.8386 |  |  | 32.0885 |  |  | 66.804 |  |  | 135.8173 |  |  | 380.8503 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 299.2219
[13 empty] | C Choked w/ reducers | 7 |  | 0.83452 |  |  | 11.4788 |  |  | 28.5961 |  |  | 58.4303 |  |  | 110.4583 |  |  | 204.1247 |  |  | 417.2638 |  |  | 1086.1874 |  |  | 28697.0517 |  |  | -1886.5284
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.93222 |  |  | 12.8386 |  |  | 32.0885 |  |  | 66.804 |  |  | 135.8173 |  |  | 380.8503 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -1886.5284
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.7978 | 2308.3616 |  | 1.2386 | 31670.5279 |  | 9.0885 | 77549.4894 |  | 27.404 | 151046.6113 |  | 74.8173 | 253409.2264 |  | 292.6503 | 369857.6678 |  | 236393 | 493576.4914 |  | 236393 | 602257.1188 |  | 236393 | 699201.8181 |  | 236393 | 819869.1204
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2354.5288 | C_100 - C this iteration | iteration | 31987.2332 | C_100 - C this iteration | iteration | 78324.9843 | C_100 - C this iteration | iteration | 152557.0774 | C_100 - C this iteration | iteration | 255943.3186 | C_100 - C this iteration | iteration | 373556.2445 | C_100 - C this iteration | iteration | 498512.2564 | C_100 - C this iteration | iteration | 608279.69 | C_100 - C this iteration | iteration | 706193.8363 | C_100 - C this iteration | iteration | 828067.8116 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.184 |  |  | 89.9986 |  |  | 89.0669 |  |  | 85.9432 |  |  | 78.2457 |  |  | 64.7516 |  |  | 44.8906 |  |  | 22.7477 |  |  | -0.71025 |  |  | -34.7906
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.184 |  |  | 29.9986 |  |  | 29.0669 |  |  | 25.9432 |  |  | 18.2457 |  |  | 4.7516 |  |  | -15.1094 |  |  | -37.2523 |  |  | -60.7103 |  |  | -94.7906
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33332 |  |  | 0.32635 |  |  | 0.30186 |  |  | 0.23318 |  |  | 0.073382 |  |  | -0.33658 |  |  | -1.6376 |  |  | 85.4773 |  |  | 2.7246
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82644 |  |  | 0.82846 |  |  | 0.83909 |  |  | 0.87184 |  |  | 0.95725 |  |  | 1.211 |  |  | 2.1476 |  |  | -47.248 |  |  | -1.411
[13 empty] | C Non choked w/ reducers | 7 |  | 0.95087 |  |  | 12.9678 |  |  | 32.4222 |  |  | 67.5844 |  |  | 138.0641 |  |  | 404.2387 |  |  | #NUM! |  |  | #NUM! |  |  | 51.7504 |  |  | 311.2006
[13 empty] | C Choked w/ reducers | 7 |  | 0.85121 |  |  | 11.5941 |  |  | 28.8892 |  |  | 59.072 |  |  | 111.8983 |  |  | 207.7615 |  |  | 429.8152 |  |  | 1161.1321 |  |  | -44103.3004 |  |  | -1770.528
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.95087 |  |  | 12.9678 |  |  | 32.4222 |  |  | 67.5844 |  |  | 138.0641 |  |  | 404.2387 |  |  | #NUM! |  |  | #NUM! |  |  | -44103.3004 |  |  | -1770.528
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.7791 | 2354.5288 |  | 1.3678 | 31987.2332 |  | 9.4222 | 78324.9843 |  | 28.1844 | 152557.0774 |  | 77.0641 | 255943.3186 |  | 316.0387 | 373556.2445 |  | 236393 | 498512.2564 |  | 236393 | 608279.69 |  | 236393 | 706193.8363 |  | 236393 | 828067.8116
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2401.6194 | C_100 - C this iteration | iteration | 32307.1055 | C_100 - C this iteration | iteration | 79108.2342 | C_100 - C this iteration | iteration | 154082.6482 | C_100 - C this iteration | iteration | 258502.7518 | C_100 - C this iteration | iteration | 377291.8069 | C_100 - C this iteration | iteration | 503497.3789 | C_100 - C this iteration | iteration | 614362.4869 | C_100 - C this iteration | iteration | 713255.7746 | C_100 - C this iteration | iteration | 836348.4897 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.184 |  |  | 89.9948 |  |  | 89.0444 |  |  | 85.8579 |  |  | 78.0057 |  |  | 64.2404 |  |  | 43.9801 |  |  | 21.3923 |  |  | -2.5372 |  |  | -37.3026
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.184 |  |  | 29.9948 |  |  | 29.0444 |  |  | 25.8579 |  |  | 18.0057 |  |  | 4.2404 |  |  | -16.0199 |  |  | -38.6077 |  |  | -62.5372 |  |  | -97.3026
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33329 |  |  | 0.32618 |  |  | 0.30117 |  |  | 0.23083 |  |  | 0.066008 |  |  | -0.36425 |  |  | -1.8048 |  |  | 24.6477 |  |  | 2.6085
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82646 |  |  | 0.82854 |  |  | 0.83946 |  |  | 0.87314 |  |  | 0.96155 |  |  | 1.2283 |  |  | 2.2647 |  |  | -12.9125 |  |  | -1.3082
[13 empty] | C Non choked w/ reducers | 7 |  | 0.96989 |  |  | 13.0984 |  |  | 32.7597 |  |  | 68.3765 |  |  | 140.3779 |  |  | 431.9696 |  |  | #NUM! |  |  | #NUM! |  |  | 99.6999 |  |  | 323.1367
[13 empty] | C Choked w/ reducers | 7 |  | 0.86823 |  |  | 11.7105 |  |  | 29.1855 |  |  | 59.722 |  |  | 113.3649 |  |  | 211.509 |  |  | 443.0998 |  |  | 1247.0526 |  |  | -12469.2772 |  |  | -1667.8111
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.96989 |  |  | 13.0984 |  |  | 32.7597 |  |  | 68.3765 |  |  | 140.3779 |  |  | 431.9696 |  |  | #NUM! |  |  | #NUM! |  |  | -12469.2772 |  |  | -1667.8111
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.7601 | 2401.6194 |  | 1.4984 | 32307.1055 |  | 9.7597 | 79108.2342 |  | 28.9765 | 154082.6482 |  | 79.3779 | 258502.7518 |  | 343.7696 | 377291.8069 |  | 236393 | 503497.3789 |  | 236393 | 614362.4869 |  | 236393 | 713255.7746 |  | 236393 | 836348.4897
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2449.6518 | C_100 - C this iteration | iteration | 32630.1766 | C_100 - C this iteration | iteration | 79899.3165 | C_100 - C this iteration | iteration | 155623.4747 | C_100 - C this iteration | iteration | 261087.7793 | C_100 - C this iteration | iteration | 381064.725 | C_100 - C this iteration | iteration | 508532.3527 | C_100 - C this iteration | iteration | 620506.1118 | C_100 - C this iteration | iteration | 720388.3324 | C_100 - C this iteration | iteration | 844711.9746 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1839 |  |  | 89.991 |  |  | 89.0215 |  |  | 85.7709 |  |  | 77.7609 |  |  | 63.7189 |  |  | 43.0514 |  |  | 20.0095 |  |  | -4.401 |  |  | -39.8651
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1839 |  |  | 29.991 |  |  | 29.0215 |  |  | 25.7709 |  |  | 17.7609 |  |  | 3.7189 |  |  | -16.9486 |  |  | -39.9905 |  |  | -64.401 |  |  | -99.8651
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33327 |  |  | 0.32601 |  |  | 0.30046 |  |  | 0.2284 |  |  | 0.058364 |  |  | -0.39368 |  |  | -1.9986 |  |  | 14.6334 |  |  | 2.5051
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82647 |  |  | 0.82864 |  |  | 0.83984 |  |  | 0.87447 |  |  | 0.966 |  |  | 1.2467 |  |  | 2.4005 |  |  | -7.2599 |  |  | -1.2167
[13 empty] | C Non choked w/ reducers | 7 |  | 0.98928 |  |  | 13.2302 |  |  | 33.101 |  |  | 69.1806 |  |  | 142.7624 |  |  | 465.6221 |  |  | #NUM! |  |  | #NUM! |  |  | 134.0071 |  |  | 335.06
[13 empty] | C Choked w/ reducers | 7 |  | 0.8856 |  |  | 11.8281 |  |  | 29.4849 |  |  | 60.3804 |  |  | 114.8591 |  |  | 215.3724 |  |  | 457.185 |  |  | 1346.5611 |  |  | -7260.6814 |  |  | -1576.2114
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.98928 |  |  | 13.2302 |  |  | 33.101 |  |  | 69.1806 |  |  | 142.7624 |  |  | 465.6221 |  |  | #NUM! |  |  | #NUM! |  |  | -7260.6814 |  |  | -1576.2114
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.7407 | 2449.6518 |  | 1.6302 | 32630.1766 |  | 10.101 | 79899.3165 |  | 29.7806 | 155623.4747 |  | 81.7624 | 261087.7793 |  | 377.4221 | 381064.725 |  | 236393 | 508532.3527 |  | 236393 | 620506.1118 |  | 236393 | 720388.3324 |  | 236393 | 844711.9746
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2498.6448 | C_100 - C this iteration | iteration | 32956.4783 | C_100 - C this iteration | iteration | 80698.3097 | C_100 - C this iteration | iteration | 157179.7094 | C_100 - C this iteration | iteration | 263698.6571 | C_100 - C this iteration | iteration | 384875.3722 | C_100 - C this iteration | iteration | 513617.6762 | C_100 - C this iteration | iteration | 626711.1729 | C_100 - C this iteration | iteration | 727592.2157 | C_100 - C this iteration | iteration | 853159.0943 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1839 |  |  | 89.9871 |  |  | 88.9981 |  |  | 85.6822 |  |  | 77.5112 |  |  | 63.1869 |  |  | 42.104 |  |  | 18.599 |  |  | -6.3021 |  |  | -42.4791
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1839 |  |  | 29.9871 |  |  | 28.9981 |  |  | 25.6822 |  |  | 17.5112 |  |  | 3.1869 |  |  | -17.896 |  |  | -41.401 |  |  | -66.3021 |  |  | -102.4791
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33324 |  |  | 0.32583 |  |  | 0.29974 |  |  | 0.22592 |  |  | 0.050436 |  |  | -0.42504 |  |  | -2.226 |  |  | 10.5206 |  |  | 2.4125
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82649 |  |  | 0.82873 |  |  | 0.84022 |  |  | 0.87584 |  |  | 0.97062 |  |  | 1.2664 |  |  | 2.5599 |  |  | -4.9384 |  |  | -1.1348
[13 empty] | C Non choked w/ reducers | 7 |  | 1.0091 |  |  | 13.3634 |  |  | 33.4461 |  |  | 69.9971 |  |  | 145.2214 |  |  | 507.7212 |  |  | #NUM! |  |  | #NUM! |  |  | 163.8723 |  |  | 346.9978
[13 empty] | C Choked w/ reducers | 7 |  | 0.90331 |  |  | 11.9469 |  |  | 29.7876 |  |  | 61.0473 |  |  | 116.3814 |  |  | 219.3575 |  |  | 472.1469 |  |  | 1463.1697 |  |  | -5121.0418 |  |  | -1494.0093
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.0091 |  |  | 13.3634 |  |  | 33.4461 |  |  | 69.9971 |  |  | 145.2214 |  |  | 507.7212 |  |  | #NUM! |  |  | #NUM! |  |  | -5121.0418 |  |  | -1494.0093
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.7209 | 2498.6448 |  | 1.7634 | 32956.4783 |  | 10.4461 | 80698.3097 |  | 30.5971 | 157179.7094 |  | 84.2214 | 263698.6571 |  | 419.5212 | 384875.3722 |  | 236393 | 513617.6762 |  | 236393 | 626711.1729 |  | 236393 | 727592.2157 |  | 236393 | 853159.0943
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2548.6177 | C_100 - C this iteration | iteration | 33286.0431 | C_100 - C this iteration | iteration | 81505.2928 | C_100 - C this iteration | iteration | 158751.5065 | C_100 - C this iteration | iteration | 266335.6437 | C_100 - C this iteration | iteration | 388724.126 | C_100 - C this iteration | iteration | 518753.853 | C_100 - C this iteration | iteration | 632978.2846 | C_100 - C this iteration | iteration | 734868.1379 | C_100 - C this iteration | iteration | 861690.6853 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1839 |  |  | 89.9831 |  |  | 88.9743 |  |  | 85.5917 |  |  | 77.2564 |  |  | 62.6442 |  |  | 41.1376 |  |  | 17.1601 |  |  | -8.2415 |  |  | -45.1457
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1839 |  |  | 29.9831 |  |  | 28.9743 |  |  | 25.5917 |  |  | 17.2564 |  |  | 2.6442 |  |  | -18.8624 |  |  | -42.8399 |  |  | -68.2415 |  |  | -105.1457
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33321 |  |  | 0.32565 |  |  | 0.299 |  |  | 0.22337 |  |  | 0.04221 |  |  | -0.45852 |  |  | -2.4965 |  |  | 8.2802 |  |  | 2.329
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.8265 |  |  | 0.82882 |  |  | 0.84062 |  |  | 0.87724 |  |  | 0.97541 |  |  | 1.2874 |  |  | 2.7495 |  |  | -3.6738 |  |  | -1.061
[13 empty] | C Non choked w/ reducers | 7 |  | 1.0293 |  |  | 13.498 |  |  | 33.7952 |  |  | 70.8261 |  |  | 147.759 |  |  | 562.6193 |  |  | #NUM! |  |  | #NUM! |  |  | 191.7682 |  |  | 358.9751
[13 empty] | C Choked w/ reducers | 7 |  | 0.92137 |  |  | 12.0669 |  |  | 30.0935 |  |  | 61.723 |  |  | 117.9328 |  |  | 223.4703 |  |  | 488.0712 |  |  | 1601.7154 |  |  | -3955.1213 |  |  | -1419.8226
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.0293 |  |  | 13.498 |  |  | 33.7952 |  |  | 70.8261 |  |  | 147.759 |  |  | 562.6193 |  |  | #NUM! |  |  | #NUM! |  |  | -3955.1213 |  |  | -1419.8226
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.7007 | 2548.6177 |  | 1.898 | 33286.0431 |  | 10.7952 | 81505.2928 |  | 31.4261 | 158751.5065 |  | 86.759 | 266335.6437 |  | 474.4193 | 388724.126 |  | 236393 | 518753.853 |  | 236393 | 632978.2846 |  | 236393 | 734868.1379 |  | 236393 | 861690.6853
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2599.5901 | C_100 - C this iteration | iteration | 33618.9035 | C_100 - C this iteration | iteration | 82320.3457 | C_100 - C this iteration | iteration | 160339.0216 | C_100 - C this iteration | iteration | 268999.0001 | C_100 - C this iteration | iteration | 392611.3672 | C_100 - C this iteration | iteration | 523941.3915 | C_100 - C this iteration | iteration | 639308.0675 | C_100 - C this iteration | iteration | 742216.8192 | C_100 - C this iteration | iteration | 870307.5921 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1838 |  |  | 89.979 |  |  | 88.9499 |  |  | 85.4994 |  |  | 76.9966 |  |  | 62.0907 |  |  | 40.1518 |  |  | 15.6923 |  |  | -10.2199 |  |  | -47.8658
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1838 |  |  | 29.979 |  |  | 28.9499 |  |  | 25.4994 |  |  | 16.9966 |  |  | 2.0907 |  |  | -19.8482 |  |  | -44.3077 |  |  | -70.2199 |  |  | -107.8658
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33318 |  |  | 0.32546 |  |  | 0.29824 |  |  | 0.22074 |  |  | 0.033671 |  |  | -0.49433 |  |  | -2.8235 |  |  | 6.8709 |  |  | 2.2535
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82652 |  |  | 0.82892 |  |  | 0.84102 |  |  | 0.87868 |  |  | 0.98038 |  |  | 1.3098 |  |  | 2.9787 |  |  | -2.8783 |  |  | -0.99413
[13 empty] | C Non choked w/ reducers | 7 |  | 1.0498 |  |  | 13.634 |  |  | 34.1481 |  |  | 71.668 |  |  | 150.3797 |  |  | 638.6483 |  |  | #NUM! |  |  | #NUM! |  |  | 218.852 |  |  | 371.0157
[13 empty] | C Choked w/ reducers | 7 |  | 0.9398 |  |  | 12.1881 |  |  | 30.4028 |  |  | 62.4075 |  |  | 119.5141 |  |  | 227.7173 |  |  | 505.0555 |  |  | 1769.0494 |  |  | -3221.3821 |  |  | -1352.5274
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.0498 |  |  | 13.634 |  |  | 34.1481 |  |  | 71.668 |  |  | 150.3797 |  |  | 638.6483 |  |  | #NUM! |  |  | #NUM! |  |  | -3221.3821 |  |  | -1352.5274
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.6802 | 2599.5901 |  | 2.034 | 33618.9035 |  | 11.1481 | 82320.3457 |  | 32.268 | 160339.0216 |  | 89.3797 | 268999.0001 |  | 550.4483 | 392611.3672 |  | 236393 | 523941.3915 |  | 236393 | 639308.0675 |  | 236393 | 742216.8192 |  | 236393 | 870307.5921
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2651.5819 | C_100 - C this iteration | iteration | 33955.0926 | C_100 - C this iteration | iteration | 83143.5492 | C_100 - C this iteration | iteration | 161942.4118 | C_100 - C this iteration | iteration | 271688.9901 | C_100 - C this iteration | iteration | 396537.4809 | C_100 - C this iteration | iteration | 529180.8054 | C_100 - C this iteration | iteration | 645701.1481 | C_100 - C this iteration | iteration | 749638.9874 | C_100 - C this iteration | iteration | 879010.6681 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1838 |  |  | 89.9749 |  |  | 88.9251 |  |  | 85.4052 |  |  | 76.7315 |  |  | 61.526 |  |  | 39.1461 |  |  | 14.195 |  |  | -12.238 |  |  | -50.6406
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1838 |  |  | 29.9749 |  |  | 28.9251 |  |  | 25.4052 |  |  | 16.7315 |  |  | 1.526 |  |  | -20.8539 |  |  | -45.805 |  |  | -72.238 |  |  | -110.6406
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33315 |  |  | 0.32527 |  |  | 0.29747 |  |  | 0.21805 |  |  | 0.024802 |  |  | -0.53272 |  |  | -3.2268 |  |  | 5.9027 |  |  | 2.1848
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82653 |  |  | 0.82902 |  |  | 0.84143 |  |  | 0.88016 |  |  | 0.98555 |  |  | 1.3339 |  |  | 3.2613 |  |  | -2.3318 |  |  | -0.93335
[13 empty] | C Non choked w/ reducers | 7 |  | 1.0708 |  |  | 13.7713 |  |  | 34.5051 |  |  | 72.5232 |  |  | 153.0884 |  |  | 754.49 |  |  | #NUM! |  |  | #NUM! |  |  | 245.8254 |  |  | 383.142
[13 empty] | C Choked w/ reducers | 7 |  | 0.9586 |  |  | 12.3106 |  |  | 30.7154 |  |  | 63.1011 |  |  | 121.1263 |  |  | 232.1054 |  |  | 523.2107 |  |  | 1975.2071 |  |  | -2717.0553 |  |  | -1291.2007
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.0708 |  |  | 13.7713 |  |  | 34.5051 |  |  | 72.5232 |  |  | 153.0884 |  |  | 754.49 |  |  | #NUM! |  |  | #NUM! |  |  | -2717.0553 |  |  | -1291.2007
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.6592 | 2651.5819 |  | 2.1713 | 33955.0926 |  | 11.5051 | 83143.5492 |  | 33.1232 | 161942.4118 |  | 92.0884 | 271688.9901 |  | 666.29 | 396537.4809 |  | 236393 | 529180.8054 |  | 236393 | 645701.1481 |  | 236393 | 749638.9874 |  | 236393 | 879010.6681
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2704.6135 | C_100 - C this iteration | iteration | 34294.6435 | C_100 - C this iteration | iteration | 83974.9847 | C_100 - C this iteration | iteration | 163561.8359 | C_100 - C this iteration | iteration | 274405.8801 | C_100 - C this iteration | iteration | 400502.8557 | C_100 - C this iteration | iteration | 534472.6135 | C_100 - C this iteration | iteration | 652158.1596 | C_100 - C this iteration | iteration | 757135.3773 | C_100 - C this iteration | iteration | 887800.7747 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1837 |  |  | 89.9707 |  |  | 88.8998 |  |  | 85.3091 |  |  | 76.4611 |  |  | 60.9499 |  |  | 38.1202 |  |  | 12.6676 |  |  | -14.2968 |  |  | -53.4712
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1837 |  |  | 29.9707 |  |  | 28.8998 |  |  | 25.3091 |  |  | 16.4611 |  |  | 0.94993 |  |  | -21.8798 |  |  | -47.3324 |  |  | -74.2968 |  |  | -113.4712
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33312 |  |  | 0.32508 |  |  | 0.29668 |  |  | 0.21529 |  |  | 0.015585 |  |  | -0.57397 |  |  | -3.7365 |  |  | 5.1968 |  |  | 2.1221
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82655 |  |  | 0.82912 |  |  | 0.84186 |  |  | 0.88168 |  |  | 0.99092 |  |  | 1.3597 |  |  | 3.6184 |  |  | -1.9333 |  |  | -0.87785
[13 empty] | C Non choked w/ reducers | 7 |  | 1.0923 |  |  | 13.9101 |  |  | 34.8661 |  |  | 73.3918 |  |  | 155.8903 |  |  | 965.1309 |  |  | #NUM! |  |  | #NUM! |  |  | 273.1957 |  |  | 395.3758
[13 empty] | C Choked w/ reducers | 7 |  | 0.97777 |  |  | 12.4343 |  |  | 31.0314 |  |  | 63.8039 |  |  | 122.7702 |  |  | 236.642 |  |  | 542.6642 |  |  | 2235.5019 |  |  | -2349.0627 |  |  | -1235.0771
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.0923 |  |  | 13.9101 |  |  | 34.8661 |  |  | 73.3918 |  |  | 155.8903 |  |  | 965.1309 |  |  | #NUM! |  |  | #NUM! |  |  | -2349.0627 |  |  | -1235.0771
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.6377 | 2704.6135 |  | 2.3101 | 34294.6435 |  | 11.8661 | 83974.9847 |  | 33.9918 | 163561.8359 |  | 94.8903 | 274405.8801 |  | 876.9309 | 400502.8557 |  | 236393 | 534472.6135 |  | 236393 | 652158.1596 |  | 236393 | 757135.3773 |  | 236393 | 887800.7747
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2758.7058 | C_100 - C this iteration | iteration | 34637.5899 | C_100 - C this iteration | iteration | 84814.7345 | C_100 - C this iteration | iteration | 165197.4543 | C_100 - C this iteration | iteration | 277149.9389 | C_100 - C this iteration | iteration | 404507.8842 | C_100 - C this iteration | iteration | 539817.3396 | C_100 - C this iteration | iteration | 658679.7412 | C_100 - C this iteration | iteration | 764706.7311 | C_100 - C this iteration | iteration | 896678.7825 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1837 |  |  | 89.9664 |  |  | 88.8739 |  |  | 85.2111 |  |  | 76.1852 |  |  | 60.3623 |  |  | 37.0737 |  |  | 11.1095 |  |  | -16.3968 |  |  | -56.3587
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1837 |  |  | 29.9664 |  |  | 28.8739 |  |  | 25.2111 |  |  | 16.1852 |  |  | 0.3623 |  |  | -22.9263 |  |  | -48.8905 |  |  | -76.3968 |  |  | -116.3587
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33308 |  |  | 0.32489 |  |  | 0.29587 |  |  | 0.21245 |  |  | 0.0060021 |  |  | -0.6184 |  |  | -4.4008 |  |  | 4.6592 |  |  | 2.0646
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82657 |  |  | 0.82922 |  |  | 0.84229 |  |  | 0.88324 |  |  | 0.9965 |  |  | 1.3876 |  |  | 4.0839 |  |  | -1.6299 |  |  | -0.82697
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1141 |  |  | 14.0502 |  |  | 35.2313 |  |  | 74.2743 |  |  | 158.7913 |  |  | 1577.1799 |  |  | #NUM! |  |  | #NUM! |  |  | 301.383 |  |  | 407.738
[13 empty] | C Choked w/ reducers | 7 |  | 0.99733 |  |  | 12.5592 |  |  | 31.3508 |  |  | 64.5161 |  |  | 124.4469 |  |  | 241.3352 |  |  | 563.5621 |  |  | 2574.5198 |  |  | -2068.68 |  |  | -1183.517
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.1141 |  |  | 14.0502 |  |  | 35.2313 |  |  | 74.2743 |  |  | 158.7913 |  |  | 1577.1799 |  |  | #NUM! |  |  | #NUM! |  |  | -2068.68 |  |  | -1183.517
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.6159 | 2758.7058 |  | 2.4502 | 34637.5899 |  | 12.2313 | 84814.7345 |  | 34.8743 | 165197.4543 |  | 97.7913 | 277149.9389 |  | 1488.9799 | 404507.8842 |  | 236393 | 539817.3396 |  | 236393 | 658679.7412 |  | 236393 | 764706.7311 |  | 236393 | 896678.7825
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2813.8799 | C_100 - C this iteration | iteration | 34983.9658 | C_100 - C this iteration | iteration | 85662.8819 | C_100 - C this iteration | iteration | 166849.4288 | C_100 - C this iteration | iteration | 279921.4382 | C_100 - C this iteration | iteration | 408552.9631 | C_100 - C this iteration | iteration | 545215.513 | C_100 - C this iteration | iteration | 665266.5386 | C_100 - C this iteration | iteration | 772353.7984 | C_100 - C this iteration | iteration | 905645.5703 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1836 |  |  | 89.962 |  |  | 88.8476 |  |  | 85.1111 |  |  | 75.9038 |  |  | 59.7629 |  |  | 36.0062 |  |  | 9.5201 |  |  | -18.5391 |  |  | -59.3042
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1836 |  |  | 29.962 |  |  | 28.8476 |  |  | 25.1111 |  |  | 15.9038 |  |  | -0.23713 |  |  | -23.9938 |  |  | -50.4799 |  |  | -78.5391 |  |  | -119.3042
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33305 |  |  | 0.32469 |  |  | 0.29504 |  |  | 0.20953 |  |  | -0.0039679 |  |  | -0.66638 |  |  | -5.3025 |  |  | 4.2364 |  |  | 2.0117
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82658 |  |  | 0.82933 |  |  | 0.84273 |  |  | 0.88485 |  |  | 1.0023 |  |  | 1.4177 |  |  | 4.7158 |  |  | -1.3912 |  |  | -0.78018
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1364 |  |  | 14.1918 |  |  | 35.6006 |  |  | 75.171 |  |  | 161.7975 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 330.7752 |  |  | 420.2494
[13 empty] | C Choked w/ reducers | 7 |  | 1.0173 |  |  | 12.6854 |  |  | 31.6737 |  |  | 65.2378 |  |  | 126.1573 |  |  | 246.1934 |  |  | 586.0737 |  |  | 3034.3902 |  |  | -1847.9293 |  |  | -1135.9813
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.1364 |  |  | 14.1918 |  |  | 35.6006 |  |  | 75.171 |  |  | 161.7975 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -1847.9293 |  |  | -1135.9813
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.5936 | 2813.8799 |  | 2.5918 | 34983.9658 |  | 12.6006 | 85662.8819 |  | 35.771 | 166849.4288 |  | 100.7975 | 279921.4382 |  | 236393 | 408552.9631 |  | 236393 | 545215.513 |  | 236393 | 665266.5386 |  | 236393 | 772353.7984 |  | 236393 | 905645.5703
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2870.1575 | C_100 - C this iteration | iteration | 35333.8055 | C_100 - C this iteration | iteration | 86519.5107 | C_100 - C this iteration | iteration | 168517.9231 | C_100 - C this iteration | iteration | 282720.6526 | C_100 - C this iteration | iteration | 412638.4927 | C_100 - C this iteration | iteration | 550667.6682 | C_100 - C this iteration | iteration | 671919.204 | C_100 - C this iteration | iteration | 780077.3364 | C_100 - C this iteration | iteration | 914702.026 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1835 |  |  | 89.9575 |  |  | 88.8207 |  |  | 85.0091 |  |  | 75.6167 |  |  | 59.1514 |  |  | 34.9172 |  |  | 7.8987 |  |  | -20.7245 |  |  | -62.309
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1835 |  |  | 29.9575 |  |  | 28.8207 |  |  | 25.0091 |  |  | 15.6167 |  |  | -0.84862 |  |  | -25.0828 |  |  | -52.1013 |  |  | -80.7245 |  |  | -122.309
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33302 |  |  | 0.32448 |  |  | 0.29419 |  |  | 0.20653 |  |  | -0.014347 |  |  | -0.71835 |  |  | -6.5962 |  |  | 3.8951 |  |  | 1.9629
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.8266 |  |  | 0.82944 |  |  | 0.84318 |  |  | 0.8865 |  |  | 1.0084 |  |  | 1.4502 |  |  | 5.6224 |  |  | -1.1986 |  |  | -0.73701
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1591 |  |  | 14.3349 |  |  | 35.9742 |  |  | 76.0823 |  |  | 164.9159 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 361.7611 |  |  | 432.9304
[13 empty] | C Choked w/ reducers | 7 |  | 1.0376 |  |  | 12.8129 |  |  | 32.0001 |  |  | 65.9692 |  |  | 127.9026 |  |  | 251.2258 |  |  | 610.3957 |  |  | 3693.8302 |  |  | -1669.5995 |  |  | -1092.0127
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.1591 |  |  | 14.3349 |  |  | 35.9742 |  |  | 76.0823 |  |  | 164.9159 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -1669.5995 |  |  | -1092.0127
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.5709 | 2870.1575 |  | 2.7349 | 35333.8055 |  | 12.9742 | 86519.5107 |  | 36.6823 | 168517.9231 |  | 103.9159 | 282720.6526 |  | 236393 | 412638.4927 |  | 236393 | 550667.6682 |  | 236393 | 671919.204 |  | 236393 | 780077.3364 |  | 236393 | 914702.026
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2927.5606 | C_100 - C this iteration | iteration | 35687.1436 | C_100 - C this iteration | iteration | 87384.7058 | C_100 - C this iteration | iteration | 170203.1023 | C_100 - C this iteration | iteration | 285547.8591 | C_100 - C this iteration | iteration | 416764.8776 | C_100 - C this iteration | iteration | 556174.3448 | C_100 - C this iteration | iteration | 678638.396 | C_100 - C this iteration | iteration | 787878.1097 | C_100 - C this iteration | iteration | 923849.0463 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1835 |  |  | 89.9529 |  |  | 88.7933 |  |  | 84.9051 |  |  | 75.3239 |  |  | 58.5276 |  |  | 33.8063 |  |  | 6.2448 |  |  | -22.9538 |  |  | -65.3741
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1835 |  |  | 29.9529 |  |  | 28.7933 |  |  | 24.9051 |  |  | 15.3239 |  |  | -1.4724 |  |  | -26.1937 |  |  | -53.7552 |  |  | -82.9538 |  |  | -125.3741
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33298 |  |  | 0.32427 |  |  | 0.29333 |  |  | 0.20344 |  |  | -0.025157 |  |  | -0.77482 |  |  | -8.608 |  |  | 3.6139 |  |  | 1.9178
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82662 |  |  | 0.82955 |  |  | 0.84364 |  |  | 0.88819 |  |  | 1.0147 |  |  | 1.4856 |  |  | 7.0323 |  |  | -1.0399 |  |  | -0.69706
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1823 |  |  | 14.4794 |  |  | 36.352 |  |  | 77.0085 |  |  | 168.1539 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 394.7562 |  |  | 445.8016
[13 empty] | C Choked w/ reducers | 7 |  | 1.0584 |  |  | 12.9417 |  |  | 32.3301 |  |  | 66.7105 |  |  | 129.6838 |  |  | 256.4424 |  |  | 636.758 |  |  | 4718.88 |  |  | -1522.5217 |  |  | -1051.2207
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.1823 |  |  | 14.4794 |  |  | 36.352 |  |  | 77.0085 |  |  | 168.1539 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -1522.5217 |  |  | -1051.2207
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.5477 | 2927.5606 |  | 2.8794 | 35687.1436 |  | 13.352 | 87384.7058 |  | 37.6085 | 170203.1023 |  | 107.1539 | 285547.8591 |  | 236393 | 416764.8776 |  | 236393 | 556174.3448 |  | 236393 | 678638.396 |  | 236393 | 787878.1097 |  | 236393 | 923849.0463
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 2986.1119 | C_100 - C this iteration | iteration | 36044.015 | C_100 - C this iteration | iteration | 88258.5528 | C_100 - C this iteration | iteration | 171905.1333 | C_100 - C this iteration | iteration | 288403.3377 | C_100 - C this iteration | iteration | 420932.5264 | C_100 - C this iteration | iteration | 561736.0883 | C_100 - C this iteration | iteration | 685424.78 | C_100 - C this iteration | iteration | 795756.8908 | C_100 - C this iteration | iteration | 933087.5367 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1834 |  |  | 89.9483 |  |  | 88.7653 |  |  | 84.799 |  |  | 75.0252 |  |  | 57.8913 |  |  | 32.6731 |  |  | 4.5576 |  |  | -25.2279 |  |  | -68.5009
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1834 |  |  | 29.9483 |  |  | 28.7653 |  |  | 24.799 |  |  | 15.0252 |  |  | -2.1087 |  |  | -27.3269 |  |  | -55.4424 |  |  | -85.2279 |  |  | -128.5009
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33295 |  |  | 0.32406 |  |  | 0.29244 |  |  | 0.20027 |  |  | -0.036425 |  |  | -0.83637 |  |  | -12.1649 |  |  | 3.3783 |  |  | 1.8759
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82664 |  |  | 0.82966 |  |  | 0.84411 |  |  | 0.88993 |  |  | 1.0212 |  |  | 1.5242 |  |  | 9.5249 |  |  | -0.90691 |  |  | -0.65999
[13 empty] | C Non choked w/ reducers | 7 |  | 1.2059 |  |  | 14.6254 |  |  | 36.7342 |  |  | 77.9501 |  |  | 171.5198 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 430.2257 |  |  | 458.8835
[13 empty] | C Choked w/ reducers | 7 |  | 1.0795 |  |  | 13.0718 |  |  | 32.6637 |  |  | 67.462 |  |  | 131.5022 |  |  | 261.8537 |  |  | 665.4313 |  |  | 6530.4559 |  |  | -1399.1313 |  |  | -1013.2699
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.2059 |  |  | 14.6254 |  |  | 36.7342 |  |  | 77.9501 |  |  | 171.5198 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -1399.1313 |  |  | -1013.2699
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.5241 | 2986.1119 |  | 3.0254 | 36044.015 |  | 13.7342 | 88258.5528 |  | 38.5501 | 171905.1333 |  | 110.5198 | 288403.3377 |  | 236393 | 420932.5264 |  | 236393 | 561736.0883 |  | 236393 | 685424.78 |  | 236393 | 795756.8908 |  | 236393 | 933087.5367
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3045.8341 | C_100 - C this iteration | iteration | 36404.4551 | C_100 - C this iteration | iteration | 89141.1384 | C_100 - C this iteration | iteration | 173624.1847 | C_100 - C this iteration | iteration | 291287.3711 | C_100 - C this iteration | iteration | 425141.8517 | C_100 - C this iteration | iteration | 567353.4492 | C_100 - C this iteration | iteration | 692279.0278 | C_100 - C this iteration | iteration | 803714.4597 | C_100 - C this iteration | iteration | 942418.4121 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1833 |  |  | 89.9435 |  |  | 88.7368 |  |  | 84.6907 |  |  | 74.7205 |  |  | 57.2422 |  |  | 31.5171 |  |  | 2.8365 |  |  | -27.5477 |  |  | -71.6904
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1833 |  |  | 29.9435 |  |  | 28.7368 |  |  | 24.6907 |  |  | 14.7205 |  |  | -2.7578 |  |  | -28.4829 |  |  | -57.1635 |  |  | -87.5477 |  |  | -131.6904
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33291 |  |  | 0.32384 |  |  | 0.29154 |  |  | 0.19701 |  |  | -0.048178 |  |  | -0.90373 |  |  | -20.1532 |  |  | 3.178 |  |  | 1.8369
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82666 |  |  | 0.82977 |  |  | 0.84459 |  |  | 0.89173 |  |  | 1.0281 |  |  | 1.5664 |  |  | 15.1228 |  |  | -0.79386 |  |  | -0.6255
[13 empty] | C Non choked w/ reducers | 7 |  | 1.2301 |  |  | 14.7729 |  |  | 37.1208 |  |  | 78.9073 |  |  | 175.0228 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 468.7095 |  |  | 472.1971
[13 empty] | C Choked w/ reducers | 7 |  | 1.1011 |  |  | 13.2032 |  |  | 33.0009 |  |  | 68.2237 |  |  | 133.3588 |  |  | 267.4712 |  |  | 696.7366 |  |  | 10597.9579 |  |  | -1294.123 |  |  | -977.8703
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.2301 |  |  | 14.7729 |  |  | 37.1208 |  |  | 78.9073 |  |  | 175.0228 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -1294.123 |  |  | -977.8703
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.4999 | 3045.8341 |  | 3.1729 | 36404.4551 |  | 14.1208 | 89141.1384 |  | 39.5073 | 173624.1847 |  | 114.0228 | 291287.3711 |  | 236393 | 425141.8517 |  | 236393 | 567353.4492 |  | 236393 | 692279.0278 |  | 236393 | 803714.4597 |  | 236393 | 942418.4121
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3106.7508 | C_100 - C this iteration | iteration | 36768.4997 | C_100 - C this iteration | iteration | 90032.5497 | C_100 - C this iteration | iteration | 175360.4265 | C_100 - C this iteration | iteration | 294200.2448 | C_100 - C this iteration | iteration | 429393.2702 | C_100 - C this iteration | iteration | 573026.9837 | C_100 - C this iteration | iteration | 699201.8181 | C_100 - C this iteration | iteration | 811751.6043 | C_100 - C this iteration | iteration | 951842.5962 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1833 |  |  | 89.9386 |  |  | 88.7077 |  |  | 84.5803 |  |  | 74.4097 |  |  | 56.58 |  |  | 30.3379 |  |  | 1.0807 |  |  | -29.9141 |  |  | -74.9441
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1833 |  |  | 29.9386 |  |  | 28.7077 |  |  | 24.5803 |  |  | 14.4097 |  |  | -3.42 |  |  | -29.6621 |  |  | -58.9193 |  |  | -89.9141 |  |  | -134.9441
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33288 |  |  | 0.32362 |  |  | 0.29061 |  |  | 0.19365 |  |  | -0.060445 |  |  | -0.97773 |  |  | -54.5172 |  |  | 3.0057 |  |  | 1.8006
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82667 |  |  | 0.82989 |  |  | 0.84509 |  |  | 0.89357 |  |  | 1.0352 |  |  | 1.6128 |  |  | 39.2042 |  |  | -0.6966 |  |  | -0.59335
[13 empty] | C Non choked w/ reducers | 7 |  | 1.2547 |  |  | 14.9219 |  |  | 37.5119 |  |  | 79.8807 |  |  | 178.6729 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 510.8525 |  |  | 485.7639
[13 empty] | C Choked w/ reducers | 7 |  | 1.1232 |  |  | 13.336 |  |  | 33.3419 |  |  | 68.9959 |  |  | 135.2551 |  |  | 273.3075 |  |  | 731.0567 |  |  | 28092.8241 |  |  | -1203.6657 |  |  | -944.7702
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.2547 |  |  | 14.9219 |  |  | 37.5119 |  |  | 79.8807 |  |  | 178.6729 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -1203.6657 |  |  | -944.7702
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.4753 | 3106.7508 |  | 3.3219 | 36768.4997 |  | 14.5119 | 90032.5497 |  | 40.4807 | 175360.4265 |  | 117.6729 | 294200.2448 |  | 236393 | 429393.2702 |  | 236393 | 573026.9837 |  | 236393 | 699201.8181 |  | 236393 | 811751.6043 |  | 236393 | 951842.5962
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3168.8858 | C_100 - C this iteration | iteration | 37136.1847 | C_100 - C this iteration | iteration | 90932.8752 | C_100 - C this iteration | iteration | 177114.0308 | C_100 - C this iteration | iteration | 297142.2473 | C_100 - C this iteration | iteration | 433687.2029 | C_100 - C this iteration | iteration | 578757.2535 | C_100 - C this iteration | iteration | 706193.8363 | C_100 - C this iteration | iteration | 819869.1204 | C_100 - C this iteration | iteration | 961361.0222 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1832 |  |  | 89.9337 |  |  | 88.678 |  |  | 84.4676 |  |  | 74.0926 |  |  | 55.9046 |  |  | 29.1349 |  |  | -0.71025 |  |  | -32.3281 |  |  | -78.2632
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1832 |  |  | 29.9337 |  |  | 28.678 |  |  | 24.4676 |  |  | 14.0926 |  |  | -4.0954 |  |  | -30.8651 |  |  | -60.7103 |  |  | -92.3281 |  |  | -138.2632
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33284 |  |  | 0.32339 |  |  | 0.28967 |  |  | 0.1902 |  |  | -0.073257 |  |  | -1.0594 |  |  | 85.4773 |  |  | 2.856 |  |  | 1.7666
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82669 |  |  | 0.83001 |  |  | 0.84559 |  |  | 0.89547 |  |  | 1.0427 |  |  | 1.664 |  |  | -58.9002 |  |  | -0.61206 |  |  | -0.5633
[13 empty] | C Non choked w/ reducers | 7 |  | 1.2798 |  |  | 15.0724 |  |  | 37.9076 |  |  | 80.8707 |  |  | 182.4812 |  |  | #NUM! |  |  | #NUM! |  |  | 36.4723 |  |  | 557.4433 |  |  | 499.6058
[13 empty] | C Choked w/ reducers | 7 |  | 1.1456 |  |  | 13.4701 |  |  | 33.6866 |  |  | 69.7788 |  |  | 137.1923 |  |  | 279.3758 |  |  | 768.8531 |  |  | -43174.6884 |  |  | -1124.9238 |  |  | -913.7501
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.2798 |  |  | 15.0724 |  |  | 37.9076 |  |  | 80.8707 |  |  | 182.4812 |  |  | #NUM! |  |  | #NUM! |  |  | -43174.6884 |  |  | -1124.9238 |  |  | -913.7501
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.4502 | 3168.8858 |  | 3.4724 | 37136.1847 |  | 14.9076 | 90932.8752 |  | 41.4707 | 177114.0308 |  | 121.4812 | 297142.2473 |  | 236393 | 433687.2029 |  | 236393 | 578757.2535 |  | 236393 | 706193.8363 |  | 236393 | 819869.1204 |  | 236393 | 961361.0222
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3232.2635 | C_100 - C this iteration | iteration | 37507.5465 | C_100 - C this iteration | iteration | 91842.204 | C_100 - C this iteration | iteration | 178885.1711 | C_100 - C this iteration | iteration | 300113.6697 | C_100 - C this iteration | iteration | 438024.0749 | C_100 - C this iteration | iteration | 584544.826 | C_100 - C this iteration | iteration | 713255.7746 | C_100 - C this iteration | iteration | 828067.8116 | C_100 - C this iteration | iteration | 970974.6324 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1831 |  |  | 89.9286 |  |  | 88.6477 |  |  | 84.3527 |  |  | 73.7691 |  |  | 55.2155 |  |  | 27.9078 |  |  | -2.5372 |  |  | -34.7906 |  |  | -81.649
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1831 |  |  | 29.9286 |  |  | 28.6477 |  |  | 24.3527 |  |  | 13.7691 |  |  | -4.7845 |  |  | -32.0922 |  |  | -62.5372 |  |  | -94.7906 |  |  | -141.649
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.3328 |  |  | 0.32316 |  |  | 0.2887 |  |  | 0.18665 |  |  | -0.086651 |  |  | -1.1499 |  |  | 24.6477 |  |  | 2.7246 |  |  | 1.7349
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82671 |  |  | 0.83013 |  |  | 0.84611 |  |  | 0.89742 |  |  | 1.0505 |  |  | 1.7207 |  |  | -16.2724 |  |  | -0.53791 |  |  | -0.53517
[13 empty] | C Non choked w/ reducers | 7 |  | 1.3054 |  |  | 15.2245 |  |  | 38.3078 |  |  | 81.8777 |  |  | 186.4603 |  |  | #NUM! |  |  | #NUM! |  |  | 69.508 |  |  | 609.4669 |  |  | 513.7456
[13 empty] | C Choked w/ reducers | 7 |  | 1.1685 |  |  | 13.6055 |  |  | 34.0351 |  |  | 70.5726 |  |  | 139.1717 |  |  | 285.6907 |  |  | 810.6862 |  |  | -12206.7317 |  |  | -1055.7535 |  |  | -884.6174
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.3054 |  |  | 15.2245 |  |  | 38.3078 |  |  | 81.8777 |  |  | 186.4603 |  |  | #NUM! |  |  | #NUM! |  |  | -12206.7317 |  |  | -1055.7535 |  |  | -884.6174
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.4246 | 3232.2635 |  | 3.6245 | 37507.5465 |  | 15.3078 | 91842.204 |  | 42.4777 | 178885.1711 |  | 125.4603 | 300113.6697 |  | 236393 | 438024.0749 |  | 236393 | 584544.826 |  | 236393 | 713255.7746 |  | 236393 | 828067.8116 |  | 236393 | 970974.6324
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3296.9088 | C_100 - C this iteration | iteration | 37882.622 | C_100 - C this iteration | iteration | 92760.626 | C_100 - C this iteration | iteration | 180674.0228 | C_100 - C this iteration | iteration | 303114.8064 | C_100 - C this iteration | iteration | 442404.3157 | C_100 - C this iteration | iteration | 590390.2743 | C_100 - C this iteration | iteration | 720388.3324 | C_100 - C this iteration | iteration | 836348.4897 | C_100 - C this iteration | iteration | 980684.3787 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1831 |  |  | 89.9235 |  |  | 88.6168 |  |  | 84.2355 |  |  | 73.4392 |  |  | 54.5126 |  |  | 26.6561 |  |  | -4.401 |  |  | -37.3026 |  |  | -85.1029
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1831 |  |  | 29.9235 |  |  | 28.6168 |  |  | 24.2355 |  |  | 13.4392 |  |  | -5.4874 |  |  | -33.3439 |  |  | -64.401 |  |  | -97.3026 |  |  | -145.1029
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33277 |  |  | 0.32293 |  |  | 0.28771 |  |  | 0.183 |  |  | -0.10066 |  |  | -1.2509 |  |  | 14.6334 |  |  | 2.6085 |  |  | 1.705
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82673 |  |  | 0.83025 |  |  | 0.84663 |  |  | 0.89943 |  |  | 1.0586 |  |  | 1.784 |  |  | -9.2547 |  |  | -0.47236 |  |  | -0.50878
[13 empty] | C Non choked w/ reducers | 7 |  | 1.3315 |  |  | 15.3781 |  |  | 38.7127 |  |  | 82.9022 |  |  | 190.6239 |  |  | #NUM! |  |  | #NUM! |  |  | 92.3588 |  |  | 668.1796 |  |  | 528.2068
[13 empty] | C Choked w/ reducers | 7 |  | 1.1919 |  |  | 13.7424 |  |  | 34.3874 |  |  | 71.3775 |  |  | 141.195 |  |  | 292.2682 |  |  | 857.2437 |  |  | -7107.8049 |  |  | -994.5042 |  |  | -857.2028
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.3315 |  |  | 15.3781 |  |  | 38.7127 |  |  | 82.9022 |  |  | 190.6239 |  |  | #NUM! |  |  | #NUM! |  |  | -7107.8049 |  |  | -994.5042 |  |  | -857.2028
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.3985 | 3296.9088 |  | 3.7781 | 37882.622 |  | 15.7127 | 92760.626 |  | 43.5022 | 180674.0228 |  | 129.6239 | 303114.8064 |  | 236393 | 442404.3157 |  | 236393 | 590390.2743 |  | 236393 | 720388.3324 |  | 236393 | 836348.4897 |  | 236393 | 980684.3787
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3362.847 | C_100 - C this iteration | iteration | 38261.4482 | C_100 - C this iteration | iteration | 93688.2323 | C_100 - C this iteration | iteration | 182480.763 | C_100 - C this iteration | iteration | 306145.9545 | C_100 - C this iteration | iteration | 446828.3588 | C_100 - C this iteration | iteration | 596294.177 | C_100 - C this iteration | iteration | 727592.2157 | C_100 - C this iteration | iteration | 844711.9746 | C_100 - C this iteration | iteration | 990491.2225 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.183 |  |  | 89.9182 |  |  | 88.5852 |  |  | 84.1159 |  |  | 73.1026 |  |  | 53.7956 |  |  | 25.3791 |  |  | -6.3021 |  |  | -39.8651 |  |  | -88.6262
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.183 |  |  | 29.9182 |  |  | 28.5852 |  |  | 24.1159 |  |  | 13.1026 |  |  | -6.2044 |  |  | -34.6209 |  |  | -66.3021 |  |  | -99.8651 |  |  | -148.6262
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33273 |  |  | 0.32269 |  |  | 0.2867 |  |  | 0.17924 |  |  | -0.11533 |  |  | -1.3641 |  |  | 10.5206 |  |  | 2.5051 |  |  | 1.677
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82675 |  |  | 0.83038 |  |  | 0.84717 |  |  | 0.90149 |  |  | 1.0672 |  |  | 1.855 |  |  | -6.3725 |  |  | -0.414 |  |  | -0.48398
[13 empty] | C Non choked w/ reducers | 7 |  | 1.3581 |  |  | 15.5333 |  |  | 39.1224 |  |  | 83.9447 |  |  | 194.9876 |  |  | #NUM! |  |  | #NUM! |  |  | 111.5735 |  |  | 735.2169 |  |  | 543.0143
[13 empty] | C Choked w/ reducers | 7 |  | 1.2157 |  |  | 13.8806 |  |  | 34.7436 |  |  | 72.1938 |  |  | 143.2636 |  |  | 299.1253 |  |  | 909.3791 |  |  | -5013.2162 |  |  | -939.8839 |  |  | -831.3564
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.3581 |  |  | 15.5333 |  |  | 39.1224 |  |  | 83.9447 |  |  | 194.9876 |  |  | #NUM! |  |  | #NUM! |  |  | -5013.2162 |  |  | -939.8839 |  |  | -831.3564
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.3719 | 3362.847 |  | 3.9333 | 38261.4482 |  | 16.1224 | 93688.2323 |  | 44.5447 | 182480.763 |  | 133.9876 | 306145.9545 |  | 236393 | 446828.3588 |  | 236393 | 596294.177 |  | 236393 | 727592.2157 |  | 236393 | 844711.9746 |  | 236393 | 990491.2225
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3430.1039 | C_100 - C this iteration | iteration | 38644.0627 | C_100 - C this iteration | iteration | 94625.1146 | C_100 - C this iteration | iteration | 184305.5707 | C_100 - C this iteration | iteration | 309207.4141 | C_100 - C this iteration | iteration | 451296.6424 | C_100 - C this iteration | iteration | 602257.1188 | C_100 - C this iteration | iteration | 734868.1379 | C_100 - C this iteration | iteration | 853159.0943 | C_100 - C this iteration | iteration | 1000396.1347 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1829 |  |  | 89.9129 |  |  | 88.5531 |  |  | 83.9939 |  |  | 72.7592 |  |  | 53.0642 |  |  | 24.0765 |  |  | -8.2415 |  |  | -42.4791 |  |  | -92.2203
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1829 |  |  | 29.9129 |  |  | 28.5531 |  |  | 23.9939 |  |  | 12.7592 |  |  | -6.9358 |  |  | -35.9235 |  |  | -68.2415 |  |  | -102.4791 |  |  | -152.2203
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.33269 |  |  | 0.32244 |  |  | 0.28566 |  |  | 0.17536 |  |  | -0.13071 |  |  | -1.4921 |  |  | 8.2802 |  |  | 2.4125 |  |  | 1.6506
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82677 |  |  | 0.83051 |  |  | 0.84773 |  |  | 0.90362 |  |  | 1.0761 |  |  | 1.9352 |  |  | -4.8025 |  |  | -0.36172 |  |  | -0.46063
[13 empty] | C Non choked w/ reducers | 7 |  | 1.3853 |  |  | 15.6902 |  |  | 39.5369 |  |  | 85.0057 |  |  | 199.5688 |  |  | #NUM! |  |  | #NUM! |  |  | 128.8852 |  |  | 812.7561 |  |  | 558.1939
[13 empty] | C Choked w/ reducers | 7 |  | 1.2401 |  |  | 14.0202 |  |  | 35.1038 |  |  | 73.0216 |  |  | 145.379 |  |  | 306.2809 |  |  | 968.1645 |  |  | -3871.8446 |  |  | -890.8674 |  |  | -806.9455
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.3853 |  |  | 15.6902 |  |  | 39.5369 |  |  | 85.0057 |  |  | 199.5688 |  |  | #NUM! |  |  | #NUM! |  |  | -3871.8446 |  |  | -890.8674 |  |  | -806.9455
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.3447 | 3430.1039 |  | 4.0902 | 38644.0627 |  | 16.5369 | 94625.1146 |  | 45.6057 | 184305.5707 |  | 138.5688 | 309207.4141 |  | 236393 | 451296.6424 |  | 236393 | 602257.1188 |  | 236393 | 734868.1379 |  | 236393 | 853159.0943 |  | 236393 | 1000396.1347
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3498.706 | C_100 - C this iteration | iteration | 39030.5033 | C_100 - C this iteration | iteration | 95571.3658 | C_100 - C this iteration | iteration | 186148.6264 | C_100 - C this iteration | iteration | 312299.4882 | C_100 - C this iteration | iteration | 455809.6089 | C_100 - C this iteration | iteration | 608279.69 | C_100 - C this iteration | iteration | 742216.8192 | C_100 - C this iteration | iteration | 861690.6853 | C_100 - C this iteration | iteration | 1010400.0961 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1828 |  |  | 89.9074 |  |  | 88.5203 |  |  | 83.8695 |  |  | 72.409 |  |  | 52.3181 |  |  | 22.7477 |  |  | -10.2199 |  |  | -45.1457 |  |  | -95.8866
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1828 |  |  | 29.9074 |  |  | 28.5203 |  |  | 23.8695 |  |  | 12.409 |  |  | -7.6819 |  |  | -37.2523 |  |  | -70.2199 |  |  | -105.1457 |  |  | -155.8866
[13 empty] | Press drop ratio this iteration |  |  | 0.33468 |  |  | 0.33265 |  |  | 0.32219 |  |  | 0.2846 |  |  | 0.17137 |  |  | -0.14683 |  |  | -1.6376 |  |  | 6.8709 |  |  | 2.329 |  |  | 1.6257
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82679 |  |  | 0.83064 |  |  | 0.84829 |  |  | 0.90582 |  |  | 1.0855 |  |  | 2.0264 |  |  | -3.8149 |  |  | -0.31463 |  |  | -0.43862
[13 empty] | C Non choked w/ reducers | 7 |  | 1.413 |  |  | 15.8486 |  |  | 39.9563 |  |  | 86.0857 |  |  | 204.3873 |  |  | #NUM! |  |  | #NUM! |  |  | 145.0717 |  |  | 903.7678 |  |  | 573.7728
[13 empty] | C Choked w/ reducers | 7 |  | 1.2649 |  |  | 14.1613 |  |  | 35.468 |  |  | 73.8613 |  |  | 147.5431 |  |  | 313.7554 |  |  | 1034.9658 |  |  | -3153.5547 |  |  | -846.6304 |  |  | -783.8518
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.413 |  |  | 15.8486 |  |  | 39.9563 |  |  | 86.0857 |  |  | 204.3873 |  |  | #NUM! |  |  | #NUM! |  |  | -3153.5547 |  |  | -846.6304 |  |  | -783.8518
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.317 | 3498.706 |  | 4.2486 | 39030.5033 |  | 16.9563 | 95571.3658 |  | 46.6857 | 186148.6264 |  | 143.3873 | 312299.4882 |  | 236393 | 455809.6089 |  | 236393 | 608279.69 |  | 236393 | 742216.8192 |  | 236393 | 861690.6853 |  | 236393 | 1010400.0961
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3568.6801 | C_100 - C this iteration | iteration | 39420.8084 | C_100 - C this iteration | iteration | 96527.0794 | C_100 - C this iteration | iteration | 188010.1126 | C_100 - C this iteration | iteration | 315422.4831 | C_100 - C this iteration | iteration | 460367.7049 | C_100 - C this iteration | iteration | 614362.4869 | C_100 - C this iteration | iteration | 749638.9874 | C_100 - C this iteration | iteration | 870307.5921 | C_100 - C this iteration | iteration | 1020504.0971 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1827 |  |  | 89.9018 |  |  | 88.4868 |  |  | 83.7425 |  |  | 72.0517 |  |  | 51.557 |  |  | 21.3923 |  |  | -12.238 |  |  | -47.8658 |  |  | -99.6267
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1827 |  |  | 29.9018 |  |  | 28.4868 |  |  | 23.7425 |  |  | 12.0517 |  |  | -8.443 |  |  | -38.6077 |  |  | -72.238 |  |  | -107.8658 |  |  | -159.6267
[13 empty] | Press drop ratio this iteration |  |  | 0.33468 |  |  | 0.33261 |  |  | 0.32193 |  |  | 0.28352 |  |  | 0.16726 |  |  | -0.16376 |  |  | -1.8048 |  |  | 5.9027 |  |  | 2.2535 |  |  | 1.6022
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82682 |  |  | 0.83078 |  |  | 0.84887 |  |  | 0.90807 |  |  | 1.0954 |  |  | 2.1312 |  |  | -3.1365 |  |  | -0.272 |  |  | -0.41783
[13 empty] | C Non choked w/ reducers | 7 |  | 1.4412 |  |  | 16.0086 |  |  | 40.3806 |  |  | 87.1853 |  |  | 209.4654 |  |  | #NUM! |  |  | #NUM! |  |  | 160.5695 |  |  | 1012.4204 |  |  | 589.7798
[13 empty] | C Choked w/ reducers | 7 |  | 1.2902 |  |  | 14.3038 |  |  | 35.8362 |  |  | 74.713 |  |  | 149.7575 |  |  | 321.5711 |  |  | 1111.5504 |  |  | -2659.8466 |  |  | -806.5027 |  |  | -761.9698
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.4412 |  |  | 16.0086 |  |  | 40.3806 |  |  | 87.1853 |  |  | 209.4654 |  |  | #NUM! |  |  | #NUM! |  |  | -2659.8466 |  |  | -806.5027 |  |  | -761.9698
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.2888 | 3568.6801 |  | 4.4086 | 39420.8084 |  | 17.3806 | 96527.0794 |  | 47.7853 | 188010.1126 |  | 148.4654 | 315422.4831 |  | 236393 | 460367.7049 |  | 236393 | 614362.4869 |  | 236393 | 749638.9874 |  | 236393 | 870307.5921 |  | 236393 | 1020504.0971
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3640.0537 | C_100 - C this iteration | iteration | 39815.0164 | C_100 - C this iteration | iteration | 97492.3502 | C_100 - C this iteration | iteration | 189890.2138 | C_100 - C this iteration | iteration | 318576.7079 | C_100 - C this iteration | iteration | 464971.382 | C_100 - C this iteration | iteration | 620506.1118 | C_100 - C this iteration | iteration | 757135.3773 | C_100 - C this iteration | iteration | 879010.6681 | C_100 - C this iteration | iteration | 1030709.138 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1826 |  |  | 89.8961 |  |  | 88.4527 |  |  | 83.613 |  |  | 71.6872 |  |  | 50.7805 |  |  | 20.0095 |  |  | -14.2968 |  |  | -50.6406 |  |  | -103.4419
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1826 |  |  | 29.8961 |  |  | 28.4527 |  |  | 23.613 |  |  | 11.6872 |  |  | -9.2195 |  |  | -39.9905 |  |  | -74.2968 |  |  | -110.6406 |  |  | -163.4419
[13 empty] | Press drop ratio this iteration |  |  | 0.33468 |  |  | 0.33256 |  |  | 0.32167 |  |  | 0.28241 |  |  | 0.16303 |  |  | -0.18156 |  |  | -1.9986 |  |  | 5.1968 |  |  | 2.1848 |  |  | 1.58
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82684 |  |  | 0.83091 |  |  | 0.84946 |  |  | 0.9104 |  |  | 1.1058 |  |  | 2.2526 |  |  | -2.6417 |  |  | -0.23323 |  |  | -0.39818
[13 empty] | C Non choked w/ reducers | 7 |  | 1.4701 |  |  | 16.1703 |  |  | 40.81 |  |  | 88.3051 |  |  | 214.8286 |  |  | #NUM! |  |  | #NUM! |  |  | 175.6595 |  |  | 1144.7585 |  |  | 606.2454
[13 empty] | C Choked w/ reducers | 7 |  | 1.316 |  |  | 14.4478 |  |  | 36.2085 |  |  | 75.5769 |  |  | 152.0241 |  |  | 329.7528 |  |  | 1200.2465 |  |  | -2299.6023 |  |  | -769.934 |  |  | -741.205
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.4701 |  |  | 16.1703 |  |  | 40.81 |  |  | 88.3051 |  |  | 214.8286 |  |  | #NUM! |  |  | #NUM! |  |  | -2299.6023 |  |  | -769.934 |  |  | -741.205
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.2599 | 3640.0537 |  | 4.5703 | 39815.0164 |  | 17.81 | 97492.3502 |  | 48.9051 | 189890.2138 |  | 153.8286 | 318576.7079 |  | 236393 | 464971.382 |  | 236393 | 620506.1118 |  | 236393 | 757135.3773 |  | 236393 | 879010.6681 |  | 236393 | 1030709.138
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3712.8548 | C_100 - C this iteration | iteration | 40213.1666 | C_100 - C this iteration | iteration | 98467.2737 | C_100 - C this iteration | iteration | 191789.1159 | C_100 - C this iteration | iteration | 321762.475 | C_100 - C this iteration | iteration | 469621.0958 | C_100 - C this iteration | iteration | 626711.1729 | C_100 - C this iteration | iteration | 764706.7311 | C_100 - C this iteration | iteration | 887800.7747 | C_100 - C this iteration | iteration | 1041016.2294 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1825 |  |  | 89.8903 |  |  | 88.4179 |  |  | 83.4809 |  |  | 71.3154 |  |  | 49.9885 |  |  | 18.599 |  |  | -16.3968 |  |  | -53.4712 |  |  | -107.3338
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1825 |  |  | 29.8903 |  |  | 28.4179 |  |  | 23.4809 |  |  | 11.3154 |  |  | -10.0115 |  |  | -41.401 |  |  | -76.3968 |  |  | -113.4712 |  |  | -167.3338
[13 empty] | Press drop ratio this iteration |  |  | 0.33468 |  |  | 0.33252 |  |  | 0.3214 |  |  | 0.28127 |  |  | 0.15867 |  |  | -0.20028 |  |  | -2.226 |  |  | 4.6592 |  |  | 2.1221 |  |  | 1.559
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82686 |  |  | 0.83105 |  |  | 0.85007 |  |  | 0.9128 |  |  | 1.1167 |  |  | 2.3952 |  |  | -2.2651 |  |  | -0.19783 |  |  | -0.37956
[13 empty] | C Non choked w/ reducers | 7 |  | 1.4995 |  |  | 16.3337 |  |  | 41.2445 |  |  | 89.4457 |  |  | 220.5061 |  |  | #NUM! |  |  | #NUM! |  |  | 190.5409 |  |  | 1309.8994 |  |  | 623.2021
[13 empty] | C Choked w/ reducers | 7 |  | 1.3423 |  |  | 14.5932 |  |  | 36.585 |  |  | 76.4535 |  |  | 154.3449 |  |  | 338.3272 |  |  | 1304.1847 |  |  | -2025.1231 |  |  | -736.4679 |  |  | -721.4723
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.4995 |  |  | 16.3337 |  |  | 41.2445 |  |  | 89.4457 |  |  | 220.5061 |  |  | #NUM! |  |  | #NUM! |  |  | -2025.1231 |  |  | -736.4679 |  |  | -721.4723
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.2305 | 3712.8548 |  | 4.7337 | 40213.1666 |  | 18.2445 | 98467.2737 |  | 50.0457 | 191789.1159 |  | 159.5061 | 321762.475 |  | 236393 | 469621.0958 |  | 236393 | 626711.1729 |  | 236393 | 764706.7311 |  | 236393 | 887800.7747 |  | 236393 | 1041016.2294
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3787.1119 | C_100 - C this iteration | iteration | 40615.2983 | C_100 - C this iteration | iteration | 99451.9465 | C_100 - C this iteration | iteration | 193707.0071 | C_100 - C this iteration | iteration | 324980.0997 | C_100 - C this iteration | iteration | 474317.3068 | C_100 - C this iteration | iteration | 632978.2846 | C_100 - C this iteration | iteration | 772353.7984 | C_100 - C this iteration | iteration | 896678.7825 | C_100 - C this iteration | iteration | 1051426.3917 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1824 |  |  | 89.8844 |  |  | 88.3824 |  |  | 83.3462 |  |  | 70.9361 |  |  | 49.1805 |  |  | 17.1601 |  |  | -18.5391 |  |  | -56.3587 |  |  | -111.3039
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1824 |  |  | 29.8844 |  |  | 28.3824 |  |  | 23.3462 |  |  | 10.9361 |  |  | -10.8195 |  |  | -42.8399 |  |  | -78.5391 |  |  | -116.3587 |  |  | -171.3039
[13 empty] | Press drop ratio this iteration |  |  | 0.33468 |  |  | 0.33248 |  |  | 0.32113 |  |  | 0.28011 |  |  | 0.15417 |  |  | -0.21999 |  |  | -2.4965 |  |  | 4.2364 |  |  | 2.0646 |  |  | 1.5391
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.82688 |  |  | 0.8312 |  |  | 0.85068 |  |  | 0.91527 |  |  | 1.1282 |  |  | 2.5647 |  |  | -1.9688 |  |  | -0.16538 |  |  | -0.36192
[13 empty] | C Non choked w/ reducers | 7 |  | 1.5295 |  |  | 16.4988 |  |  | 41.6842 |  |  | 90.6077 |  |  | 226.5315 |  |  | #NUM! |  |  | #NUM! |  |  | 205.3668 |  |  | 1522.2775 |  |  | 640.6845
[13 empty] | C Choked w/ reducers | 7 |  | 1.3691 |  |  | 14.7401 |  |  | 36.9657 |  |  | 77.3429 |  |  | 156.7218 |  |  | 347.3242 |  |  | 1427.6763 |  |  | -1809.0204 |  |  | -705.723 |  |  | -702.6953
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.5295 |  |  | 16.4988 |  |  | 41.6842 |  |  | 90.6077 |  |  | 226.5315 |  |  | #NUM! |  |  | #NUM! |  |  | -1809.0204 |  |  | -705.723 |  |  | -702.6953
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.2005 | 3787.1119 |  | 4.8988 | 40615.2983 |  | 18.6842 | 99451.9465 |  | 51.2077 | 193707.0071 |  | 165.5315 | 324980.0997 |  | 236393 | 474317.3068 |  | 236393 | 632978.2846 |  | 236393 | 772353.7984 |  | 236393 | 896678.7825 |  | 236393 | 1051426.3917
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3862.8541 | C_100 - C this iteration | iteration | 41021.4513 | C_100 - C this iteration | iteration | 100446.4659 | C_100 - C this iteration | iteration | 195644.0771 | C_100 - C this iteration | iteration | 328229.9007 | C_100 - C this iteration | iteration | 479060.4798 | C_100 - C this iteration | iteration | 639308.0675 | C_100 - C this iteration | iteration | 780077.3364 | C_100 - C this iteration | iteration | 905645.5703 | C_100 - C this iteration | iteration | 1061940.6556 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1823 |  |  | 89.8783 |  |  | 88.3461 |  |  | 83.2087 |  |  | 70.5492 |  |  | 48.3564 |  |  | 15.6923 |  |  | -20.7245 |  |  | -59.3042 |  |  | -115.3539
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1823 |  |  | 29.8783 |  |  | 28.3461 |  |  | 23.2087 |  |  | 10.5492 |  |  | -11.6436 |  |  | -44.3077 |  |  | -80.7245 |  |  | -119.3042 |  |  | -175.3539
[13 empty] | Press drop ratio this iteration |  |  | 0.33468 |  |  | 0.33243 |  |  | 0.32085 |  |  | 0.27892 |  |  | 0.14953 |  |  | -0.24079 |  |  | -2.8235 |  |  | 3.8951 |  |  | 2.0117 |  |  | 1.5201
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82691 |  |  | 0.83134 |  |  | 0.85132 |  |  | 0.91782 |  |  | 1.1403 |  |  | 2.7697 |  |  | -1.7296 |  |  | -0.13553 |  |  | -0.34517
[13 empty] | C Non choked w/ reducers | 7 |  | 1.56 |  |  | 16.6655 |  |  | 42.1291 |  |  | 91.7917 |  |  | 232.9438 |  |  | #NUM! |  |  | #NUM! |  |  | 220.2625 |  |  | 1806.1905 |  |  | 658.7296
[13 empty] | C Choked w/ reducers | 7 |  | 1.3965 |  |  | 14.8885 |  |  | 37.3507 |  |  | 78.2454 |  |  | 159.1571 |  |  | 356.7765 |  |  | 1576.8281 |  |  | -1634.4455 |  |  | -677.3778 |  |  | -684.8048
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.56 |  |  | 16.6655 |  |  | 42.1291 |  |  | 91.7917 |  |  | 232.9438 |  |  | #NUM! |  |  | #NUM! |  |  | -1634.4455 |  |  | -677.3778 |  |  | -684.8048
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.17 | 3862.8541 |  | 5.0655 | 41021.4513 |  | 19.1291 | 100446.4659 |  | 52.3917 | 195644.0771 |  | 171.9438 | 328229.9007 |  | 236393 | 479060.4798 |  | 236393 | 639308.0675 |  | 236393 | 780077.3364 |  | 236393 | 905645.5703 |  | 236393 | 1061940.6556
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 3940.1112 | C_100 - C this iteration | iteration | 41431.6658 | C_100 - C this iteration | iteration | 101450.9306 | C_100 - C this iteration | iteration | 197600.5179 | C_100 - C this iteration | iteration | 331512.1997 | C_100 - C this iteration | iteration | 483851.0846 | C_100 - C this iteration | iteration | 645701.1481 | C_100 - C this iteration | iteration | 787878.1097 | C_100 - C this iteration | iteration | 914702.026 | C_100 - C this iteration | iteration | 1072560.0622 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1822 |  |  | 89.8722 |  |  | 88.3092 |  |  | 83.0685 |  |  | 70.1545 |  |  | 47.5156 |  |  | 14.195 |  |  | -22.9538 |  |  | -62.309 |  |  | -119.4852
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1822 |  |  | 29.8722 |  |  | 28.3092 |  |  | 23.0685 |  |  | 10.1545 |  |  | -12.4844 |  |  | -45.805 |  |  | -82.9538 |  |  | -122.309 |  |  | -179.4852
[13 empty] | Press drop ratio this iteration |  |  | 0.33468 |  |  | 0.33239 |  |  | 0.32057 |  |  | 0.2777 |  |  | 0.14474 |  |  | -0.26274 |  |  | -3.2268 |  |  | 3.6139 |  |  | 1.9629 |  |  | 1.5022
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82693 |  |  | 0.83149 |  |  | 0.85197 |  |  | 0.92045 |  |  | 1.1531 |  |  | 3.0225 |  |  | -1.5326 |  |  | -0.10799 |  |  | -0.32926
[13 empty] | C Non choked w/ reducers | 7 |  | 1.5913 |  |  | 16.834 |  |  | 42.5795 |  |  | 92.9986 |  |  | 239.7885 |  |  | #NUM! |  |  | #NUM! |  |  | 235.3368 |  |  | 2205.9716 |  |  | 677.3773
[13 empty] | C Choked w/ reducers | 7 |  | 1.4245 |  |  | 15.0384 |  |  | 37.74 |  |  | 79.1612 |  |  | 161.653 |  |  | 366.7203 |  |  | 1760.5851 |  |  | -1490.4644 |  |  | -651.1596 |  |  | -667.7382
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.5913 |  |  | 16.834 |  |  | 42.5795 |  |  | 92.9986 |  |  | 239.7885 |  |  | #NUM! |  |  | #NUM! |  |  | -1490.4644 |  |  | -651.1596 |  |  | -667.7382
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.1387 | 3940.1112 |  | 5.234 | 41431.6658 |  | 19.5795 | 101450.9306 |  | 53.5986 | 197600.5179 |  | 178.7885 | 331512.1997 |  | 236393 | 483851.0846 |  | 236393 | 645701.1481 |  | 236393 | 787878.1097 |  | 236393 | 914702.026 |  | 236393 | 1072560.0622
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 4018.9134 | C_100 - C this iteration | iteration | 41845.9824 | C_100 - C this iteration | iteration | 102465.4399 | C_100 - C this iteration | iteration | 199576.5231 | C_100 - C this iteration | iteration | 334827.3217 | C_100 - C this iteration | iteration | 488689.5955 | C_100 - C this iteration | iteration | 652158.1596 | C_100 - C this iteration | iteration | 795756.8908 | C_100 - C this iteration | iteration | 923849.0463 | C_100 - C this iteration | iteration | 1083285.6628 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1821 |  |  | 89.8659 |  |  | 88.2715 |  |  | 82.9254 |  |  | 69.7519 |  |  | 46.6579 |  |  | 12.6676 |  |  | -25.2279 |  |  | -65.3741 |  |  | -123.6996
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1821 |  |  | 29.8659 |  |  | 28.2715 |  |  | 22.9254 |  |  | 9.7519 |  |  | -13.3421 |  |  | -47.3324 |  |  | -85.2279 |  |  | -125.3741 |  |  | -183.6996
[13 empty] | Press drop ratio this iteration |  |  | 0.33468 |  |  | 0.33234 |  |  | 0.32028 |  |  | 0.27646 |  |  | 0.13981 |  |  | -0.28595 |  |  | -3.7365 |  |  | 3.3783 |  |  | 1.9178 |  |  | 1.485
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82696 |  |  | 0.83165 |  |  | 0.85263 |  |  | 0.92316 |  |  | 1.1666 |  |  | 3.3419 |  |  | -1.3674 |  |  | -0.082506 |  |  | -0.31412
[13 empty] | C Non choked w/ reducers | 7 |  | 1.6231 |  |  | 17.0043 |  |  | 43.0352 |  |  | 94.2289 |  |  | 247.119 |  |  | #NUM! |  |  | #NUM! |  |  | 250.6887 |  |  | 2812.017 |  |  | 696.6704
[13 empty] | C Choked w/ reducers | 7 |  | 1.4529 |  |  | 15.1898 |  |  | 38.1337 |  |  | 80.0907 |  |  | 164.212 |  |  | 377.1959 |  |  | 1992.5968 |  |  | -1369.672 |  |  | -626.8356 |  |  | -651.4387
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.6231 |  |  | 17.0043 |  |  | 43.0352 |  |  | 94.2289 |  |  | 247.119 |  |  | #NUM! |  |  | #NUM! |  |  | -1369.672 |  |  | -626.8356 |  |  | -651.4387
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.1069 | 4018.9134 |  | 5.4043 | 41845.9824 |  | 20.0352 | 102465.4399 |  | 54.8289 | 199576.5231 |  | 186.119 | 334827.3217 |  | 236393 | 488689.5955 |  | 236393 | 652158.1596 |  | 236393 | 795756.8908 |  | 236393 | 923849.0463 |  | 236393 | 1083285.6628
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 4099.2917 | C_100 - C this iteration | iteration | 42264.4423 | C_100 - C this iteration | iteration | 103490.0943 | C_100 - C this iteration | iteration | 201572.2883 | C_100 - C this iteration | iteration | 338175.595 | C_100 - C this iteration | iteration | 493576.4914 | C_100 - C this iteration | iteration | 658679.7412 | C_100 - C this iteration | iteration | 803714.4597 | C_100 - C this iteration | iteration | 933087.5367 | C_100 - C this iteration | iteration | 1094118.5194 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.182 |  |  | 89.8595 |  |  | 88.233 |  |  | 82.7795 |  |  | 69.3412 |  |  | 45.783 |  |  | 11.1095 |  |  | -27.5477 |  |  | -68.5009 |  |  | -127.9986
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.182 |  |  | 29.8595 |  |  | 28.233 |  |  | 22.7795 |  |  | 9.3412 |  |  | -14.217 |  |  | -48.8905 |  |  | -87.5477 |  |  | -128.5009 |  |  | -187.9986
[13 empty] | Press drop ratio this iteration |  |  | 0.33468 |  |  | 0.33229 |  |  | 0.31998 |  |  | 0.27518 |  |  | 0.13471 |  |  | -0.31053 |  |  | -4.4008 |  |  | 3.178 |  |  | 1.8759 |  |  | 1.4688
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82698 |  |  | 0.8318 |  |  | 0.85331 |  |  | 0.92596 |  |  | 1.1809 |  |  | 3.7582 |  |  | -1.2271 |  |  | -0.058859 |  |  | -0.2997
[13 empty] | C Non choked w/ reducers | 7 |  | 1.6555 |  |  | 17.1762 |  |  | 43.4965 |  |  | 95.4835 |  |  | 254.9988 |  |  | #NUM! |  |  | #NUM! |  |  | 266.4126 |  |  | 3841.6256 |  |  | 716.6549
[13 empty] | C Choked w/ reducers | 7 |  | 1.482 |  |  | 15.3428 |  |  | 38.5318 |  |  | 81.0342 |  |  | 166.8364 |  |  | 388.248 |  |  | 2294.7777 |  |  | -1266.8747 |  |  | -604.2058 |  |  | -635.8544
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.6555 |  |  | 17.1762 |  |  | 43.4965 |  |  | 95.4835 |  |  | 254.9988 |  |  | #NUM! |  |  | #NUM! |  |  | -1266.8747 |  |  | -604.2058 |  |  | -635.8544
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.0745 | 4099.2917 |  | 5.5762 | 42264.4423 |  | 20.4965 | 103490.0943 |  | 56.0835 | 201572.2883 |  | 193.9988 | 338175.595 |  | 236393 | 493576.4914 |  | 236393 | 658679.7412 |  | 236393 | 803714.4597 |  | 236393 | 933087.5367 |  | 236393 | 1094118.5194
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 4181.2775 | C_100 - C this iteration | iteration | 42687.0867 | C_100 - C this iteration | iteration | 104524.9952 | C_100 - C this iteration | iteration | 203588.0112 | C_100 - C this iteration | iteration | 341557.3509 | C_100 - C this iteration | iteration | 498512.2564 | C_100 - C this iteration | iteration | 665266.5386 | C_100 - C this iteration | iteration | 811751.6043 | C_100 - C this iteration | iteration | 942418.4121 | C_100 - C this iteration | iteration | 1105059.7046 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1819 |  |  | 89.8529 |  |  | 88.1938 |  |  | 82.6307 |  |  | 68.9222 |  |  | 44.8906 |  |  | 9.5201 |  |  | -29.9141 |  |  | -71.6904 |  |  | -132.3841
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1819 |  |  | 29.8529 |  |  | 28.1938 |  |  | 22.6307 |  |  | 8.9222 |  |  | -15.1094 |  |  | -50.4799 |  |  | -89.9141 |  |  | -131.6904 |  |  | -192.3841
[13 empty] | Press drop ratio this iteration |  |  | 0.33468 |  |  | 0.33224 |  |  | 0.31968 |  |  | 0.27388 |  |  | 0.12945 |  |  | -0.33658 |  |  | -5.3025 |  |  | 3.0057 |  |  | 1.8369 |  |  | 1.4532
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82701 |  |  | 0.83196 |  |  | 0.85401 |  |  | 0.92885 |  |  | 1.1961 |  |  | 4.3234 |  |  | -1.1063 |  |  | -0.036863 |  |  | -0.28596
[13 empty] | C Non choked w/ reducers | 7 |  | 1.6887 |  |  | 17.35 |  |  | 43.9634 |  |  | 96.7632 |  |  | 263.5034 |  |  | #NUM! |  |  | #NUM! |  |  | 282.6012 |  |  | 5982.157 |  |  | 737.3809
[13 empty] | C Choked w/ reducers | 7 |  | 1.5116 |  |  | 15.4974 |  |  | 38.9344 |  |  | 81.992 |  |  | 169.5291 |  |  | 399.9265 |  |  | 2704.6796 |  |  | -1178.322 |  |  | -583.0973 |  |  | -620.9384
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.6887 |  |  | 17.35 |  |  | 43.9634 |  |  | 96.7632 |  |  | 263.5034 |  |  | #NUM! |  |  | #NUM! |  |  | -1178.322 |  |  | -583.0973 |  |  | -620.9384
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.0413 | 4181.2775 |  | 5.75 | 42687.0867 |  | 20.9634 | 104524.9952 |  | 57.3632 | 203588.0112 |  | 202.5034 | 341557.3509 |  | 236393 | 498512.2564 |  | 236393 | 665266.5386 |  | 236393 | 811751.6043 |  | 236393 | 942418.4121 |  | 236393 | 1105059.7046
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 4264.9031 | C_100 - C this iteration | iteration | 43113.9575 | C_100 - C this iteration | iteration | 105570.2452 | C_100 - C this iteration | iteration | 205623.8913 | C_100 - C this iteration | iteration | 344972.9244 | C_100 - C this iteration | iteration | 503497.3789 | C_100 - C this iteration | iteration | 671919.204 | C_100 - C this iteration | iteration | 819869.1204 | C_100 - C this iteration | iteration | 951842.5962 | C_100 - C this iteration | iteration | 1116110.3017 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1817 |  |  | 89.8463 |  |  | 88.1537 |  |  | 82.4788 |  |  | 68.4948 |  |  | 43.9801 |  |  | 7.8987 |  |  | -32.3281 |  |  | -74.9441 |  |  | -136.8578
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1817 |  |  | 29.8463 |  |  | 28.1537 |  |  | 22.4788 |  |  | 8.4948 |  |  | -16.0199 |  |  | -52.1013 |  |  | -92.3281 |  |  | -134.9441 |  |  | -196.8578
[13 empty] | Press drop ratio this iteration |  |  | 0.33468 |  |  | 0.33219 |  |  | 0.31937 |  |  | 0.27254 |  |  | 0.12402 |  |  | -0.36425 |  |  | -6.5962 |  |  | 2.856 |  |  | 1.8006 |  |  | 1.4384
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82703 |  |  | 0.83212 |  |  | 0.85472 |  |  | 0.93184 |  |  | 1.2122 |  |  | 5.1342 |  |  | -1.0014 |  |  | -0.016353 |  |  | -0.27285
[13 empty] | C Non choked w/ reducers | 7 |  | 1.7224 |  |  | 17.5256 |  |  | 44.436 |  |  | 98.0687 |  |  | 272.7241 |  |  | #NUM! |  |  | #NUM! |  |  | 299.3493 |  |  | 13159.1572 |  |  | 758.9026
[13 empty] | C Choked w/ reducers | 7 |  | 1.5419 |  |  | 15.6535 |  |  | 39.3416 |  |  | 82.9644 |  |  | 172.2928 |  |  | 412.2873 |  |  | 3292.4662 |  |  | -1101.2381 |  |  | -563.3599 |  |  | -606.6474
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.7224 |  |  | 17.5256 |  |  | 44.436 |  |  | 98.0687 |  |  | 272.7241 |  |  | #NUM! |  |  | #NUM! |  |  | -1101.2381 |  |  | -563.3599 |  |  | -606.6474
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.0076 | 4264.9031 |  | 5.9256 | 43113.9575 |  | 21.436 | 105570.2452 |  | 58.6687 | 205623.8913 |  | 211.7241 | 344972.9244 |  | 236393 | 503497.3789 |  | 236393 | 671919.204 |  | 236393 | 819869.1204 |  | 236393 | 951842.5962 |  | 236393 | 1116110.3017
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 4350.2011 | C_100 - C this iteration | iteration | 43545.0971 | C_100 - C this iteration | iteration | 106625.9476 | C_100 - C this iteration | iteration | 207680.1302 | C_100 - C this iteration | iteration | 348422.6537 | C_100 - C this iteration | iteration | 508532.3527 | C_100 - C this iteration | iteration | 678638.396 | C_100 - C this iteration | iteration | 828067.8116 | C_100 - C this iteration | iteration | 961361.0222 | C_100 - C this iteration | iteration | 1127271.4047 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1816 |  |  | 89.8394 |  |  | 88.1129 |  |  | 82.3239 |  |  | 68.0589 |  |  | 43.0514 |  |  | 6.2448 |  |  | -34.7906 |  |  | -78.2632 |  |  | -141.4213
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1816 |  |  | 29.8394 |  |  | 28.1129 |  |  | 22.3239 |  |  | 8.0589 |  |  | -16.9486 |  |  | -53.7552 |  |  | -94.7906 |  |  | -138.2632 |  |  | -201.4213
[13 empty] | Press drop ratio this iteration |  |  | 0.33468 |  |  | 0.33214 |  |  | 0.31906 |  |  | 0.27117 |  |  | 0.11841 |  |  | -0.39368 |  |  | -8.608 |  |  | 2.7246 |  |  | 1.7666 |  |  | 1.4243
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82706 |  |  | 0.83229 |  |  | 0.85545 |  |  | 0.93492 |  |  | 1.2293 |  |  | 6.3952 |  |  | -0.90933 |  |  | 0.0028117 |  |  | -0.26033
[13 empty] | C Non choked w/ reducers | 7 |  | 1.7569 |  |  | 17.7029 |  |  | 44.9144 |  |  | 99.4011 |  |  | 282.7725 |  |  | #NUM! |  |  | #NUM! |  |  | 316.7555 |  |  | -74731.0357 |  |  | 781.2786
[13 empty] | C Choked w/ reducers | 7 |  | 1.5727 |  |  | 15.8113 |  |  | 39.7535 |  |  | 83.9517 |  |  | 175.1304 |  |  | 425.3931 |  |  | 4206.1362 |  |  | -1033.5242 |  |  | -544.8629 |  |  | -592.942
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.7569 |  |  | 17.7029 |  |  | 44.9144 |  |  | 99.4011 |  |  | 282.7725 |  |  | #NUM! |  |  | #NUM! |  |  | -1033.5242 |  |  | -544.8629 |  |  | -592.942
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.9731 | 4350.2011 |  | 6.1029 | 43545.0971 |  | 21.9144 | 106625.9476 |  | 60.0011 | 207680.1302 |  | 221.7725 | 348422.6537 |  | 236393 | 508532.3527 |  | 236393 | 678638.396 |  | 236393 | 828067.8116 |  | 236393 | 961361.0222 |  | 236393 | 1127271.4047
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 4437.2051 | C_100 - C this iteration | iteration | 43980.5481 | C_100 - C this iteration | iteration | 107692.2071 | C_100 - C this iteration | iteration | 209756.9315 | C_100 - C this iteration | iteration | 351906.8802 | C_100 - C this iteration | iteration | 513617.6762 | C_100 - C this iteration | iteration | 685424.78 | C_100 - C this iteration | iteration | 836348.4897 | C_100 - C this iteration | iteration | 970974.6324 | C_100 - C this iteration | iteration | 1138544.1187 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1815 |  |  | 89.8325 |  |  | 88.0712 |  |  | 82.1659 |  |  | 67.6141 |  |  | 42.104 |  |  | 4.5576 |  |  | -37.3026 |  |  | -81.649 |  |  | -146.0766
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1815 |  |  | 29.8325 |  |  | 28.0712 |  |  | 22.1659 |  |  | 7.6141 |  |  | -17.896 |  |  | -55.4424 |  |  | -97.3026 |  |  | -141.649 |  |  | -206.0766
[13 empty] | Press drop ratio this iteration |  |  | 0.33467 |  |  | 0.33209 |  |  | 0.31873 |  |  | 0.26977 |  |  | 0.11261 |  |  | -0.42504 |  |  | -12.1649 |  |  | 2.6085 |  |  | 1.7349 |  |  | 1.4107
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82708 |  |  | 0.83246 |  |  | 0.8562 |  |  | 0.93811 |  |  | 1.2476 |  |  | 8.6245 |  |  | -0.82794 |  |  | 0.020756 |  |  | -0.24837
[13 empty] | C Non choked w/ reducers | 7 |  | 1.792 |  |  | 17.8822 |  |  | 45.3987 |  |  | 100.7611 |  |  | 293.786 |  |  | #NUM! |  |  | #NUM! |  |  | 334.9252 |  |  | -9889.7747 |  |  | 804.5733
[13 empty] | C Choked w/ reducers | 7 |  | 1.6042 |  |  | 15.9706 |  |  | 40.17 |  |  | 84.9543 |  |  | 178.0452 |  |  | 439.3145 |  |  | 5820.87 |  |  | -973.5645 |  |  | -527.4912 |  |  | -579.7861
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.792 |  |  | 17.8822 |  |  | 45.3987 |  |  | 100.7611 |  |  | 293.786 |  |  | #NUM! |  |  | #NUM! |  |  | -973.5645 |  |  | -527.4912 |  |  | -579.7861
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.938 | 4437.2051 |  | 6.2822 | 43980.5481 |  | 22.3987 | 107692.2071 |  | 61.3611 | 209756.9315 |  | 232.786 | 351906.8802 |  | 236393 | 513617.6762 |  | 236393 | 685424.78 |  | 236393 | 836348.4897 |  | 236393 | 970974.6324 |  | 236393 | 1138544.1187
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 4525.9492 | C_100 - C this iteration | iteration | 44420.3536 | C_100 - C this iteration | iteration | 108769.1292 | C_100 - C this iteration | iteration | 211854.5008 | C_100 - C this iteration | iteration | 355425.949 | C_100 - C this iteration | iteration | 518753.853 | C_100 - C this iteration | iteration | 692279.0278 | C_100 - C this iteration | iteration | 844711.9746 | C_100 - C this iteration | iteration | 980684.3787 | C_100 - C this iteration | iteration | 1149929.5599 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1813 |  |  | 89.8254 |  |  | 88.0288 |  |  | 82.0047 |  |  | 67.1605 |  |  | 41.1376 |  |  | 2.8365 |  |  | -39.8651 |  |  | -85.1029 |  |  | -150.8255
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1813 |  |  | 29.8254 |  |  | 28.0288 |  |  | 22.0047 |  |  | 7.1605 |  |  | -18.8624 |  |  | -57.1635 |  |  | -99.8651 |  |  | -145.1029 |  |  | -210.8255
[13 empty] | Press drop ratio this iteration |  |  | 0.33467 |  |  | 0.33204 |  |  | 0.3184 |  |  | 0.26834 |  |  | 0.10662 |  |  | -0.45852 |  |  | -20.1532 |  |  | 2.5051 |  |  | 1.705 |  |  | 1.3978
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82711 |  |  | 0.83263 |  |  | 0.85696 |  |  | 0.9414 |  |  | 1.2671 |  |  | 13.6313 |  |  | -0.75549 |  |  | 0.03759 |  |  | -0.23692
[13 empty] | C Non choked w/ reducers | 7 |  | 1.8279 |  |  | 18.0632 |  |  | 45.8889 |  |  | 102.1498 |  |  | 305.9368 |  |  | #NUM! |  |  | #NUM! |  |  | 353.9727 |  |  | -5337.6799 |  |  | 828.8567
[13 empty] | C Choked w/ reducers | 7 |  | 1.6363 |  |  | 16.1316 |  |  | 40.5913 |  |  | 85.9725 |  |  | 181.0404 |  |  | 454.1315 |  |  | 9446.4055 |  |  | -920.0943 |  |  | -511.1441 |  |  | -567.1464
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.8279 |  |  | 18.0632 |  |  | 45.8889 |  |  | 102.1498 |  |  | 305.9368 |  |  | #NUM! |  |  | #NUM! |  |  | -920.0943 |  |  | -511.1441 |  |  | -567.1464
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.9021 | 4525.9492 |  | 6.4632 | 44420.3536 |  | 22.8889 | 108769.1292 |  | 62.7498 | 211854.5008 |  | 244.9368 | 355425.949 |  | 236393 | 518753.853 |  | 236393 | 692279.0278 |  | 236393 | 844711.9746 |  | 236393 | 980684.3787 |  | 236393 | 1149929.5599
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 4616.4682 | C_100 - C this iteration | iteration | 44864.5571 | C_100 - C this iteration | iteration | 109856.8205 | C_100 - C this iteration | iteration | 213973.0458 | C_100 - C this iteration | iteration | 358980.2085 | C_100 - C this iteration | iteration | 523941.3915 | C_100 - C this iteration | iteration | 699201.8181 | C_100 - C this iteration | iteration | 853159.0943 | C_100 - C this iteration | iteration | 990491.2225 | C_100 - C this iteration | iteration | 1161428.8555 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1812 |  |  | 89.8182 |  |  | 87.9854 |  |  | 81.8403 |  |  | 66.6977 |  |  | 40.1518 |  |  | 1.0807 |  |  | -42.4791 |  |  | -88.6262 |  |  | -155.6698
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1812 |  |  | 29.8182 |  |  | 27.9854 |  |  | 21.8403 |  |  | 6.6977 |  |  | -19.8482 |  |  | -58.9193 |  |  | -102.4791 |  |  | -148.6262 |  |  | -215.6698
[13 empty] | Press drop ratio this iteration |  |  | 0.33467 |  |  | 0.33198 |  |  | 0.31807 |  |  | 0.26687 |  |  | 0.10042 |  |  | -0.49433 |  |  | -54.5172 |  |  | 2.4125 |  |  | 1.677 |  |  | 1.3854
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82714 |  |  | 0.83281 |  |  | 0.85775 |  |  | 0.94481 |  |  | 1.288 |  |  | 35.1694 |  |  | -0.69059 |  |  | 0.053411 |  |  | -0.22597
[13 empty] | C Non choked w/ reducers | 7 |  | 1.8644 |  |  | 18.2462 |  |  | 46.3853 |  |  | 103.5682 |  |  | 319.4439 |  |  | #NUM! |  |  | #NUM! |  |  | 374.0242 |  |  | -3673.6851 |  |  | 854.2057
[13 empty] | C Choked w/ reducers | 7 |  | 1.669 |  |  | 16.2942 |  |  | 41.0174 |  |  | 87.0066 |  |  | 184.1195 |  |  | 469.9347 |  |  | 25040.3155 |  |  | -872.1098 |  |  | -495.732 |  |  | -554.9923
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.8644 |  |  | 18.2462 |  |  | 46.3853 |  |  | 103.5682 |  |  | 319.4439 |  |  | #NUM! |  |  | #NUM! |  |  | -872.1098 |  |  | -495.732 |  |  | -554.9923
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.8656 | 4616.4682 |  | 6.6462 | 44864.5571 |  | 23.3853 | 109856.8205 |  | 64.1682 | 213973.0458 |  | 258.4439 | 358980.2085 |  | 236393 | 523941.3915 |  | 236393 | 699201.8181 |  | 236393 | 853159.0943 |  | 236393 | 990491.2225 |  | 236393 | 1161428.8555
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 4708.7976 | C_100 - C this iteration | iteration | 45313.2027 | C_100 - C this iteration | iteration | 110955.3887 | C_100 - C this iteration | iteration | 216112.7763 | C_100 - C this iteration | iteration | 362570.0106 | C_100 - C this iteration | iteration | 529180.8054 | C_100 - C this iteration | iteration | 706193.8363 | C_100 - C this iteration | iteration | 861690.6853 | C_100 - C this iteration | iteration | 1000396.1347 | C_100 - C this iteration | iteration | 1173043.1441 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.181 |  |  | 89.8108 |  |  | 87.9412 |  |  | 81.6726 |  |  | 66.2256 |  |  | 39.1461 |  |  | -0.71025 |  |  | -45.1457 |  |  | -92.2203 |  |  | -160.6115
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.181 |  |  | 29.8108 |  |  | 27.9412 |  |  | 21.6726 |  |  | 6.2256 |  |  | -20.8539 |  |  | -60.7103 |  |  | -105.1457 |  |  | -152.2203 |  |  | -220.6115
[13 empty] | Press drop ratio this iteration |  |  | 0.33467 |  |  | 0.33193 |  |  | 0.31773 |  |  | 0.26536 |  |  | 0.094005 |  |  | -0.53272 |  |  | 85.4773 |  |  | 2.329 |  |  | 1.6506 |  |  | 1.3736
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82717 |  |  | 0.83299 |  |  | 0.85855 |  |  | 0.94834 |  |  | 1.3103 |  |  | -52.574 |  |  | -0.63212 |  |  | 0.068304 |  |  | -0.21548
[13 empty] | C Non choked w/ reducers | 7 |  | 1.9017 |  |  | 18.4311 |  |  | 46.8878 |  |  | 105.0174 |  |  | 334.5905 |  |  | #NUM! |  |  | 38.5115 |  |  | 395.2205 |  |  | -2810.5213 |  |  | 880.7044
[13 empty] | C Choked w/ reducers | 7 |  | 1.7024 |  |  | 16.4585 |  |  | 41.4484 |  |  | 88.0572 |  |  | 187.2863 |  |  | 486.8275 |  |  | -38483.4152 |  |  | -828.8042 |  |  | -481.176 |  |  | -543.2955
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.9017 |  |  | 18.4311 |  |  | 46.8878 |  |  | 105.0174 |  |  | 334.5905 |  |  | #NUM! |  |  | -38483.4152 |  |  | -828.8042 |  |  | -481.176 |  |  | -543.2955
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.8283 | 4708.7976 |  | 6.8311 | 45313.2027 |  | 23.8878 | 110955.3887 |  | 65.6174 | 216112.7763 |  | 273.5905 | 362570.0106 |  | 236393 | 529180.8054 |  | 236393 | 706193.8363 |  | 236393 | 861690.6853 |  | 236393 | 1000396.1347 |  | 236393 | 1173043.1441
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 4802.9735 | C_100 - C this iteration | iteration | 45766.3347 | C_100 - C this iteration | iteration | 112064.9426 | C_100 - C this iteration | iteration | 218273.9041 | C_100 - C this iteration | iteration | 366195.7107 | C_100 - C this iteration | iteration | 534472.6135 | C_100 - C this iteration | iteration | 713255.7746 | C_100 - C this iteration | iteration | 870307.5921 | C_100 - C this iteration | iteration | 1010400.0961 | C_100 - C this iteration | iteration | 1184773.5755 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1808 |  |  | 89.8033 |  |  | 87.8961 |  |  | 81.5015 |  |  | 65.744 |  |  | 38.1202 |  |  | -2.5372 |  |  | -47.8658 |  |  | -95.8866 |  |  | -165.6525
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1808 |  |  | 29.8033 |  |  | 27.8961 |  |  | 21.5015 |  |  | 5.744 |  |  | -21.8798 |  |  | -62.5372 |  |  | -107.8658 |  |  | -155.8866 |  |  | -225.6525
[13 empty] | Press drop ratio this iteration |  |  | 0.33467 |  |  | 0.33187 |  |  | 0.31738 |  |  | 0.26382 |  |  | 0.087369 |  |  | -0.57397 |  |  | 24.6477 |  |  | 2.2535 |  |  | 1.6257 |  |  | 1.3622
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.8272 |  |  | 0.83317 |  |  | 0.85937 |  |  | 0.95198 |  |  | 1.3344 |  |  | -14.4483 |  |  | -0.5792 |  |  | 0.082346 |  |  | -0.20542
[13 empty] | C Non choked w/ reducers | 7 |  | 1.9398 |  |  | 18.6179 |  |  | 47.3967 |  |  | 106.4985 |  |  | 351.7512 |  |  | #NUM! |  |  | 73.7825 |  |  | 417.7209 |  |  | -2281.8013 |  |  | 908.446
[13 empty] | C Choked w/ reducers | 7 |  | 1.7364 |  |  | 16.6245 |  |  | 41.8843 |  |  | 89.1245 |  |  | 190.5448 |  |  | 504.9282 |  |  | -10880.3733 |  |  | -789.5215 |  |  | -467.4054 |  |  | -532.03
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.9398 |  |  | 18.6179 |  |  | 47.3967 |  |  | 106.4985 |  |  | 351.7512 |  |  | #NUM! |  |  | -10880.3733 |  |  | -789.5215 |  |  | -467.4054 |  |  | -532.03
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.7902 | 4802.9735 |  | 7.0179 | 45766.3347 |  | 24.3967 | 112064.9426 |  | 67.0985 | 218273.9041 |  | 290.7512 | 366195.7107 |  | 236393 | 534472.6135 |  | 236393 | 713255.7746 |  | 236393 | 870307.5921 |  | 236393 | 1010400.0961 |  | 236393 | 1184773.5755
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 4899.033 | C_100 - C this iteration | iteration | 46223.9981 | C_100 - C this iteration | iteration | 113185.592 | C_100 - C this iteration | iteration | 220456.6431 | C_100 - C this iteration | iteration | 369857.6678 | C_100 - C this iteration | iteration | 539817.3396 | C_100 - C this iteration | iteration | 720388.3324 | C_100 - C this iteration | iteration | 879010.6681 | C_100 - C this iteration | iteration | 1020504.0971 | C_100 - C this iteration | iteration | 1196621.3113 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1807 |  |  | 89.7956 |  |  | 87.8501 |  |  | 81.327 |  |  | 65.2527 |  |  | 37.0737 |  |  | -4.401 |  |  | -50.6406 |  |  | -99.6267 |  |  | -170.7948
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1807 |  |  | 29.7956 |  |  | 27.8501 |  |  | 21.327 |  |  | 5.2527 |  |  | -22.9263 |  |  | -64.401 |  |  | -110.6406 |  |  | -159.6267 |  |  | -230.7948
[13 empty] | Press drop ratio this iteration |  |  | 0.33467 |  |  | 0.33182 |  |  | 0.31702 |  |  | 0.26224 |  |  | 0.080498 |  |  | -0.6184 |  |  | 14.6334 |  |  | 2.1848 |  |  | 1.6022 |  |  | 1.3513
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82723 |  |  | 0.83336 |  |  | 0.86021 |  |  | 0.95576 |  |  | 1.3603 |  |  | -8.1717 |  |  | -0.53106 |  |  | 0.095605 |  |  | -0.19577
[13 empty] | C Non choked w/ reducers | 7 |  | 1.9786 |  |  | 18.8066 |  |  | 47.9119 |  |  | 108.0127 |  |  | 371.4334 |  |  | #NUM! |  |  | 98.5849 |  |  | 441.7073 |  |  | -1924.431 |  |  | 937.5328
[13 empty] | C Choked w/ reducers | 7 |  | 1.7712 |  |  | 16.7922 |  |  | 42.3253 |  |  | 90.2089 |  |  | 193.8992 |  |  | 524.3729 |  |  | -6335.4854 |  |  | -753.7228 |  |  | -454.3573 |  |  | -521.1716
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.9786 |  |  | 18.8066 |  |  | 47.9119 |  |  | 108.0127 |  |  | 371.4334 |  |  | #NUM! |  |  | -6335.4854 |  |  | -753.7228 |  |  | -454.3573 |  |  | -521.1716
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.7514 | 4899.033 |  | 7.2066 | 46223.9981 |  | 24.9119 | 113185.592 |  | 68.6127 | 220456.6431 |  | 310.4334 | 369857.6678 |  | 236393 | 539817.3396 |  | 236393 | 720388.3324 |  | 236393 | 879010.6681 |  | 236393 | 1020504.0971 |  | 236393 | 1196621.3113
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 4997.0137 | C_100 - C this iteration | iteration | 46686.238 | C_100 - C this iteration | iteration | 114317.4479 | C_100 - C this iteration | iteration | 222661.2095 | C_100 - C this iteration | iteration | 373556.2445 | C_100 - C this iteration | iteration | 545215.513 | C_100 - C this iteration | iteration | 727592.2157 | C_100 - C this iteration | iteration | 887800.7747 | C_100 - C this iteration | iteration | 1030709.138 | C_100 - C this iteration | iteration | 1208587.5244 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1805 |  |  | 89.7878 |  |  | 87.8032 |  |  | 81.1489 |  |  | 64.7516 |  |  | 36.0062 |  |  | -6.3021 |  |  | -53.4712 |  |  | -103.4419 |  |  | -176.0405
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1805 |  |  | 29.7878 |  |  | 27.8032 |  |  | 21.1489 |  |  | 4.7516 |  |  | -23.9938 |  |  | -66.3021 |  |  | -113.4712 |  |  | -163.4419 |  |  | -236.0405
[13 empty] | Press drop ratio this iteration |  |  | 0.33467 |  |  | 0.33176 |  |  | 0.31665 |  |  | 0.26062 |  |  | 0.073382 |  |  | -0.66638 |  |  | 10.5206 |  |  | 2.1221 |  |  | 1.58 |  |  | 1.3408
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82726 |  |  | 0.83355 |  |  | 0.86108 |  |  | 0.95967 |  |  | 1.3882 |  |  | -5.5939 |  |  | -0.48711 |  |  | 0.10814 |  |  | -0.1865
[13 empty] | C Non choked w/ reducers | 7 |  | 2.0182 |  |  | 18.9973 |  |  | 48.4336 |  |  | 109.5613 |  |  | 394.3447 |  |  | #NUM! |  |  | 119.7951 |  |  | 467.3893 |  |  | -1666.5442 |  |  | 968.0786
[13 empty] | C Choked w/ reducers | 7 |  | 1.8066 |  |  | 16.9616 |  |  | 42.7714 |  |  | 91.3109 |  |  | 197.3538 |  |  | 545.3191 |  |  | -4468.4904 |  |  | -720.9613 |  |  | -441.9754 |  |  | -510.698
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.0182 |  |  | 18.9973 |  |  | 48.4336 |  |  | 109.5613 |  |  | 394.3447 |  |  | #NUM! |  |  | -4468.4904 |  |  | -720.9613 |  |  | -441.9754 |  |  | -510.698
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.7118 | 4997.0137 |  | 7.3973 | 46686.238 |  | 25.4336 | 114317.4479 |  | 70.1613 | 222661.2095 |  | 333.3447 | 373556.2445 |  | 236393 | 545215.513 |  | 236393 | 727592.2157 |  | 236393 | 887800.7747 |  | 236393 | 1030709.138 |  | 236393 | 1208587.5244
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 5096.954 | C_100 - C this iteration | iteration | 47153.1004 | C_100 - C this iteration | iteration | 115460.6224 | C_100 - C this iteration | iteration | 224887.8216 | C_100 - C this iteration | iteration | 377291.8069 | C_100 - C this iteration | iteration | 550667.6682 | C_100 - C this iteration | iteration | 734868.1379 | C_100 - C this iteration | iteration | 896678.7825 | C_100 - C this iteration | iteration | 1041016.2294 | C_100 - C this iteration | iteration | 1220673.3996 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1803 |  |  | 89.7798 |  |  | 87.7553 |  |  | 80.9673 |  |  | 64.2404 |  |  | 34.9172 |  |  | -8.2415 |  |  | -56.3587 |  |  | -107.3338 |  |  | -181.3917
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1803 |  |  | 29.7798 |  |  | 27.7553 |  |  | 20.9673 |  |  | 4.2404 |  |  | -25.0828 |  |  | -68.2415 |  |  | -116.3587 |  |  | -167.3338 |  |  | -241.3917
[13 empty] | Press drop ratio this iteration |  |  | 0.33467 |  |  | 0.3317 |  |  | 0.31628 |  |  | 0.25896 |  |  | 0.066008 |  |  | -0.71835 |  |  | 8.2802 |  |  | 2.0646 |  |  | 1.559 |  |  | 1.3308
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82729 |  |  | 0.83375 |  |  | 0.86196 |  |  | 0.96372 |  |  | 1.4185 |  |  | -4.1897 |  |  | -0.44682 |  |  | 0.12001 |  |  | -0.17761
[13 empty] | C Non choked w/ reducers | 7 |  | 2.0585 |  |  | 19.19 |  |  | 48.962 |  |  | 111.1456 |  |  | 421.5079 |  |  | #NUM! |  |  | 139.2419 |  |  | 495.0111 |  |  | -1471.5416 |  |  | 1000.2095
[13 empty] | C Choked w/ reducers | 7 |  | 1.8427 |  |  | 17.1327 |  |  | 43.2227 |  |  | 92.4309 |  |  | 200.9136 |  |  | 567.9498 |  |  | -3451.1379 |  |  | -690.8637 |  |  | -430.2089 |  |  | -500.5885
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.0585 |  |  | 19.19 |  |  | 48.962 |  |  | 111.1456 |  |  | 421.5079 |  |  | #NUM! |  |  | -3451.1379 |  |  | -690.8637 |  |  | -430.2089 |  |  | -500.5885
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.6715 | 5096.954 |  | 7.59 | 47153.1004 |  | 25.962 | 115460.6224 |  | 71.7456 | 224887.8216 |  | 360.5079 | 377291.8069 |  | 236393 | 550667.6682 |  | 236393 | 734868.1379 |  | 236393 | 896678.7825 |  | 236393 | 1041016.2294 |  | 236393 | 1220673.3996
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 5198.893 | C_100 - C this iteration | iteration | 47624.6314 | C_100 - C this iteration | iteration | 116615.2286 | C_100 - C this iteration | iteration | 227136.6998 | C_100 - C this iteration | iteration | 381064.725 | C_100 - C this iteration | iteration | 556174.3448 | C_100 - C this iteration | iteration | 742216.8192 | C_100 - C this iteration | iteration | 905645.5703 | C_100 - C this iteration | iteration | 1051426.3917 | C_100 - C this iteration | iteration | 1232880.1336 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1801 |  |  | 89.7717 |  |  | 87.7065 |  |  | 80.782 |  |  | 63.7189 |  |  | 33.8063 |  |  | -10.2199 |  |  | -59.3042 |  |  | -111.3039 |  |  | -186.8503
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1801 |  |  | 29.7717 |  |  | 27.7065 |  |  | 20.782 |  |  | 3.7189 |  |  | -26.1937 |  |  | -70.2199 |  |  | -119.3042 |  |  | -171.3039 |  |  | -246.8503
[13 empty] | Press drop ratio this iteration |  |  | 0.33466 |  |  | 0.33164 |  |  | 0.3159 |  |  | 0.25726 |  |  | 0.058364 |  |  | -0.77482 |  |  | 6.8709 |  |  | 2.0117 |  |  | 1.5391 |  |  | 1.3211
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82732 |  |  | 0.83395 |  |  | 0.86287 |  |  | 0.96792 |  |  | 1.4514 |  |  | -3.3064 |  |  | -0.40977 |  |  | 0.13127 |  |  | -0.16905
[13 empty] | C Non choked w/ reducers | 7 |  | 2.0997 |  |  | 19.3846 |  |  | 49.4971 |  |  | 112.7671 |  |  | 454.4685 |  |  | #NUM! |  |  | 157.7585 |  |  | 524.8592 |  |  | -1318.8207 |  |  | 1034.0662
[13 empty] | C Choked w/ reducers | 7 |  | 1.8796 |  |  | 17.3056 |  |  | 43.6793 |  |  | 93.5693 |  |  | 204.5835 |  |  | 592.4789 |  |  | -2810.8959 |  |  | -663.1153 |  |  | -419.0123 |  |  | -490.8238
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.0997 |  |  | 19.3846 |  |  | 49.4971 |  |  | 112.7671 |  |  | 454.4685 |  |  | #NUM! |  |  | -2810.8959 |  |  | -663.1153 |  |  | -419.0123 |  |  | -490.8238
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.6303 | 5198.893 |  | 7.7846 | 47624.6314 |  | 26.4971 | 116615.2286 |  | 73.3671 | 227136.6998 |  | 393.4685 | 381064.725 |  | 236393 | 556174.3448 |  | 236393 | 742216.8192 |  | 236393 | 905645.5703 |  | 236393 | 1051426.3917 |  | 236393 | 1232880.1336
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 5302.8709 | C_100 - C this iteration | iteration | 48100.8777 | C_100 - C this iteration | iteration | 117781.3809 | C_100 - C this iteration | iteration | 229408.0668 | C_100 - C this iteration | iteration | 384875.3722 | C_100 - C this iteration | iteration | 561736.0883 | C_100 - C this iteration | iteration | 749638.9874 | C_100 - C this iteration | iteration | 914702.026 | C_100 - C this iteration | iteration | 1061940.6556 | C_100 - C this iteration | iteration | 1245208.935 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1799 |  |  | 89.7633 |  |  | 87.6566 |  |  | 80.593 |  |  | 63.1869 |  |  | 32.6731 |  |  | -12.238 |  |  | -62.309 |  |  | -115.3539 |  |  | -192.4188
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1799 |  |  | 29.7633 |  |  | 27.6566 |  |  | 20.593 |  |  | 3.1869 |  |  | -27.3269 |  |  | -72.238 |  |  | -122.309 |  |  | -175.3539 |  |  | -252.4188
[13 empty] | Press drop ratio this iteration |  |  | 0.33466 |  |  | 0.33158 |  |  | 0.31551 |  |  | 0.25552 |  |  | 0.050436 |  |  | -0.83637 |  |  | 5.9027 |  |  | 1.9629 |  |  | 1.5201 |  |  | 1.3118
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.82735 |  |  | 0.83415 |  |  | 0.86379 |  |  | 0.97228 |  |  | 1.4872 |  |  | -2.6996 |  |  | -0.37558 |  |  | 0.14195 |  |  | -0.16083
[13 empty] | C Non choked w/ reducers | 7 |  | 2.1417 |  |  | 19.5814 |  |  | 50.039 |  |  | 114.4271 |  |  | 495.6971 |  |  | #NUM! |  |  | 175.8265 |  |  | 557.2735 |  |  | -1195.897 |  |  | 1069.806
[13 empty] | C Choked w/ reducers | 7 |  | 1.9172 |  |  | 17.4803 |  |  | 44.1411 |  |  | 94.7266 |  |  | 208.3689 |  |  | 619.1583 |  |  | -2370.8331 |  |  | -637.4492 |  |  | -408.3444 |  |  | -481.3861
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.1417 |  |  | 19.5814 |  |  | 50.039 |  |  | 114.4271 |  |  | 495.6971 |  |  | #NUM! |  |  | -2370.8331 |  |  | -637.4492 |  |  | -408.3444 |  |  | -481.3861
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.5883 | 5302.8709 |  | 7.9814 | 48100.8777 |  | 27.039 | 117781.3809 |  | 75.0271 | 229408.0668 |  | 434.6971 | 384875.3722 |  | 236393 | 561736.0883 |  | 236393 | 749638.9874 |  | 236393 | 914702.026 |  | 236393 | 1061940.6556 |  | 236393 | 1245208.935
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 5408.9283 | C_100 - C this iteration | iteration | 48581.8865 | C_100 - C this iteration | iteration | 118959.1947 | C_100 - C this iteration | iteration | 231702.1475 | C_100 - C this iteration | iteration | 388724.126 | C_100 - C this iteration | iteration | 567353.4492 | C_100 - C this iteration | iteration | 757135.3773 | C_100 - C this iteration | iteration | 923849.0463 | C_100 - C this iteration | iteration | 1072560.0622 | C_100 - C this iteration | iteration | 1257661.0243 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1797 |  |  | 89.7549 |  |  | 87.6058 |  |  | 80.4002 |  |  | 62.6442 |  |  | 31.5171 |  |  | -14.2968 |  |  | -65.3741 |  |  | -119.4852 |  |  | -198.0991
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1797 |  |  | 29.7549 |  |  | 27.6058 |  |  | 20.4002 |  |  | 2.6442 |  |  | -28.4829 |  |  | -74.2968 |  |  | -125.3741 |  |  | -179.4852 |  |  | -258.0991
[13 empty] | Press drop ratio this iteration |  |  | 0.33466 |  |  | 0.33151 |  |  | 0.31511 |  |  | 0.25373 |  |  | 0.04221 |  |  | -0.90373 |  |  | 5.1968 |  |  | 1.9178 |  |  | 1.5022 |  |  | 1.3029
[13 empty] | Expansion factor | 12 |  | 0.82571 |  |  | 0.82739 |  |  | 0.83436 |  |  | 0.86475 |  |  | 0.9768 |  |  | 1.5265 |  |  | -2.2571 |  |  | -0.34394 |  |  | 0.1521 |  |  | -0.15292
[13 empty] | C Non choked w/ reducers | 7 |  | 2.1845 |  |  | 19.7801 |  |  | 50.5879 |  |  | 116.1275 |  |  | 549.4523 |  |  | #NUM! |  |  | 193.7699 |  |  | 592.6606 |  |  | -1094.7636 |  |  | 1107.6052
[13 empty] | C Choked w/ reducers | 7 |  | 1.9555 |  |  | 17.6568 |  |  | 44.6084 |  |  | 95.9033 |  |  | 212.2757 |  |  | 648.2866 |  |  | -2049.7322 |  |  | -613.6374 |  |  | -398.1677 |  |  | -472.2585
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.1845 |  |  | 19.7801 |  |  | 50.5879 |  |  | 116.1275 |  |  | 549.4523 |  |  | #NUM! |  |  | -2049.7322 |  |  | -613.6374 |  |  | -398.1677 |  |  | -472.2585
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.5455 | 5408.9283 |  | 8.1801 | 48581.8865 |  | 27.5879 | 118959.1947 |  | 76.7275 | 231702.1475 |  | 488.4523 | 388724.126 |  | 236393 | 567353.4492 |  | 236393 | 757135.3773 |  | 236393 | 923849.0463 |  | 236393 | 1072560.0622 |  | 236393 | 1257661.0243
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 5517.1069 | C_100 - C this iteration | iteration | 49067.7054 | C_100 - C this iteration | iteration | 120148.7867 | C_100 - C this iteration | iteration | 234019.169 | C_100 - C this iteration | iteration | 392611.3672 | C_100 - C this iteration | iteration | 573026.9837 | C_100 - C this iteration | iteration | 764706.7311 | C_100 - C this iteration | iteration | 933087.5367 | C_100 - C this iteration | iteration | 1083285.6628 | C_100 - C this iteration | iteration | 1270237.6345 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1795 |  |  | 89.7462 |  |  | 87.554 |  |  | 80.2035 |  |  | 62.0907 |  |  | 30.3379 |  |  | -16.3968 |  |  | -68.5009 |  |  | -123.6996 |  |  | -203.8936
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1795 |  |  | 29.7462 |  |  | 27.554 |  |  | 20.2035 |  |  | 2.0907 |  |  | -29.6621 |  |  | -76.3968 |  |  | -128.5009 |  |  | -183.6996 |  |  | -263.8936
[13 empty] | Press drop ratio this iteration |  |  | 0.33466 |  |  | 0.33145 |  |  | 0.31471 |  |  | 0.2519 |  |  | 0.033671 |  |  | -0.97773 |  |  | 4.6592 |  |  | 1.8759 |  |  | 1.485 |  |  | 1.2943
[13 empty] | Expansion factor | 12 |  | 0.82571 |  |  | 0.82742 |  |  | 0.83457 |  |  | 0.86572 |  |  | 0.98149 |  |  | 1.5696 |  |  | -1.9202 |  |  | -0.31458 |  |  | 0.16176 |  |  | -0.1453
[13 empty] | C Non choked w/ reducers | 7 |  | 2.2282 |  |  | 19.981 |  |  | 51.1439 |  |  | 117.8697 |  |  | 623.8854 |  |  | #NUM! |  |  | 211.8339 |  |  | 631.5118 |  |  | -1010.0489 |  |  | 1147.6623
[13 empty] | C Choked w/ reducers | 7 |  | 1.9946 |  |  | 17.835 |  |  | 45.0812 |  |  | 97.0999 |  |  | 216.3099 |  |  | 680.2202 |  |  | -1805.0774 |  |  | -591.484 |  |  | -388.4484 |  |  | -463.4257
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.2282 |  |  | 19.981 |  |  | 51.1439 |  |  | 117.8697 |  |  | 623.8854 |  |  | #NUM! |  |  | -1805.0774 |  |  | -591.484 |  |  | -388.4484 |  |  | -463.4257
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.5018 | 5517.1069 |  | 8.381 | 49067.7054 |  | 28.1439 | 120148.7867 |  | 78.4697 | 234019.169 |  | 562.8854 | 392611.3672 |  | 236393 | 573026.9837 |  | 236393 | 764706.7311 |  | 236393 | 933087.5367 |  | 236393 | 1083285.6628 |  | 236393 | 1270237.6345
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 5627.449 | C_100 - C this iteration | iteration | 49558.3824 | C_100 - C this iteration | iteration | 121350.2745 | C_100 - C this iteration | iteration | 236359.3607 | C_100 - C this iteration | iteration | 396537.4809 | C_100 - C this iteration | iteration | 578757.2535 | C_100 - C this iteration | iteration | 772353.7984 | C_100 - C this iteration | iteration | 942418.4121 | C_100 - C this iteration | iteration | 1094118.5194 | C_100 - C this iteration | iteration | 1282940.0109 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1793 |  |  | 89.7374 |  |  | 87.5011 |  |  | 80.0029 |  |  | 61.526 |  |  | 29.1349 |  |  | -18.5391 |  |  | -71.6904 |  |  | -127.9986 |  |  | -209.8046
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1793 |  |  | 29.7374 |  |  | 27.5011 |  |  | 20.0029 |  |  | 1.526 |  |  | -30.8651 |  |  | -78.5391 |  |  | -131.6904 |  |  | -187.9986 |  |  | -269.8046
[13 empty] | Press drop ratio this iteration |  |  | 0.33466 |  |  | 0.33138 |  |  | 0.31429 |  |  | 0.25003 |  |  | 0.024802 |  |  | -1.0594 |  |  | 4.2364 |  |  | 1.8369 |  |  | 1.4688 |  |  | 1.286
[13 empty] | Expansion factor | 12 |  | 0.82571 |  |  | 0.82745 |  |  | 0.83479 |  |  | 0.86672 |  |  | 0.98637 |  |  | 1.6172 |  |  | -1.6552 |  |  | -0.28727 |  |  | 0.17096 |  |  | -0.13797
[13 empty] | C Non choked w/ reducers | 7 |  | 2.2728 |  |  | 20.184 |  |  | 51.7071 |  |  | 119.6556 |  |  | 737.2722 |  |  | #NUM! |  |  | 230.2224 |  |  | 674.4275 |  |  | -938.0147 |  |  | 1190.2017
[13 empty] | C Choked w/ reducers | 7 |  | 2.0345 |  |  | 18.0152 |  |  | 45.5595 |  |  | 98.3168 |  |  | 220.4782 |  |  | 715.3883 |  |  | -1612.456 |  |  | -570.8199 |  |  | -379.1556 |  |  | -454.8729
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.2728 |  |  | 20.184 |  |  | 51.7071 |  |  | 119.6556 |  |  | 737.2722 |  |  | #NUM! |  |  | -1612.456 |  |  | -570.8199 |  |  | -379.1556 |  |  | -454.8729
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.4572 | 5627.449 |  | 8.584 | 49558.3824 |  | 28.7071 | 121350.2745 |  | 80.2556 | 236359.3607 |  | 676.2722 | 396537.4809 |  | 236393 | 578757.2535 |  | 236393 | 772353.7984 |  | 236393 | 942418.4121 |  | 236393 | 1094118.5194 |  | 236393 | 1282940.0109
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 5739.998 | C_100 - C this iteration | iteration | 50053.9663 | C_100 - C this iteration | iteration | 122563.7773 | C_100 - C this iteration | iteration | 238722.9543 | C_100 - C this iteration | iteration | 400502.8557 | C_100 - C this iteration | iteration | 584544.826 | C_100 - C this iteration | iteration | 780077.3364 | C_100 - C this iteration | iteration | 951842.5962 | C_100 - C this iteration | iteration | 1105059.7046 | C_100 - C this iteration | iteration | 1295769.411 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.179 |  |  | 89.7284 |  |  | 87.4471 |  |  | 79.7982 |  |  | 60.9499 |  |  | 27.9078 |  |  | -20.7245 |  |  | -74.9441 |  |  | -132.3841 |  |  | -215.8344
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.179 |  |  | 29.7284 |  |  | 27.4471 |  |  | 19.7982 |  |  | 0.94993 |  |  | -32.0922 |  |  | -80.7245 |  |  | -134.9441 |  |  | -192.3841 |  |  | -275.8344
[13 empty] | Press drop ratio this iteration |  |  | 0.33466 |  |  | 0.33132 |  |  | 0.31387 |  |  | 0.2481 |  |  | 0.015585 |  |  | -1.1499 |  |  | 3.8951 |  |  | 1.8006 |  |  | 1.4532 |  |  | 1.278
[13 empty] | Expansion factor | 12 |  | 0.82571 |  |  | 0.82749 |  |  | 0.83501 |  |  | 0.86775 |  |  | 0.99143 |  |  | 1.6699 |  |  | -1.4413 |  |  | -0.26181 |  |  | 0.17972 |  |  | -0.1309
[13 empty] | C Non choked w/ reducers | 7 |  | 2.3183 |  |  | 20.389 |  |  | 52.2777 |  |  | 121.4872 |  |  | 943.3997 |  |  | #NUM! |  |  | 249.1187 |  |  | 722.1492 |  |  | -875.9791 |  |  | 1235.4781
[13 empty] | C Choked w/ reducers | 7 |  | 2.0752 |  |  | 18.1971 |  |  | 46.0435 |  |  | 99.5547 |  |  | 224.7876 |  |  | 754.3124 |  |  | -1456.85 |  |  | -551.4982 |  |  | -370.2612 |  |  | -446.5867
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.3183 |  |  | 20.389 |  |  | 52.2777 |  |  | 121.4872 |  |  | 943.3997 |  |  | #NUM! |  |  | -1456.85 |  |  | -551.4982 |  |  | -370.2612 |  |  | -446.5867
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.4117 | 5739.998 |  | 8.789 | 50053.9663 |  | 29.2777 | 122563.7773 |  | 82.0872 | 238722.9543 |  | 882.3997 | 400502.8557 |  | 236393 | 584544.826 |  | 236393 | 780077.3364 |  | 236393 | 951842.5962 |  | 236393 | 1105059.7046 |  | 236393 | 1295769.411
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 5854.798 | C_100 - C this iteration | iteration | 50554.5059 | C_100 - C this iteration | iteration | 123789.415 | C_100 - C this iteration | iteration | 241110.1838 | C_100 - C this iteration | iteration | 404507.8842 | C_100 - C this iteration | iteration | 590390.2743 | C_100 - C this iteration | iteration | 787878.1097 | C_100 - C this iteration | iteration | 961361.0222 | C_100 - C this iteration | iteration | 1116110.3017 | C_100 - C this iteration | iteration | 1308727.1051 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1788 |  |  | 89.7192 |  |  | 87.3921 |  |  | 79.5895 |  |  | 60.3623 |  |  | 26.6561 |  |  | -22.9538 |  |  | -78.2632 |  |  | -136.8578 |  |  | -221.9854
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1788 |  |  | 29.7192 |  |  | 27.3921 |  |  | 19.5895 |  |  | 0.3623 |  |  | -33.3439 |  |  | -82.9538 |  |  | -138.2632 |  |  | -196.8578 |  |  | -281.9854
[13 empty] | Press drop ratio this iteration |  |  | 0.33466 |  |  | 0.33125 |  |  | 0.31344 |  |  | 0.24613 |  |  | 0.0060021 |  |  | -1.2509 |  |  | 3.6139 |  |  | 1.7666 |  |  | 1.4384 |  |  | 1.2703
[13 empty] | Expansion factor | 12 |  | 0.82571 |  |  | 0.82752 |  |  | 0.83524 |  |  | 0.8688 |  |  | 0.9967 |  |  | 1.7287 |  |  | -1.2651 |  |  | -0.23802 |  |  | 0.18808 |  |  | -0.12408
[13 empty] | C Non choked w/ reducers | 7 |  | 2.3647 |  |  | 20.5963 |  |  | 52.8557 |  |  | 123.3664 |  |  | 1542.1608 |  |  | #NUM! |  |  | 268.6993 |  |  | 775.6051 |  |  | -821.9679 |  |  | 1283.7813
[13 empty] | C Choked w/ reducers | 7 |  | 2.1167 |  |  | 18.381 |  |  | 46.5332 |  |  | 100.814 |  |  | 229.2457 |  |  | 797.6324 |  |  | -1328.5136 |  |  | -533.3906 |  |  | -361.7396 |  |  | -438.5544
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.3647 |  |  | 20.5963 |  |  | 52.8557 |  |  | 123.3664 |  |  | 1542.1608 |  |  | #NUM! |  |  | -1328.5136 |  |  | -533.3906 |  |  | -361.7396 |  |  | -438.5544
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.3653 | 5854.798 |  | 8.9963 | 50554.5059 |  | 29.8557 | 123789.415 |  | 83.9664 | 241110.1838 |  | 1481.1608 | 404507.8842 |  | 236393 | 590390.2743 |  | 236393 | 787878.1097 |  | 236393 | 961361.0222 |  | 236393 | 1116110.3017 |  | 236393 | 1308727.1051
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 5971.8939 | C_100 - C this iteration | iteration | 51060.051 | C_100 - C this iteration | iteration | 125027.3092 | C_100 - C this iteration | iteration | 243521.2857 | C_100 - C this iteration | iteration | 408552.9631 | C_100 - C this iteration | iteration | 596294.177 | C_100 - C this iteration | iteration | 795756.8908 | C_100 - C this iteration | iteration | 970974.6324 | C_100 - C this iteration | iteration | 1127271.4047 | C_100 - C this iteration | iteration | 1321814.3762 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1785 |  |  | 89.7099 |  |  | 87.336 |  |  | 79.3765 |  |  | 59.7629 |  |  | 25.3791 |  |  | -25.2279 |  |  | -81.649 |  |  | -141.4213 |  |  | -228.26
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1785 |  |  | 29.7099 |  |  | 27.336 |  |  | 19.3765 |  |  | -0.23713 |  |  | -34.6209 |  |  | -85.2279 |  |  | -141.649 |  |  | -201.4213 |  |  | -288.26
[13 empty] | Press drop ratio this iteration |  |  | 0.33465 |  |  | 0.33118 |  |  | 0.313 |  |  | 0.24411 |  |  | -0.0039679 |  |  | -1.3641 |  |  | 3.3783 |  |  | 1.7349 |  |  | 1.4243 |  |  | 1.2629
[13 empty] | Expansion factor | 12 |  | 0.82571 |  |  | 0.82756 |  |  | 0.83547 |  |  | 0.86988 |  |  | 1.0022 |  |  | 1.7947 |  |  | -1.1174 |  |  | -0.21574 |  |  | 0.19607 |  |  | -0.1175
[13 empty] | C Non choked w/ reducers | 7 |  | 2.412 |  |  | 20.8057 |  |  | 53.4414 |  |  | 125.2954 |  |  | #NUM! |  |  | #NUM! |  |  | 289.1423 |  |  | 835.9725 |  |  | -774.4956 |  |  | 1335.4434
[13 empty] | C Choked w/ reducers | 7 |  | 2.1591 |  |  | 18.5667 |  |  | 47.0287 |  |  | 102.0953 |  |  | 233.8605 |  |  | 846.1423 |  |  | -1220.8463 |  |  | -516.3847 |  |  | -353.5672 |  |  | -430.764
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.412 |  |  | 20.8057 |  |  | 53.4414 |  |  | 125.2954 |  |  | #NUM! |  |  | #NUM! |  |  | -1220.8463 |  |  | -516.3847 |  |  | -353.5672 |  |  | -430.764
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.318 | 5971.8939 |  | 9.2057 | 51060.051 |  | 30.4414 | 125027.3092 |  | 85.8954 | 243521.2857 |  | 236393 | 408552.9631 |  | 236393 | 596294.177 |  | 236393 | 795756.8908 |  | 236393 | 970974.6324 |  | 236393 | 1127271.4047 |  | 236393 | 1321814.3762
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 6091.3318 | C_100 - C this iteration | iteration | 51570.6515 | C_100 - C this iteration | iteration | 126277.5823 | C_100 - C this iteration | iteration | 245956.4985 | C_100 - C this iteration | iteration | 412638.4927 | C_100 - C this iteration | iteration | 602257.1188 | C_100 - C this iteration | iteration | 803714.4597 | C_100 - C this iteration | iteration | 980684.3787 | C_100 - C this iteration | iteration | 1138544.1187 | C_100 - C this iteration | iteration | 1335032.5199 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1783 |  |  | 89.7003 |  |  | 87.2787 |  |  | 79.1592 |  |  | 59.1514 |  |  | 24.0765 |  |  | -27.5477 |  |  | -85.1029 |  |  | -146.0766 |  |  | -234.6607
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1783 |  |  | 29.7003 |  |  | 27.2787 |  |  | 19.1592 |  |  | -0.84862 |  |  | -35.9235 |  |  | -87.5477 |  |  | -145.1029 |  |  | -206.0766 |  |  | -294.6607
[13 empty] | Press drop ratio this iteration |  |  | 0.33465 |  |  | 0.33111 |  |  | 0.31255 |  |  | 0.24203 |  |  | -0.014347 |  |  | -1.4921 |  |  | 3.178 |  |  | 1.705 |  |  | 1.4107 |  |  | 1.2557
[13 empty] | Expansion factor | 12 |  | 0.82571 |  |  | 0.8276 |  |  | 0.83571 |  |  | 0.87098 |  |  | 1.0079 |  |  | 1.8692 |  |  | -0.99188 |  |  | -0.19484 |  |  | 0.2037 |  |  | -0.11116
[13 empty] | C Non choked w/ reducers | 7 |  | 2.4602 |  |  | 21.0173 |  |  | 54.0348 |  |  | 127.2765 |  |  | #NUM! |  |  | #NUM! |  |  | 310.636 |  |  | 904.7688 |  |  | -732.4228 |  |  | 1390.846
[13 empty] | C Choked w/ reducers | 7 |  | 2.2023 |  |  | 18.7544 |  |  | 47.5302 |  |  | 103.3992 |  |  | 238.6408 |  |  | 900.8399 |  |  | -1129.2187 |  |  | -500.3817 |  |  | -345.7225 |  |  | -423.2043
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.4602 |  |  | 21.0173 |  |  | 54.0348 |  |  | 127.2765 |  |  | #NUM! |  |  | #NUM! |  |  | -1129.2187 |  |  | -500.3817 |  |  | -345.7225 |  |  | -423.2043
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.2698 | 6091.3318 |  | 9.4173 | 51570.6515 |  | 31.0348 | 126277.5823 |  | 87.8765 | 245956.4985 |  | 236393 | 412638.4927 |  | 236393 | 602257.1188 |  | 236393 | 803714.4597 |  | 236393 | 980684.3787 |  | 236393 | 1138544.1187 |  | 236393 | 1335032.5199
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 6213.1584 | C_100 - C this iteration | iteration | 52086.358 | C_100 - C this iteration | iteration | 127540.3581 | C_100 - C this iteration | iteration | 248416.0635 | C_100 - C this iteration | iteration | 416764.8776 | C_100 - C this iteration | iteration | 608279.69 | C_100 - C this iteration | iteration | 811751.6043 | C_100 - C this iteration | iteration | 990491.2225 | C_100 - C this iteration | iteration | 1149929.5599 | C_100 - C this iteration | iteration | 1348382.8451 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.178 |  |  | 89.6906 |  |  | 87.2203 |  |  | 78.9376 |  |  | 58.5276 |  |  | 22.7477 |  |  | -29.9141 |  |  | -88.6262 |  |  | -150.8255 |  |  | -241.1901
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.178 |  |  | 29.6906 |  |  | 27.2203 |  |  | 18.9376 |  |  | -1.4724 |  |  | -37.2523 |  |  | -89.9141 |  |  | -148.6262 |  |  | -210.8255 |  |  | -301.1901
[13 empty] | Press drop ratio this iteration |  |  | 0.33465 |  |  | 0.33103 |  |  | 0.31209 |  |  | 0.23991 |  |  | -0.025157 |  |  | -1.6376 |  |  | 3.0057 |  |  | 1.677 |  |  | 1.3978 |  |  | 1.2488
[13 empty] | Expansion factor | 12 |  | 0.82571 |  |  | 0.82763 |  |  | 0.83595 |  |  | 0.87212 |  |  | 1.0138 |  |  | 1.954 |  |  | -0.88389 |  |  | -0.1752 |  |  | 0.211 |  |  | -0.10503
[13 empty] | C Non choked w/ reducers | 7 |  | 2.5094 |  |  | 21.2311 |  |  | 54.6362 |  |  | 129.3122 |  |  | #NUM! |  |  | #NUM! |  |  | 333.3861 |  |  | 983.9843 |  |  | -694.8611 |  |  | 1450.4305
[13 empty] | C Choked w/ reducers | 7 |  | 2.2463 |  |  | 18.944 |  |  | 48.0376 |  |  | 104.7264 |  |  | 243.5961 |  |  | 962.996 |  |  | -1050.288 |  |  | -485.2942 |  |  | -338.1855 |  |  | -415.865
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.5094 |  |  | 21.2311 |  |  | 54.6362 |  |  | 129.3122 |  |  | #NUM! |  |  | #NUM! |  |  | -1050.288 |  |  | -485.2942 |  |  | -338.1855 |  |  | -415.865
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.2206 | 6213.1584 |  | 9.6311 | 52086.358 |  | 31.6362 | 127540.3581 |  | 89.9122 | 248416.0635 |  | 236393 | 416764.8776 |  | 236393 | 608279.69 |  | 236393 | 811751.6043 |  | 236393 | 990491.2225 |  | 236393 | 1149929.5599 |  | 236393 | 1348382.8451
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 6337.4216 | C_100 - C this iteration | iteration | 52607.2216 | C_100 - C this iteration | iteration | 128815.7617 | C_100 - C this iteration | iteration | 250900.2241 | C_100 - C this iteration | iteration | 420932.5264 | C_100 - C this iteration | iteration | 614362.4869 | C_100 - C this iteration | iteration | 819869.1204 | C_100 - C this iteration | iteration | 1000396.1347 | C_100 - C this iteration | iteration | 1161428.8555 | C_100 - C this iteration | iteration | 1361866.6736 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1777 |  |  | 89.6806 |  |  | 87.1607 |  |  | 78.7115 |  |  | 57.8913 |  |  | 21.3923 |  |  | -32.3281 |  |  | -92.2203 |  |  | -155.6698 |  |  | -247.8508
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1777 |  |  | 29.6806 |  |  | 27.1607 |  |  | 18.7115 |  |  | -2.1087 |  |  | -38.6077 |  |  | -92.3281 |  |  | -152.2203 |  |  | -215.6698 |  |  | -307.8508
[13 empty] | Press drop ratio this iteration |  |  | 0.33465 |  |  | 0.33096 |  |  | 0.31162 |  |  | 0.23772 |  |  | -0.036425 |  |  | -1.8048 |  |  | 2.856 |  |  | 1.6506 |  |  | 1.3854 |  |  | 1.2421
[13 empty] | Expansion factor | 12 |  | 0.82571 |  |  | 0.82767 |  |  | 0.8362 |  |  | 0.87328 |  |  | 1.02 |  |  | 2.0514 |  |  | -0.79002 |  |  | -0.15671 |  |  | 0.21799 |  |  | -0.099119
[13 empty] | C Non choked w/ reducers | 7 |  | 2.5596 |  |  | 21.4472 |  |  | 55.2456 |  |  | 131.4052 |  |  | #NUM! |  |  | #NUM! |  |  | 357.6225 |  |  | 1076.2825 |  |  | -661.1074 |  |  | 1514.7097
[13 empty] | C Choked w/ reducers | 7 |  | 2.2913 |  |  | 19.1356 |  |  | 48.5512 |  |  | 106.0775 |  |  | 248.7363 |  |  | 1034.255 |  |  | -981.5798 |  |  | -471.0446 |  |  | -330.9381 |  |  | -408.7361
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.5596 |  |  | 21.4472 |  |  | 55.2456 |  |  | 131.4052 |  |  | #NUM! |  |  | #NUM! |  |  | -981.5798 |  |  | -471.0446 |  |  | -330.9381 |  |  | -408.7361
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.1704 | 6337.4216 |  | 9.8472 | 52607.2216 |  | 32.2456 | 128815.7617 |  | 92.0052 | 250900.2241 |  | 236393 | 420932.5264 |  | 236393 | 614362.4869 |  | 236393 | 819869.1204 |  | 236393 | 1000396.1347 |  | 236393 | 1161428.8555 |  | 236393 | 1361866.6736
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 6464.17 | C_100 - C this iteration | iteration | 53133.2938 | C_100 - C this iteration | iteration | 130103.9193 | C_100 - C this iteration | iteration | 253409.2264 | C_100 - C this iteration | iteration | 425141.8517 | C_100 - C this iteration | iteration | 620506.1118 | C_100 - C this iteration | iteration | 828067.8116 | C_100 - C this iteration | iteration | 1010400.0961 | C_100 - C this iteration | iteration | 1173043.1441 | C_100 - C this iteration | iteration | 1375485.3403 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1774 |  |  | 89.6705 |  |  | 87.0999 |  |  | 78.4809 |  |  | 57.2422 |  |  | 20.0095 |  |  | -34.7906 |  |  | -95.8866 |  |  | -160.6115 |  |  | -254.6453
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1774 |  |  | 29.6705 |  |  | 27.0999 |  |  | 18.4809 |  |  | -2.7578 |  |  | -39.9905 |  |  | -94.7906 |  |  | -155.8866 |  |  | -220.6115 |  |  | -314.6453
[13 empty] | Press drop ratio this iteration |  |  | 0.33465 |  |  | 0.33088 |  |  | 0.31114 |  |  | 0.23548 |  |  | -0.048178 |  |  | -1.9986 |  |  | 2.7246 |  |  | 1.6257 |  |  | 1.3736 |  |  | 1.2356
[13 empty] | Expansion factor | 12 |  | 0.82571 |  |  | 0.82771 |  |  | 0.83645 |  |  | 0.87447 |  |  | 1.0265 |  |  | 2.1643 |  |  | -0.70768 |  |  | -0.13927 |  |  | 0.22468 |  |  | -0.093403
[13 empty] | C Non choked w/ reducers | 7 |  | 2.6108 |  |  | 21.6656 |  |  | 55.8632 |  |  | 133.5582 |  |  | #NUM! |  |  | #NUM! |  |  | 383.6088 |  |  | 1185.3118 |  |  | -630.598 |  |  | 1584.2835
[13 empty] | C Choked w/ reducers | 7 |  | 2.3371 |  |  | 19.3291 |  |  | 49.0709 |  |  | 107.4531 |  |  | 254.0725 |  |  | 1116.7833 |  |  | -921.2236 |  |  | -457.564 |  |  | -323.9633 |  |  | -401.8084
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.6108 |  |  | 21.6656 |  |  | 55.8632 |  |  | 133.5582 |  |  | #NUM! |  |  | #NUM! |  |  | -921.2236 |  |  | -457.564 |  |  | -323.9633 |  |  | -401.8084
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.1192 | 6464.17 |  | 10.0656 | 53133.2938 |  | 32.8632 | 130103.9193 |  | 94.1582 | 253409.2264 |  | 236393 | 425141.8517 |  | 236393 | 620506.1118 |  | 236393 | 828067.8116 |  | 236393 | 1010400.0961 |  | 236393 | 1173043.1441 |  | 236393 | 1375485.3403
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 6593.4534 | C_100 - C this iteration | iteration | 53664.6267 | C_100 - C this iteration | iteration | 131404.9585 | C_100 - C this iteration | iteration | 255943.3186 | C_100 - C this iteration | iteration | 429393.2702 | C_100 - C this iteration | iteration | 626711.1729 | C_100 - C this iteration | iteration | 836348.4897 | C_100 - C this iteration | iteration | 1020504.0971 | C_100 - C this iteration | iteration | 1184773.5755 | C_100 - C this iteration | iteration | 1389240.1937 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1771 |  |  | 89.6601 |  |  | 87.0379 |  |  | 78.2457 |  |  | 56.58 |  |  | 18.599 |  |  | -37.3026 |  |  | -99.6267 |  |  | -165.6525 |  |  | -261.5764
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1771 |  |  | 29.6601 |  |  | 27.0379 |  |  | 18.2457 |  |  | -3.42 |  |  | -41.401 |  |  | -97.3026 |  |  | -159.6267 |  |  | -225.6525 |  |  | -321.5764
[13 empty] | Press drop ratio this iteration |  |  | 0.33464 |  |  | 0.33081 |  |  | 0.31065 |  |  | 0.23318 |  |  | -0.060445 |  |  | -2.226 |  |  | 2.6085 |  |  | 1.6022 |  |  | 1.3622 |  |  | 1.2294
[13 empty] | Expansion factor | 12 |  | 0.82571 |  |  | 0.82775 |  |  | 0.83671 |  |  | 0.8757 |  |  | 1.0332 |  |  | 2.2968 |  |  | -0.63489 |  |  | -0.12281 |  |  | 0.2311 |  |  | -0.087878
[13 empty] | C Non choked w/ reducers | 7 |  | 2.6631 |  |  | 21.8863 |  |  | 56.4892 |  |  | 135.7743 |  |  | #NUM! |  |  | #NUM! |  |  | 411.6521 |  |  | 1316.2082 |  |  | -602.8757 |  |  | 1659.8576
[13 empty] | C Choked w/ reducers | 7 |  | 2.3838 |  |  | 19.5246 |  |  | 49.5969 |  |  | 108.8539 |  |  | 259.6163 |  |  | 1213.4938 |  |  | -867.779 |  |  | -444.7906 |  |  | -317.2458 |  |  | -395.0731
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.6631 |  |  | 21.8863 |  |  | 56.4892 |  |  | 135.7743 |  |  | #NUM! |  |  | #NUM! |  |  | -867.779 |  |  | -444.7906 |  |  | -317.2458 |  |  | -395.0731
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.0669 | 6593.4534 |  | 10.2863 | 53664.6267 |  | 33.4892 | 131404.9585 |  | 96.3743 | 255943.3186 |  | 236393 | 429393.2702 |  | 236393 | 626711.1729 |  | 236393 | 836348.4897 |  | 236393 | 1020504.0971 |  | 236393 | 1184773.5755 |  | 236393 | 1389240.1937
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 6725.3225 | C_100 - C this iteration | iteration | 54201.273 | C_100 - C this iteration | iteration | 132719.0081 | C_100 - C this iteration | iteration | 258502.7518 | C_100 - C this iteration | iteration | 433687.2029 | C_100 - C this iteration | iteration | 632978.2846 | C_100 - C this iteration | iteration | 844711.9746 | C_100 - C this iteration | iteration | 1030709.138 | C_100 - C this iteration | iteration | 1196621.3113 | C_100 - C this iteration | iteration | 1403132.5957 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1768 |  |  | 89.6496 |  |  | 86.9746 |  |  | 78.0057 |  |  | 55.9046 |  |  | 17.1601 |  |  | -39.8651 |  |  | -103.4419 |  |  | -170.7948 |  |  | -268.6468
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1768 |  |  | 29.6496 |  |  | 26.9746 |  |  | 18.0057 |  |  | -4.0954 |  |  | -42.8399 |  |  | -99.8651 |  |  | -163.4419 |  |  | -230.7948 |  |  | -328.6468
[13 empty] | Press drop ratio this iteration |  |  | 0.33464 |  |  | 0.33073 |  |  | 0.31014 |  |  | 0.23083 |  |  | -0.073257 |  |  | -2.4965 |  |  | 2.5051 |  |  | 1.58 |  |  | 1.3513 |  |  | 1.2233
[13 empty] | Expansion factor | 12 |  | 0.82572 |  |  | 0.82779 |  |  | 0.83697 |  |  | 0.87696 |  |  | 1.0403 |  |  | 2.4544 |  |  | -0.57009 |  |  | -0.10725 |  |  | 0.23725 |  |  | -0.082536
[13 empty] | C Non choked w/ reducers | 7 |  | 2.7163 |  |  | 22.1093 |  |  | 57.1237 |  |  | 138.0568 |  |  | #NUM! |  |  | #NUM! |  |  | 442.1163 |  |  | 1476.4401 |  |  | -577.5656 |  |  | 1742.2684
[13 empty] | C Choked w/ reducers | 7 |  | 2.4315 |  |  | 19.7222 |  |  | 50.1293 |  |  | 110.2807 |  |  | 265.3806 |  |  | 1328.398 |  |  | -820.1187 |  |  | -432.6694 |  |  | -310.771 |  |  | -388.5221
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.7163 |  |  | 22.1093 |  |  | 57.1237 |  |  | 138.0568 |  |  | #NUM! |  |  | #NUM! |  |  | -820.1187 |  |  | -432.6694 |  |  | -310.771 |  |  | -388.5221
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.0137 | 6725.3225 |  | 10.5093 | 54201.273 |  | 34.1237 | 132719.0081 |  | 98.6568 | 258502.7518 |  | 236393 | 433687.2029 |  | 236393 | 632978.2846 |  | 236393 | 844711.9746 |  | 236393 | 1030709.138 |  | 236393 | 1196621.3113 |  | 236393 | 1403132.5957
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 6859.8289 | C_100 - C this iteration | iteration | 54743.2857 | C_100 - C this iteration | iteration | 134046.1982 | C_100 - C this iteration | iteration | 261087.7793 | C_100 - C this iteration | iteration | 438024.0749 | C_100 - C this iteration | iteration | 639308.0675 | C_100 - C this iteration | iteration | 853159.0943 | C_100 - C this iteration | iteration | 1041016.2294 | C_100 - C this iteration | iteration | 1208587.5244 | C_100 - C this iteration | iteration | 1417163.9216 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1765 |  |  | 89.6388 |  |  | 86.9101 |  |  | 77.7609 |  |  | 55.2155 |  |  | 15.6923 |  |  | -42.4791 |  |  | -107.3338 |  |  | -176.0405 |  |  | -275.8593
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1765 |  |  | 29.6388 |  |  | 26.9101 |  |  | 17.7609 |  |  | -4.7845 |  |  | -44.3077 |  |  | -102.4791 |  |  | -167.3338 |  |  | -236.0405 |  |  | -335.8593
[13 empty] | Press drop ratio this iteration |  |  | 0.33464 |  |  | 0.33065 |  |  | 0.30963 |  |  | 0.2284 |  |  | -0.086651 |  |  | -2.8235 |  |  | 2.4125 |  |  | 1.559 |  |  | 1.3408 |  |  | 1.2175
[13 empty] | Expansion factor | 12 |  | 0.82572 |  |  | 0.82784 |  |  | 0.83724 |  |  | 0.87825 |  |  | 1.0476 |  |  | 2.6449 |  |  | -0.51204 |  |  | -0.092508 |  |  | 0.24316 |  |  | -0.077369
[13 empty] | C Non choked w/ reducers | 7 |  | 2.7707 |  |  | 22.3346 |  |  | 57.767 |  |  | 140.4092 |  |  | #NUM! |  |  | #NUM! |  |  | 475.4385 |  |  | 1677.303 |  |  | -554.3576 |  |  | 1832.5148
[13 empty] | C Choked w/ reducers | 7 |  | 2.4802 |  |  | 19.9218 |  |  | 50.6682 |  |  | 111.7342 |  |  | 271.3792 |  |  | 1467.178 |  |  | -777.3482 |  |  | -421.1507 |  |  | -304.5257 |  |  | -382.1476
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.7707 |  |  | 22.3346 |  |  | 57.767 |  |  | 140.4092 |  |  | #NUM! |  |  | #NUM! |  |  | -777.3482 |  |  | -421.1507 |  |  | -304.5257 |  |  | -382.1476
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9593 | 6859.8289 |  | 10.7346 | 54743.2857 |  | 34.767 | 134046.1982 |  | 101.0092 | 261087.7793 |  | 236393 | 438024.0749 |  | 236393 | 639308.0675 |  | 236393 | 853159.0943 |  | 236393 | 1041016.2294 |  | 236393 | 1208587.5244 |  | 236393 | 1417163.9216
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 6997.0255 | C_100 - C this iteration | iteration | 55290.7186 | C_100 - C this iteration | iteration | 135386.6601 | C_100 - C this iteration | iteration | 263698.6571 | C_100 - C this iteration | iteration | 442404.3157 | C_100 - C this iteration | iteration | 645701.1481 | C_100 - C this iteration | iteration | 861690.6853 | C_100 - C this iteration | iteration | 1051426.3917 | C_100 - C this iteration | iteration | 1220673.3996 | C_100 - C this iteration | iteration | 1431335.5608 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1761 |  |  | 89.6279 |  |  | 86.8443 |  |  | 77.5112 |  |  | 54.5126 |  |  | 14.195 |  |  | -45.1457 |  |  | -111.3039 |  |  | -181.3917 |  |  | -283.2168
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1761 |  |  | 29.6279 |  |  | 26.8443 |  |  | 17.5112 |  |  | -5.4874 |  |  | -45.805 |  |  | -105.1457 |  |  | -171.3039 |  |  | -241.3917 |  |  | -343.2168
[13 empty] | Press drop ratio this iteration |  |  | 0.33464 |  |  | 0.33057 |  |  | 0.30911 |  |  | 0.22592 |  |  | -0.10066 |  |  | -3.2268 |  |  | 2.329 |  |  | 1.5391 |  |  | 1.3308 |  |  | 1.2119
[13 empty] | Expansion factor | 12 |  | 0.82572 |  |  | 0.82788 |  |  | 0.83752 |  |  | 0.87957 |  |  | 1.0553 |  |  | 2.8799 |  |  | -0.45975 |  |  | -0.078535 |  |  | 0.24884 |  |  | -0.072369
[13 empty] | C Non choked w/ reducers | 7 |  | 2.8261 |  |  | 22.5624 |  |  | 58.4191 |  |  | 142.8353 |  |  | #NUM! |  |  | #NUM! |  |  | 512.152 |  |  | 1936.7322 |  |  | -532.9928 |  |  | 1931.7991
[13 empty] | C Choked w/ reducers | 7 |  | 2.5298 |  |  | 20.1235 |  |  | 51.2137 |  |  | 113.2151 |  |  | 277.6272 |  |  | 1638.1568 |  |  | -738.7481 |  |  | -410.1899 |  |  | -298.4975 |  |  | -375.9423
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.8261 |  |  | 22.5624 |  |  | 58.4191 |  |  | 142.8353 |  |  | #NUM! |  |  | #NUM! |  |  | -738.7481 |  |  | -410.1899 |  |  | -298.4975 |  |  | -375.9423
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9039 | 6997.0255 |  | 10.9624 | 55290.7186 |  | 35.4191 | 135386.6601 |  | 103.4353 | 263698.6571 |  | 236393 | 442404.3157 |  | 236393 | 645701.1481 |  | 236393 | 861690.6853 |  | 236393 | 1051426.3917 |  | 236393 | 1220673.3996 |  | 236393 | 1431335.5608
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 7136.966 | C_100 - C this iteration | iteration | 55843.6258 | C_100 - C this iteration | iteration | 136740.5267 | C_100 - C this iteration | iteration | 266335.6437 | C_100 - C this iteration | iteration | 446828.3588 | C_100 - C this iteration | iteration | 652158.1596 | C_100 - C this iteration | iteration | 870307.5921 | C_100 - C this iteration | iteration | 1061940.6556 | C_100 - C this iteration | iteration | 1232880.1336 | C_100 - C this iteration | iteration | 1445648.9164 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1758 |  |  | 89.6167 |  |  | 86.7771 |  |  | 77.2564 |  |  | 53.7956 |  |  | 12.6676 |  |  | -47.8658 |  |  | -115.3539 |  |  | -186.8503 |  |  | -290.7222
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1758 |  |  | 29.6167 |  |  | 26.7771 |  |  | 17.2564 |  |  | -6.2044 |  |  | -47.3324 |  |  | -107.8658 |  |  | -175.3539 |  |  | -246.8503 |  |  | -350.7222
[13 empty] | Press drop ratio this iteration |  |  | 0.33463 |  |  | 0.33048 |  |  | 0.30857 |  |  | 0.22337 |  |  | -0.11533 |  |  | -3.7365 |  |  | 2.2535 |  |  | 1.5201 |  |  | 1.3211 |  |  | 1.2064
[13 empty] | Expansion factor | 12 |  | 0.82572 |  |  | 0.82792 |  |  | 0.8378 |  |  | 0.88093 |  |  | 1.0634 |  |  | 3.1768 |  |  | -0.41241 |  |  | -0.065272 |  |  | 0.25429 |  |  | -0.067529
[13 empty] | C Non choked w/ reducers | 7 |  | 2.8827 |  |  | 22.7925 |  |  | 59.0802 |  |  | 145.3392 |  |  | #NUM! |  |  | #NUM! |  |  | 552.916 |  |  | 2285.0238 |  |  | -513.2534 |  |  | 2041.5827
[13 empty] | C Choked w/ reducers | 7 |  | 2.5804 |  |  | 20.3273 |  |  | 51.7659 |  |  | 114.7243 |  |  | 284.1408 |  |  | 1854.0348 |  |  | -703.7337 |  |  | -399.7465 |  |  | -292.6749 |  |  | -369.8992
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.8827 |  |  | 22.7925 |  |  | 59.0802 |  |  | 145.3392 |  |  | #NUM! |  |  | #NUM! |  |  | -703.7337 |  |  | -399.7465 |  |  | -292.6749 |  |  | -369.8992
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8473 | 7136.966 |  | 11.1925 | 55843.6258 |  | 36.0802 | 136740.5267 |  | 105.9392 | 266335.6437 |  | 236393 | 446828.3588 |  | 236393 | 652158.1596 |  | 236393 | 870307.5921 |  | 236393 | 1061940.6556 |  | 236393 | 1232880.1336 |  | 236393 | 1445648.9164
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 7279.7054 | C_100 - C this iteration | iteration | 56402.062 | C_100 - C this iteration | iteration | 138107.932 | C_100 - C this iteration | iteration | 268999.0001 | C_100 - C this iteration | iteration | 451296.6424 | C_100 - C this iteration | iteration | 658679.7412 | C_100 - C this iteration | iteration | 879010.6681 | C_100 - C this iteration | iteration | 1072560.0622 | C_100 - C this iteration | iteration | 1245208.935 | C_100 - C this iteration | iteration | 1460105.4056 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1754 |  |  | 89.6052 |  |  | 86.7086 |  |  | 76.9966 |  |  | 53.0642 |  |  | 11.1095 |  |  | -50.6406 |  |  | -119.4852 |  |  | -192.4188 |  |  | -298.3784
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1754 |  |  | 29.6052 |  |  | 26.7086 |  |  | 16.9966 |  |  | -6.9358 |  |  | -48.8905 |  |  | -110.6406 |  |  | -179.4852 |  |  | -252.4188 |  |  | -358.3784
[13 empty] | Press drop ratio this iteration |  |  | 0.33463 |  |  | 0.3304 |  |  | 0.30803 |  |  | 0.22074 |  |  | -0.13071 |  |  | -4.4008 |  |  | 2.1848 |  |  | 1.5022 |  |  | 1.3118 |  |  | 1.2011
[13 empty] | Expansion factor | 12 |  | 0.82572 |  |  | 0.82797 |  |  | 0.83809 |  |  | 0.88233 |  |  | 1.0718 |  |  | 3.5638 |  |  | -0.36936 |  |  | -0.052669 |  |  | 0.25954 |  |  | -0.062843
[13 empty] | C Non choked w/ reducers | 7 |  | 2.9403 |  |  | 23.0251 |  |  | 59.7506 |  |  | 147.9252 |  |  | #NUM! |  |  | #NUM! |  |  | 598.5579 |  |  | 2777.7012 |  |  | -494.9547 |  |  | 2163.6585
[13 empty] | C Choked w/ reducers | 7 |  | 2.632 |  |  | 20.5332 |  |  | 52.3248 |  |  | 116.2626 |  |  | 290.9379 |  |  | 2135.2026 |  |  | -671.8248 |  |  | -389.7841 |  |  | -287.0472 |  |  | -364.0118
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.9403 |  |  | 23.0251 |  |  | 59.7506 |  |  | 147.9252 |  |  | #NUM! |  |  | #NUM! |  |  | -671.8248 |  |  | -389.7841 |  |  | -287.0472 |  |  | -364.0118
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7897 | 7279.7054 |  | 11.4251 | 56402.062 |  | 36.7506 | 138107.932 |  | 108.5252 | 268999.0001 |  | 236393 | 451296.6424 |  | 236393 | 658679.7412 |  | 236393 | 879010.6681 |  | 236393 | 1072560.0622 |  | 236393 | 1245208.935 |  | 236393 | 1460105.4056
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 7425.2995 | C_100 - C this iteration | iteration | 56966.0827 | C_100 - C this iteration | iteration | 139489.0113 | C_100 - C this iteration | iteration | 271688.9901 | C_100 - C this iteration | iteration | 455809.6089 | C_100 - C this iteration | iteration | 665266.5386 | C_100 - C this iteration | iteration | 887800.7747 | C_100 - C this iteration | iteration | 1083285.6628 | C_100 - C this iteration | iteration | 1257661.0243 | C_100 - C this iteration | iteration | 1474706.4597 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.175 |  |  | 89.5936 |  |  | 86.6388 |  |  | 76.7315 |  |  | 52.3181 |  |  | 9.5201 |  |  | -53.4712 |  |  | -123.6996 |  |  | -198.0991 |  |  | -306.1885
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.175 |  |  | 29.5936 |  |  | 26.6388 |  |  | 16.7315 |  |  | -7.6819 |  |  | -50.4799 |  |  | -113.4712 |  |  | -183.6996 |  |  | -258.0991 |  |  | -366.1885
[13 empty] | Press drop ratio this iteration |  |  | 0.33463 |  |  | 0.33031 |  |  | 0.30747 |  |  | 0.21805 |  |  | -0.14683 |  |  | -5.3025 |  |  | 2.1221 |  |  | 1.485 |  |  | 1.3029 |  |  | 1.196
[13 empty] | Expansion factor | 12 |  | 0.82572 |  |  | 0.82801 |  |  | 0.83838 |  |  | 0.88377 |  |  | 1.0807 |  |  | 4.089 |  |  | -0.33005 |  |  | -0.04068 |  |  | 0.26459 |  |  | -0.058304
[13 empty] | C Non choked w/ reducers | 7 |  | 2.9992 |  |  | 23.2602 |  |  | 60.4304 |  |  | 150.5983 |  |  | #NUM! |  |  | #NUM! |  |  | 650.133 |  |  | 3528.6805 |  |  | -477.9394 |  |  | 2300.252
[13 empty] | C Choked w/ reducers | 7 |  | 2.6847 |  |  | 20.7412 |  |  | 52.8907 |  |  | 117.8309 |  |  | 298.038 |  |  | 2516.6005 |  |  | -642.6231 |  |  | -380.2694 |  |  | -281.6045 |  |  | -358.274
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.9992 |  |  | 23.2602 |  |  | 60.4304 |  |  | 150.5983 |  |  | #NUM! |  |  | #NUM! |  |  | -642.6231 |  |  | -380.2694 |  |  | -281.6045 |  |  | -358.274
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7308 | 7425.2995 |  | 11.6602 | 56966.0827 |  | 37.4304 | 139489.0113 |  | 111.1983 | 271688.9901 |  | 236393 | 455809.6089 |  | 236393 | 665266.5386 |  | 236393 | 887800.7747 |  | 236393 | 1083285.6628 |  | 236393 | 1257661.0243 |  | 236393 | 1474706.4597
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 7573.8055 | C_100 - C this iteration | iteration | 57535.7435 | C_100 - C this iteration | iteration | 140883.9014 | C_100 - C this iteration | iteration | 274405.8801 | C_100 - C this iteration | iteration | 460367.7049 | C_100 - C this iteration | iteration | 671919.204 | C_100 - C this iteration | iteration | 896678.7825 | C_100 - C this iteration | iteration | 1094118.5194 | C_100 - C this iteration | iteration | 1270237.6345 | C_100 - C this iteration | iteration | 1489453.5242 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1746 |  |  | 89.5817 |  |  | 86.5675 |  |  | 76.4611 |  |  | 51.557 |  |  | 7.8987 |  |  | -56.3587 |  |  | -127.9986 |  |  | -203.8936 |  |  | -314.1557
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1746 |  |  | 29.5817 |  |  | 26.5675 |  |  | 16.4611 |  |  | -8.443 |  |  | -52.1013 |  |  | -116.3587 |  |  | -187.9986 |  |  | -263.8936 |  |  | -374.1557
[13 empty] | Press drop ratio this iteration |  |  | 0.33462 |  |  | 0.33022 |  |  | 0.3069 |  |  | 0.21529 |  |  | -0.16376 |  |  | -6.5962 |  |  | 2.0646 |  |  | 1.4688 |  |  | 1.2943 |  |  | 1.191
[13 empty] | Expansion factor | 12 |  | 0.82572 |  |  | 0.82806 |  |  | 0.83868 |  |  | 0.88524 |  |  | 1.09 |  |  | 4.8427 |  |  | -0.29402 |  |  | -0.029264 |  |  | 0.26944 |  |  | -0.053907
[13 empty] | C Non choked w/ reducers | 7 |  | 3.0592 |  |  | 23.4978 |  |  | 61.1199 |  |  | 153.3637 |  |  | #NUM! |  |  | #NUM! |  |  | 709.0101 |  |  | 4814.418 |  |  | -462.0721 |  |  | 2454.1591
[13 empty] | C Choked w/ reducers | 7 |  | 2.7384 |  |  | 20.9514 |  |  | 53.4636 |  |  | 119.4301 |  |  | 305.4623 |  |  | 3063.5134 |  |  | -615.7959 |  |  | -371.1723 |  |  | -276.3375 |  |  | -352.68
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.0592 |  |  | 23.4978 |  |  | 61.1199 |  |  | 153.3637 |  |  | #NUM! |  |  | #NUM! |  |  | -615.7959 |  |  | -371.1723 |  |  | -276.3375 |  |  | -352.68
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6708 | 7573.8055 |  | 11.8978 | 57535.7435 |  | 38.1199 | 140883.9014 |  | 113.9637 | 274405.8801 |  | 236393 | 460367.7049 |  | 236393 | 671919.204 |  | 236393 | 896678.7825 |  | 236393 | 1094118.5194 |  | 236393 | 1270237.6345 |  | 236393 | 1489453.5242
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 7725.2816 | C_100 - C this iteration | iteration | 58111.1009 | C_100 - C this iteration | iteration | 142292.7405 | C_100 - C this iteration | iteration | 277149.9389 | C_100 - C this iteration | iteration | 464971.382 | C_100 - C this iteration | iteration | 678638.396 | C_100 - C this iteration | iteration | 905645.5703 | C_100 - C this iteration | iteration | 1105059.7046 | C_100 - C this iteration | iteration | 1282940.0109 | C_100 - C this iteration | iteration | 1504348.0595 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1742 |  |  | 89.5696 |  |  | 86.4948 |  |  | 76.1852 |  |  | 50.7805 |  |  | 6.2448 |  |  | -59.3042 |  |  | -132.3841 |  |  | -209.8046 |  |  | -322.2829
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1742 |  |  | 29.5696 |  |  | 26.4948 |  |  | 16.1852 |  |  | -9.2195 |  |  | -53.7552 |  |  | -119.3042 |  |  | -192.3841 |  |  | -269.8046 |  |  | -382.2829
[13 empty] | Press drop ratio this iteration |  |  | 0.33462 |  |  | 0.33013 |  |  | 0.30632 |  |  | 0.21245 |  |  | -0.18156 |  |  | -8.608 |  |  | 2.0117 |  |  | 1.4532 |  |  | 1.286 |  |  | 1.1862
[13 empty] | Expansion factor | 12 |  | 0.82573 |  |  | 0.82811 |  |  | 0.83899 |  |  | 0.88675 |  |  | 1.0998 |  |  | 6.0148 |  |  | -0.26088 |  |  | -0.018382 |  |  | 0.27412 |  |  | -0.049645
[13 empty] | C Non choked w/ reducers | 7 |  | 3.1204 |  |  | 23.7379 |  |  | 61.8191 |  |  | 156.227 |  |  | #NUM! |  |  | #NUM! |  |  | 777.0003 |  |  | 7524.572 |  |  | -447.2364 |  |  | 2628.9419
[13 empty] | C Choked w/ reducers | 7 |  | 2.7931 |  |  | 21.1638 |  |  | 54.0436 |  |  | 121.0612 |  |  | 313.234 |  |  | 3913.6482 |  |  | -591.0626 |  |  | -362.4652 |  |  | -271.2376 |  |  | -347.224
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.1204 |  |  | 23.7379 |  |  | 61.8191 |  |  | 156.227 |  |  | #NUM! |  |  | #NUM! |  |  | -591.0626 |  |  | -362.4652 |  |  | -271.2376 |  |  | -347.224
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6096 | 7725.2816 |  | 12.1379 | 58111.1009 |  | 38.8191 | 142292.7405 |  | 116.827 | 277149.9389 |  | 236393 | 464971.382 |  | 236393 | 678638.396 |  | 236393 | 905645.5703 |  | 236393 | 1105059.7046 |  | 236393 | 1282940.0109 |  | 236393 | 1504348.0595
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 7879.7872 | C_100 - C this iteration | iteration | 58692.2119 | C_100 - C this iteration | iteration | 143715.6679 | C_100 - C this iteration | iteration | 279921.4382 | C_100 - C this iteration | iteration | 469621.0958 | C_100 - C this iteration | iteration | 685424.78 | C_100 - C this iteration | iteration | 914702.026 | C_100 - C this iteration | iteration | 1116110.3017 | C_100 - C this iteration | iteration | 1295769.411 | C_100 - C this iteration | iteration | 1519391.5401 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1737 |  |  | 89.5572 |  |  | 86.4206 |  |  | 75.9038 |  |  | 49.9885 |  |  | 4.5576 |  |  | -62.309 |  |  | -136.8578 |  |  | -215.8344 |  |  | -330.5735
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1737 |  |  | 29.5572 |  |  | 26.4206 |  |  | 15.9038 |  |  | -10.0115 |  |  | -55.4424 |  |  | -122.309 |  |  | -196.8578 |  |  | -275.8344 |  |  | -390.5735
[13 empty] | Press drop ratio this iteration |  |  | 0.33462 |  |  | 0.33004 |  |  | 0.30572 |  |  | 0.20953 |  |  | -0.20028 |  |  | -12.1649 |  |  | 1.9629 |  |  | 1.4384 |  |  | 1.278 |  |  | 1.1815
[13 empty] | Expansion factor | 12 |  | 0.82573 |  |  | 0.82815 |  |  | 0.8393 |  |  | 0.88831 |  |  | 1.1101 |  |  | 8.0869 |  |  | -0.2303 |  |  | -0.008 |  |  | 0.27863 |  |  | -0.045513
[13 empty] | C Non choked w/ reducers | 7 |  | 3.1828 |  |  | 23.9805 |  |  | 62.5284 |  |  | 159.1945 |  |  | #NUM! |  |  | #NUM! |  |  | 856.5527 |  |  | 16978.5138 |  |  | -433.3308 |  |  | 2829.2106
[13 empty] | C Choked w/ reducers | 7 |  | 2.849 |  |  | 21.3784 |  |  | 54.6309 |  |  | 122.7251 |  |  | 321.379 |  |  | 5416.096 |  |  | -568.1853 |  |  | -354.1231 |  |  | -266.2966 |  |  | -341.901
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.1828 |  |  | 23.9805 |  |  | 62.5284 |  |  | 159.1945 |  |  | #NUM! |  |  | #NUM! |  |  | -568.1853 |  |  | -354.1231 |  |  | -266.2966 |  |  | -341.901
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5472 | 7879.7872 |  | 12.3805 | 58692.2119 |  | 39.5284 | 143715.6679 |  | 119.7945 | 279921.4382 |  | 236393 | 469621.0958 |  | 236393 | 685424.78 |  | 236393 | 914702.026 |  | 236393 | 1116110.3017 |  | 236393 | 1295769.411 |  | 236393 | 1519391.5401
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 8037.3829 | C_100 - C this iteration | iteration | 59279.134 | C_100 - C this iteration | iteration | 145152.8245 | C_100 - C this iteration | iteration | 282720.6526 | C_100 - C this iteration | iteration | 474317.3068 | C_100 - C this iteration | iteration | 692279.0278 | C_100 - C this iteration | iteration | 923849.0463 | C_100 - C this iteration | iteration | 1127271.4047 | C_100 - C this iteration | iteration | 1308727.1051 | C_100 - C this iteration | iteration | 1534585.4555 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1733 |  |  | 89.5446 |  |  | 86.3449 |  |  | 75.6167 |  |  | 49.1805 |  |  | 2.8365 |  |  | -65.3741 |  |  | -141.4213 |  |  | -221.9854 |  |  | -339.0308
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1733 |  |  | 29.5446 |  |  | 26.3449 |  |  | 15.6167 |  |  | -10.8195 |  |  | -57.1635 |  |  | -125.3741 |  |  | -201.4213 |  |  | -281.9854 |  |  | -399.0308
[13 empty] | Press drop ratio this iteration |  |  | 0.33461 |  |  | 0.32994 |  |  | 0.30511 |  |  | 0.20653 |  |  | -0.21999 |  |  | -20.1532 |  |  | 1.9178 |  |  | 1.4243 |  |  | 1.2703 |  |  | 1.177
[13 empty] | Expansion factor | 12 |  | 0.82573 |  |  | 0.8282 |  |  | 0.83962 |  |  | 0.88991 |  |  | 1.1209 |  |  | 12.7406 |  |  | -0.202 |  |  | 0.001914 |  |  | 0.28298 |  |  | -0.041506
[13 empty] | C Non choked w/ reducers | 7 |  | 3.2465 |  |  | 24.2258 |  |  | 63.2479 |  |  | 162.2729 |  |  | #NUM! |  |  | #NUM! |  |  | 951.0645 |  |  | -69706.2353 |  |  | -420.2672 |  |  | 3061.0395
[13 empty] | C Choked w/ reducers | 7 |  | 2.906 |  |  | 21.5952 |  |  | 55.2256 |  |  | 124.4229 |  |  | 329.9253 |  |  | 8789.5176 |  |  | -546.9608 |  |  | -346.1227 |  |  | -261.5069 |  |  | -336.7059
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.2465 |  |  | 24.2258 |  |  | 63.2479 |  |  | 162.2729 |  |  | #NUM! |  |  | #NUM! |  |  | -546.9608 |  |  | -346.1227 |  |  | -261.5069 |  |  | -336.7059
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.4835 | 8037.3829 |  | 12.6258 | 59279.134 |  | 40.2479 | 145152.8245 |  | 122.8729 | 282720.6526 |  | 236393 | 474317.3068 |  | 236393 | 692279.0278 |  | 236393 | 923849.0463 |  | 236393 | 1127271.4047 |  | 236393 | 1308727.1051 |  | 236393 | 1534585.4555
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 8198.1306 | C_100 - C this iteration | iteration | 59871.9254 | C_100 - C this iteration | iteration | 146604.3528 | C_100 - C this iteration | iteration | 285547.8591 | C_100 - C this iteration | iteration | 479060.4798 | C_100 - C this iteration | iteration | 699201.8181 | C_100 - C this iteration | iteration | 933087.5367 | C_100 - C this iteration | iteration | 1138544.1187 | C_100 - C this iteration | iteration | 1321814.3762 | C_100 - C this iteration | iteration | 1549931.31 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1728 |  |  | 89.5317 |  |  | 86.2677 |  |  | 75.3239 |  |  | 48.3564 |  |  | 1.0807 |  |  | -68.5009 |  |  | -146.0766 |  |  | -228.26 |  |  | -347.658
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1728 |  |  | 29.5317 |  |  | 26.2677 |  |  | 15.3239 |  |  | -11.6436 |  |  | -58.9193 |  |  | -128.5009 |  |  | -206.0766 |  |  | -288.26 |  |  | -407.658
[13 empty] | Press drop ratio this iteration |  |  | 0.33461 |  |  | 0.32985 |  |  | 0.30449 |  |  | 0.20344 |  |  | -0.24079 |  |  | -54.5172 |  |  | 1.8759 |  |  | 1.4107 |  |  | 1.2629 |  |  | 1.1726
[13 empty] | Expansion factor | 12 |  | 0.82573 |  |  | 0.82825 |  |  | 0.83995 |  |  | 0.89155 |  |  | 1.1323 |  |  | 32.76 |  |  | -0.17575 |  |  | 0.011389 |  |  | 0.28718 |  |  | -0.03762
[13 empty] | C Non choked w/ reducers | 7 |  | 3.3114 |  |  | 24.4736 |  |  | 63.9779 |  |  | 165.4697 |  |  | #NUM! |  |  | #NUM! |  |  | 1065.3919 |  |  | -11509.3998 |  |  | -407.968 |  |  | 3332.5981
[13 empty] | C Choked w/ reducers | 7 |  | 2.9641 |  |  | 21.8143 |  |  | 55.8277 |  |  | 126.1556 |  |  | 338.904 |  |  | 23299.0521 |  |  | -527.2146 |  |  | -338.4431 |  |  | -256.8616 |  |  | -331.6339
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.3114 |  |  | 24.4736 |  |  | 63.9779 |  |  | 165.4697 |  |  | #NUM! |  |  | #NUM! |  |  | -527.2146 |  |  | -338.4431 |  |  | -256.8616 |  |  | -331.6339
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.4186 | 8198.1306 |  | 12.8736 | 59871.9254 |  | 40.9779 | 146604.3528 |  | 126.0697 | 285547.8591 |  | 236393 | 479060.4798 |  | 236393 | 699201.8181 |  | 236393 | 933087.5367 |  | 236393 | 1138544.1187 |  | 236393 | 1321814.3762 |  | 236393 | 1549931.31
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 8362.0932 | C_100 - C this iteration | iteration | 60470.6446 | C_100 - C this iteration | iteration | 148070.3963 | C_100 - C this iteration | iteration | 288403.3377 | C_100 - C this iteration | iteration | 483851.0846 | C_100 - C this iteration | iteration | 706193.8363 | C_100 - C this iteration | iteration | 942418.4121 | C_100 - C this iteration | iteration | 1149929.5599 | C_100 - C this iteration | iteration | 1335032.5199 | C_100 - C this iteration | iteration | 1565430.6231 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1723 |  |  | 89.5186 |  |  | 86.189 |  |  | 75.0252 |  |  | 47.5156 |  |  | -0.71025 |  |  | -71.6904 |  |  | -150.8255 |  |  | -234.6607 |  |  | -356.4586
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1723 |  |  | 29.5186 |  |  | 26.189 |  |  | 15.0252 |  |  | -12.4844 |  |  | -60.7103 |  |  | -131.6904 |  |  | -210.8255 |  |  | -294.6607 |  |  | -416.4586
[13 empty] | Press drop ratio this iteration |  |  | 0.33461 |  |  | 0.32975 |  |  | 0.30386 |  |  | 0.20027 |  |  | -0.26274 |  |  | 85.4773 |  |  | 1.8369 |  |  | 1.3978 |  |  | 1.2557 |  |  | 1.1683
[13 empty] | Expansion factor | 12 |  | 0.82573 |  |  | 0.8283 |  |  | 0.84028 |  |  | 0.89325 |  |  | 1.1444 |  |  | -48.7963 |  |  | -0.15132 |  |  | 0.020452 |  |  | 0.29122 |  |  | -0.03385
[13 empty] | C Non choked w/ reducers | 7 |  | 3.3777 |  |  | 24.7242 |  |  | 64.7185 |  |  | 168.7931 |  |  | #NUM! |  |  | 40.0453 |  |  | 1206.7289 |  |  | -6298.452 |  |  | -396.3652 |  |  | 3655.1407
[13 empty] | C Choked w/ reducers | 7 |  | 3.0234 |  |  | 22.0357 |  |  | 56.4375 |  |  | 127.9245 |  |  | 348.3497 |  |  | -35807.3403 |  |  | -508.7958 |  |  | -331.0649 |  |  | -252.3538 |  |  | -326.6806
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.3777 |  |  | 24.7242 |  |  | 64.7185 |  |  | 168.7931 |  |  | #NUM! |  |  | -35807.3403 |  |  | -508.7958 |  |  | -331.0649 |  |  | -252.3538 |  |  | -326.6806
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.3523 | 8362.0932 |  | 13.1242 | 60470.6446 |  | 41.7185 | 148070.3963 |  | 129.3931 | 288403.3377 |  | 236393 | 483851.0846 |  | 236393 | 706193.8363 |  | 236393 | 942418.4121 |  | 236393 | 1149929.5599 |  | 236393 | 1335032.5199 |  | 236393 | 1565430.6231
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 8529.3351 | C_100 - C this iteration | iteration | 61075.3511 | C_100 - C this iteration | iteration | 149551.1003 | C_100 - C this iteration | iteration | 291287.3711 | C_100 - C this iteration | iteration | 488689.5955 | C_100 - C this iteration | iteration | 713255.7746 | C_100 - C this iteration | iteration | 951842.5962 | C_100 - C this iteration | iteration | 1161428.8555 | C_100 - C this iteration | iteration | 1348382.8451 | C_100 - C this iteration | iteration | 1581084.9294 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1718 |  |  | 89.5052 |  |  | 86.1087 |  |  | 74.7205 |  |  | 46.6579 |  |  | -2.5372 |  |  | -74.9441 |  |  | -155.6698 |  |  | -241.1901 |  |  | -365.4362
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1718 |  |  | 29.5052 |  |  | 26.1087 |  |  | 14.7205 |  |  | -13.3421 |  |  | -62.5372 |  |  | -134.9441 |  |  | -215.6698 |  |  | -301.1901 |  |  | -425.4362
[13 empty] | Press drop ratio this iteration |  |  | 0.3346 |  |  | 0.32965 |  |  | 0.30321 |  |  | 0.19701 |  |  | -0.28595 |  |  | 24.6477 |  |  | 1.8006 |  |  | 1.3854 |  |  | 1.2488 |  |  | 1.1642
[13 empty] | Expansion factor | 12 |  | 0.82574 |  |  | 0.82836 |  |  | 0.84062 |  |  | 0.89498 |  |  | 1.1572 |  |  | -13.359 |  |  | -0.12855 |  |  | 0.029127 |  |  | 0.29513 |  |  | -0.030191
[13 empty] | C Non choked w/ reducers | 7 |  | 3.4453 |  |  | 24.9774 |  |  | 65.4701 |  |  | 172.252 |  |  | #NUM! |  |  | 77.0147 |  |  | 1386.2095 |  |  | -4347.0278 |  |  | -385.3987 |  |  | 4044.6129
[13 empty] | C Choked w/ reducers | 7 |  | 3.0839 |  |  | 22.2593 |  |  | 57.0551 |  |  | 129.7306 |  |  | 358.3005 |  |  | -10123.7696 |  |  | -491.5735 |  |  | -323.97 |  |  | -247.9774 |  |  | -321.8417
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.4453 |  |  | 24.9774 |  |  | 65.4701 |  |  | 172.252 |  |  | #NUM! |  |  | -10123.7696 |  |  | -491.5735 |  |  | -323.97 |  |  | -247.9774 |  |  | -321.8417
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.2847 | 8529.3351 |  | 13.3774 | 61075.3511 |  | 42.4701 | 149551.1003 |  | 132.852 | 291287.3711 |  | 236393 | 488689.5955 |  | 236393 | 713255.7746 |  | 236393 | 951842.5962 |  | 236393 | 1161428.8555 |  | 236393 | 1348382.8451 |  | 236393 | 1581084.9294
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 8699.9218 | C_100 - C this iteration | iteration | 61686.1046 | C_100 - C this iteration | iteration | 151046.6113 | C_100 - C this iteration | iteration | 294200.2448 | C_100 - C this iteration | iteration | 493576.4914 | C_100 - C this iteration | iteration | 720388.3324 | C_100 - C this iteration | iteration | 961361.0222 | C_100 - C this iteration | iteration | 1173043.1441 | C_100 - C this iteration | iteration | 1361866.6736 | C_100 - C this iteration | iteration | 1596895.7787 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1712 |  |  | 89.4915 |  |  | 86.0267 |  |  | 74.4097 |  |  | 45.783 |  |  | -4.401 |  |  | -78.2632 |  |  | -160.6115 |  |  | -247.8508 |  |  | -374.5942
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1712 |  |  | 29.4915 |  |  | 26.0267 |  |  | 14.4097 |  |  | -14.217 |  |  | -64.401 |  |  | -138.2632 |  |  | -220.6115 |  |  | -307.8508 |  |  | -434.5942
[13 empty] | Press drop ratio this iteration |  |  | 0.3346 |  |  | 0.32955 |  |  | 0.30254 |  |  | 0.19365 |  |  | -0.31053 |  |  | 14.6334 |  |  | 1.7666 |  |  | 1.3736 |  |  | 1.2421 |  |  | 1.1602
[13 empty] | Expansion factor | 12 |  | 0.82574 |  |  | 0.82841 |  |  | 0.84097 |  |  | 0.89677 |  |  | 1.1707 |  |  | -7.5249 |  |  | -0.10727 |  |  | 0.037437 |  |  | 0.2989 |  |  | -0.026639
[13 empty] | C Non choked w/ reducers | 7 |  | 3.5142 |  |  | 25.2333 |  |  | 66.2329 |  |  | 175.8565 |  |  | #NUM! |  |  | 103.3225 |  |  | 1622.0365 |  |  | -3325.0515 |  |  | -375.0152 |  |  | 4524.382
[13 empty] | C Choked w/ reducers | 7 |  | 3.1456 |  |  | 22.4854 |  |  | 57.6805 |  |  | 131.5753 |  |  | 368.799 |  |  | -5894.9259 |  |  | -475.4334 |  |  | -317.1422 |  |  | -243.7265 |  |  | -317.1132
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.5142 |  |  | 25.2333 |  |  | 66.2329 |  |  | 175.8565 |  |  | #NUM! |  |  | -5894.9259 |  |  | -475.4334 |  |  | -317.1422 |  |  | -243.7265 |  |  | -317.1132
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.2158 | 8699.9218 |  | 13.6333 | 61686.1046 |  | 43.2329 | 151046.6113 |  | 136.4565 | 294200.2448 |  | 236393 | 493576.4914 |  | 236393 | 720388.3324 |  | 236393 | 961361.0222 |  | 236393 | 1173043.1441 |  | 236393 | 1361866.6736 |  | 236393 | 1596895.7787
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 8873.9202 | C_100 - C this iteration | iteration | 62302.9656 | C_100 - C this iteration | iteration | 152557.0774 | C_100 - C this iteration | iteration | 297142.2473 | C_100 - C this iteration | iteration | 498512.2564 | C_100 - C this iteration | iteration | 727592.2157 | C_100 - C this iteration | iteration | 970974.6324 | C_100 - C this iteration | iteration | 1184773.5755 | C_100 - C this iteration | iteration | 1375485.3403 | C_100 - C this iteration | iteration | 1612864.7365 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1707 |  |  | 89.4776 |  |  | 85.9432 |  |  | 74.0926 |  |  | 44.8906 |  |  | -6.3021 |  |  | -81.649 |  |  | -165.6525 |  |  | -254.6453 |  |  | -383.9362
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1707 |  |  | 29.4776 |  |  | 25.9432 |  |  | 14.0926 |  |  | -15.1094 |  |  | -66.3021 |  |  | -141.649 |  |  | -225.6525 |  |  | -314.6453 |  |  | -443.9362
[13 empty] | Press drop ratio this iteration |  |  | 0.3346 |  |  | 0.32944 |  |  | 0.30186 |  |  | 0.1902 |  |  | -0.33658 |  |  | 10.5206 |  |  | 1.7349 |  |  | 1.3622 |  |  | 1.2356 |  |  | 1.1563
[13 empty] | Expansion factor | 12 |  | 0.82574 |  |  | 0.82846 |  |  | 0.84133 |  |  | 0.89861 |  |  | 1.185 |  |  | -5.1289 |  |  | -0.087342 |  |  | 0.045404 |  |  | 0.30255 |  |  | -0.02319
[13 empty] | C Non choked w/ reducers | 7 |  | 3.5845 |  |  | 25.492 |  |  | 67.007 |  |  | 179.6176 |  |  | #NUM! |  |  | 126.0965 |  |  | 1946.1521 |  |  | -2695.9694 |  |  | -365.1671 |  |  | 5130.1225
[13 empty] | C Choked w/ reducers | 7 |  | 3.2086 |  |  | 22.7138 |  |  | 58.314 |  |  | 133.4598 |  |  | 379.8925 |  |  | -4157.7588 |  |  | -460.2754 |  |  | -310.566 |  |  | -239.5956 |  |  | -312.491
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.5845 |  |  | 25.492 |  |  | 67.007 |  |  | 179.6176 |  |  | #NUM! |  |  | -4157.7588 |  |  | -460.2754 |  |  | -310.566 |  |  | -239.5956 |  |  | -312.491
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.1455 | 8873.9202 |  | 13.892 | 62302.9656 |  | 44.007 | 152557.0774 |  | 140.2176 | 297142.2473 |  | 236393 | 498512.2564 |  | 236393 | 727592.2157 |  | 236393 | 970974.6324 |  | 236393 | 1184773.5755 |  | 236393 | 1375485.3403 |  | 236393 | 1612864.7365
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 9051.3986 | C_100 - C this iteration | iteration | 62925.9953 | C_100 - C this iteration | iteration | 154082.6482 | C_100 - C this iteration | iteration | 300113.6697 | C_100 - C this iteration | iteration | 503497.3789 | C_100 - C this iteration | iteration | 734868.1379 | C_100 - C this iteration | iteration | 980684.3787 | C_100 - C this iteration | iteration | 1196621.3113 | C_100 - C this iteration | iteration | 1389240.1937 | C_100 - C this iteration | iteration | 1628993.3838 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1701 |  |  | 89.4633 |  |  | 85.8579 |  |  | 73.7691 |  |  | 43.9801 |  |  | -8.2415 |  |  | -85.1029 |  |  | -170.7948 |  |  | -261.5764 |  |  | -393.4661
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1701 |  |  | 29.4633 |  |  | 25.8579 |  |  | 13.7691 |  |  | -16.0199 |  |  | -68.2415 |  |  | -145.1029 |  |  | -230.7948 |  |  | -321.5764 |  |  | -453.4661
[13 empty] | Press drop ratio this iteration |  |  | 0.33459 |  |  | 0.32933 |  |  | 0.30117 |  |  | 0.18665 |  |  | -0.36425 |  |  | 8.2802 |  |  | 1.705 |  |  | 1.3513 |  |  | 1.2294 |  |  | 1.1525
[13 empty] | Expansion factor | 12 |  | 0.82574 |  |  | 0.82852 |  |  | 0.84169 |  |  | 0.9005 |  |  | 1.2002 |  |  | -3.8238 |  |  | -0.06865 |  |  | 0.053046 |  |  | 0.30607 |  |  | -0.01984
[13 empty] | C Non choked w/ reducers | 7 |  | 3.6563 |  |  | 25.7534 |  |  | 67.7929 |  |  | 183.5476 |  |  | #NUM! |  |  | 147.2447 |  |  | 2420.2226 |  |  | -2269.5783 |  |  | -355.8121 |  |  | 5919.1477
[13 empty] | C Choked w/ reducers | 7 |  | 3.2728 |  |  | 22.9445 |  |  | 58.9556 |  |  | 135.3854 |  |  | 391.6341 |  |  | -3211.1513 |  |  | -446.0113 |  |  | -304.2276 |  |  | -235.5794 |  |  | -307.9717
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.6563 |  |  | 25.7534 |  |  | 67.7929 |  |  | 183.5476 |  |  | #NUM! |  |  | -3211.1513 |  |  | -446.0113 |  |  | -304.2276 |  |  | -235.5794 |  |  | -307.9717
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.0737 | 9051.3986 |  | 14.1534 | 62925.9953 |  | 44.7929 | 154082.6482 |  | 144.1476 | 300113.6697 |  | 236393 | 503497.3789 |  | 236393 | 734868.1379 |  | 236393 | 980684.3787 |  | 236393 | 1196621.3113 |  | 236393 | 1389240.1937 |  | 236393 | 1628993.3838
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 9232.4266 | C_100 - C this iteration | iteration | 63555.2553 | C_100 - C this iteration | iteration | 155623.4747 | C_100 - C this iteration | iteration | 303114.8064 | C_100 - C this iteration | iteration | 508532.3527 | C_100 - C this iteration | iteration | 742216.8192 | C_100 - C this iteration | iteration | 990491.2225 | C_100 - C this iteration | iteration | 1208587.5244 | C_100 - C this iteration | iteration | 1403132.5957 | C_100 - C this iteration | iteration | 1645283.3177 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1695 |  |  | 89.4488 |  |  | 85.7709 |  |  | 73.4392 |  |  | 43.0514 |  |  | -10.2199 |  |  | -88.6262 |  |  | -176.0405 |  |  | -268.6468 |  |  | -403.1874
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1695 |  |  | 29.4488 |  |  | 25.7709 |  |  | 13.4392 |  |  | -16.9486 |  |  | -70.2199 |  |  | -148.6262 |  |  | -236.0405 |  |  | -328.6468 |  |  | -463.1874
[13 empty] | Press drop ratio this iteration |  |  | 0.33459 |  |  | 0.32923 |  |  | 0.30046 |  |  | 0.183 |  |  | -0.39368 |  |  | 6.8709 |  |  | 1.677 |  |  | 1.3408 |  |  | 1.2233 |  |  | 1.1488
[13 empty] | Expansion factor | 12 |  | 0.82574 |  |  | 0.82858 |  |  | 0.84206 |  |  | 0.90245 |  |  | 1.2164 |  |  | -3.0028 |  |  | -0.051083 |  |  | 0.060382 |  |  | 0.30948 |  |  | -0.016587
[13 empty] | C Non choked w/ reducers | 7 |  | 3.7294 |  |  | 26.0177 |  |  | 68.5907 |  |  | 187.6602 |  |  | #NUM! |  |  | 167.6515 |  |  | 3180.7008 |  |  | -1961.3924 |  |  | -346.9122 |  |  | 6989.7497
[13 empty] | C Choked w/ reducers | 7 |  | 3.3382 |  |  | 23.1778 |  |  | 59.6055 |  |  | 137.3536 |  |  | 404.0833 |  |  | -2615.4307 |  |  | -432.5631 |  |  | -298.1138 |  |  | -231.673 |  |  | -303.5515
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.7294 |  |  | 26.0177 |  |  | 68.5907 |  |  | 187.6602 |  |  | #NUM! |  |  | -2615.4307 |  |  | -432.5631 |  |  | -298.1138 |  |  | -231.673 |  |  | -303.5515
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.0006 | 9232.4266 |  | 14.4177 | 63555.2553 |  | 45.5907 | 155623.4747 |  | 148.2602 | 303114.8064 |  | 236393 | 508532.3527 |  | 236393 | 742216.8192 |  | 236393 | 990491.2225 |  | 236393 | 1208587.5244 |  | 236393 | 1403132.5957 |  | 236393 | 1645283.3177
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 9417.0751 | C_100 - C this iteration | iteration | 64190.8078 | C_100 - C this iteration | iteration | 157179.7094 | C_100 - C this iteration | iteration | 306145.9545 | C_100 - C this iteration | iteration | 513617.6762 | C_100 - C this iteration | iteration | 749638.9874 | C_100 - C this iteration | iteration | 1000396.1347 | C_100 - C this iteration | iteration | 1220673.3996 | C_100 - C this iteration | iteration | 1417163.9216 | C_100 - C this iteration | iteration | 1661736.1508 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1689 |  |  | 89.434 |  |  | 85.6822 |  |  | 73.1026 |  |  | 42.104 |  |  | -12.238 |  |  | -92.2203 |  |  | -181.3917 |  |  | -275.8593 |  |  | -413.1042
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1689 |  |  | 29.434 |  |  | 25.6822 |  |  | 13.1026 |  |  | -17.896 |  |  | -72.238 |  |  | -152.2203 |  |  | -241.3917 |  |  | -335.8593 |  |  | -473.1042
[13 empty] | Press drop ratio this iteration |  |  | 0.33458 |  |  | 0.32911 |  |  | 0.29974 |  |  | 0.17924 |  |  | -0.42504 |  |  | 5.9027 |  |  | 1.6506 |  |  | 1.3308 |  |  | 1.2175 |  |  | 1.1452
[13 empty] | Expansion factor | 12 |  | 0.82575 |  |  | 0.82863 |  |  | 0.84244 |  |  | 0.90446 |  |  | 1.2336 |  |  | -2.4387 |  |  | -0.034546 |  |  | 0.067428 |  |  | 0.31278 |  |  | -0.013426
[13 empty] | C Non choked w/ reducers | 7 |  | 3.8041 |  |  | 26.2848 |  |  | 69.4007 |  |  | 191.9707 |  |  | #NUM! |  |  | 187.844 |  |  | 4601.544 |  |  | -1728.1549 |  |  | -338.4332 |  |  | 8525.7951
[13 empty] | C Choked w/ reducers | 7 |  | 3.405 |  |  | 23.4134 |  |  | 60.2639 |  |  | 139.3659 |  |  | 417.3074 |  |  | -2205.9692 |  |  | -419.8619 |  |  | -292.2125 |  |  | -227.872 |  |  | -299.2272
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.8041 |  |  | 26.2848 |  |  | 69.4007 |  |  | 191.9707 |  |  | #NUM! |  |  | -2205.9692 |  |  | -419.8619 |  |  | -292.2125 |  |  | -227.872 |  |  | -299.2272
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.92594 | 9417.0751 |  | 14.6848 | 64190.8078 |  | 46.4007 | 157179.7094 |  | 152.5707 | 306145.9545 |  | 236393 | 513617.6762 |  | 236393 | 749638.9874 |  | 236393 | 1000396.1347 |  | 236393 | 1220673.3996 |  | 236393 | 1417163.9216 |  | 236393 | 1661736.1508
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 9605.4166 | C_100 - C this iteration | iteration | 64832.7159 | C_100 - C this iteration | iteration | 158751.5065 | C_100 - C this iteration | iteration | 309207.4141 | C_100 - C this iteration | iteration | 518753.853 | C_100 - C this iteration | iteration | 757135.3773 | C_100 - C this iteration | iteration | 1010400.0961 | C_100 - C this iteration | iteration | 1232880.1336 | C_100 - C this iteration | iteration | 1431335.5608 | C_100 - C this iteration | iteration | 1678353.5123 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1682 |  |  | 89.4189 |  |  | 85.5917 |  |  | 72.7592 |  |  | 41.1376 |  |  | -14.2968 |  |  | -95.8866 |  |  | -186.8503 |  |  | -283.2168 |  |  | -423.2203
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1682 |  |  | 29.4189 |  |  | 25.5917 |  |  | 12.7592 |  |  | -18.8624 |  |  | -74.2968 |  |  | -155.8866 |  |  | -246.8503 |  |  | -343.2168 |  |  | -483.2203
[13 empty] | Press drop ratio this iteration |  |  | 0.33458 |  |  | 0.329 |  |  | 0.299 |  |  | 0.17536 |  |  | -0.45852 |  |  | 5.1968 |  |  | 1.6257 |  |  | 1.3211 |  |  | 1.2119 |  |  | 1.1418
[13 empty] | Expansion factor | 12 |  | 0.82575 |  |  | 0.82869 |  |  | 0.84283 |  |  | 0.90652 |  |  | 1.252 |  |  | -2.0275 |  |  | -0.018954 |  |  | 0.0742 |  |  | 0.31597 |  |  | -0.010354
[13 empty] | C Non choked w/ reducers | 7 |  | 3.8802 |  |  | 26.5548 |  |  | 70.2232 |  |  | 196.4964 |  |  | #NUM! |  |  | 208.1939 |  |  | 8209.056 |  |  | -1545.4229 |  |  | -330.3445 |  |  | 10915.7622
[13 empty] | C Choked w/ reducers | 7 |  | 3.4731 |  |  | 23.6515 |  |  | 60.9309 |  |  | 141.4238 |  |  | 431.3821 |  |  | -1907.1971 |  |  | -407.846 |  |  | -286.5125 |  |  | -224.1718 |  |  | -294.9956
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.8802 |  |  | 26.5548 |  |  | 70.2232 |  |  | 196.4964 |  |  | #NUM! |  |  | -1907.1971 |  |  | -407.846 |  |  | -286.5125 |  |  | -224.1718 |  |  | -294.9956
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.84981 | 9605.4166 |  | 14.9548 | 64832.7159 |  | 47.2232 | 158751.5065 |  | 157.0964 | 309207.4141 |  | 236393 | 518753.853 |  | 236393 | 757135.3773 |  | 236393 | 1010400.0961 |  | 236393 | 1232880.1336 |  | 236393 | 1431335.5608 |  | 236393 | 1678353.5123
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 9797.525 | C_100 - C this iteration | iteration | 65481.043 | C_100 - C this iteration | iteration | 160339.0216 | C_100 - C this iteration | iteration | 312299.4882 | C_100 - C this iteration | iteration | 523941.3915 | C_100 - C this iteration | iteration | 764706.7311 | C_100 - C this iteration | iteration | 1020504.0971 | C_100 - C this iteration | iteration | 1245208.935 | C_100 - C this iteration | iteration | 1445648.9164 | C_100 - C this iteration | iteration | 1695137.0475 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1675 |  |  | 89.4035 |  |  | 85.4994 |  |  | 72.409 |  |  | 40.1518 |  |  | -16.3968 |  |  | -99.6267 |  |  | -192.4188 |  |  | -290.7222 |  |  | -433.5398
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1675 |  |  | 29.4035 |  |  | 25.4994 |  |  | 12.409 |  |  | -19.8482 |  |  | -76.3968 |  |  | -159.6267 |  |  | -252.4188 |  |  | -350.7222 |  |  | -493.5398
[13 empty] | Press drop ratio this iteration |  |  | 0.33457 |  |  | 0.32889 |  |  | 0.29824 |  |  | 0.17137 |  |  | -0.49433 |  |  | 4.6592 |  |  | 1.6022 |  |  | 1.3118 |  |  | 1.2064 |  |  | 1.1384
[13 empty] | Expansion factor | 12 |  | 0.82575 |  |  | 0.82875 |  |  | 0.84323 |  |  | 0.90865 |  |  | 1.2717 |  |  | -1.7143 |  |  | -0.0042305 |  |  | 0.080712 |  |  | 0.31905 |  |  | -0.0073675
[13 empty] | C Non choked w/ reducers | 7 |  | 3.9578 |  |  | 26.8277 |  |  | 71.0585 |  |  | 201.2569 |  |  | #NUM! |  |  | 228.9999 |  |  | 36012.5145 |  |  | -1398.3419 |  |  | -322.6182 |  |  | 15147.0677
[13 empty] | C Choked w/ reducers | 7 |  | 3.5426 |  |  | 23.8922 |  |  | 61.6067 |  |  | 143.529 |  |  | 446.3937 |  |  | -1679.5552 |  |  | -396.4606 |  |  | -281.0033 |  |  | -220.5683 |  |  | -290.8537
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.9578 |  |  | 26.8277 |  |  | 71.0585 |  |  | 201.2569 |  |  | #NUM! |  |  | -1679.5552 |  |  | -396.4606 |  |  | -281.0033 |  |  | -220.5683 |  |  | -290.8537
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.77216 | 9797.525 |  | 15.2277 | 65481.043 |  | 48.0585 | 160339.0216 |  | 161.8569 | 312299.4882 |  | 236393 | 523941.3915 |  | 236393 | 764706.7311 |  | 236393 | 1020504.0971 |  | 236393 | 1245208.935 |  | 236393 | 1445648.9164 |  | 236393 | 1695137.0475
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 9993.4755 | C_100 - C this iteration | iteration | 66135.8535 | C_100 - C this iteration | iteration | 161942.4118 | C_100 - C this iteration | iteration | 315422.4831 | C_100 - C this iteration | iteration | 529180.8054 | C_100 - C this iteration | iteration | 772353.7984 | C_100 - C this iteration | iteration | 1030709.138 | C_100 - C this iteration | iteration | 1257661.0243 | C_100 - C this iteration | iteration | 1460105.4056 | C_100 - C this iteration | iteration | 1712088.4179 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1668 |  |  | 89.3878 |  |  | 85.4052 |  |  | 72.0517 |  |  | 39.1461 |  |  | -18.5391 |  |  | -103.4419 |  |  | -198.0991 |  |  | -298.3784 |  |  | -444.0667
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1668 |  |  | 29.3878 |  |  | 25.4052 |  |  | 12.0517 |  |  | -20.8539 |  |  | -78.5391 |  |  | -163.4419 |  |  | -258.0991 |  |  | -358.3784 |  |  | -504.0667
[13 empty] | Press drop ratio this iteration |  |  | 0.33457 |  |  | 0.32877 |  |  | 0.29747 |  |  | 0.16726 |  |  | -0.53272 |  |  | 4.2364 |  |  | 1.58 |  |  | 1.3029 |  |  | 1.2011 |  |  | 1.1351
[13 empty] | Expansion factor | 12 |  | 0.82575 |  |  | 0.82881 |  |  | 0.84364 |  |  | 0.91084 |  |  | 1.2928 |  |  | -1.468 |  |  | 0.0096915 |  |  | 0.086978 |  |  | 0.32204 |  |  | -0.0044643
[13 empty] | C Non choked w/ reducers | 7 |  | 4.037 |  |  | 27.1036 |  |  | 71.907 |  |  | 206.2742 |  |  | #NUM! |  |  | 250.5284 |  |  | -15398.94 |  |  | -1277.3641 |  |  | -315.2292 |  |  | 24684.2712
[13 empty] | C Choked w/ reducers | 7 |  | 3.6135 |  |  | 24.1353 |  |  | 62.2914 |  |  | 145.6832 |  |  | 462.4402 |  |  | -1500.3284 |  |  | -385.6565 |  |  | -275.6752 |  |  | -217.0577 |  |  | -286.7984
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.037 |  |  | 27.1036 |  |  | 71.907 |  |  | 206.2742 |  |  | #NUM! |  |  | -1500.3284 |  |  | -385.6565 |  |  | -275.6752 |  |  | -217.0577 |  |  | -286.7984
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.69296 | 9993.4755 |  | 15.5036 | 66135.8535 |  | 48.907 | 161942.4118 |  | 166.8742 | 315422.4831 |  | 236393 | 529180.8054 |  | 236393 | 772353.7984 |  | 236393 | 1030709.138 |  | 236393 | 1257661.0243 |  | 236393 | 1460105.4056 |  | 236393 | 1712088.4179
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 10193.345 | C_100 - C this iteration | iteration | 66797.212 | C_100 - C this iteration | iteration | 163561.8359 | C_100 - C this iteration | iteration | 318576.7079 | C_100 - C this iteration | iteration | 534472.6135 | C_100 - C this iteration | iteration | 780077.3364 | C_100 - C this iteration | iteration | 1041016.2294 | C_100 - C this iteration | iteration | 1270237.6345 | C_100 - C this iteration | iteration | 1474706.4597 | C_100 - C this iteration | iteration | 1729209.3021 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1661 |  |  | 89.3718 |  |  | 85.3091 |  |  | 71.6872 |  |  | 38.1202 |  |  | -20.7245 |  |  | -107.3338 |  |  | -203.8936 |  |  | -306.1885 |  |  | -454.8051
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1661 |  |  | 29.3718 |  |  | 25.3091 |  |  | 11.6872 |  |  | -21.8798 |  |  | -80.7245 |  |  | -167.3338 |  |  | -263.8936 |  |  | -366.1885 |  |  | -514.8051
[13 empty] | Press drop ratio this iteration |  |  | 0.33456 |  |  | 0.32865 |  |  | 0.29668 |  |  | 0.16303 |  |  | -0.57397 |  |  | 3.8951 |  |  | 1.559 |  |  | 1.2943 |  |  | 1.196 |  |  | 1.1319
[13 empty] | Expansion factor | 12 |  | 0.82576 |  |  | 0.82888 |  |  | 0.84405 |  |  | 0.9131 |  |  | 1.3154 |  |  | -1.2692 |  |  | 0.022874 |  |  | 0.09301 |  |  | 0.32494 |  |  | -0.0016413
[13 empty] | C Non choked w/ reducers | 7 |  | 4.1178 |  |  | 27.3825 |  |  | 72.7688 |  |  | 211.5735 |  |  | #NUM! |  |  | 273.0378 |  |  | -6393.4949 |  |  | -1176.0725 |  |  | -308.1546 |  |  | 66304.8692
[13 empty] | C Choked w/ reducers | 7 |  | 3.6858 |  |  | 24.381 |  |  | 62.9851 |  |  | 147.8881 |  |  | 479.6341 |  |  | -1355.543 |  |  | -375.3894 |  |  | -270.5191 |  |  | -213.6363 |  |  | -282.827
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.1178 |  |  | 27.3825 |  |  | 72.7688 |  |  | 211.5735 |  |  | #NUM! |  |  | -1355.543 |  |  | -375.3894 |  |  | -270.5191 |  |  | -213.6363 |  |  | -282.827
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.61216 | 10193.345 |  | 15.7825 | 66797.212 |  | 49.7688 | 163561.8359 |  | 172.1735 | 318576.7079 |  | 236393 | 534472.6135 |  | 236393 | 780077.3364 |  | 236393 | 1041016.2294 |  | 236393 | 1270237.6345 |  | 236393 | 1474706.4597 |  | 236393 | 1729209.3021
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 10397.2119 | C_100 - C this iteration | iteration | 67465.1841 | C_100 - C this iteration | iteration | 165197.4543 | C_100 - C this iteration | iteration | 321762.475 | C_100 - C this iteration | iteration | 539817.3396 | C_100 - C this iteration | iteration | 787878.1097 | C_100 - C this iteration | iteration | 1051426.3917 | C_100 - C this iteration | iteration | 1282940.0109 | C_100 - C this iteration | iteration | 1489453.5242 | C_100 - C this iteration | iteration | 1746501.3951 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1653 |  |  | 89.3555 |  |  | 85.2111 |  |  | 71.3154 |  |  | 37.0737 |  |  | -22.9538 |  |  | -111.3039 |  |  | -209.8046 |  |  | -314.1557 |  |  | -465.7594
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1653 |  |  | 29.3555 |  |  | 25.2111 |  |  | 11.3154 |  |  | -22.9263 |  |  | -82.9538 |  |  | -171.3039 |  |  | -269.8046 |  |  | -374.1557 |  |  | -525.7594
[13 empty] | Press drop ratio this iteration |  |  | 0.33456 |  |  | 0.32852 |  |  | 0.29587 |  |  | 0.15867 |  |  | -0.6184 |  |  | 3.6139 |  |  | 1.5391 |  |  | 1.286 |  |  | 1.191 |  |  | 1.1288
[13 empty] | Expansion factor | 12 |  | 0.82576 |  |  | 0.82894 |  |  | 0.84448 |  |  | 0.91542 |  |  | 1.3399 |  |  | -1.1054 |  |  | 0.035371 |  |  | 0.09882 |  |  | 0.32774 |  |  | 0.0011044
[13 empty] | C Non choked w/ reducers | 7 |  | 4.2002 |  |  | 27.6644 |  |  | 73.6445 |  |  | 217.1838 |  |  | #NUM! |  |  | 296.7953 |  |  | -4052.9407 |  |  | -1089.9953 |  |  | -301.3736 |  |  | -97320.2252
[13 empty] | C Choked w/ reducers | 7 |  | 3.7596 |  |  | 24.6294 |  |  | 63.6882 |  |  | 150.1457 |  |  | 498.1048 |  |  | -1236.1309 |  |  | -365.6195 |  |  | -265.5266 |  |  | -210.3006 |  |  | -278.9369
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.2002 |  |  | 27.6644 |  |  | 73.6445 |  |  | 217.1838 |  |  | #NUM! |  |  | -1236.1309 |  |  | -365.6195 |  |  | -265.5266 |  |  | -210.3006 |  |  | -278.9369
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.52975 | 10397.2119 |  | 16.0644 | 67465.1841 |  | 50.6445 | 165197.4543 |  | 177.7838 | 321762.475 |  | 236393 | 539817.3396 |  | 236393 | 787878.1097 |  | 236393 | 1051426.3917 |  | 236393 | 1282940.0109 |  | 236393 | 1489453.5242 |  | 236393 | 1746501.3951
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 10605.1561 | C_100 - C this iteration | iteration | 68139.836 | C_100 - C this iteration | iteration | 166849.4288 | C_100 - C this iteration | iteration | 324980.0997 | C_100 - C this iteration | iteration | 545215.513 | C_100 - C this iteration | iteration | 795756.8908 | C_100 - C this iteration | iteration | 1061940.6556 | C_100 - C this iteration | iteration | 1295769.411 | C_100 - C this iteration | iteration | 1504348.0595 | C_100 - C this iteration | iteration | 1763966.4091 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1645 |  |  | 89.3388 |  |  | 85.1111 |  |  | 70.9361 |  |  | 36.0062 |  |  | -25.2279 |  |  | -115.3539 |  |  | -215.8344 |  |  | -322.2829 |  |  | -476.9339
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1645 |  |  | 29.3388 |  |  | 25.1111 |  |  | 10.9361 |  |  | -23.9938 |  |  | -85.2279 |  |  | -175.3539 |  |  | -275.8344 |  |  | -382.2829 |  |  | -536.9339
[13 empty] | Press drop ratio this iteration |  |  | 0.33455 |  |  | 0.3284 |  |  | 0.29504 |  |  | 0.15417 |  |  | -0.66638 |  |  | 3.3783 |  |  | 1.5201 |  |  | 1.278 |  |  | 1.1862 |  |  | 1.1258
[13 empty] | Expansion factor | 12 |  | 0.82576 |  |  | 0.82901 |  |  | 0.84491 |  |  | 0.91782 |  |  | 1.3662 |  |  | -0.9681 |  |  | 0.047233 |  |  | 0.10442 |  |  | 0.33046 |  |  | 0.0037752
[13 empty] | C Non choked w/ reducers | 7 |  | 4.2843 |  |  | 27.9494 |  |  | 74.5342 |  |  | 223.1382 |  |  | #NUM! |  |  | 322.0915 |  |  | -2976.1676 |  |  | -1015.9203 |  |  | -294.8673 |  |  | -28117.3331
[13 empty] | C Choked w/ reducers | 7 |  | 3.8348 |  |  | 24.8803 |  |  | 64.4006 |  |  | 152.458 |  |  | 518.0017 |  |  | -1135.9506 |  |  | -356.3109 |  |  | -260.6896 |  |  | -207.0473 |  |  | -275.1255
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.2843 |  |  | 27.9494 |  |  | 74.5342 |  |  | 223.1382 |  |  | #NUM! |  |  | -1135.9506 |  |  | -356.3109 |  |  | -260.6896 |  |  | -207.0473 |  |  | -275.1255
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.44569 | 10605.1561 |  | 16.3494 | 68139.836 |  | 51.5342 | 166849.4288 |  | 183.7382 | 324980.0997 |  | 236393 | 545215.513 |  | 236393 | 795756.8908 |  | 236393 | 1061940.6556 |  | 236393 | 1295769.411 |  | 236393 | 1504348.0595 |  | 236393 | 1763966.4091
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 10817.2592 | C_100 - C this iteration | iteration | 68821.2343 | C_100 - C this iteration | iteration | 168517.9231 | C_100 - C this iteration | iteration | 328229.9007 | C_100 - C this iteration | iteration | 550667.6682 | C_100 - C this iteration | iteration | 803714.4597 | C_100 - C this iteration | iteration | 1072560.0622 | C_100 - C this iteration | iteration | 1308727.1051 | C_100 - C this iteration | iteration | 1519391.5401 | C_100 - C this iteration | iteration | 1781606.0732 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1637 |  |  | 89.3218 |  |  | 85.0091 |  |  | 70.5492 |  |  | 34.9172 |  |  | -27.5477 |  |  | -119.4852 |  |  | -221.9854 |  |  | -330.5735 |  |  | -488.333
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1637 |  |  | 29.3218 |  |  | 25.0091 |  |  | 10.5492 |  |  | -25.0828 |  |  | -87.5477 |  |  | -179.4852 |  |  | -281.9854 |  |  | -390.5735 |  |  | -548.333
[13 empty] | Press drop ratio this iteration |  |  | 0.33454 |  |  | 0.32827 |  |  | 0.29419 |  |  | 0.14953 |  |  | -0.71835 |  |  | 3.178 |  |  | 1.5022 |  |  | 1.2703 |  |  | 1.1815 |  |  | 1.1229
[13 empty] | Expansion factor | 12 |  | 0.82577 |  |  | 0.82907 |  |  | 0.84536 |  |  | 0.92029 |  |  | 1.3948 |  |  | -0.85143 |  |  | 0.058505 |  |  | 0.10982 |  |  | 0.3331 |  |  | 0.0063738
[13 empty] | C Non choked w/ reducers | 7 |  | 4.3701 |  |  | 28.2375 |  |  | 75.4384 |  |  | 229.4753 |  |  | #NUM! |  |  | 349.254 |  |  | -2356.8597 |  |  | -951.4809 |  |  | -288.6182 |  |  | -16449.2706
[13 empty] | C Choked w/ reducers | 7 |  | 3.9115 |  |  | 25.1339 |  |  | 65.1226 |  |  | 154.827 |  |  | 539.4987 |  |  | -1050.6947 |  |  | -347.431 |  |  | -256.0008 |  |  | -203.8732 |  |  | -271.3903
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.3701 |  |  | 28.2375 |  |  | 75.4384 |  |  | 229.4753 |  |  | #NUM! |  |  | -1050.6947 |  |  | -347.431 |  |  | -256.0008 |  |  | -203.8732 |  |  | -271.3903
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.35994 | 10817.2592 |  | 16.6375 | 68821.2343 |  | 52.4384 | 168517.9231 |  | 190.0753 | 328229.9007 |  | 236393 | 550667.6682 |  | 236393 | 803714.4597 |  | 236393 | 1072560.0622 |  | 236393 | 1308727.1051 |  | 236393 | 1519391.5401 |  | 236393 | 1781606.0732
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 11033.6044 | C_100 - C this iteration | iteration | 69509.4467 | C_100 - C this iteration | iteration | 170203.1023 | C_100 - C this iteration | iteration | 331512.1997 | C_100 - C this iteration | iteration | 556174.3448 | C_100 - C this iteration | iteration | 811751.6043 | C_100 - C this iteration | iteration | 1083285.6628 | C_100 - C this iteration | iteration | 1321814.3762 | C_100 - C this iteration | iteration | 1534585.4555 | C_100 - C this iteration | iteration | 1799422.1339 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1629 |  |  | 89.3044 |  |  | 84.9051 |  |  | 70.1545 |  |  | 33.8063 |  |  | -29.9141 |  |  | -123.6996 |  |  | -228.26 |  |  | -339.0308 |  |  | -499.9612
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1629 |  |  | 29.3044 |  |  | 24.9051 |  |  | 10.1545 |  |  | -26.1937 |  |  | -89.9141 |  |  | -183.6996 |  |  | -288.26 |  |  | -399.0308 |  |  | -559.9612
[13 empty] | Press drop ratio this iteration |  |  | 0.33454 |  |  | 0.32814 |  |  | 0.29333 |  |  | 0.14474 |  |  | -0.77482 |  |  | 3.0057 |  |  | 1.485 |  |  | 1.2629 |  |  | 1.177 |  |  | 1.12
[13 empty] | Expansion factor | 12 |  | 0.82577 |  |  | 0.82914 |  |  | 0.84581 |  |  | 0.92284 |  |  | 1.4258 |  |  | -0.75105 |  |  | 0.069227 |  |  | 0.11502 |  |  | 0.33565 |  |  | 0.0089026
[13 empty] | C Non choked w/ reducers | 7 |  | 4.4575 |  |  | 28.5288 |  |  | 76.3575 |  |  | 236.2402 |  |  | #NUM! |  |  | 378.6638 |  |  | -1954.3434 |  |  | -894.8947 |  |  | -282.6106 |  |  | -11632.8407
[13 empty] | C Choked w/ reducers | 7 |  | 3.9898 |  |  | 25.3902 |  |  | 65.8545 |  |  | 157.2551 |  |  | 562.799 |  |  | -977.2526 |  |  | -338.9501 |  |  | -251.4533 |  |  | -200.7754 |  |  | -267.729
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.4575 |  |  | 28.5288 |  |  | 76.3575 |  |  | 236.2402 |  |  | #NUM! |  |  | -977.2526 |  |  | -338.9501 |  |  | -251.4533 |  |  | -200.7754 |  |  | -267.729
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.27247 | 11033.6044 |  | 16.9288 | 69509.4467 |  | 53.3575 | 170203.1023 |  | 196.8402 | 331512.1997 |  | 236393 | 556174.3448 |  | 236393 | 811751.6043 |  | 236393 | 1083285.6628 |  | 236393 | 1321814.3762 |  | 236393 | 1534585.4555 |  | 236393 | 1799422.1339
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 11254.2765 | C_100 - C this iteration | iteration | 70204.5411 | C_100 - C this iteration | iteration | 171905.1333 | C_100 - C this iteration | iteration | 334827.3217 | C_100 - C this iteration | iteration | 561736.0883 | C_100 - C this iteration | iteration | 819869.1204 | C_100 - C this iteration | iteration | 1094118.5194 | C_100 - C this iteration | iteration | 1335032.5199 | C_100 - C this iteration | iteration | 1549931.31 | C_100 - C this iteration | iteration | 1817416.3553 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.162 |  |  | 89.2867 |  |  | 84.799 |  |  | 69.7519 |  |  | 32.6731 |  |  | -32.3281 |  |  | -127.9986 |  |  | -234.6607 |  |  | -347.658 |  |  | -511.8232
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.162 |  |  | 29.2867 |  |  | 24.799 |  |  | 9.7519 |  |  | -27.3269 |  |  | -92.3281 |  |  | -187.9986 |  |  | -294.6607 |  |  | -407.658 |  |  | -571.8232
[13 empty] | Press drop ratio this iteration |  |  | 0.33453 |  |  | 0.32801 |  |  | 0.29244 |  |  | 0.13981 |  |  | -0.83637 |  |  | 2.856 |  |  | 1.4688 |  |  | 1.2557 |  |  | 1.1726 |  |  | 1.1172
[13 empty] | Expansion factor | 12 |  | 0.82577 |  |  | 0.82921 |  |  | 0.84628 |  |  | 0.92547 |  |  | 1.4597 |  |  | -0.6638 |  |  | 0.079438 |  |  | 0.12005 |  |  | 0.33813 |  |  | 0.011364
[13 empty] | C Non choked w/ reducers | 7 |  | 4.5468 |  |  | 28.8232 |  |  | 77.2918 |  |  | 243.4856 |  |  | #NUM! |  |  | 410.7743 |  |  | -1671.5885 |  |  | -844.7939 |  |  | -276.8298 |  |  | -9002.3733
[13 empty] | C Choked w/ reducers | 7 |  | 4.0696 |  |  | 25.6491 |  |  | 66.5962 |  |  | 159.7444 |  |  | 588.142 |  |  | -913.3223 |  |  | -330.8415 |  |  | -247.0404 |  |  | -197.751 |  |  | -264.1394
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.5468 |  |  | 28.8232 |  |  | 77.2918 |  |  | 243.4856 |  |  | #NUM! |  |  | -913.3223 |  |  | -330.8415 |  |  | -247.0404 |  |  | -197.751 |  |  | -264.1394
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.18325 | 11254.2765 |  | 17.2232 | 70204.5411 |  | 54.2918 | 171905.1333 |  | 204.0856 | 334827.3217 |  | 236393 | 561736.0883 |  | 236393 | 819869.1204 |  | 236393 | 1094118.5194 |  | 236393 | 1335032.5199 |  | 236393 | 1549931.31 |  | 236393 | 1817416.3553
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 11479.362 | C_100 - C this iteration | iteration | 70906.5865 | C_100 - C this iteration | iteration | 173624.1847 | C_100 - C this iteration | iteration | 338175.595 | C_100 - C this iteration | iteration | 567353.4492 | C_100 - C this iteration | iteration | 828067.8116 | C_100 - C this iteration | iteration | 1105059.7046 | C_100 - C this iteration | iteration | 1348382.8451 | C_100 - C this iteration | iteration | 1565430.6231 | C_100 - C this iteration | iteration | 1835590.5188 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.161 |  |  | 89.2687 |  |  | 84.6907 |  |  | 69.3412 |  |  | 31.5171 |  |  | -34.7906 |  |  | -132.3841 |  |  | -241.1901 |  |  | -356.4586 |  |  | -523.9235
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.161 |  |  | 29.2687 |  |  | 24.6907 |  |  | 9.3412 |  |  | -28.4829 |  |  | -94.7906 |  |  | -192.3841 |  |  | -301.1901 |  |  | -416.4586 |  |  | -583.9235
[13 empty] | Press drop ratio this iteration |  |  | 0.33452 |  |  | 0.32787 |  |  | 0.29154 |  |  | 0.13471 |  |  | -0.90373 |  |  | 2.7246 |  |  | 1.4532 |  |  | 1.2488 |  |  | 1.1683 |  |  | 1.1145
[13 empty] | Expansion factor | 12 |  | 0.82578 |  |  | 0.82928 |  |  | 0.84675 |  |  | 0.92819 |  |  | 1.4967 |  |  | -0.58727 |  |  | 0.089171 |  |  | 0.1249 |  |  | 0.34054 |  |  | 0.01376
[13 empty] | C Non choked w/ reducers | 7 |  | 4.6378 |  |  | 29.1209 |  |  | 78.2417 |  |  | 251.2742 |  |  | #NUM! |  |  | 446.1368 |  |  | -1461.957 |  |  | -800.1112 |  |  | -271.2624 |  |  | -7344.6979
[13 empty] | C Choked w/ reducers | 7 |  | 4.1511 |  |  | 25.9109 |  |  | 67.3482 |  |  | 162.2975 |  |  | 615.8111 |  |  | -857.1632 |  |  | -323.0805 |  |  | -242.7562 |  |  | -194.7974 |  |  | -260.6193
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.6378 |  |  | 29.1209 |  |  | 78.2417 |  |  | 251.2742 |  |  | #NUM! |  |  | -857.1632 |  |  | -323.0805 |  |  | -242.7562 |  |  | -194.7974 |  |  | -260.6193
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.092236 | 11479.362 |  | 17.5209 | 70906.5865 |  | 55.2417 | 173624.1847 |  | 211.8742 | 338175.595 |  | 236393 | 567353.4492 |  | 236393 | 828067.8116 |  | 236393 | 1105059.7046 |  | 236393 | 1348382.8451 |  | 236393 | 1565430.6231 |  | 236393 | 1835590.5188
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 11708.9493 | C_100 - C this iteration | iteration | 71615.6524 | C_100 - C this iteration | iteration | 175360.4265 | C_100 - C this iteration | iteration | 341557.3509 | C_100 - C this iteration | iteration | 573026.9837 | C_100 - C this iteration | iteration | 836348.4897 | C_100 - C this iteration | iteration | 1116110.3017 | C_100 - C this iteration | iteration | 1361866.6736 | C_100 - C this iteration | iteration | 1581084.9294 | C_100 - C this iteration | iteration | 1853946.424 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1601 |  |  | 89.2503 |  |  | 84.5803 |  |  | 68.9222 |  |  | 30.3379 |  |  | -37.3026 |  |  | -136.8578 |  |  | -247.8508 |  |  | -365.4362 |  |  | -536.2671
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1601 |  |  | 29.2503 |  |  | 24.5803 |  |  | 8.9222 |  |  | -29.6621 |  |  | -97.3026 |  |  | -196.8578 |  |  | -307.8508 |  |  | -425.4362 |  |  | -596.2671
[13 empty] | Press drop ratio this iteration |  |  | 0.33452 |  |  | 0.32773 |  |  | 0.29061 |  |  | 0.12945 |  |  | -0.97773 |  |  | 2.6085 |  |  | 1.4384 |  |  | 1.2421 |  |  | 1.1642 |  |  | 1.1119
[13 empty] | Expansion factor | 12 |  | 0.82578 |  |  | 0.82935 |  |  | 0.84724 |  |  | 0.93099 |  |  | 1.5373 |  |  | -0.51961 |  |  | 0.098456 |  |  | 0.12958 |  |  | 0.34287 |  |  | 0.016092
[13 empty] | C Non choked w/ reducers | 7 |  | 4.7306 |  |  | 29.4218 |  |  | 79.2076 |  |  | 259.6807 |  |  | #NUM! |  |  | 485.4337 |  |  | -1300.2481 |  |  | -760.0018 |  |  | -265.8961 |  |  | -6204.2179
[13 empty] | C Choked w/ reducers | 7 |  | 4.2341 |  |  | 26.1754 |  |  | 68.1105 |  |  | 164.9169 |  |  | 646.1451 |  |  | -807.435 |  |  | -315.6448 |  |  | -238.5948 |  |  | -191.912 |  |  | -257.1667
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.7306 |  |  | 29.4218 |  |  | 79.2076 |  |  | 259.6807 |  |  | #NUM! |  |  | -807.435 |  |  | -315.6448 |  |  | -238.5948 |  |  | -191.912 |  |  | -257.1667
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.00059933 | 11708.9493 |  | 17.8218 | 71615.6524 |  | 56.2076 | 175360.4265 |  | 220.2807 | 341557.3509 |  | 236393 | 573026.9837 |  | 236393 | 836348.4897 |  | 236393 | 1116110.3017 |  | 236393 | 1361866.6736 |  | 236393 | 1581084.9294 |  | 236393 | 1853946.424
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 11943.1283 | C_100 - C this iteration | iteration | 72331.8089 | C_100 - C this iteration | iteration | 177114.0308 | C_100 - C this iteration | iteration | 344972.9244 | C_100 - C this iteration | iteration | 578757.2535 | C_100 - C this iteration | iteration | 844711.9746 | C_100 - C this iteration | iteration | 1127271.4047 | C_100 - C this iteration | iteration | 1375485.3403 | C_100 - C this iteration | iteration | 1596895.7787 | C_100 - C this iteration | iteration | 1872485.8882 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.159 |  |  | 89.2315 |  |  | 84.4676 |  |  | 68.4948 |  |  | 29.1349 |  |  | -39.8651 |  |  | -141.4213 |  |  | -254.6453 |  |  | -374.5942 |  |  | -548.8588
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.159 |  |  | 29.2315 |  |  | 24.4676 |  |  | 8.4948 |  |  | -30.8651 |  |  | -99.8651 |  |  | -201.4213 |  |  | -314.6453 |  |  | -434.5942 |  |  | -608.8588
[13 empty] | Press drop ratio this iteration |  |  | 0.33451 |  |  | 0.32759 |  |  | 0.28967 |  |  | 0.12402 |  |  | -1.0594 |  |  | 2.5051 |  |  | 1.4243 |  |  | 1.2356 |  |  | 1.1602 |  |  | 1.1093
[13 empty] | Expansion factor | 12 |  | 0.82578 |  |  | 0.82943 |  |  | 0.84774 |  |  | 0.93389 |  |  | 1.5822 |  |  | -0.45938 |  |  | 0.10732 |  |  | 0.13411 |  |  | 0.34514 |  |  | 0.018364
[13 empty] | C Non choked w/ reducers | 7 |  | 4.8253 |  |  | 29.7261 |  |  | 80.1901 |  |  | 268.7956 |  |  | #NUM! |  |  | 529.5263 |  |  | -1171.6508 |  |  | -723.7879 |  |  | -260.7195 |  |  | -5371.4202
[13 empty] | C Choked w/ reducers | 7 |  | 4.3189 |  |  | 26.4427 |  |  | 68.8833 |  |  | 167.6053 |  |  | 679.5514 |  |  | -763.089 |  |  | -308.5137 |  |  | -234.5508 |  |  | -189.0924 |  |  | -253.7796
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.8253 |  |  | 29.7261 |  |  | 80.1901 |  |  | 268.7956 |  |  | #NUM! |  |  | -763.089 |  |  | -308.5137 |  |  | -234.5508 |  |  | -189.0924 |  |  | -253.7796
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.095296 | 11943.1283 |  | 18.1261 | 72331.8089 |  | 57.1901 | 177114.0308 |  | 229.3956 | 344972.9244 |  | 236393 | 578757.2535 |  | 236393 | 844711.9746 |  | 236393 | 1127271.4047 |  | 236393 | 1375485.3403 |  | 236393 | 1596895.7787 |  | 236393 | 1872485.8882
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 12181.9908 | C_100 - C this iteration | iteration | 73055.127 | C_100 - C this iteration | iteration | 178885.1711 | C_100 - C this iteration | iteration | 348422.6537 | C_100 - C this iteration | iteration | 584544.826 | C_100 - C this iteration | iteration | 853159.0943 | C_100 - C this iteration | iteration | 1138544.1187 | C_100 - C this iteration | iteration | 1389240.1937 | C_100 - C this iteration | iteration | 1612864.7365 | C_100 - C this iteration | iteration | 1891210.7471 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.158 |  |  | 89.2123 |  |  | 84.3527 |  |  | 68.0589 |  |  | 27.9078 |  |  | -42.4791 |  |  | -146.0766 |  |  | -261.5764 |  |  | -383.9362 |  |  | -561.7036
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.158 |  |  | 29.2123 |  |  | 24.3527 |  |  | 8.0589 |  |  | -32.0922 |  |  | -102.4791 |  |  | -206.0766 |  |  | -321.5764 |  |  | -443.9362 |  |  | -621.7036
[13 empty] | Press drop ratio this iteration |  |  | 0.3345 |  |  | 0.32745 |  |  | 0.2887 |  |  | 0.11841 |  |  | -1.1499 |  |  | 2.4125 |  |  | 1.4107 |  |  | 1.2294 |  |  | 1.1563 |  |  | 1.1068
[13 empty] | Expansion factor | 12 |  | 0.82579 |  |  | 0.8295 |  |  | 0.84825 |  |  | 0.93688 |  |  | 1.632 |  |  | -0.40542 |  |  | 0.1158 |  |  | 0.13848 |  |  | 0.34734 |  |  | 0.020576
[13 empty] | C Non choked w/ reducers | 7 |  | 4.9219 |  |  | 30.0337 |  |  | 81.1894 |  |  | 278.7288 |  |  | #NUM! |  |  | 579.5213 |  |  | -1066.8894 |  |  | -690.9197 |  |  | -255.722 |  |  | -4736.4938
[13 empty] | C Choked w/ reducers | 7 |  | 4.4053 |  |  | 26.7129 |  |  | 69.667 |  |  | 170.3658 |  |  | 716.5256 |  |  | -723.2926 |  |  | -301.6686 |  |  | -230.6192 |  |  | -186.3362 |  |  | -250.456
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.9219 |  |  | 30.0337 |  |  | 81.1894 |  |  | 278.7288 |  |  | #NUM! |  |  | -723.2926 |  |  | -301.6686 |  |  | -230.6192 |  |  | -186.3362 |  |  | -250.456
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.19189 | 12181.9908 |  | 18.4337 | 73055.127 |  | 58.1894 | 178885.1711 |  | 239.3288 | 348422.6537 |  | 236393 | 584544.826 |  | 236393 | 853159.0943 |  | 236393 | 1138544.1187 |  | 236393 | 1389240.1937 |  | 236393 | 1612864.7365 |  | 236393 | 1891210.7471
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 12425.6306 | C_100 - C this iteration | iteration | 73785.6783 | C_100 - C this iteration | iteration | 180674.0228 | C_100 - C this iteration | iteration | 351906.8802 | C_100 - C this iteration | iteration | 590390.2743 | C_100 - C this iteration | iteration | 861690.6853 | C_100 - C this iteration | iteration | 1149929.5599 | C_100 - C this iteration | iteration | 1403132.5957 | C_100 - C this iteration | iteration | 1628993.3838 | C_100 - C this iteration | iteration | 1910122.8546 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1569 |  |  | 89.1928 |  |  | 84.2355 |  |  | 67.6141 |  |  | 26.6561 |  |  | -45.1457 |  |  | -150.8255 |  |  | -268.6468 |  |  | -393.4661 |  |  | -574.8065
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1569 |  |  | 29.1928 |  |  | 24.2355 |  |  | 7.6141 |  |  | -33.3439 |  |  | -105.1457 |  |  | -210.8255 |  |  | -328.6468 |  |  | -453.4661 |  |  | -634.8065
[13 empty] | Press drop ratio this iteration |  |  | 0.33449 |  |  | 0.3273 |  |  | 0.28771 |  |  | 0.11261 |  |  | -1.2509 |  |  | 2.329 |  |  | 1.3978 |  |  | 1.2233 |  |  | 1.1525 |  |  | 1.1044
[13 empty] | Expansion factor | 12 |  | 0.82579 |  |  | 0.82958 |  |  | 0.84877 |  |  | 0.93997 |  |  | 1.6875 |  |  | -0.35682 |  |  | 0.1239 |  |  | 0.14272 |  |  | 0.34947 |  |  | 0.02273
[13 empty] | C Non choked w/ reducers | 7 |  | 5.0204 |  |  | 30.3447 |  |  | 82.2061 |  |  | 289.6164 |  |  | #NUM! |  |  | 636.8703 |  |  | -979.8586 |  |  | -660.9465 |  |  | -250.8939 |  |  | -4236.3283
[13 empty] | C Choked w/ reducers | 7 |  | 4.4934 |  |  | 26.9859 |  |  | 70.4615 |  |  | 173.2012 |  |  | 757.6755 |  |  | -687.3767 |  |  | -295.092 |  |  | -226.7951 |  |  | -183.6414 |  |  | -247.1942
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.0204 |  |  | 30.3447 |  |  | 82.2061 |  |  | 289.6164 |  |  | #NUM! |  |  | -687.3767 |  |  | -295.092 |  |  | -226.7951 |  |  | -183.6414 |  |  | -247.1942
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.29043 | 12425.6306 |  | 18.7447 | 73785.6783 |  | 59.2061 | 180674.0228 |  | 250.2164 | 351906.8802 |  | 236393 | 590390.2743 |  | 236393 | 861690.6853 |  | 236393 | 1149929.5599 |  | 236393 | 1403132.5957 |  | 236393 | 1628993.3838 |  | 236393 | 1910122.8546
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 12674.1432 | C_100 - C this iteration | iteration | 74523.5351 | C_100 - C this iteration | iteration | 182480.763 | C_100 - C this iteration | iteration | 355425.949 | C_100 - C this iteration | iteration | 596294.177 | C_100 - C this iteration | iteration | 870307.5921 | C_100 - C this iteration | iteration | 1161428.8555 | C_100 - C this iteration | iteration | 1417163.9216 | C_100 - C this iteration | iteration | 1645283.3177 | C_100 - C this iteration | iteration | 1929224.0831 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1558 |  |  | 89.1728 |  |  | 84.1159 |  |  | 67.1605 |  |  | 25.3791 |  |  | -47.8658 |  |  | -155.6698 |  |  | -275.8593 |  |  | -403.1874 |  |  | -588.1729
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1558 |  |  | 29.1728 |  |  | 24.1159 |  |  | 7.1605 |  |  | -34.6209 |  |  | -107.8658 |  |  | -215.6698 |  |  | -335.8593 |  |  | -463.1874 |  |  | -648.1729
[13 empty] | Press drop ratio this iteration |  |  | 0.33449 |  |  | 0.32715 |  |  | 0.2867 |  |  | 0.10662 |  |  | -1.3641 |  |  | 2.2535 |  |  | 1.3854 |  |  | 1.2175 |  |  | 1.1488 |  |  | 1.102
[13 empty] | Expansion factor | 12 |  | 0.8258 |  |  | 0.82966 |  |  | 0.8493 |  |  | 0.94317 |  |  | 1.7497 |  |  | -0.31282 |  |  | 0.13166 |  |  | 0.14681 |  |  | 0.35155 |  |  | 0.024829
[13 empty] | C Non choked w/ reducers | 7 |  | 5.1209 |  |  | 30.6592 |  |  | 83.2407 |  |  | 301.6286 |  |  | #NUM! |  |  | 703.5189 |  |  | -906.3756 |  |  | -633.4951 |  |  | -246.2261 |  |  | -3832.0735
[13 empty] | C Choked w/ reducers | 7 |  | 4.5834 |  |  | 27.2619 |  |  | 71.2673 |  |  | 176.1149 |  |  | 803.7554 |  |  | -654.7972 |  |  | -288.7681 |  |  | -223.074 |  |  | -181.0057 |  |  | -243.9925
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.1209 |  |  | 30.6592 |  |  | 83.2407 |  |  | 301.6286 |  |  | #NUM! |  |  | -654.7972 |  |  | -288.7681 |  |  | -223.074 |  |  | -181.0057 |  |  | -243.9925
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.39094 | 12674.1432 |  | 19.0592 | 74523.5351 |  | 60.2407 | 182480.763 |  | 262.2286 | 355425.949 |  | 236393 | 596294.177 |  | 236393 | 870307.5921 |  | 236393 | 1161428.8555 |  | 236393 | 1417163.9216 |  | 236393 | 1645283.3177 |  | 236393 | 1929224.0831
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 12927.6261 | C_100 - C this iteration | iteration | 75268.7704 | C_100 - C this iteration | iteration | 184305.5707 | C_100 - C this iteration | iteration | 358980.2085 | C_100 - C this iteration | iteration | 602257.1188 | C_100 - C this iteration | iteration | 879010.6681 | C_100 - C this iteration | iteration | 1173043.1441 | C_100 - C this iteration | iteration | 1431335.5608 | C_100 - C this iteration | iteration | 1661736.1508 | C_100 - C this iteration | iteration | 1948516.324 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1546 |  |  | 89.1525 |  |  | 83.9939 |  |  | 66.6977 |  |  | 24.0765 |  |  | -50.6406 |  |  | -160.6115 |  |  | -283.2168 |  |  | -413.1042 |  |  | -601.8079
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1546 |  |  | 29.1525 |  |  | 23.9939 |  |  | 6.6977 |  |  | -35.9235 |  |  | -110.6406 |  |  | -220.6115 |  |  | -343.2168 |  |  | -473.1042 |  |  | -661.8079
[13 empty] | Press drop ratio this iteration |  |  | 0.33448 |  |  | 0.327 |  |  | 0.28566 |  |  | 0.10042 |  |  | -1.4921 |  |  | 2.1848 |  |  | 1.3736 |  |  | 1.2119 |  |  | 1.1452 |  |  | 1.0997
[13 empty] | Expansion factor | 12 |  | 0.8258 |  |  | 0.82974 |  |  | 0.84984 |  |  | 0.94647 |  |  | 1.82 |  |  | -0.27281 |  |  | 0.1391 |  |  | 0.15077 |  |  | 0.35356 |  |  | 0.026875
[13 empty] | C Non choked w/ reducers | 7 |  | 5.2235 |  |  | 30.9771 |  |  | 84.2937 |  |  | 314.9816 |  |  | #NUM! |  |  | 782.141 |  |  | -843.4783 |  |  | -608.254 |  |  | -241.7103 |  |  | -3498.5039
[13 empty] | C Choked w/ reducers | 7 |  | 4.6751 |  |  | 27.5408 |  |  | 72.0846 |  |  | 179.1103 |  |  | 855.7129 |  |  | -625.1072 |  |  | -282.6821 |  |  | -219.4517 |  |  | -178.4271 |  |  | -240.849
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.2235 |  |  | 30.9771 |  |  | 84.2937 |  |  | 314.9816 |  |  | #NUM! |  |  | -625.1072 |  |  | -282.6821 |  |  | -219.4517 |  |  | -178.4271 |  |  | -240.849
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.49346 | 12927.6261 |  | 19.3771 | 75268.7704 |  | 61.2937 | 184305.5707 |  | 275.5816 | 358980.2085 |  | 236393 | 602257.1188 |  | 236393 | 879010.6681 |  | 236393 | 1173043.1441 |  | 236393 | 1431335.5608 |  | 236393 | 1661736.1508 |  | 236393 | 1948516.324
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 13186.1786 | C_100 - C this iteration | iteration | 76021.4581 | C_100 - C this iteration | iteration | 186148.6264 | C_100 - C this iteration | iteration | 362570.0106 | C_100 - C this iteration | iteration | 608279.69 | C_100 - C this iteration | iteration | 887800.7747 | C_100 - C this iteration | iteration | 1184773.5755 | C_100 - C this iteration | iteration | 1445648.9164 | C_100 - C this iteration | iteration | 1678353.5123 | C_100 - C this iteration | iteration | 1968001.4872 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1533 |  |  | 89.1317 |  |  | 83.8695 |  |  | 66.2256 |  |  | 22.7477 |  |  | -53.4712 |  |  | -165.6525 |  |  | -290.7222 |  |  | -423.2203 |  |  | -615.7169
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1533 |  |  | 29.1317 |  |  | 23.8695 |  |  | 6.2256 |  |  | -37.2523 |  |  | -113.4712 |  |  | -225.6525 |  |  | -350.7222 |  |  | -483.2203 |  |  | -675.7169
[13 empty] | Press drop ratio this iteration |  |  | 0.33447 |  |  | 0.32684 |  |  | 0.2846 |  |  | 0.094005 |  |  | -1.6376 |  |  | 2.1221 |  |  | 1.3622 |  |  | 1.2064 |  |  | 1.1418 |  |  | 1.0974
[13 empty] | Expansion factor | 12 |  | 0.82581 |  |  | 0.82982 |  |  | 0.8504 |  |  | 0.94989 |  |  | 1.9 |  |  | -0.23627 |  |  | 0.14622 |  |  | 0.1546 |  |  | 0.35552 |  |  | 0.028868
[13 empty] | C Non choked w/ reducers | 7 |  | 5.328 |  |  | 31.2986 |  |  | 85.3656 |  |  | 329.9556 |  |  | #NUM! |  |  | 876.5188 |  |  | -789.0104 |  |  | -584.9613 |  |  | -237.3387 |  |  | -3218.528
[13 empty] | C Choked w/ reducers | 7 |  | 4.7687 |  |  | 27.8227 |  |  | 72.9134 |  |  | 182.191 |  |  | 914.7553 |  |  | -597.9361 |  |  | -276.8206 |  |  | -215.9242 |  |  | -175.9039 |  |  | -237.7623
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.328 |  |  | 31.2986 |  |  | 85.3656 |  |  | 329.9556 |  |  | #NUM! |  |  | -597.9361 |  |  | -276.8206 |  |  | -215.9242 |  |  | -175.9039 |  |  | -237.7623
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.59805 | 13186.1786 |  | 19.6986 | 76021.4581 |  | 62.3656 | 186148.6264 |  | 290.5556 | 362570.0106 |  | 236393 | 608279.69 |  | 236393 | 887800.7747 |  | 236393 | 1184773.5755 |  | 236393 | 1445648.9164 |  | 236393 | 1678353.5123 |  | 236393 | 1968001.4872
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 13449.9022 | C_100 - C this iteration | iteration | 76781.6727 | C_100 - C this iteration | iteration | 188010.1126 | C_100 - C this iteration | iteration | 366195.7107 | C_100 - C this iteration | iteration | 614362.4869 | C_100 - C this iteration | iteration | 896678.7825 | C_100 - C this iteration | iteration | 1196621.3113 | C_100 - C this iteration | iteration | 1460105.4056 | C_100 - C this iteration | iteration | 1695137.0475 | C_100 - C this iteration | iteration | 1987681.5021 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1521 |  |  | 89.1105 |  |  | 83.7425 |  |  | 65.744 |  |  | 21.3923 |  |  | -56.3587 |  |  | -170.7948 |  |  | -298.3784 |  |  | -433.5398 |  |  | -629.9055
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1521 |  |  | 29.1105 |  |  | 23.7425 |  |  | 5.744 |  |  | -38.6077 |  |  | -116.3587 |  |  | -230.7948 |  |  | -358.3784 |  |  | -493.5398 |  |  | -689.9055
[13 empty] | Press drop ratio this iteration |  |  | 0.33446 |  |  | 0.32668 |  |  | 0.28352 |  |  | 0.087369 |  |  | -1.8048 |  |  | 2.0646 |  |  | 1.3513 |  |  | 1.2011 |  |  | 1.1384 |  |  | 1.0953
[13 empty] | Expansion factor | 12 |  | 0.82581 |  |  | 0.8299 |  |  | 0.85097 |  |  | 0.95343 |  |  | 1.9919 |  |  | -0.20278 |  |  | 0.15306 |  |  | 0.15831 |  |  | 0.35743 |  |  | 0.03081
[13 empty] | C Non choked w/ reducers | 7 |  | 5.4347 |  |  | 31.6236 |  |  | 86.457 |  |  | 346.9208 |  |  | #NUM! |  |  | 992.1872 |  |  | -741.3647 |  |  | -563.3947 |  |  | -233.1039 |  |  | -2980.1538
[13 empty] | C Choked w/ reducers | 7 |  | 4.8641 |  |  | 28.1076 |  |  | 73.7542 |  |  | 185.3608 |  |  | 982.4447 |  |  | -572.9744 |  |  | -271.1708 |  |  | -212.4875 |  |  | -173.434 |  |  | -234.7308
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.4347 |  |  | 31.6236 |  |  | 86.457 |  |  | 346.9208 |  |  | #NUM! |  |  | -572.9744 |  |  | -271.1708 |  |  | -212.4875 |  |  | -173.434 |  |  | -234.7308
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.70473 | 13449.9022 |  | 20.0236 | 76781.6727 |  | 63.457 | 188010.1126 |  | 307.5208 | 366195.7107 |  | 236393 | 614362.4869 |  | 236393 | 896678.7825 |  | 236393 | 1196621.3113 |  | 236393 | 1460105.4056 |  | 236393 | 1695137.0475 |  | 236393 | 1987681.5021
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 13718.9002 | C_100 - C this iteration | iteration | 77549.4894 | C_100 - C this iteration | iteration | 189890.2138 | C_100 - C this iteration | iteration | 369857.6678 | C_100 - C this iteration | iteration | 620506.1118 | C_100 - C this iteration | iteration | 905645.5703 | C_100 - C this iteration | iteration | 1208587.5244 | C_100 - C this iteration | iteration | 1474706.4597 | C_100 - C this iteration | iteration | 1712088.4179 | C_100 - C this iteration | iteration | 2007558.3171 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1507 |  |  | 89.0889 |  |  | 83.613 |  |  | 65.2527 |  |  | 20.0095 |  |  | -59.3042 |  |  | -176.0405 |  |  | -306.1885 |  |  | -444.0667 |  |  | -644.3794
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1507 |  |  | 29.0889 |  |  | 23.613 |  |  | 5.2527 |  |  | -39.9905 |  |  | -119.3042 |  |  | -236.0405 |  |  | -366.1885 |  |  | -504.0667 |  |  | -704.3794
[13 empty] | Press drop ratio this iteration |  |  | 0.33445 |  |  | 0.32652 |  |  | 0.28241 |  |  | 0.080498 |  |  | -1.9986 |  |  | 2.0117 |  |  | 1.3408 |  |  | 1.196 |  |  | 1.1351 |  |  | 1.0931
[13 empty] | Expansion factor | 12 |  | 0.82582 |  |  | 0.82999 |  |  | 0.85155 |  |  | 0.95709 |  |  | 2.0984 |  |  | -0.17197 |  |  | 0.15962 |  |  | 0.1619 |  |  | 0.35928 |  |  | 0.032703
[13 empty] | C Non choked w/ reducers | 7 |  | 5.5436 |  |  | 31.9523 |  |  | 87.5685 |  |  | 366.3783 |  |  | #NUM! |  |  | 1137.5869 |  |  | -699.3187 |  |  | -543.3649 |  |  | -228.9993 |  |  | -2774.7191
[13 empty] | C Choked w/ reducers | 7 |  | 4.9615 |  |  | 28.3955 |  |  | 74.6071 |  |  | 188.6239 |  |  | 1060.8388 |  |  | -549.961 |  |  | -265.7213 |  |  | -209.1381 |  |  | -171.0159 |  |  | -231.7529
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.5436 |  |  | 31.9523 |  |  | 87.5685 |  |  | 366.3783 |  |  | #NUM! |  |  | -549.961 |  |  | -265.7213 |  |  | -209.1381 |  |  | -171.0159 |  |  | -231.7529
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.81355 | 13718.9002 |  | 20.3523 | 77549.4894 |  | 64.5685 | 189890.2138 |  | 326.9783 | 369857.6678 |  | 236393 | 620506.1118 |  | 236393 | 905645.5703 |  | 236393 | 1208587.5244 |  | 236393 | 1474706.4597 |  | 236393 | 1712088.4179 |  | 236393 | 2007558.3171
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 13993.2783 | C_100 - C this iteration | iteration | 78324.9843 | C_100 - C this iteration | iteration | 191789.1159 | C_100 - C this iteration | iteration | 373556.2445 | C_100 - C this iteration | iteration | 626711.1729 | C_100 - C this iteration | iteration | 914702.026 | C_100 - C this iteration | iteration | 1220673.3996 | C_100 - C this iteration | iteration | 1489453.5242 | C_100 - C this iteration | iteration | 1729209.3021 | C_100 - C this iteration | iteration | 2027633.9003 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1494 |  |  | 89.0669 |  |  | 83.4809 |  |  | 64.7516 |  |  | 18.599 |  |  | -62.309 |  |  | -181.3917 |  |  | -314.1557 |  |  | -454.8051 |  |  | -659.1441
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1494 |  |  | 29.0669 |  |  | 23.4809 |  |  | 4.7516 |  |  | -41.401 |  |  | -122.309 |  |  | -241.3917 |  |  | -374.1557 |  |  | -514.8051 |  |  | -719.1441
[13 empty] | Press drop ratio this iteration |  |  | 0.33444 |  |  | 0.32635 |  |  | 0.28127 |  |  | 0.073382 |  |  | -2.226 |  |  | 1.9629 |  |  | 1.3308 |  |  | 1.191 |  |  | 1.1319 |  |  | 1.091
[13 empty] | Expansion factor | 12 |  | 0.82582 |  |  | 0.83007 |  |  | 0.85215 |  |  | 0.96088 |  |  | 2.2234 |  |  | -0.14355 |  |  | 0.16592 |  |  | 0.16539 |  |  | 0.36108 |  |  | 0.034549
[13 empty] | C Non choked w/ reducers | 7 |  | 5.6546 |  |  | 32.2847 |  |  | 88.7006 |  |  | 389.0276 |  |  | #NUM! |  |  | 1326.2644 |  |  | -661.9263 |  |  | -524.7092 |  |  | -225.0185 |  |  | -2595.811
[13 empty] | C Choked w/ reducers | 7 |  | 5.0608 |  |  | 28.6866 |  |  | 75.4724 |  |  | 191.9846 |  |  | 1152.7046 |  |  | -528.6746 |  |  | -260.4613 |  |  | -205.8727 |  |  | -168.6478 |  |  | -228.8273
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.6546 |  |  | 32.2847 |  |  | 88.7006 |  |  | 389.0276 |  |  | #NUM! |  |  | -528.6746 |  |  | -260.4613 |  |  | -205.8727 |  |  | -168.6478 |  |  | -228.8273
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.92456 | 13993.2783 |  | 20.6847 | 78324.9843 |  | 65.7006 | 191789.1159 |  | 349.6276 | 373556.2445 |  | 236393 | 626711.1729 |  | 236393 | 914702.026 |  | 236393 | 1220673.3996 |  | 236393 | 1489453.5242 |  | 236393 | 1729209.3021 |  | 236393 | 2027633.9003
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 14273.1438 | C_100 - C this iteration | iteration | 79108.2342 | C_100 - C this iteration | iteration | 193707.0071 | C_100 - C this iteration | iteration | 377291.8069 | C_100 - C this iteration | iteration | 632978.2846 | C_100 - C this iteration | iteration | 923849.0463 | C_100 - C this iteration | iteration | 1232880.1336 | C_100 - C this iteration | iteration | 1504348.0595 | C_100 - C this iteration | iteration | 1746501.3951 | C_100 - C this iteration | iteration | 2047910.2393 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1479 |  |  | 89.0444 |  |  | 83.3462 |  |  | 64.2404 |  |  | 17.1601 |  |  | -65.3741 |  |  | -186.8503 |  |  | -322.2829 |  |  | -465.7594 |  |  | -674.2056
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1479 |  |  | 29.0444 |  |  | 23.3462 |  |  | 4.2404 |  |  | -42.8399 |  |  | -125.3741 |  |  | -246.8503 |  |  | -382.2829 |  |  | -525.7594 |  |  | -734.2056
[13 empty] | Press drop ratio this iteration |  |  | 0.33443 |  |  | 0.32618 |  |  | 0.28011 |  |  | 0.066008 |  |  | -2.4965 |  |  | 1.9178 |  |  | 1.3211 |  |  | 1.1862 |  |  | 1.1288 |  |  | 1.089
[13 empty] | Expansion factor | 12 |  | 0.82583 |  |  | 0.83016 |  |  | 0.85276 |  |  | 0.96481 |  |  | 2.372 |  |  | -0.11725 |  |  | 0.17198 |  |  | 0.16876 |  |  | 0.36283 |  |  | 0.036348
[13 empty] | C Non choked w/ reducers | 7 |  | 5.7678 |  |  | 32.6208 |  |  | 89.8539 |  |  | 415.8794 |  |  | #NUM! |  |  | 1581.4257 |  |  | -628.4433 |  |  | -507.2873 |  |  | -221.1557 |  |  | -2438.58
[13 empty] | C Choked w/ reducers | 7 |  | 5.1621 |  |  | 28.9807 |  |  | 76.3504 |  |  | 195.4475 |  |  | 1261.8528 |  |  | -508.926 |  |  | -255.3806 |  |  | -202.6878 |  |  | -166.3281 |  |  | -225.9526
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.7678 |  |  | 32.6208 |  |  | 89.8539 |  |  | 415.8794 |  |  | #NUM! |  |  | -508.926 |  |  | -255.3806 |  |  | -202.6878 |  |  | -166.3281 |  |  | -225.9526
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.0378 | 14273.1438 |  | 21.0208 | 79108.2342 |  | 66.8539 | 193707.0071 |  | 376.4794 | 377291.8069 |  | 236393 | 632978.2846 |  | 236393 | 923849.0463 |  | 236393 | 1232880.1336 |  | 236393 | 1504348.0595 |  | 236393 | 1746501.3951 |  | 236393 | 2047910.2393
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 14558.6067 | C_100 - C this iteration | iteration | 79899.3165 | C_100 - C this iteration | iteration | 195644.0771 | C_100 - C this iteration | iteration | 381064.725 | C_100 - C this iteration | iteration | 639308.0675 | C_100 - C this iteration | iteration | 933087.5367 | C_100 - C this iteration | iteration | 1245208.935 | C_100 - C this iteration | iteration | 1519391.5401 | C_100 - C this iteration | iteration | 1763966.4091 | C_100 - C this iteration | iteration | 2068389.3417 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1464 |  |  | 89.0215 |  |  | 83.2087 |  |  | 63.7189 |  |  | 15.6923 |  |  | -68.5009 |  |  | -192.4188 |  |  | -330.5735 |  |  | -476.9339 |  |  | -689.5699
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1464 |  |  | 29.0215 |  |  | 23.2087 |  |  | 3.7189 |  |  | -44.3077 |  |  | -128.5009 |  |  | -252.4188 |  |  | -390.5735 |  |  | -536.9339 |  |  | -749.5699
[13 empty] | Press drop ratio this iteration |  |  | 0.33442 |  |  | 0.32601 |  |  | 0.27892 |  |  | 0.058364 |  |  | -2.8235 |  |  | 1.8759 |  |  | 1.3118 |  |  | 1.1815 |  |  | 1.1258 |  |  | 1.087
[13 empty] | Expansion factor | 12 |  | 0.82583 |  |  | 0.83025 |  |  | 0.85339 |  |  | 0.96889 |  |  | 2.5518 |  |  | -0.09284 |  |  | 0.1778 |  |  | 0.17203 |  |  | 0.36454 |  |  | 0.038103
[13 empty] | C Non choked w/ reducers | 7 |  | 5.8833 |  |  | 32.9607 |  |  | 91.0293 |  |  | 448.4604 |  |  | #NUM! |  |  | 1946.4217 |  |  | -598.2766 |  |  | -490.9774 |  |  | -217.4051 |  |  | -2299.2911
[13 empty] | C Choked w/ reducers | 7 |  | 5.2654 |  |  | 29.2781 |  |  | 77.2413 |  |  | 199.0175 |  |  | 1393.6807 |  |  | -490.5529 |  |  | -250.47 |  |  | -199.5806 |  |  | -164.0554 |  |  | -223.1273
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.8833 |  |  | 32.9607 |  |  | 91.0293 |  |  | 448.4604 |  |  | #NUM! |  |  | -490.5529 |  |  | -250.47 |  |  | -199.5806 |  |  | -164.0554 |  |  | -223.1273
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.1533 | 14558.6067 |  | 21.3607 | 79899.3165 |  | 68.0293 | 195644.0771 |  | 409.0604 | 381064.725 |  | 236393 | 639308.0675 |  | 236393 | 933087.5367 |  | 236393 | 1245208.935 |  | 236393 | 1519391.5401 |  | 236393 | 1763966.4091 |  | 236393 | 2068389.3417
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 14849.7788 | C_100 - C this iteration | iteration | 80698.3097 | C_100 - C this iteration | iteration | 197600.5179 | C_100 - C this iteration | iteration | 384875.3722 | C_100 - C this iteration | iteration | 645701.1481 | C_100 - C this iteration | iteration | 942418.4121 | C_100 - C this iteration | iteration | 1257661.0243 | C_100 - C this iteration | iteration | 1534585.4555 | C_100 - C this iteration | iteration | 1781606.0732 | C_100 - C this iteration | iteration | 2089073.2351 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1448 |  |  | 88.9981 |  |  | 83.0685 |  |  | 63.1869 |  |  | 14.195 |  |  | -71.6904 |  |  | -198.0991 |  |  | -339.0308 |  |  | -488.333 |  |  | -705.2429
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1448 |  |  | 28.9981 |  |  | 23.0685 |  |  | 3.1869 |  |  | -45.805 |  |  | -131.6904 |  |  | -258.0991 |  |  | -399.0308 |  |  | -548.333 |  |  | -765.2429
[13 empty] | Press drop ratio this iteration |  |  | 0.3344 |  |  | 0.32583 |  |  | 0.2777 |  |  | 0.050436 |  |  | -3.2268 |  |  | 1.8369 |  |  | 1.3029 |  |  | 1.177 |  |  | 1.1229 |  |  | 1.0851
[13 empty] | Expansion factor | 12 |  | 0.82584 |  |  | 0.83034 |  |  | 0.85403 |  |  | 0.97311 |  |  | 2.7734 |  |  | -0.070138 |  |  | 0.1834 |  |  | 0.17521 |  |  | 0.36619 |  |  | 0.039814
[13 empty] | C Non choked w/ reducers | 7 |  | 6.0011 |  |  | 33.3044 |  |  | 92.2272 |  |  | 489.2121 |  |  | #NUM! |  |  | 2512.6768 |  |  | -570.9476 |  |  | -475.6733 |  |  | -213.7618 |  |  | -2175.0209
[13 empty] | C Choked w/ reducers | 7 |  | 5.3708 |  |  | 29.5786 |  |  | 78.1454 |  |  | 202.7 |  |  | 1556.0945 |  |  | -473.415 |  |  | -245.7209 |  |  | -196.548 |  |  | -161.8282 |  |  | -220.3503
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.0011 |  |  | 33.3044 |  |  | 92.2272 |  |  | 489.2121 |  |  | #NUM! |  |  | -473.415 |  |  | -245.7209 |  |  | -196.548 |  |  | -161.8282 |  |  | -220.3503
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.2711 | 14849.7788 |  | 21.7044 | 80698.3097 |  | 69.2272 | 197600.5179 |  | 449.8121 | 384875.3722 |  | 236393 | 645701.1481 |  | 236393 | 942418.4121 |  | 236393 | 1257661.0243 |  | 236393 | 1534585.4555 |  | 236393 | 1781606.0732 |  | 236393 | 2089073.2351
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 15146.7744 | C_100 - C this iteration | iteration | 81505.2928 | C_100 - C this iteration | iteration | 199576.5231 | C_100 - C this iteration | iteration | 388724.126 | C_100 - C this iteration | iteration | 652158.1596 | C_100 - C this iteration | iteration | 951842.5962 | C_100 - C this iteration | iteration | 1270237.6345 | C_100 - C this iteration | iteration | 1549931.31 | C_100 - C this iteration | iteration | 1799422.1339 | C_100 - C this iteration | iteration | 2109963.9674 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1432 |  |  | 88.9743 |  |  | 82.9254 |  |  | 62.6442 |  |  | 12.6676 |  |  | -74.9441 |  |  | -203.8936 |  |  | -347.658 |  |  | -499.9612 |  |  | -721.231
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1432 |  |  | 28.9743 |  |  | 22.9254 |  |  | 2.6442 |  |  | -47.3324 |  |  | -134.9441 |  |  | -263.8936 |  |  | -407.658 |  |  | -559.9612 |  |  | -781.231
[13 empty] | Press drop ratio this iteration |  |  | 0.33439 |  |  | 0.32565 |  |  | 0.27646 |  |  | 0.04221 |  |  | -3.7365 |  |  | 1.8006 |  |  | 1.2943 |  |  | 1.1726 |  |  | 1.12 |  |  | 1.0832
[13 empty] | Expansion factor | 12 |  | 0.82585 |  |  | 0.83044 |  |  | 0.85468 |  |  | 0.9775 |  |  | 3.0535 |  |  | -0.04897 |  |  | 0.1888 |  |  | 0.17829 |  |  | 0.36781 |  |  | 0.041483
[13 empty] | C Non choked w/ reducers | 7 |  | 6.1213 |  |  | 33.652 |  |  | 93.4485 |  |  | 542.3416 |  |  | #NUM! |  |  | 3511.9045 |  |  | -546.066 |  |  | -461.282 |  |  | -210.2209 |  |  | -2063.4488
[13 empty] | C Choked w/ reducers | 7 |  | 5.4783 |  |  | 29.8824 |  |  | 79.063 |  |  | 206.5005 |  |  | 1761.1582 |  |  | -457.3903 |  |  | -241.1251 |  |  | -193.5873 |  |  | -159.645 |  |  | -217.6203
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.1213 |  |  | 33.652 |  |  | 93.4485 |  |  | 542.3416 |  |  | #NUM! |  |  | -457.3903 |  |  | -241.1251 |  |  | -193.5873 |  |  | -159.645 |  |  | -217.6203
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.3913 | 15146.7744 |  | 22.052 | 81505.2928 |  | 70.4485 | 199576.5231 |  | 502.9416 | 388724.126 |  | 236393 | 652158.1596 |  | 236393 | 951842.5962 |  | 236393 | 1270237.6345 |  | 236393 | 1549931.31 |  | 236393 | 1799422.1339 |  | 236393 | 2109963.9674
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 15449.7099 | C_100 - C this iteration | iteration | 82320.3457 | C_100 - C this iteration | iteration | 201572.2883 | C_100 - C this iteration | iteration | 392611.3672 | C_100 - C this iteration | iteration | 658679.7412 | C_100 - C this iteration | iteration | 961361.0222 | C_100 - C this iteration | iteration | 1282940.0109 | C_100 - C this iteration | iteration | 1565430.6231 | C_100 - C this iteration | iteration | 1817416.3553 | C_100 - C this iteration | iteration | 2131063.6071 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1415 |  |  | 88.9499 |  |  | 82.7795 |  |  | 62.0907 |  |  | 11.1095 |  |  | -78.2632 |  |  | -209.8046 |  |  | -356.4586 |  |  | -511.8232 |  |  | -737.5405
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1415 |  |  | 28.9499 |  |  | 22.7795 |  |  | 2.0907 |  |  | -48.8905 |  |  | -138.2632 |  |  | -269.8046 |  |  | -416.4586 |  |  | -571.8232 |  |  | -797.5405
[13 empty] | Press drop ratio this iteration |  |  | 0.33438 |  |  | 0.32546 |  |  | 0.27518 |  |  | 0.033671 |  |  | -4.4008 |  |  | 1.7666 |  |  | 1.286 |  |  | 1.1683 |  |  | 1.1172 |  |  | 1.0814
[13 empty] | Expansion factor | 12 |  | 0.82585 |  |  | 0.83054 |  |  | 0.85535 |  |  | 0.98205 |  |  | 3.4186 |  |  | -0.02919 |  |  | 0.19399 |  |  | 0.18127 |  |  | 0.36938 |  |  | 0.043111
[13 empty] | C Non choked w/ reducers | 7 |  | 6.2439 |  |  | 34.0035 |  |  | 94.694 |  |  | 615.9021 |  |  | #NUM! |  |  | 5752.7094 |  |  | -523.3099 |  |  | -447.7216 |  |  | -206.7777 |  |  | -1962.709
[13 empty] | C Choked w/ reducers | 7 |  | 5.588 |  |  | 30.1895 |  |  | 79.9944 |  |  | 210.4249 |  |  | 2028.2411 |  |  | -442.3726 |  |  | -236.675 |  |  | -190.6959 |  |  | -157.5045 |  |  | -214.936
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.2439 |  |  | 34.0035 |  |  | 94.694 |  |  | 615.9021 |  |  | #NUM! |  |  | -442.3726 |  |  | -236.675 |  |  | -190.6959 |  |  | -157.5045 |  |  | -214.936
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5139 | 15449.7099 |  | 22.4035 | 82320.3457 |  | 71.694 | 201572.2883 |  | 576.5021 | 392611.3672 |  | 236393 | 658679.7412 |  | 236393 | 961361.0222 |  | 236393 | 1282940.0109 |  | 236393 | 1565430.6231 |  | 236393 | 1817416.3553 |  | 236393 | 2131063.6071
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 15758.7041 | C_100 - C this iteration | iteration | 83143.5492 | C_100 - C this iteration | iteration | 203588.0112 | C_100 - C this iteration | iteration | 396537.4809 | C_100 - C this iteration | iteration | 665266.5386 | C_100 - C this iteration | iteration | 970974.6324 | C_100 - C this iteration | iteration | 1295769.411 | C_100 - C this iteration | iteration | 1581084.9294 | C_100 - C this iteration | iteration | 1835590.5188 | C_100 - C this iteration | iteration | 2152374.2432 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1398 |  |  | 88.9251 |  |  | 82.6307 |  |  | 61.526 |  |  | 9.5201 |  |  | -81.649 |  |  | -215.8344 |  |  | -365.4362 |  |  | -523.9235 |  |  | -754.1778
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1398 |  |  | 28.9251 |  |  | 22.6307 |  |  | 1.526 |  |  | -50.4799 |  |  | -141.649 |  |  | -275.8344 |  |  | -425.4362 |  |  | -583.9235 |  |  | -814.1778
[13 empty] | Press drop ratio this iteration |  |  | 0.33437 |  |  | 0.32527 |  |  | 0.27388 |  |  | 0.024802 |  |  | -5.3025 |  |  | 1.7349 |  |  | 1.278 |  |  | 1.1642 |  |  | 1.1145 |  |  | 1.0796
[13 empty] | Expansion factor | 12 |  | 0.82586 |  |  | 0.83063 |  |  | 0.85604 |  |  | 0.98678 |  |  | 3.9142 |  |  | -0.010669 |  |  | 0.199 |  |  | 0.18417 |  |  | 0.3709 |  |  | 0.044699
[13 empty] | C Non choked w/ reducers | 7 |  | 6.369 |  |  | 34.359 |  |  | 95.9643 |  |  | 727.9482 |  |  | #NUM! |  |  | 15375.6473 |  |  | -502.412 |  |  | -434.9199 |  |  | -203.4281 |  |  | -1871.2841
[13 empty] | C Choked w/ reducers | 7 |  | 5.6999 |  |  | 30.4999 |  |  | 80.9399 |  |  | 214.4798 |  |  | 2390.5331 |  |  | -428.2686 |  |  | -232.3636 |  |  | -187.8712 |  |  | -155.4055 |  |  | -212.2965
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.369 |  |  | 34.359 |  |  | 95.9643 |  |  | 727.9482 |  |  | #NUM! |  |  | -428.2686 |  |  | -232.3636 |  |  | -187.8712 |  |  | -155.4055 |  |  | -212.2965
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.639 | 15758.7041 |  | 22.759 | 83143.5492 |  | 72.9643 | 203588.0112 |  | 688.5482 | 396537.4809 |  | 236393 | 665266.5386 |  | 236393 | 970974.6324 |  | 236393 | 1295769.411 |  | 236393 | 1581084.9294 |  | 236393 | 1835590.5188 |  | 236393 | 2152374.2432
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 16073.8782 | C_100 - C this iteration | iteration | 83974.9847 | C_100 - C this iteration | iteration | 205623.8913 | C_100 - C this iteration | iteration | 400502.8557 | C_100 - C this iteration | iteration | 671919.204 | C_100 - C this iteration | iteration | 980684.3787 | C_100 - C this iteration | iteration | 1308727.1051 | C_100 - C this iteration | iteration | 1596895.7787 | C_100 - C this iteration | iteration | 1853946.424 | C_100 - C this iteration | iteration | 2173897.9856 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1379 |  |  | 88.8998 |  |  | 82.4788 |  |  | 60.9499 |  |  | 7.8987 |  |  | -85.1029 |  |  | -221.9854 |  |  | -374.5942 |  |  | -536.2671 |  |  | -771.1495
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1379 |  |  | 28.8998 |  |  | 22.4788 |  |  | 0.94993 |  |  | -52.1013 |  |  | -145.1029 |  |  | -281.9854 |  |  | -434.5942 |  |  | -596.2671 |  |  | -831.1495
[13 empty] | Press drop ratio this iteration |  |  | 0.33435 |  |  | 0.32508 |  |  | 0.27254 |  |  | 0.015585 |  |  | -6.5962 |  |  | 1.705 |  |  | 1.2703 |  |  | 1.1602 |  |  | 1.1119 |  |  | 1.0778
[13 empty] | Expansion factor | 12 |  | 0.82587 |  |  | 0.83073 |  |  | 0.85674 |  |  | 0.99169 |  |  | 4.6252 |  |  | 0.0067048 |  |  | 0.20383 |  |  | 0.18698 |  |  | 0.37239 |  |  | 0.046248
[13 empty] | C Non choked w/ reducers | 7 |  | 6.4966 |  |  | 34.7186 |  |  | 97.2604 |  |  | 931.6139 |  |  | #NUM! |  |  | -23915.6641 |  |  | -483.1478 |  |  | -422.8128 |  |  | -200.1679 |  |  | -1787.9279
[13 empty] | C Choked w/ reducers | 7 |  | 5.814 |  |  | 30.8137 |  |  | 81.8998 |  |  | 218.672 |  |  | 2910.0488 |  |  | -414.9964 |  |  | -228.1843 |  |  | -185.111 |  |  | -153.3467 |  |  | -209.7004
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.4966 |  |  | 34.7186 |  |  | 97.2604 |  |  | 931.6139 |  |  | #NUM! |  |  | -414.9964 |  |  | -228.1843 |  |  | -185.111 |  |  | -153.3467 |  |  | -209.7004
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7666 | 16073.8782 |  | 23.1186 | 83974.9847 |  | 74.2604 | 205623.8913 |  | 892.2139 | 400502.8557 |  | 236393 | 671919.204 |  | 236393 | 980684.3787 |  | 236393 | 1308727.1051 |  | 236393 | 1596895.7787 |  | 236393 | 1853946.424 |  | 236393 | 2173897.9856
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 16395.3557 | C_100 - C this iteration | iteration | 84814.7345 | C_100 - C this iteration | iteration | 207680.1302 | C_100 - C this iteration | iteration | 404507.8842 | C_100 - C this iteration | iteration | 678638.396 | C_100 - C this iteration | iteration | 990491.2225 | C_100 - C this iteration | iteration | 1321814.3762 | C_100 - C this iteration | iteration | 1612864.7365 | C_100 - C this iteration | iteration | 1872485.8882 | C_100 - C this iteration | iteration | 2195636.9655 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.136 |  |  | 88.8739 |  |  | 82.3239 |  |  | 60.3623 |  |  | 6.2448 |  |  | -88.6262 |  |  | -228.26 |  |  | -383.9362 |  |  | -548.8588 |  |  | -788.4623
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.136 |  |  | 28.8739 |  |  | 22.3239 |  |  | 0.3623 |  |  | -53.7552 |  |  | -148.6262 |  |  | -288.26 |  |  | -443.9362 |  |  | -608.8588 |  |  | -848.4623
[13 empty] | Press drop ratio this iteration |  |  | 0.33434 |  |  | 0.32489 |  |  | 0.27117 |  |  | 0.0060021 |  |  | -8.608 |  |  | 1.677 |  |  | 1.2629 |  |  | 1.1563 |  |  | 1.1093 |  |  | 1.0761
[13 empty] | Expansion factor | 12 |  | 0.82587 |  |  | 0.83084 |  |  | 0.85746 |  |  | 0.9968 |  |  | 5.7309 |  |  | 0.023033 |  |  | 0.20849 |  |  | 0.18971 |  |  | 0.37384 |  |  | 0.04776
[13 empty] | C Non choked w/ reducers | 7 |  | 6.6268 |  |  | 35.0822 |  |  | 98.5831 |  |  | 1523.1389 |  |  | #NUM! |  |  | -6808.0276 |  |  | -465.3281 |  |  | -411.3432 |  |  | -196.9935 |  |  | -1711.6071
[13 empty] | C Choked w/ reducers | 7 |  | 5.9304 |  |  | 31.1309 |  |  | 82.8744 |  |  | 223.0087 |  |  | 3717.5967 |  |  | -402.4834 |  |  | -224.1309 |  |  | -182.4129 |  |  | -151.327 |  |  | -207.1468
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.6268 |  |  | 35.0822 |  |  | 98.5831 |  |  | 1523.1389 |  |  | #NUM! |  |  | -402.4834 |  |  | -224.1309 |  |  | -182.4129 |  |  | -151.327 |  |  | -207.1468
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8968 | 16395.3557 |  | 23.4822 | 84814.7345 |  | 75.5831 | 207680.1302 |  | 1483.7389 | 404507.8842 |  | 236393 | 678638.396 |  | 236393 | 990491.2225 |  | 236393 | 1321814.3762 |  | 236393 | 1612864.7365 |  | 236393 | 1872485.8882 |  | 236393 | 2195636.9655
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 16723.2629 | C_100 - C this iteration | iteration | 85662.8819 | C_100 - C this iteration | iteration | 209756.9315 | C_100 - C this iteration | iteration | 408552.9631 | C_100 - C this iteration | iteration | 685424.78 | C_100 - C this iteration | iteration | 1000396.1347 | C_100 - C this iteration | iteration | 1335032.5199 | C_100 - C this iteration | iteration | 1628993.3838 | C_100 - C this iteration | iteration | 1891210.7471 | C_100 - C this iteration | iteration | 2217593.3351 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1341 |  |  | 88.8476 |  |  | 82.1659 |  |  | 59.7629 |  |  | 4.5576 |  |  | -92.2203 |  |  | -234.6607 |  |  | -393.4661 |  |  | -561.7036 |  |  | -806.1231
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1341 |  |  | 28.8476 |  |  | 22.1659 |  |  | -0.23713 |  |  | -55.4424 |  |  | -152.2203 |  |  | -294.6607 |  |  | -453.4661 |  |  | -621.7036 |  |  | -866.1231
[13 empty] | Press drop ratio this iteration |  |  | 0.33432 |  |  | 0.32469 |  |  | 0.26977 |  |  | -0.0039679 |  |  | -12.1649 |  |  | 1.6506 |  |  | 1.2557 |  |  | 1.1525 |  |  | 1.1068 |  |  | 1.0744
[13 empty] | Expansion factor | 12 |  | 0.82588 |  |  | 0.83094 |  |  | 0.8582 |  |  | 1.0021 |  |  | 7.6857 |  |  | 0.038404 |  |  | 0.21298 |  |  | 0.19237 |  |  | 0.37525 |  |  | 0.049235
[13 empty] | C Non choked w/ reducers | 7 |  | 6.7595 |  |  | 35.45 |  |  | 99.9334 |  |  | #NUM! |  |  | #NUM! |  |  | -3994.8207 |  |  | -448.7918 |  |  | -400.4604 |  |  | -193.9012 |  |  | -1641.4575
[13 empty] | C Choked w/ reducers | 7 |  | 6.0491 |  |  | 31.4515 |  |  | 83.8641 |  |  | 227.498 |  |  | 5144.7804 |  |  | -390.6654 |  |  | -220.1975 |  |  | -179.7747 |  |  | -149.3452 |  |  | -204.6347
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.7595 |  |  | 35.45 |  |  | 99.9334 |  |  | #NUM! |  |  | #NUM! |  |  | -390.6654 |  |  | -220.1975 |  |  | -179.7747 |  |  | -149.3452 |  |  | -204.6347
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.0295 | 16723.2629 |  | 23.85 | 85662.8819 |  | 76.9334 | 209756.9315 |  | 236393 | 408552.9631 |  | 236393 | 685424.78 |  | 236393 | 1000396.1347 |  | 236393 | 1335032.5199 |  | 236393 | 1628993.3838 |  | 236393 | 1891210.7471 |  | 236393 | 2217593.3351
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 17057.7281 | C_100 - C this iteration | iteration | 86519.5107 | C_100 - C this iteration | iteration | 211854.5008 | C_100 - C this iteration | iteration | 412638.4927 | C_100 - C this iteration | iteration | 692279.0278 | C_100 - C this iteration | iteration | 1010400.0961 | C_100 - C this iteration | iteration | 1348382.8451 | C_100 - C this iteration | iteration | 1645283.3177 | C_100 - C this iteration | iteration | 1910122.8546 | C_100 - C this iteration | iteration | 2239769.2685 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.132 |  |  | 88.8207 |  |  | 82.0047 |  |  | 59.1514 |  |  | 2.8365 |  |  | -95.8866 |  |  | -241.1901 |  |  | -403.1874 |  |  | -574.8065 |  |  | -824.1389
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.132 |  |  | 28.8207 |  |  | 22.0047 |  |  | -0.84862 |  |  | -57.1635 |  |  | -155.8866 |  |  | -301.1901 |  |  | -463.1874 |  |  | -634.8065 |  |  | -884.1389
[13 empty] | Press drop ratio this iteration |  |  | 0.33431 |  |  | 0.32448 |  |  | 0.26834 |  |  | -0.014347 |  |  | -20.1532 |  |  | 1.6257 |  |  | 1.2488 |  |  | 1.1488 |  |  | 1.1044 |  |  | 1.0728
[13 empty] | Expansion factor | 12 |  | 0.82589 |  |  | 0.83105 |  |  | 0.85895 |  |  | 1.0076 |  |  | 12.076 |  |  | 0.052897 |  |  | 0.21732 |  |  | 0.19494 |  |  | 0.37663 |  |  | 0.050675
[13 empty] | C Non choked w/ reducers | 7 |  | 6.895 |  |  | 35.822 |  |  | 101.3121 |  |  | #NUM! |  |  | #NUM! |  |  | -2838.79 |  |  | -433.4009 |  |  | -390.1186 |  |  | -190.8876 |  |  | -1576.7514
[13 empty] | C Choked w/ reducers | 7 |  | 6.1702 |  |  | 31.7756 |  |  | 84.8692 |  |  | 232.1483 |  |  | 8349.2128 |  |  | -379.4851 |  |  | -216.3788 |  |  | -177.1945 |  |  | -147.4002 |  |  | -202.1629
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.895 |  |  | 35.822 |  |  | 101.3121 |  |  | #NUM! |  |  | #NUM! |  |  | -379.4851 |  |  | -216.3788 |  |  | -177.1945 |  |  | -147.4002 |  |  | -202.1629
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.165 | 17057.7281 |  | 24.222 | 86519.5107 |  | 78.3121 | 211854.5008 |  | 236393 | 412638.4927 |  | 236393 | 692279.0278 |  | 236393 | 1010400.0961 |  | 236393 | 1348382.8451 |  | 236393 | 1645283.3177 |  | 236393 | 1910122.8546 |  | 236393 | 2239769.2685
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 17398.8827 | C_100 - C this iteration | iteration | 87384.7058 | C_100 - C this iteration | iteration | 213973.0458 | C_100 - C this iteration | iteration | 416764.8776 | C_100 - C this iteration | iteration | 699201.8181 | C_100 - C this iteration | iteration | 1020504.0971 | C_100 - C this iteration | iteration | 1361866.6736 | C_100 - C this iteration | iteration | 1661736.1508 | C_100 - C this iteration | iteration | 1929224.0831 | C_100 - C this iteration | iteration | 2262166.9612 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1299 |  |  | 88.7933 |  |  | 81.8403 |  |  | 58.5276 |  |  | 1.0807 |  |  | -99.6267 |  |  | -247.8508 |  |  | -413.1042 |  |  | -588.1729 |  |  | -842.5168
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1299 |  |  | 28.7933 |  |  | 21.8403 |  |  | -1.4724 |  |  | -58.9193 |  |  | -159.6267 |  |  | -307.8508 |  |  | -473.1042 |  |  | -648.1729 |  |  | -902.5168
[13 empty] | Press drop ratio this iteration |  |  | 0.33429 |  |  | 0.32427 |  |  | 0.26687 |  |  | -0.025157 |  |  | -54.5172 |  |  | 1.6022 |  |  | 1.2421 |  |  | 1.1452 |  |  | 1.102 |  |  | 1.0712
[13 empty] | Expansion factor | 12 |  | 0.8259 |  |  | 0.83115 |  |  | 0.85972 |  |  | 1.0134 |  |  | 30.9621 |  |  | 0.066581 |  |  | 0.22151 |  |  | 0.19745 |  |  | 0.37797 |  |  | 0.052081
[13 empty] | C Non choked w/ reducers | 7 |  | 7.0331 |  |  | 36.1984 |  |  | 102.7204 |  |  | #NUM! |  |  | #NUM! |  |  | -2208.371 |  |  | -419.0369 |  |  | -380.277 |  |  | -187.9497 |  |  | -1516.8709
[13 empty] | C Choked w/ reducers | 7 |  | 6.2938 |  |  | 32.1033 |  |  | 85.8901 |  |  | 236.9687 |  |  | 22131.9021 |  |  | -368.8914 |  |  | -212.6695 |  |  | -174.6703 |  |  | -145.491 |  |  | -199.7307
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.0331 |  |  | 36.1984 |  |  | 102.7204 |  |  | #NUM! |  |  | #NUM! |  |  | -368.8914 |  |  | -212.6695 |  |  | -174.6703 |  |  | -145.491 |  |  | -199.7307
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.3031 | 17398.8827 |  | 24.5984 | 87384.7058 |  | 79.7204 | 213973.0458 |  | 236393 | 416764.8776 |  | 236393 | 699201.8181 |  | 236393 | 1020504.0971 |  | 236393 | 1361866.6736 |  | 236393 | 1661736.1508 |  | 236393 | 1929224.0831 |  | 236393 | 2262166.9612
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 17746.8603 | C_100 - C this iteration | iteration | 88258.5528 | C_100 - C this iteration | iteration | 216112.7763 | C_100 - C this iteration | iteration | 420932.5264 | C_100 - C this iteration | iteration | 706193.8363 | C_100 - C this iteration | iteration | 1030709.138 | C_100 - C this iteration | iteration | 1375485.3403 | C_100 - C this iteration | iteration | 1678353.5123 | C_100 - C this iteration | iteration | 1948516.324 | C_100 - C this iteration | iteration | 2284788.6308 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1276 |  |  | 88.7653 |  |  | 81.6726 |  |  | 57.8913 |  |  | -0.71025 |  |  | -103.4419 |  |  | -254.6453 |  |  | -423.2203 |  |  | -601.8079 |  |  | -861.2641
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1276 |  |  | 28.7653 |  |  | 21.6726 |  |  | -2.1087 |  |  | -60.7103 |  |  | -163.4419 |  |  | -314.6453 |  |  | -483.2203 |  |  | -661.8079 |  |  | -921.2641
[13 empty] | Press drop ratio this iteration |  |  | 0.33428 |  |  | 0.32406 |  |  | 0.26536 |  |  | -0.036425 |  |  | 85.4773 |  |  | 1.58 |  |  | 1.2356 |  |  | 1.1418 |  |  | 1.0997 |  |  | 1.0697
[13 empty] | Expansion factor | 12 |  | 0.82591 |  |  | 0.83127 |  |  | 0.86051 |  |  | 1.0194 |  |  | -45.9774 |  |  | 0.079522 |  |  | 0.22556 |  |  | 0.19988 |  |  | 0.37927 |  |  | 0.053452
[13 empty] | C Non choked w/ reducers | 7 |  | 7.1741 |  |  | 36.579 |  |  | 104.1593 |  |  | #NUM! |  |  | 41.5651 |  |  | -1811.2206 |  |  | -405.5969 |  |  | -370.8986 |  |  | -185.0843 |  |  | -1461.2885
[13 empty] | C Choked w/ reducers | 7 |  | 6.4198 |  |  | 32.4346 |  |  | 86.9272 |  |  | 241.9691 |  |  | -34013.5962 |  |  | -358.8385 |  |  | -209.065 |  |  | -172.2001 |  |  | -143.6166 |  |  | -197.3369
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.1741 |  |  | 36.579 |  |  | 104.1593 |  |  | #NUM! |  |  | -34013.5962 |  |  | -358.8385 |  |  | -209.065 |  |  | -172.2001 |  |  | -143.6166 |  |  | -197.3369
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.4441 | 17746.8603 |  | 24.979 | 88258.5528 |  | 81.1593 | 216112.7763 |  | 236393 | 420932.5264 |  | 236393 | 706193.8363 |  | 236393 | 1030709.138 |  | 236393 | 1375485.3403 |  | 236393 | 1678353.5123 |  | 236393 | 1948516.324 |  | 236393 | 2284788.6308
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 18101.7975 | C_100 - C this iteration | iteration | 89141.1384 | C_100 - C this iteration | iteration | 218273.9041 | C_100 - C this iteration | iteration | 425141.8517 | C_100 - C this iteration | iteration | 713255.7746 | C_100 - C this iteration | iteration | 1041016.2294 | C_100 - C this iteration | iteration | 1389240.1937 | C_100 - C this iteration | iteration | 1695137.0475 | C_100 - C this iteration | iteration | 1968001.4872 | C_100 - C this iteration | iteration | 2307636.5171 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1253 |  |  | 88.7368 |  |  | 81.5015 |  |  | 57.2422 |  |  | -2.5372 |  |  | -107.3338 |  |  | -261.5764 |  |  | -433.5398 |  |  | -615.7169 |  |  | -880.3883
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1253 |  |  | 28.7368 |  |  | 21.5015 |  |  | -2.7578 |  |  | -62.5372 |  |  | -167.3338 |  |  | -321.5764 |  |  | -493.5398 |  |  | -675.7169 |  |  | -940.3883
[13 empty] | Press drop ratio this iteration |  |  | 0.33426 |  |  | 0.32384 |  |  | 0.26382 |  |  | -0.048178 |  |  | 24.6477 |  |  | 1.559 |  |  | 1.2294 |  |  | 1.1384 |  |  | 1.0974 |  |  | 1.0682
[13 empty] | Expansion factor | 12 |  | 0.82591 |  |  | 0.83138 |  |  | 0.86133 |  |  | 1.0257 |  |  | -12.5461 |  |  | 0.091774 |  |  | 0.22947 |  |  | 0.20224 |  |  | 0.38054 |  |  | 0.054791
[13 empty] | C Non choked w/ reducers | 7 |  | 7.3179 |  |  | 36.964 |  |  | 105.6299 |  |  | #NUM! |  |  | 80.1995 |  |  | -1537.8976 |  |  | -392.9917 |  |  | -361.9503 |  |  | -182.2886 |  |  | -1409.551
[13 empty] | C Choked w/ reducers | 7 |  | 6.5484 |  |  | 32.7694 |  |  | 87.9808 |  |  | 247.1601 |  |  | -9616.6263 |  |  | -349.2854 |  |  | -205.5606 |  |  | -169.7823 |  |  | -141.776 |  |  | -194.9808
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.3179 |  |  | 36.964 |  |  | 105.6299 |  |  | #NUM! |  |  | -9616.6263 |  |  | -349.2854 |  |  | -205.5606 |  |  | -169.7823 |  |  | -141.776 |  |  | -194.9808
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.5879 | 18101.7975 |  | 25.364 | 89141.1384 |  | 82.6299 | 218273.9041 |  | 236393 | 425141.8517 |  | 236393 | 713255.7746 |  | 236393 | 1041016.2294 |  | 236393 | 1389240.1937 |  | 236393 | 1695137.0475 |  | 236393 | 1968001.4872 |  | 236393 | 2307636.5171
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 18463.8335 | C_100 - C this iteration | iteration | 90032.5497 | C_100 - C this iteration | iteration | 220456.6431 | C_100 - C this iteration | iteration | 429393.2702 | C_100 - C this iteration | iteration | 720388.3324 | C_100 - C this iteration | iteration | 1051426.3917 | C_100 - C this iteration | iteration | 1403132.5957 | C_100 - C this iteration | iteration | 1712088.4179 | C_100 - C this iteration | iteration | 1987681.5021 | C_100 - C this iteration | iteration | 2330712.8822 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1229 |  |  | 88.7077 |  |  | 81.327 |  |  | 56.58 |  |  | -4.401 |  |  | -111.3039 |  |  | -268.6468 |  |  | -444.0667 |  |  | -629.9055 |  |  | -899.8968
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1229 |  |  | 28.7077 |  |  | 21.327 |  |  | -3.42 |  |  | -64.401 |  |  | -171.3039 |  |  | -328.6468 |  |  | -504.0667 |  |  | -689.9055 |  |  | -959.8968
[13 empty] | Press drop ratio this iteration |  |  | 0.33424 |  |  | 0.32362 |  |  | 0.26224 |  |  | -0.060445 |  |  | 14.6334 |  |  | 1.5391 |  |  | 1.2233 |  |  | 1.1351 |  |  | 1.0953 |  |  | 1.0667
[13 empty] | Expansion factor | 12 |  | 0.82592 |  |  | 0.83149 |  |  | 0.86216 |  |  | 1.0322 |  |  | -7.0423 |  |  | 0.10339 |  |  | 0.23325 |  |  | 0.20454 |  |  | 0.38178 |  |  | 0.056099
[13 empty] | C Non choked w/ reducers | 7 |  | 7.4645 |  |  | 37.3535 |  |  | 107.1335 |  |  | #NUM! |  |  | 107.973 |  |  | -1338.1704 |  |  | -381.143 |  |  | -353.4017 |  |  | -179.56 |  |  | -1361.2667
[13 empty] | C Choked w/ reducers | 7 |  | 6.6795 |  |  | 33.108 |  |  | 89.0513 |  |  | 252.5531 |  |  | -5599.6236 |  |  | -340.1949 |  |  | -202.152 |  |  | -167.4151 |  |  | -139.9683 |  |  | -192.6614
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.4645 |  |  | 37.3535 |  |  | 107.1335 |  |  | #NUM! |  |  | -5599.6236 |  |  | -340.1949 |  |  | -202.152 |  |  | -167.4151 |  |  | -139.9683 |  |  | -192.6614
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.7345 | 18463.8335 |  | 25.7535 | 90032.5497 |  | 84.1335 | 220456.6431 |  | 236393 | 429393.2702 |  | 236393 | 720388.3324 |  | 236393 | 1051426.3917 |  | 236393 | 1403132.5957 |  | 236393 | 1712088.4179 |  | 236393 | 1987681.5021 |  | 236393 | 2330712.8822
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 18833.1102 | C_100 - C this iteration | iteration | 90932.8752 | C_100 - C this iteration | iteration | 222661.2095 | C_100 - C this iteration | iteration | 433687.2029 | C_100 - C this iteration | iteration | 727592.2157 | C_100 - C this iteration | iteration | 1061940.6556 | C_100 - C this iteration | iteration | 1417163.9216 | C_100 - C this iteration | iteration | 1729209.3021 | C_100 - C this iteration | iteration | 2007558.3171 | C_100 - C this iteration | iteration | 2354020.0111 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1204 |  |  | 88.678 |  |  | 81.1489 |  |  | 55.9046 |  |  | -6.3021 |  |  | -115.3539 |  |  | -275.8593 |  |  | -454.8051 |  |  | -644.3794 |  |  | -919.7974
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1204 |  |  | 28.678 |  |  | 21.1489 |  |  | -4.0954 |  |  | -66.3021 |  |  | -175.3539 |  |  | -335.8593 |  |  | -514.8051 |  |  | -704.3794 |  |  | -979.7974
[13 empty] | Press drop ratio this iteration |  |  | 0.33422 |  |  | 0.32339 |  |  | 0.26062 |  |  | -0.073257 |  |  | 10.5206 |  |  | 1.5201 |  |  | 1.2175 |  |  | 1.1319 |  |  | 1.0931 |  |  | 1.0652
[13 empty] | Expansion factor | 12 |  | 0.82593 |  |  | 0.83161 |  |  | 0.86301 |  |  | 1.0391 |  |  | -4.782 |  |  | 0.11442 |  |  | 0.23691 |  |  | 0.20678 |  |  | 0.38299 |  |  | 0.057375
[13 empty] | C Non choked w/ reducers | 7 |  | 7.6141 |  |  | 37.7476 |  |  | 108.6712 |  |  | #NUM! |  |  | 132.2687 |  |  | -1185.7452 |  |  | -369.9822 |  |  | -345.2256 |  |  | -176.8959 |  |  | -1316.0955
[13 empty] | C Choked w/ reducers | 7 |  | 6.8133 |  |  | 33.4503 |  |  | 90.1391 |  |  | 258.1606 |  |  | -3949.4787 |  |  | -331.5336 |  |  | -198.8353 |  |  | -165.0969 |  |  | -138.1927 |  |  | -190.378
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.6141 |  |  | 37.7476 |  |  | 108.6712 |  |  | #NUM! |  |  | -3949.4787 |  |  | -331.5336 |  |  | -198.8353 |  |  | -165.0969 |  |  | -138.1927 |  |  | -190.378
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.8841 | 18833.1102 |  | 26.1476 | 90932.8752 |  | 85.6712 | 222661.2095 |  | 236393 | 433687.2029 |  | 236393 | 727592.2157 |  | 236393 | 1061940.6556 |  | 236393 | 1417163.9216 |  | 236393 | 1729209.3021 |  | 236393 | 2007558.3171 |  | 236393 | 2354020.0111
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 19209.7724 | C_100 - C this iteration | iteration | 91842.204 | C_100 - C this iteration | iteration | 224887.8216 | C_100 - C this iteration | iteration | 438024.0749 | C_100 - C this iteration | iteration | 734868.1379 | C_100 - C this iteration | iteration | 1072560.0622 | C_100 - C this iteration | iteration | 1431335.5608 | C_100 - C this iteration | iteration | 1746501.3951 | C_100 - C this iteration | iteration | 2027633.9003 | C_100 - C this iteration | iteration | 2377560.2112 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1178 |  |  | 88.6477 |  |  | 80.9673 |  |  | 55.2155 |  |  | -8.2415 |  |  | -119.4852 |  |  | -283.2168 |  |  | -465.7594 |  |  | -659.1441 |  |  | -940.0981
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1178 |  |  | 28.6477 |  |  | 20.9673 |  |  | -4.7845 |  |  | -68.2415 |  |  | -179.4852 |  |  | -343.2168 |  |  | -525.7594 |  |  | -719.1441 |  |  | -1000.0981
[13 empty] | Press drop ratio this iteration |  |  | 0.3342 |  |  | 0.32316 |  |  | 0.25896 |  |  | -0.086651 |  |  | 8.2802 |  |  | 1.5022 |  |  | 1.2119 |  |  | 1.1288 |  |  | 1.091 |  |  | 1.0638
[13 empty] | Expansion factor | 12 |  | 0.82594 |  |  | 0.83173 |  |  | 0.86388 |  |  | 1.0462 |  |  | -3.5507 |  |  | 0.12489 |  |  | 0.24046 |  |  | 0.20895 |  |  | 0.38417 |  |  | 0.058622
[13 empty] | C Non choked w/ reducers | 7 |  | 7.7668 |  |  | 38.1462 |  |  | 110.2445 |  |  | #NUM! |  |  | 155.0787 |  |  | -1065.5243 |  |  | -359.4488 |  |  | -337.397 |  |  | -174.2939 |  |  | -1273.7406
[13 empty] | C Choked w/ reducers | 7 |  | 6.9498 |  |  | 33.7963 |  |  | 91.2448 |  |  | 263.996 |  |  | -3050.2909 |  |  | -323.2712 |  |  | -195.6066 |  |  | -162.826 |  |  | -136.4481 |  |  | -188.1296
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.7668 |  |  | 38.1462 |  |  | 110.2445 |  |  | #NUM! |  |  | -3050.2909 |  |  | -323.2712 |  |  | -195.6066 |  |  | -162.826 |  |  | -136.4481 |  |  | -188.1296
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.0368 | 19209.7724 |  | 26.5462 | 91842.204 |  | 87.2445 | 224887.8216 |  | 236393 | 438024.0749 |  | 236393 | 734868.1379 |  | 236393 | 1072560.0622 |  | 236393 | 1431335.5608 |  | 236393 | 1746501.3951 |  | 236393 | 2027633.9003 |  | 236393 | 2377560.2112
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 19593.9678 | C_100 - C this iteration | iteration | 92760.626 | C_100 - C this iteration | iteration | 227136.6998 | C_100 - C this iteration | iteration | 442404.3157 | C_100 - C this iteration | iteration | 742216.8192 | C_100 - C this iteration | iteration | 1083285.6628 | C_100 - C this iteration | iteration | 1445648.9164 | C_100 - C this iteration | iteration | 1763966.4091 | C_100 - C this iteration | iteration | 2047910.2393 | C_100 - C this iteration | iteration | 2401335.8133 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1151 |  |  | 88.6168 |  |  | 80.782 |  |  | 54.5126 |  |  | -10.2199 |  |  | -123.6996 |  |  | -290.7222 |  |  | -476.9339 |  |  | -674.2056 |  |  | -960.8068
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1151 |  |  | 28.6168 |  |  | 20.782 |  |  | -5.4874 |  |  | -70.2199 |  |  | -183.6996 |  |  | -350.7222 |  |  | -536.9339 |  |  | -734.2056 |  |  | -1020.8068
[13 empty] | Press drop ratio this iteration |  |  | 0.33418 |  |  | 0.32293 |  |  | 0.25726 |  |  | -0.10066 |  |  | 6.8709 |  |  | 1.485 |  |  | 1.2064 |  |  | 1.1258 |  |  | 1.089 |  |  | 1.0624
[13 empty] | Expansion factor | 12 |  | 0.82595 |  |  | 0.83186 |  |  | 0.86477 |  |  | 1.0537 |  |  | -2.7762 |  |  | 0.13486 |  |  | 0.24388 |  |  | 0.21107 |  |  | 0.38531 |  |  | 0.059839
[13 empty] | C Non choked w/ reducers | 7 |  | 7.9225 |  |  | 38.5495 |  |  | 111.8547 |  |  | #NUM! |  |  | 177.3443 |  |  | -968.2201 |  |  | -349.4894 |  |  | -329.8932 |  |  | -171.7517 |  |  | -1233.9419
[13 empty] | C Choked w/ reducers | 7 |  | 7.089 |  |  | 34.1462 |  |  | 92.3686 |  |  | 270.074 |  |  | -2484.4125 |  |  | -315.3801 |  |  | -192.4623 |  |  | -160.6012 |  |  | -134.7339 |  |  | -185.9155
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.9225 |  |  | 38.5495 |  |  | 111.8547 |  |  | #NUM! |  |  | -2484.4125 |  |  | -315.3801 |  |  | -192.4623 |  |  | -160.6012 |  |  | -134.7339 |  |  | -185.9155
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.1925 | 19593.9678 |  | 26.9495 | 92760.626 |  | 88.8547 | 227136.6998 |  | 236393 | 442404.3157 |  | 236393 | 742216.8192 |  | 236393 | 1083285.6628 |  | 236393 | 1445648.9164 |  | 236393 | 1763966.4091 |  | 236393 | 2047910.2393 |  | 236393 | 2401335.8133
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 19985.8472 | C_100 - C this iteration | iteration | 93688.2323 | C_100 - C this iteration | iteration | 229408.0668 | C_100 - C this iteration | iteration | 446828.3588 | C_100 - C this iteration | iteration | 749638.9874 | C_100 - C this iteration | iteration | 1094118.5194 | C_100 - C this iteration | iteration | 1460105.4056 | C_100 - C this iteration | iteration | 1781606.0732 | C_100 - C this iteration | iteration | 2068389.3417 | C_100 - C this iteration | iteration | 2425349.1714 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1122 |  |  | 88.5852 |  |  | 80.593 |  |  | 53.7956 |  |  | -12.238 |  |  | -127.9986 |  |  | -298.3784 |  |  | -488.333 |  |  | -689.5699 |  |  | -981.9317
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1122 |  |  | 28.5852 |  |  | 20.593 |  |  | -6.2044 |  |  | -72.238 |  |  | -187.9986 |  |  | -358.3784 |  |  | -548.333 |  |  | -749.5699 |  |  | -1041.9317
[13 empty] | Press drop ratio this iteration |  |  | 0.33416 |  |  | 0.32269 |  |  | 0.25552 |  |  | -0.11533 |  |  | 5.9027 |  |  | 1.4688 |  |  | 1.2011 |  |  | 1.1229 |  |  | 1.087 |  |  | 1.0611
[13 empty] | Expansion factor | 12 |  | 0.82596 |  |  | 0.83198 |  |  | 0.86569 |  |  | 1.0615 |  |  | -2.2441 |  |  | 0.14435 |  |  | 0.2472 |  |  | 0.21313 |  |  | 0.38643 |  |  | 0.061028
[13 empty] | C Non choked w/ reducers | 7 |  | 8.0813 |  |  | 38.9575 |  |  | 113.5033 |  |  | #NUM! |  |  | 199.6457 |  |  | -887.8051 |  |  | -340.0562 |  |  | -322.6934 |  |  | -169.2671 |  |  | -1196.4704
[13 empty] | C Choked w/ reducers | 7 |  | 7.231 |  |  | 34.4999 |  |  | 93.511 |  |  | 276.4104 |  |  | -2095.4627 |  |  | -307.8353 |  |  | -189.399 |  |  | -158.4208 |  |  | -133.0493 |  |  | -183.7349
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 8.0813 |  |  | 38.9575 |  |  | 113.5033 |  |  | #NUM! |  |  | -2095.4627 |  |  | -307.8353 |  |  | -189.399 |  |  | -158.4208 |  |  | -133.0493 |  |  | -183.7349
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.3513 | 19985.8472 |  | 27.3575 | 93688.2323 |  | 90.5033 | 229408.0668 |  | 236393 | 446828.3588 |  | 236393 | 749638.9874 |  | 236393 | 1094118.5194 |  | 236393 | 1460105.4056 |  | 236393 | 1781606.0732 |  | 236393 | 2068389.3417 |  | 236393 | 2425349.1714
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 20385.5641 | C_100 - C this iteration | iteration | 94625.1146 | C_100 - C this iteration | iteration | 231702.1475 | C_100 - C this iteration | iteration | 451296.6424 | C_100 - C this iteration | iteration | 757135.3773 | C_100 - C this iteration | iteration | 1105059.7046 | C_100 - C this iteration | iteration | 1474706.4597 | C_100 - C this iteration | iteration | 1799422.1339 | C_100 - C this iteration | iteration | 2089073.2351 | C_100 - C this iteration | iteration | 2449602.6631 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1093 |  |  | 88.5531 |  |  | 80.4002 |  |  | 53.0642 |  |  | -14.2968 |  |  | -132.3841 |  |  | -306.1885 |  |  | -499.9612 |  |  | -705.2429 |  |  | -1003.4813
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1093 |  |  | 28.5531 |  |  | 20.4002 |  |  | -6.9358 |  |  | -74.2968 |  |  | -192.3841 |  |  | -366.1885 |  |  | -559.9612 |  |  | -765.2429 |  |  | -1063.4813
[13 empty] | Press drop ratio this iteration |  |  | 0.33414 |  |  | 0.32244 |  |  | 0.25373 |  |  | -0.13071 |  |  | 5.1968 |  |  | 1.4532 |  |  | 1.196 |  |  | 1.12 |  |  | 1.0851 |  |  | 1.0598
[13 empty] | Expansion factor | 12 |  | 0.82598 |  |  | 0.83211 |  |  | 0.86663 |  |  | 1.0697 |  |  | -1.8561 |  |  | 0.1534 |  |  | 0.25042 |  |  | 0.21513 |  |  | 0.38752 |  |  | 0.062189
[13 empty] | C Non choked w/ reducers | 7 |  | 8.2434 |  |  | 39.3703 |  |  | 115.192 |  |  | #NUM! |  |  | 222.4123 |  |  | -820.1971 |  |  | -331.107 |  |  | -315.7788 |  |  | -166.8381 |  |  | -1161.1236
[13 empty] | C Choked w/ reducers | 7 |  | 7.3759 |  |  | 34.8576 |  |  | 94.6726 |  |  | 283.0226 |  |  | -1811.6574 |  |  | -300.614 |  |  | -186.4136 |  |  | -156.2836 |  |  | -131.3933 |  |  | -181.5871
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 8.2434 |  |  | 39.3703 |  |  | 115.192 |  |  | #NUM! |  |  | -1811.6574 |  |  | -300.614 |  |  | -186.4136 |  |  | -156.2836 |  |  | -131.3933 |  |  | -181.5871
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.5134 | 20385.5641 |  | 27.7703 | 94625.1146 |  | 92.192 | 231702.1475 |  | 236393 | 451296.6424 |  | 236393 | 757135.3773 |  | 236393 | 1105059.7046 |  | 236393 | 1474706.4597 |  | 236393 | 1799422.1339 |  | 236393 | 2089073.2351 |  | 236393 | 2449602.6631
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 20793.2754 | C_100 - C this iteration | iteration | 95571.3658 | C_100 - C this iteration | iteration | 234019.169 | C_100 - C this iteration | iteration | 455809.6089 | C_100 - C this iteration | iteration | 764706.7311 | C_100 - C this iteration | iteration | 1116110.3017 | C_100 - C this iteration | iteration | 1489453.5242 | C_100 - C this iteration | iteration | 1817416.3553 | C_100 - C this iteration | iteration | 2109963.9674 | C_100 - C this iteration | iteration | 2474098.6898 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1062 |  |  | 88.5203 |  |  | 80.2035 |  |  | 52.3181 |  |  | -16.3968 |  |  | -136.8578 |  |  | -314.1557 |  |  | -511.8232 |  |  | -721.231 |  |  | -1025.4639
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1062 |  |  | 28.5203 |  |  | 20.2035 |  |  | -7.6819 |  |  | -76.3968 |  |  | -196.8578 |  |  | -374.1557 |  |  | -571.8232 |  |  | -781.231 |  |  | -1085.4639
[13 empty] | Press drop ratio this iteration |  |  | 0.33412 |  |  | 0.32219 |  |  | 0.2519 |  |  | -0.14683 |  |  | 4.6592 |  |  | 1.4384 |  |  | 1.191 |  |  | 1.1172 |  |  | 1.0832 |  |  | 1.0585
[13 empty] | Expansion factor | 12 |  | 0.82599 |  |  | 0.83224 |  |  | 0.86759 |  |  | 1.0783 |  |  | -1.5607 |  |  | 0.16203 |  |  | 0.25353 |  |  | 0.21708 |  |  | 0.38859 |  |  | 0.063323
[13 empty] | C Non choked w/ reducers | 7 |  | 8.4087 |  |  | 39.788 |  |  | 116.9223 |  |  | #NUM! |  |  | 246.0097 |  |  | -762.5324 |  |  | -322.6038 |  |  | -309.1317 |  |  | -164.4626 |  |  | -1127.722
[13 empty] | C Choked w/ reducers | 7 |  | 7.5236 |  |  | 35.2192 |  |  | 95.8538 |  |  | 289.9295 |  |  | -1595.4191 |  |  | -293.6953 |  |  | -183.503 |  |  | -154.1882 |  |  | -129.7655 |  |  | -179.4714
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 8.4087 |  |  | 39.788 |  |  | 116.9223 |  |  | #NUM! |  |  | -1595.4191 |  |  | -293.6953 |  |  | -183.503 |  |  | -154.1882 |  |  | -129.7655 |  |  | -179.4714
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.6787 | 20793.2754 |  | 28.188 | 95571.3658 |  | 93.9223 | 234019.169 |  | 236393 | 455809.6089 |  | 236393 | 764706.7311 |  | 236393 | 1116110.3017 |  | 236393 | 1489453.5242 |  | 236393 | 1817416.3553 |  | 236393 | 2109963.9674 |  | 236393 | 2474098.6898
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 21209.1409 | C_100 - C this iteration | iteration | 96527.0794 | C_100 - C this iteration | iteration | 236359.3607 | C_100 - C this iteration | iteration | 460367.7049 | C_100 - C this iteration | iteration | 772353.7984 | C_100 - C this iteration | iteration | 1127271.4047 | C_100 - C this iteration | iteration | 1504348.0595 | C_100 - C this iteration | iteration | 1835590.5188 | C_100 - C this iteration | iteration | 2131063.6071 | C_100 - C this iteration | iteration | 2498839.6767 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1031 |  |  | 88.4868 |  |  | 80.0029 |  |  | 51.557 |  |  | -18.5391 |  |  | -141.4213 |  |  | -322.2829 |  |  | -523.9235 |  |  | -737.5405 |  |  | -1047.8885
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1031 |  |  | 28.4868 |  |  | 20.0029 |  |  | -8.443 |  |  | -78.5391 |  |  | -201.4213 |  |  | -382.2829 |  |  | -583.9235 |  |  | -797.5405 |  |  | -1107.8885
[13 empty] | Press drop ratio this iteration |  |  | 0.3341 |  |  | 0.32193 |  |  | 0.25003 |  |  | -0.16376 |  |  | 4.2364 |  |  | 1.4243 |  |  | 1.1862 |  |  | 1.1145 |  |  | 1.0814 |  |  | 1.0573
[13 empty] | Expansion factor | 12 |  | 0.826 |  |  | 0.83237 |  |  | 0.86857 |  |  | 1.0873 |  |  | -1.3283 |  |  | 0.17027 |  |  | 0.25655 |  |  | 0.21897 |  |  | 0.38963 |  |  | 0.064431
[13 empty] | C Non choked w/ reducers | 7 |  | 8.5774 |  |  | 40.2106 |  |  | 118.696 |  |  | #NUM! |  |  | 270.7855 |  |  | -712.7433 |  |  | -314.5126 |  |  | -302.7363 |  |  | -162.1389 |  |  | -1096.1059
[13 empty] | C Choked w/ reducers | 7 |  | 7.6744 |  |  | 35.5848 |  |  | 97.0552 |  |  | 297.1518 |  |  | -1425.1705 |  |  | -287.0602 |  |  | -180.6642 |  |  | -152.1334 |  |  | -128.1649 |  |  | -177.3871
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 8.5774 |  |  | 40.2106 |  |  | 118.696 |  |  | #NUM! |  |  | -1425.1705 |  |  | -287.0602 |  |  | -180.6642 |  |  | -152.1334 |  |  | -128.1649 |  |  | -177.3871
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.8474 | 21209.1409 |  | 28.6106 | 96527.0794 |  | 95.696 | 236359.3607 |  | 236393 | 460367.7049 |  | 236393 | 772353.7984 |  | 236393 | 1127271.4047 |  | 236393 | 1504348.0595 |  | 236393 | 1835590.5188 |  | 236393 | 2131063.6071 |  | 236393 | 2498839.6767
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 21633.3237 | C_100 - C this iteration | iteration | 97492.3502 | C_100 - C this iteration | iteration | 238722.9543 | C_100 - C this iteration | iteration | 464971.382 | C_100 - C this iteration | iteration | 780077.3364 | C_100 - C this iteration | iteration | 1138544.1187 | C_100 - C this iteration | iteration | 1519391.5401 | C_100 - C this iteration | iteration | 1853946.424 | C_100 - C this iteration | iteration | 2152374.2432 | C_100 - C this iteration | iteration | 2523828.0734 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0997 |  |  | 88.4527 |  |  | 79.7982 |  |  | 50.7805 |  |  | -20.7245 |  |  | -146.0766 |  |  | -330.5735 |  |  | -536.2671 |  |  | -754.1778 |  |  | -1070.7638
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0997 |  |  | 28.4527 |  |  | 19.7982 |  |  | -9.2195 |  |  | -80.7245 |  |  | -206.0766 |  |  | -390.5735 |  |  | -596.2671 |  |  | -814.1778 |  |  | -1130.7638
[13 empty] | Press drop ratio this iteration |  |  | 0.33407 |  |  | 0.32167 |  |  | 0.2481 |  |  | -0.18156 |  |  | 3.8951 |  |  | 1.4107 |  |  | 1.1815 |  |  | 1.1119 |  |  | 1.0796 |  |  | 1.056
[13 empty] | Expansion factor | 12 |  | 0.82601 |  |  | 0.83251 |  |  | 0.86958 |  |  | 1.0968 |  |  | -1.1407 |  |  | 0.17815 |  |  | 0.25948 |  |  | 0.22082 |  |  | 0.39064 |  |  | 0.065514
[13 empty] | C Non choked w/ reducers | 7 |  | 8.7494 |  |  | 40.6382 |  |  | 120.5152 |  |  | #NUM! |  |  | 297.0985 |  |  | -669.2989 |  |  | -306.8027 |  |  | -296.5777 |  |  | -159.8652 |  |  | -1066.1325
[13 empty] | C Choked w/ reducers | 7 |  | 7.8282 |  |  | 35.9546 |  |  | 98.2771 |  |  | 304.7121 |  |  | -1287.638 |  |  | -280.691 |  |  | -177.8945 |  |  | -150.1179 |  |  | -126.5909 |  |  | -175.3335
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 8.7494 |  |  | 40.6382 |  |  | 120.5152 |  |  | #NUM! |  |  | -1287.638 |  |  | -280.691 |  |  | -177.8945 |  |  | -150.1179 |  |  | -126.5909 |  |  | -175.3335
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0194 | 21633.3237 |  | 29.0382 | 97492.3502 |  | 97.5152 | 238722.9543 |  | 236393 | 464971.382 |  | 236393 | 780077.3364 |  | 236393 | 1138544.1187 |  | 236393 | 1519391.5401 |  | 236393 | 1853946.424 |  | 236393 | 2152374.2432 |  | 236393 | 2523828.0734
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 22065.9902 | C_100 - C this iteration | iteration | 98467.2737 | C_100 - C this iteration | iteration | 241110.1838 | C_100 - C this iteration | iteration | 469621.0958 | C_100 - C this iteration | iteration | 787878.1097 | C_100 - C this iteration | iteration | 1149929.5599 | C_100 - C this iteration | iteration | 1534585.4555 | C_100 - C this iteration | iteration | 1872485.8882 | C_100 - C this iteration | iteration | 2173897.9856 | C_100 - C this iteration | iteration | 2549066.3542 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0963 |  |  | 88.4179 |  |  | 79.5895 |  |  | 49.9885 |  |  | -22.9538 |  |  | -150.8255 |  |  | -339.0308 |  |  | -548.8588 |  |  | -771.1495 |  |  | -1094.0988
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0963 |  |  | 28.4179 |  |  | 19.5895 |  |  | -10.0115 |  |  | -82.9538 |  |  | -210.8255 |  |  | -399.0308 |  |  | -608.8588 |  |  | -831.1495 |  |  | -1154.0988
[13 empty] | Press drop ratio this iteration |  |  | 0.33405 |  |  | 0.3214 |  |  | 0.24613 |  |  | -0.20028 |  |  | 3.6139 |  |  | 1.3978 |  |  | 1.177 |  |  | 1.1093 |  |  | 1.0778 |  |  | 1.0548
[13 empty] | Expansion factor | 12 |  | 0.82603 |  |  | 0.83265 |  |  | 0.87062 |  |  | 1.1068 |  |  | -0.98619 |  |  | 0.18568 |  |  | 0.26232 |  |  | 0.22262 |  |  | 0.39163 |  |  | 0.066571
[13 empty] | C Non choked w/ reducers | 7 |  | 8.925 |  |  | 41.071 |  |  | 122.3817 |  |  | #NUM! |  |  | 325.3422 |  |  | -631.0416 |  |  | -299.4466 |  |  | -290.6424 |  |  | -157.6397 |  |  | -1037.6739
[13 empty] | C Choked w/ reducers | 7 |  | 7.985 |  |  | 36.3284 |  |  | 99.5203 |  |  | 312.6355 |  |  | -1174.2078 |  |  | -274.5718 |  |  | -175.1915 |  |  | -148.1407 |  |  | -125.0429 |  |  | -173.3099
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 8.925 |  |  | 41.071 |  |  | 122.3817 |  |  | #NUM! |  |  | -1174.2078 |  |  | -274.5718 |  |  | -175.1915 |  |  | -148.1407 |  |  | -125.0429 |  |  | -173.3099
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.195 | 22065.9902 |  | 29.471 | 98467.2737 |  | 99.3817 | 241110.1838 |  | 236393 | 469621.0958 |  | 236393 | 787878.1097 |  | 236393 | 1149929.5599 |  | 236393 | 1534585.4555 |  | 236393 | 1872485.8882 |  | 236393 | 2173897.9856 |  | 236393 | 2549066.3542
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 22507.31 | C_100 - C this iteration | iteration | 99451.9465 | C_100 - C this iteration | iteration | 243521.2857 | C_100 - C this iteration | iteration | 474317.3068 | C_100 - C this iteration | iteration | 795756.8908 | C_100 - C this iteration | iteration | 1161428.8555 | C_100 - C this iteration | iteration | 1549931.31 | C_100 - C this iteration | iteration | 1891210.7471 | C_100 - C this iteration | iteration | 2195636.9655 | C_100 - C this iteration | iteration | 2574557.0177 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0927 |  |  | 88.3824 |  |  | 79.3765 |  |  | 49.1805 |  |  | -25.2279 |  |  | -155.6698 |  |  | -347.658 |  |  | -561.7036 |  |  | -788.4623 |  |  | -1117.9029
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0927 |  |  | 28.3824 |  |  | 19.3765 |  |  | -10.8195 |  |  | -85.2279 |  |  | -215.6698 |  |  | -407.658 |  |  | -621.7036 |  |  | -848.4623 |  |  | -1177.9029
[13 empty] | Press drop ratio this iteration |  |  | 0.33402 |  |  | 0.32113 |  |  | 0.24411 |  |  | -0.21999 |  |  | 3.3783 |  |  | 1.3854 |  |  | 1.1726 |  |  | 1.1068 |  |  | 1.0761 |  |  | 1.0537
[13 empty] | Expansion factor | 12 |  | 0.82604 |  |  | 0.83279 |  |  | 0.87168 |  |  | 1.1173 |  |  | -0.85669 |  |  | 0.19289 |  |  | 0.26507 |  |  | 0.22437 |  |  | 0.39259 |  |  | 0.067605
[13 empty] | C Non choked w/ reducers | 7 |  | 9.104 |  |  | 41.5089 |  |  | 124.2978 |  |  | #NUM! |  |  | 355.9687 |  |  | -597.08 |  |  | -292.4193 |  |  | -284.9178 |  |  | -155.4608 |  |  | -1010.6153
[13 empty] | C Choked w/ reducers | 7 |  | 8.1451 |  |  | 36.7064 |  |  | 100.7852 |  |  | 320.9492 |  |  | -1079.0459 |  |  | -268.6876 |  |  | -172.5525 |  |  | -146.2007 |  |  | -123.5202 |  |  | -171.3157
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 9.104 |  |  | 41.5089 |  |  | 124.2978 |  |  | #NUM! |  |  | -1079.0459 |  |  | -268.6876 |  |  | -172.5525 |  |  | -146.2007 |  |  | -123.5202 |  |  | -171.3157
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.374 | 22507.31 |  | 29.9089 | 99451.9465 |  | 101.2978 | 243521.2857 |  | 236393 | 474317.3068 |  | 236393 | 795756.8908 |  | 236393 | 1161428.8555 |  | 236393 | 1549931.31 |  | 236393 | 1891210.7471 |  | 236393 | 2195636.9655 |  | 236393 | 2574557.0177
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 22957.4562 | C_100 - C this iteration | iteration | 100446.4659 | C_100 - C this iteration | iteration | 245956.4985 | C_100 - C this iteration | iteration | 479060.4798 | C_100 - C this iteration | iteration | 803714.4597 | C_100 - C this iteration | iteration | 1173043.1441 | C_100 - C this iteration | iteration | 1565430.6231 | C_100 - C this iteration | iteration | 1910122.8546 | C_100 - C this iteration | iteration | 2217593.3351 | C_100 - C this iteration | iteration | 2600302.5879 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.089 |  |  | 88.3461 |  |  | 79.1592 |  |  | 48.3564 |  |  | -27.5477 |  |  | -160.6115 |  |  | -356.4586 |  |  | -574.8065 |  |  | -806.1231 |  |  | -1142.1855
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.089 |  |  | 28.3461 |  |  | 19.1592 |  |  | -11.6436 |  |  | -87.5477 |  |  | -220.6115 |  |  | -416.4586 |  |  | -634.8065 |  |  | -866.1231 |  |  | -1202.1855
[13 empty] | Press drop ratio this iteration |  |  | 0.33399 |  |  | 0.32085 |  |  | 0.24203 |  |  | -0.24079 |  |  | 3.178 |  |  | 1.3736 |  |  | 1.1683 |  |  | 1.1044 |  |  | 1.0744 |  |  | 1.0525
[13 empty] | Expansion factor | 12 |  | 0.82605 |  |  | 0.83294 |  |  | 0.87278 |  |  | 1.1284 |  |  | -0.74662 |  |  | 0.1998 |  |  | 0.26774 |  |  | 0.22608 |  |  | 0.39353 |  |  | 0.068614
[13 empty] | C Non choked w/ reducers | 7 |  | 9.2867 |  |  | 41.9521 |  |  | 126.2657 |  |  | #NUM! |  |  | 389.5152 |  |  | -566.7164 |  |  | -285.698 |  |  | -279.3922 |  |  | -153.327 |  |  | -984.8532
[13 empty] | C Choked w/ reducers | 7 |  | 8.3083 |  |  | 37.0887 |  |  | 102.0724 |  |  | 329.6837 |  |  | -998.0608 |  |  | -263.0249 |  |  | -169.9752 |  |  | -144.2966 |  |  | -122.0222 |  |  | -169.3503
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 9.2867 |  |  | 41.9521 |  |  | 126.2657 |  |  | #NUM! |  |  | -998.0608 |  |  | -263.0249 |  |  | -169.9752 |  |  | -144.2966 |  |  | -122.0222 |  |  | -169.3503
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5567 | 22957.4562 |  | 30.3521 | 100446.4659 |  | 103.2657 | 245956.4985 |  | 236393 | 479060.4798 |  | 236393 | 803714.4597 |  | 236393 | 1173043.1441 |  | 236393 | 1565430.6231 |  | 236393 | 1910122.8546 |  | 236393 | 2217593.3351 |  | 236393 | 2600302.5879
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 23416.6053 | C_100 - C this iteration | iteration | 101450.9306 | C_100 - C this iteration | iteration | 248416.0635 | C_100 - C this iteration | iteration | 483851.0846 | C_100 - C this iteration | iteration | 811751.6043 | C_100 - C this iteration | iteration | 1184773.5755 | C_100 - C this iteration | iteration | 1581084.9294 | C_100 - C this iteration | iteration | 1929224.0831 | C_100 - C this iteration | iteration | 2239769.2685 | C_100 - C this iteration | iteration | 2626305.6138 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0851 |  |  | 88.3092 |  |  | 78.9376 |  |  | 47.5156 |  |  | -29.9141 |  |  | -165.6525 |  |  | -365.4362 |  |  | -588.1729 |  |  | -824.1389 |  |  | -1166.9562
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0851 |  |  | 28.3092 |  |  | 18.9376 |  |  | -12.4844 |  |  | -89.9141 |  |  | -225.6525 |  |  | -425.4362 |  |  | -648.1729 |  |  | -884.1389 |  |  | -1226.9562
[13 empty] | Press drop ratio this iteration |  |  | 0.33396 |  |  | 0.32057 |  |  | 0.23991 |  |  | -0.26274 |  |  | 3.0057 |  |  | 1.3622 |  |  | 1.1642 |  |  | 1.102 |  |  | 1.0728 |  |  | 1.0514
[13 empty] | Expansion factor | 12 |  | 0.82607 |  |  | 0.83308 |  |  | 0.87389 |  |  | 1.1401 |  |  | -0.65192 |  |  | 0.20642 |  |  | 0.27033 |  |  | 0.22774 |  |  | 0.39445 |  |  | 0.069601
[13 empty] | C Non choked w/ reducers | 7 |  | 9.4731 |  |  | 42.4006 |  |  | 128.2879 |  |  | #NUM! |  |  | 426.6386 |  |  | -539.3968 |  |  | -279.2623 |  |  | -274.055 |  |  | -151.2369 |  |  | -960.294
[13 empty] | C Choked w/ reducers | 7 |  | 8.4748 |  |  | 37.4753 |  |  | 103.3825 |  |  | 338.8724 |  |  | -928.2978 |  |  | -257.5709 |  |  | -167.4575 |  |  | -142.4276 |  |  | -120.5484 |  |  | -167.4131
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 9.4731 |  |  | 42.4006 |  |  | 128.2879 |  |  | #NUM! |  |  | -928.2978 |  |  | -257.5709 |  |  | -167.4575 |  |  | -142.4276 |  |  | -120.5484 |  |  | -167.4131
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.7431 | 23416.6053 |  | 30.8006 | 101450.9306 |  | 105.2879 | 248416.0635 |  | 236393 | 483851.0846 |  | 236393 | 811751.6043 |  | 236393 | 1184773.5755 |  | 236393 | 1581084.9294 |  | 236393 | 1929224.0831 |  | 236393 | 2239769.2685 |  | 236393 | 2626305.6138
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 23884.9374 | C_100 - C this iteration | iteration | 102465.4399 | C_100 - C this iteration | iteration | 250900.2241 | C_100 - C this iteration | iteration | 488689.5955 | C_100 - C this iteration | iteration | 819869.1204 | C_100 - C this iteration | iteration | 1196621.3113 | C_100 - C this iteration | iteration | 1596895.7787 | C_100 - C this iteration | iteration | 1948516.324 | C_100 - C this iteration | iteration | 2262166.9612 | C_100 - C this iteration | iteration | 2652568.6699 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0811 |  |  | 88.2715 |  |  | 78.7115 |  |  | 46.6579 |  |  | -32.3281 |  |  | -170.7948 |  |  | -374.5942 |  |  | -601.8079 |  |  | -842.5168 |  |  | -1192.2247
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0811 |  |  | 28.2715 |  |  | 18.7115 |  |  | -13.3421 |  |  | -92.3281 |  |  | -230.7948 |  |  | -434.5942 |  |  | -661.8079 |  |  | -902.5168 |  |  | -1252.2247
[13 empty] | Press drop ratio this iteration |  |  | 0.33393 |  |  | 0.32028 |  |  | 0.23772 |  |  | -0.28595 |  |  | 2.856 |  |  | 1.3513 |  |  | 1.1602 |  |  | 1.0997 |  |  | 1.0712 |  |  | 1.0503
[13 empty] | Expansion factor | 12 |  | 0.82608 |  |  | 0.83323 |  |  | 0.87504 |  |  | 1.1524 |  |  | -0.56961 |  |  | 0.21278 |  |  | 0.27285 |  |  | 0.22936 |  |  | 0.39535 |  |  | 0.070565
[13 empty] | C Non choked w/ reducers | 7 |  | 9.6632 |  |  | 42.8545 |  |  | 130.367 |  |  | #NUM! |  |  | 468.1609 |  |  | -514.6757 |  |  | -273.0934 |  |  | -268.896 |  |  | -149.189 |  |  | -936.853
[13 empty] | C Choked w/ reducers | 7 |  | 8.6447 |  |  | 37.8662 |  |  | 104.7163 |  |  | 348.5525 |  |  | -867.5701 |  |  | -252.3141 |  |  | -164.9972 |  |  | -140.5927 |  |  | -119.098 |  |  | -165.5035
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 9.6632 |  |  | 42.8545 |  |  | 130.367 |  |  | #NUM! |  |  | -867.5701 |  |  | -252.3141 |  |  | -164.9972 |  |  | -140.5927 |  |  | -119.098 |  |  | -165.5035
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.9332 | 23884.9374 |  | 31.2545 | 102465.4399 |  | 107.367 | 250900.2241 |  | 236393 | 488689.5955 |  | 236393 | 819869.1204 |  | 236393 | 1196621.3113 |  | 236393 | 1596895.7787 |  | 236393 | 1948516.324 |  | 236393 | 2262166.9612 |  | 236393 | 2652568.6699
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 24362.6362 | C_100 - C this iteration | iteration | 103490.0943 | C_100 - C this iteration | iteration | 253409.2264 | C_100 - C this iteration | iteration | 493576.4914 | C_100 - C this iteration | iteration | 828067.8116 | C_100 - C this iteration | iteration | 1208587.5244 | C_100 - C this iteration | iteration | 1612864.7365 | C_100 - C this iteration | iteration | 1968001.4872 | C_100 - C this iteration | iteration | 2284788.6308 | C_100 - C this iteration | iteration | 2679094.3566 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0769 |  |  | 88.233 |  |  | 78.4809 |  |  | 45.783 |  |  | -34.7906 |  |  | -176.0405 |  |  | -383.9362 |  |  | -615.7169 |  |  | -861.2641 |  |  | -1218.0011
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0769 |  |  | 28.233 |  |  | 18.4809 |  |  | -14.217 |  |  | -94.7906 |  |  | -236.0405 |  |  | -443.9362 |  |  | -675.7169 |  |  | -921.2641 |  |  | -1278.0011
[13 empty] | Press drop ratio this iteration |  |  | 0.3339 |  |  | 0.31998 |  |  | 0.23548 |  |  | -0.31053 |  |  | 2.7246 |  |  | 1.3408 |  |  | 1.1563 |  |  | 1.0974 |  |  | 1.0697 |  |  | 1.0493
[13 empty] | Expansion factor | 12 |  | 0.8261 |  |  | 0.83339 |  |  | 0.87622 |  |  | 1.1655 |  |  | -0.49741 |  |  | 0.21888 |  |  | 0.27529 |  |  | 0.23094 |  |  | 0.39622 |  |  | 0.071508
[13 empty] | C Non choked w/ reducers | 7 |  | 9.8572 |  |  | 43.314 |  |  | 132.5059 |  |  | #NUM! |  |  | 515.1352 |  |  | -492.191 |  |  | -267.1741 |  |  | -263.9061 |  |  | -147.1821 |  |  | -914.4534
[13 empty] | C Choked w/ reducers | 7 |  | 8.818 |  |  | 38.2615 |  |  | 106.0742 |  |  | 358.7653 |  |  | -814.2242 |  |  | -247.2435 |  |  | -162.5922 |  |  | -138.7909 |  |  | -117.6706 |  |  | -163.621
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 9.8572 |  |  | 43.314 |  |  | 132.5059 |  |  | #NUM! |  |  | -814.2242 |  |  | -247.2435 |  |  | -162.5922 |  |  | -138.7909 |  |  | -117.6706 |  |  | -163.621
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.1272 | 24362.6362 |  | 31.714 | 103490.0943 |  | 109.5059 | 253409.2264 |  | 236393 | 493576.4914 |  | 236393 | 828067.8116 |  | 236393 | 1208587.5244 |  | 236393 | 1612864.7365 |  | 236393 | 1968001.4872 |  | 236393 | 2284788.6308 |  | 236393 | 2679094.3566
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 24849.8889 | C_100 - C this iteration | iteration | 104524.9952 | C_100 - C this iteration | iteration | 255943.3186 | C_100 - C this iteration | iteration | 498512.2564 | C_100 - C this iteration | iteration | 836348.4897 | C_100 - C this iteration | iteration | 1220673.3996 | C_100 - C this iteration | iteration | 1628993.3838 | C_100 - C this iteration | iteration | 1987681.5021 | C_100 - C this iteration | iteration | 2307636.5171 | C_100 - C this iteration | iteration | 2705885.3002 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0725 |  |  | 88.1938 |  |  | 78.2457 |  |  | 44.8906 |  |  | -37.3026 |  |  | -181.3917 |  |  | -393.4661 |  |  | -629.9055 |  |  | -880.3883 |  |  | -1244.2957
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0725 |  |  | 28.1938 |  |  | 18.2457 |  |  | -15.1094 |  |  | -97.3026 |  |  | -241.3917 |  |  | -453.4661 |  |  | -689.9055 |  |  | -940.3883 |  |  | -1304.2957
[13 empty] | Press drop ratio this iteration |  |  | 0.33387 |  |  | 0.31968 |  |  | 0.23318 |  |  | -0.33658 |  |  | 2.6085 |  |  | 1.3308 |  |  | 1.1525 |  |  | 1.0953 |  |  | 1.0682 |  |  | 1.0482
[13 empty] | Expansion factor | 12 |  | 0.82612 |  |  | 0.83355 |  |  | 0.87743 |  |  | 1.1794 |  |  | -0.43359 |  |  | 0.22473 |  |  | 0.27766 |  |  | 0.23248 |  |  | 0.39708 |  |  | 0.072429
[13 empty] | C Non choked w/ reducers | 7 |  | 10.0551 |  |  | 43.779 |  |  | 134.7076 |  |  | #NUM! |  |  | 568.9407 |  |  | -471.6448 |  |  | -261.4887 |  |  | -259.0766 |  |  | -145.2147 |  |  | -893.0252
[13 empty] | C Choked w/ reducers | 7 |  | 8.9948 |  |  | 38.6613 |  |  | 107.4571 |  |  | 369.557 |  |  | -766.9871 |  |  | -242.3492 |  |  | -160.2408 |  |  | -137.0213 |  |  | -116.2657 |  |  | -161.765
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 10.0551 |  |  | 43.779 |  |  | 134.7076 |  |  | #NUM! |  |  | -766.9871 |  |  | -242.3492 |  |  | -160.2408 |  |  | -137.0213 |  |  | -116.2657 |  |  | -161.765
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.3251 | 24849.8889 |  | 32.179 | 104524.9952 |  | 111.7076 | 255943.3186 |  | 236393 | 498512.2564 |  | 236393 | 836348.4897 |  | 236393 | 1220673.3996 |  | 236393 | 1628993.3838 |  | 236393 | 1987681.5021 |  | 236393 | 2307636.5171 |  | 236393 | 2705885.3002
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 25346.8867 | C_100 - C this iteration | iteration | 105570.2452 | C_100 - C this iteration | iteration | 258502.7518 | C_100 - C this iteration | iteration | 503497.3789 | C_100 - C this iteration | iteration | 844711.9746 | C_100 - C this iteration | iteration | 1232880.1336 | C_100 - C this iteration | iteration | 1645283.3177 | C_100 - C this iteration | iteration | 2007558.3171 | C_100 - C this iteration | iteration | 2330712.8822 | C_100 - C this iteration | iteration | 2732944.1532 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0679 |  |  | 88.1537 |  |  | 78.0057 |  |  | 43.9801 |  |  | -39.8651 |  |  | -186.8503 |  |  | -403.1874 |  |  | -644.3794 |  |  | -899.8968 |  |  | -1271.1187
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0679 |  |  | 28.1537 |  |  | 18.0057 |  |  | -16.0199 |  |  | -99.8651 |  |  | -246.8503 |  |  | -463.1874 |  |  | -704.3794 |  |  | -959.8968 |  |  | -1331.1187
[13 empty] | Press drop ratio this iteration |  |  | 0.33384 |  |  | 0.31937 |  |  | 0.23083 |  |  | -0.36425 |  |  | 2.5051 |  |  | 1.3211 |  |  | 1.1488 |  |  | 1.0931 |  |  | 1.0667 |  |  | 1.0472
[13 empty] | Expansion factor | 12 |  | 0.82614 |  |  | 0.83371 |  |  | 0.87867 |  |  | 1.1942 |  |  | -0.37676 |  |  | 0.23036 |  |  | 0.27997 |  |  | 0.23398 |  |  | 0.39791 |  |  | 0.073329
[13 empty] | C Non choked w/ reducers | 7 |  | 10.2571 |  |  | 44.2497 |  |  | 136.9753 |  |  | #NUM! |  |  | 631.4276 |  |  | -452.7905 |  |  | -256.0229 |  |  | -254.3994 |  |  | -143.2857 |  |  | -872.5045
[13 empty] | C Choked w/ reducers | 7 |  | 9.1752 |  |  | 39.0657 |  |  | 108.8655 |  |  | 380.9792 |  |  | -724.8626 |  |  | -237.6219 |  |  | -157.9409 |  |  | -135.283 |  |  | -114.8827 |  |  | -159.9349
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 10.2571 |  |  | 44.2497 |  |  | 136.9753 |  |  | #NUM! |  |  | -724.8626 |  |  | -237.6219 |  |  | -157.9409 |  |  | -135.283 |  |  | -114.8827 |  |  | -159.9349
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.5271 | 25346.8867 |  | 32.6497 | 105570.2452 |  | 113.9753 | 258502.7518 |  | 236393 | 503497.3789 |  | 236393 | 844711.9746 |  | 236393 | 1232880.1336 |  | 236393 | 1645283.3177 |  | 236393 | 2007558.3171 |  | 236393 | 2330712.8822 |  | 236393 | 2732944.1532
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 25853.8244 | C_100 - C this iteration | iteration | 106625.9476 | C_100 - C this iteration | iteration | 261087.7793 | C_100 - C this iteration | iteration | 508532.3527 | C_100 - C this iteration | iteration | 853159.0943 | C_100 - C this iteration | iteration | 1245208.935 | C_100 - C this iteration | iteration | 1661736.1508 | C_100 - C this iteration | iteration | 2027633.9003 | C_100 - C this iteration | iteration | 2354020.0111 | C_100 - C this iteration | iteration | 2760273.5947 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0632 |  |  | 88.1129 |  |  | 77.7609 |  |  | 43.0514 |  |  | -42.4791 |  |  | -192.4188 |  |  | -413.1042 |  |  | -659.1441 |  |  | -919.7974 |  |  | -1298.4809
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0632 |  |  | 28.1129 |  |  | 17.7609 |  |  | -16.9486 |  |  | -102.4791 |  |  | -252.4188 |  |  | -473.1042 |  |  | -719.1441 |  |  | -979.7974 |  |  | -1358.4809
[13 empty] | Press drop ratio this iteration |  |  | 0.3338 |  |  | 0.31906 |  |  | 0.2284 |  |  | -0.39368 |  |  | 2.4125 |  |  | 1.3118 |  |  | 1.1452 |  |  | 1.091 |  |  | 1.0652 |  |  | 1.0462
[13 empty] | Expansion factor | 12 |  | 0.82615 |  |  | 0.83387 |  |  | 0.87994 |  |  | 1.2099 |  |  | -0.32586 |  |  | 0.23578 |  |  | 0.2822 |  |  | 0.23544 |  |  | 0.39873 |  |  | 0.07421
[13 empty] | C Non choked w/ reducers | 7 |  | 10.4631 |  |  | 44.7262 |  |  | 139.3124 |  |  | #NUM! |  |  | 705.1439 |  |  | -435.4216 |  |  | -250.7636 |  |  | -249.8669 |  |  | -141.3939 |  |  | -852.8331
[13 empty] | C Choked w/ reducers | 7 |  | 9.3592 |  |  | 39.4746 |  |  | 110.3003 |  |  | 393.0897 |  |  | -687.0598 |  |  | -233.0528 |  |  | -155.691 |  |  | -133.5752 |  |  | -113.5211 |  |  | -158.1304
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 10.4631 |  |  | 44.7262 |  |  | 139.3124 |  |  | #NUM! |  |  | -687.0598 |  |  | -233.0528 |  |  | -155.691 |  |  | -133.5752 |  |  | -113.5211 |  |  | -158.1304
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.7331 | 25853.8244 |  | 33.1262 | 106625.9476 |  | 116.3124 | 261087.7793 |  | 236393 | 508532.3527 |  | 236393 | 853159.0943 |  | 236393 | 1245208.935 |  | 236393 | 1661736.1508 |  | 236393 | 2027633.9003 |  | 236393 | 2354020.0111 |  | 236393 | 2760273.5947
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 26370.9009 | C_100 - C this iteration | iteration | 107692.2071 | C_100 - C this iteration | iteration | 263698.6571 | C_100 - C this iteration | iteration | 513617.6762 | C_100 - C this iteration | iteration | 861690.6853 | C_100 - C this iteration | iteration | 1257661.0243 | C_100 - C this iteration | iteration | 1678353.5123 | C_100 - C this iteration | iteration | 2047910.2393 | C_100 - C this iteration | iteration | 2377560.2112 | C_100 - C this iteration | iteration | 2787876.3306 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0583 |  |  | 88.0712 |  |  | 77.5112 |  |  | 42.104 |  |  | -45.1457 |  |  | -198.0991 |  |  | -423.2203 |  |  | -674.2056 |  |  | -940.0981 |  |  | -1326.3931
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0583 |  |  | 28.0712 |  |  | 17.5112 |  |  | -17.896 |  |  | -105.1457 |  |  | -258.0991 |  |  | -483.2203 |  |  | -734.2056 |  |  | -1000.0981 |  |  | -1386.3931
[13 empty] | Press drop ratio this iteration |  |  | 0.33376 |  |  | 0.31873 |  |  | 0.22592 |  |  | -0.42504 |  |  | 2.329 |  |  | 1.3029 |  |  | 1.1418 |  |  | 1.089 |  |  | 1.0638 |  |  | 1.0452
[13 empty] | Expansion factor | 12 |  | 0.82617 |  |  | 0.83404 |  |  | 0.88125 |  |  | 1.2266 |  |  | -0.28001 |  |  | 0.24098 |  |  | 0.28438 |  |  | 0.23686 |  |  | 0.39952 |  |  | 0.07507
[13 empty] | C Non choked w/ reducers | 7 |  | 10.6732 |  |  | 45.2086 |  |  | 141.7229 |  |  | #NUM! |  |  | 793.7055 |  |  | -419.364 |  |  | -245.6985 |  |  | -245.4723 |  |  | -139.5383 |  |  | -833.9576
[13 empty] | C Choked w/ reducers | 7 |  | 9.5469 |  |  | 39.8882 |  |  | 111.7623 |  |  | 405.954 |  |  | -652.943 |  |  | -228.6339 |  |  | -153.4892 |  |  | -131.8971 |  |  | -112.1804 |  |  | -156.3507
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 10.6732 |  |  | 45.2086 |  |  | 141.7229 |  |  | #NUM! |  |  | -652.943 |  |  | -228.6339 |  |  | -153.4892 |  |  | -131.8971 |  |  | -112.1804 |  |  | -156.3507
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.9432 | 26370.9009 |  | 33.6086 | 107692.2071 |  | 118.7229 | 263698.6571 |  | 236393 | 513617.6762 |  | 236393 | 861690.6853 |  | 236393 | 1257661.0243 |  | 236393 | 1678353.5123 |  | 236393 | 2047910.2393 |  | 236393 | 2377560.2112 |  | 236393 | 2787876.3306
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 26898.3189 | C_100 - C this iteration | iteration | 108769.1292 | C_100 - C this iteration | iteration | 266335.6437 | C_100 - C this iteration | iteration | 518753.853 | C_100 - C this iteration | iteration | 870307.5921 | C_100 - C this iteration | iteration | 1270237.6345 | C_100 - C this iteration | iteration | 1695137.0475 | C_100 - C this iteration | iteration | 2068389.3417 | C_100 - C this iteration | iteration | 2401335.8133 | C_100 - C this iteration | iteration | 2815755.094 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0532 |  |  | 88.0288 |  |  | 77.2564 |  |  | 41.1376 |  |  | -47.8658 |  |  | -203.8936 |  |  | -433.5398 |  |  | -689.5699 |  |  | -960.8068 |  |  | -1354.8664
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0532 |  |  | 28.0288 |  |  | 17.2564 |  |  | -18.8624 |  |  | -107.8658 |  |  | -263.8936 |  |  | -493.5398 |  |  | -749.5699 |  |  | -1020.8068 |  |  | -1414.8664
[13 empty] | Press drop ratio this iteration |  |  | 0.33373 |  |  | 0.3184 |  |  | 0.22337 |  |  | -0.45852 |  |  | 2.2535 |  |  | 1.2943 |  |  | 1.1384 |  |  | 1.087 |  |  | 1.0624 |  |  | 1.0443
[13 empty] | Expansion factor | 12 |  | 0.82619 |  |  | 0.83421 |  |  | 0.88259 |  |  | 1.2444 |  |  | -0.2385 |  |  | 0.246 |  |  | 0.2865 |  |  | 0.23825 |  |  | 0.4003 |  |  | 0.075911
[13 empty] | C Non choked w/ reducers | 7 |  | 10.8877 |  |  | 45.6969 |  |  | 144.2108 |  |  | #NUM! |  |  | 902.4283 |  |  | -404.4702 |  |  | -240.8164 |  |  | -241.209 |  |  | -137.7176 |  |  | -815.829
[13 empty] | C Choked w/ reducers | 7 |  | 9.7384 |  |  | 40.3065 |  |  | 113.2521 |  |  | 419.6458 |  |  | -621.9956 |  |  | -224.3576 |  |  | -151.3341 |  |  | -130.2479 |  |  | -110.8601 |  |  | -154.5956
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 10.8877 |  |  | 45.6969 |  |  | 144.2108 |  |  | #NUM! |  |  | -621.9956 |  |  | -224.3576 |  |  | -151.3341 |  |  | -130.2479 |  |  | -110.8601 |  |  | -154.5956
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 6.1577 | 26898.3189 |  | 34.0969 | 108769.1292 |  | 121.2108 | 266335.6437 |  | 236393 | 518753.853 |  | 236393 | 870307.5921 |  | 236393 | 1270237.6345 |  | 236393 | 1695137.0475 |  | 236393 | 2068389.3417 |  | 236393 | 2401335.8133 |  | 236393 | 2815755.094
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 27436.2853 | C_100 - C this iteration | iteration | 109856.8205 | C_100 - C this iteration | iteration | 268999.0001 | C_100 - C this iteration | iteration | 523941.3915 | C_100 - C this iteration | iteration | 879010.6681 | C_100 - C this iteration | iteration | 1282940.0109 | C_100 - C this iteration | iteration | 1712088.4179 | C_100 - C this iteration | iteration | 2089073.2351 | C_100 - C this iteration | iteration | 2425349.1714 | C_100 - C this iteration | iteration | 2843912.6449 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0478 |  |  | 87.9854 |  |  | 76.9966 |  |  | 40.1518 |  |  | -50.6406 |  |  | -209.8046 |  |  | -444.0667 |  |  | -705.2429 |  |  | -981.9317 |  |  | -1383.9119
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0478 |  |  | 27.9854 |  |  | 16.9966 |  |  | -19.8482 |  |  | -110.6406 |  |  | -269.8046 |  |  | -504.0667 |  |  | -765.2429 |  |  | -1041.9317 |  |  | -1443.9119
[13 empty] | Press drop ratio this iteration |  |  | 0.33369 |  |  | 0.31807 |  |  | 0.22074 |  |  | -0.49433 |  |  | 2.1848 |  |  | 1.286 |  |  | 1.1351 |  |  | 1.0851 |  |  | 1.0611 |  |  | 1.0434
[13 empty] | Expansion factor | 12 |  | 0.82621 |  |  | 0.83439 |  |  | 0.88397 |  |  | 1.2635 |  |  | -0.20075 |  |  | 0.25083 |  |  | 0.28855 |  |  | 0.23961 |  |  | 0.40106 |  |  | 0.076734
[13 empty] | C Non choked w/ reducers | 7 |  | 11.1065 |  |  | 46.1913 |  |  | 146.7805 |  |  | #NUM! |  |  | 1039.4674 |  |  | -390.614 |  |  | -236.1071 |  |  | -237.0707 |  |  | -135.931 |  |  | -798.4023
[13 empty] | C Choked w/ reducers | 7 |  | 9.9337 |  |  | 40.7297 |  |  | 114.7707 |  |  | 434.249 |  |  | -593.7929 |  |  | -220.217 |  |  | -149.2241 |  |  | -128.6268 |  |  | -109.5599 |  |  | -152.8645
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 11.1065 |  |  | 46.1913 |  |  | 146.7805 |  |  | #NUM! |  |  | -593.7929 |  |  | -220.217 |  |  | -149.2241 |  |  | -128.6268 |  |  | -109.5599 |  |  | -152.8645
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 6.3765 | 27436.2853 |  | 34.5913 | 109856.8205 |  | 123.7805 | 268999.0001 |  | 236393 | 523941.3915 |  | 236393 | 879010.6681 |  | 236393 | 1282940.0109 |  | 236393 | 1712088.4179 |  | 236393 | 2089073.2351 |  | 236393 | 2425349.1714 |  | 236393 | 2843912.6449
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 27985.011 | C_100 - C this iteration | iteration | 110955.3887 | C_100 - C this iteration | iteration | 271688.9901 | C_100 - C this iteration | iteration | 529180.8054 | C_100 - C this iteration | iteration | 887800.7747 | C_100 - C this iteration | iteration | 1295769.411 | C_100 - C this iteration | iteration | 1729209.3021 | C_100 - C this iteration | iteration | 2109963.9674 | C_100 - C this iteration | iteration | 2449602.6631 | C_100 - C this iteration | iteration | 2872351.7713 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0423 |  |  | 87.9412 |  |  | 76.7315 |  |  | 39.1461 |  |  | -53.4712 |  |  | -215.8344 |  |  | -454.8051 |  |  | -721.231 |  |  | -1003.4813 |  |  | -1413.5412
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0423 |  |  | 27.9412 |  |  | 16.7315 |  |  | -20.8539 |  |  | -113.4712 |  |  | -275.8344 |  |  | -514.8051 |  |  | -781.231 |  |  | -1063.4813 |  |  | -1473.5412
[13 empty] | Press drop ratio this iteration |  |  | 0.33365 |  |  | 0.31773 |  |  | 0.21805 |  |  | -0.53272 |  |  | 2.1221 |  |  | 1.278 |  |  | 1.1319 |  |  | 1.0832 |  |  | 1.0598 |  |  | 1.0424
[13 empty] | Expansion factor | 12 |  | 0.82623 |  |  | 0.83456 |  |  | 0.88538 |  |  | 1.284 |  |  | -0.16628 |  |  | 0.25548 |  |  | 0.29055 |  |  | 0.24093 |  |  | 0.4018 |  |  | 0.077538
[13 empty] | C Non choked w/ reducers | 7 |  | 11.3297 |  |  | 46.6918 |  |  | 149.4367 |  |  | #NUM! |  |  | 1218.0124 |  |  | -377.6868 |  |  | -231.5609 |  |  | -233.0518 |  |  | -134.1774 |  |  | -781.6361
[13 empty] | C Choked w/ reducers | 7 |  | 10.133 |  |  | 41.1576 |  |  | 116.3188 |  |  | 449.8589 |  |  | -567.9829 |  |  | -216.2054 |  |  | -147.1578 |  |  | -127.0332 |  |  | -108.2792 |  |  | -151.1569
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 11.3297 |  |  | 46.6918 |  |  | 149.4367 |  |  | #NUM! |  |  | -567.9829 |  |  | -216.2054 |  |  | -147.1578 |  |  | -127.0332 |  |  | -108.2792 |  |  | -151.1569
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 6.5997 | 27985.011 |  | 35.0918 | 110955.3887 |  | 126.4367 | 271688.9901 |  | 236393 | 529180.8054 |  | 236393 | 887800.7747 |  | 236393 | 1295769.411 |  | 236393 | 1729209.3021 |  | 236393 | 2109963.9674 |  | 236393 | 2449602.6631 |  | 236393 | 2872351.7713
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 28544.7112 | C_100 - C this iteration | iteration | 112064.9426 | C_100 - C this iteration | iteration | 274405.8801 | C_100 - C this iteration | iteration | 534472.6135 | C_100 - C this iteration | iteration | 896678.7825 | C_100 - C this iteration | iteration | 1308727.1051 | C_100 - C this iteration | iteration | 1746501.3951 | C_100 - C this iteration | iteration | 2131063.6071 | C_100 - C this iteration | iteration | 2474098.6898 | C_100 - C this iteration | iteration | 2901075.2891 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0365 |  |  | 87.8961 |  |  | 76.4611 |  |  | 38.1202 |  |  | -56.3587 |  |  | -221.9854 |  |  | -465.7594 |  |  | -737.5405 |  |  | -1025.4639 |  |  | -1443.7661
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0365 |  |  | 27.8961 |  |  | 16.4611 |  |  | -21.8798 |  |  | -116.3587 |  |  | -281.9854 |  |  | -525.7594 |  |  | -797.5405 |  |  | -1085.4639 |  |  | -1503.7661
[13 empty] | Press drop ratio this iteration |  |  | 0.3336 |  |  | 0.31738 |  |  | 0.21529 |  |  | -0.57397 |  |  | 2.0646 |  |  | 1.2703 |  |  | 1.1288 |  |  | 1.0814 |  |  | 1.0585 |  |  | 1.0416
[13 empty] | Expansion factor | 12 |  | 0.82626 |  |  | 0.83475 |  |  | 0.88684 |  |  | 1.306 |  |  | -0.13469 |  |  | 0.25997 |  |  | 0.2925 |  |  | 0.24222 |  |  | 0.40252 |  |  | 0.078324
[13 empty] | C Non choked w/ reducers | 7 |  | 11.5575 |  |  | 47.1987 |  |  | 152.1847 |  |  | #NUM! |  |  | 1460.8904 |  |  | -365.5951 |  |  | -227.1691 |  |  | -229.1468 |  |  | -132.4558 |  |  | -765.492
[13 empty] | C Choked w/ reducers | 7 |  | 10.3363 |  |  | 41.5906 |  |  | 117.8975 |  |  | 466.5851 |  |  | -544.2717 |  |  | -212.3167 |  |  | -145.1337 |  |  | -125.4663 |  |  | -107.0176 |  |  | -149.4723
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 11.5575 |  |  | 47.1987 |  |  | 152.1847 |  |  | #NUM! |  |  | -544.2717 |  |  | -212.3167 |  |  | -145.1337 |  |  | -125.4663 |  |  | -107.0176 |  |  | -149.4723
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 6.8275 | 28544.7112 |  | 35.5987 | 112064.9426 |  | 129.1847 | 274405.8801 |  | 236393 | 534472.6135 |  | 236393 | 896678.7825 |  | 236393 | 1308727.1051 |  | 236393 | 1746501.3951 |  | 236393 | 2131063.6071 |  | 236393 | 2474098.6898 |  | 236393 | 2901075.2891
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 29115.6054 | C_100 - C this iteration | iteration | 113185.592 | C_100 - C this iteration | iteration | 277149.9389 | C_100 - C this iteration | iteration | 539817.3396 | C_100 - C this iteration | iteration | 905645.5703 | C_100 - C this iteration | iteration | 1321814.3762 | C_100 - C this iteration | iteration | 1763966.4091 | C_100 - C this iteration | iteration | 2152374.2432 | C_100 - C this iteration | iteration | 2498839.6767 | C_100 - C this iteration | iteration | 2930086.0419 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0305 |  |  | 87.8501 |  |  | 76.1852 |  |  | 37.0737 |  |  | -59.3042 |  |  | -228.26 |  |  | -476.9339 |  |  | -754.1778 |  |  | -1047.8885 |  |  | -1474.5986
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0305 |  |  | 27.8501 |  |  | 16.1852 |  |  | -22.9263 |  |  | -119.3042 |  |  | -288.26 |  |  | -536.9339 |  |  | -814.1778 |  |  | -1107.8885 |  |  | -1534.5986
[13 empty] | Press drop ratio this iteration |  |  | 0.33356 |  |  | 0.31702 |  |  | 0.21245 |  |  | -0.6184 |  |  | 2.0117 |  |  | 1.2629 |  |  | 1.1258 |  |  | 1.0796 |  |  | 1.0573 |  |  | 1.0407
[13 empty] | Expansion factor | 12 |  | 0.82628 |  |  | 0.83493 |  |  | 0.88833 |  |  | 1.3296 |  |  | -0.10563 |  |  | 0.2643 |  |  | 0.29439 |  |  | 0.24348 |  |  | 0.40323 |  |  | 0.079093
[13 empty] | C Non choked w/ reducers | 7 |  | 11.7899 |  |  | 47.7119 |  |  | 155.0302 |  |  | #NUM! |  |  | 1811.3479 |  |  | -354.2572 |  |  | -222.9234 |  |  | -225.3507 |  |  | -130.7654 |  |  | -749.9349
[13 empty] | C Choked w/ reducers | 7 |  | 10.5438 |  |  | 42.0285 |  |  | 119.5076 |  |  | 484.5532 |  |  | -522.4111 |  |  | -208.5452 |  |  | -143.1506 |  |  | -123.9255 |  |  | -105.7747 |  |  | -147.8105
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 11.7899 |  |  | 47.7119 |  |  | 155.0302 |  |  | #NUM! |  |  | -522.4111 |  |  | -208.5452 |  |  | -143.1506 |  |  | -123.9255 |  |  | -105.7747 |  |  | -147.8105
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7.0599 | 29115.6054 |  | 36.1119 | 113185.592 |  | 132.0302 | 277149.9389 |  | 236393 | 539817.3396 |  | 236393 | 905645.5703 |  | 236393 | 1321814.3762 |  | 236393 | 1763966.4091 |  | 236393 | 2152374.2432 |  | 236393 | 2498839.6767 |  | 236393 | 2930086.0419
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 29697.9175 | C_100 - C this iteration | iteration | 114317.4479 | C_100 - C this iteration | iteration | 279921.4382 | C_100 - C this iteration | iteration | 545215.513 | C_100 - C this iteration | iteration | 914702.026 | C_100 - C this iteration | iteration | 1335032.5199 | C_100 - C this iteration | iteration | 1781606.0732 | C_100 - C this iteration | iteration | 2173897.9856 | C_100 - C this iteration | iteration | 2523828.0734 | C_100 - C this iteration | iteration | 2959386.9024 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0243 |  |  | 87.8032 |  |  | 75.9038 |  |  | 36.0062 |  |  | -62.309 |  |  | -234.6607 |  |  | -488.333 |  |  | -771.1495 |  |  | -1070.7638 |  |  | -1506.0507
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0243 |  |  | 27.8032 |  |  | 15.9038 |  |  | -23.9938 |  |  | -122.309 |  |  | -294.6607 |  |  | -548.333 |  |  | -831.1495 |  |  | -1130.7638 |  |  | -1566.0507
[13 empty] | Press drop ratio this iteration |  |  | 0.33351 |  |  | 0.31665 |  |  | 0.20953 |  |  | -0.66638 |  |  | 1.9629 |  |  | 1.2557 |  |  | 1.1229 |  |  | 1.0778 |  |  | 1.056 |  |  | 1.0398
[13 empty] | Expansion factor | 12 |  | 0.8263 |  |  | 0.83512 |  |  | 0.88986 |  |  | 1.3552 |  |  | -0.078812 |  |  | 0.26848 |  |  | 0.29623 |  |  | 0.2447 |  |  | 0.40392 |  |  | 0.079845
[13 empty] | C Non choked w/ reducers | 7 |  | 12.027 |  |  | 48.2315 |  |  | 157.9793 |  |  | #NUM! |  |  | 2362.4737 |  |  | -343.6022 |  |  | -218.8163 |  |  | -221.6587 |  |  | -129.1053 |  |  | -734.9321
[13 empty] | C Choked w/ reducers | 7 |  | 10.7554 |  |  | 42.4714 |  |  | 121.1502 |  |  | 503.9088 |  |  | -502.191 |  |  | -204.8853 |  |  | -141.2071 |  |  | -122.4101 |  |  | -104.5501 |  |  | -146.1709
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 12.027 |  |  | 48.2315 |  |  | 157.9793 |  |  | #NUM! |  |  | -502.191 |  |  | -204.8853 |  |  | -141.2071 |  |  | -122.4101 |  |  | -104.5501 |  |  | -146.1709
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7.297 | 29697.9175 |  | 36.6315 | 114317.4479 |  | 134.9793 | 279921.4382 |  | 236393 | 545215.513 |  | 236393 | 914702.026 |  | 236393 | 1335032.5199 |  | 236393 | 1781606.0732 |  | 236393 | 2173897.9856 |  | 236393 | 2523828.0734 |  | 236393 | 2959386.9024
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 30291.8759 | C_100 - C this iteration | iteration | 115460.6224 | C_100 - C this iteration | iteration | 282720.6526 | C_100 - C this iteration | iteration | 550667.6682 | C_100 - C this iteration | iteration | 923849.0463 | C_100 - C this iteration | iteration | 1348382.8451 | C_100 - C this iteration | iteration | 1799422.1339 | C_100 - C this iteration | iteration | 2195636.9655 | C_100 - C this iteration | iteration | 2549066.3542 | C_100 - C this iteration | iteration | 2988980.7714 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0178 |  |  | 87.7553 |  |  | 75.6167 |  |  | 34.9172 |  |  | -65.3741 |  |  | -241.1901 |  |  | -499.9612 |  |  | -788.4623 |  |  | -1094.0988 |  |  | -1538.135
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0178 |  |  | 27.7553 |  |  | 15.6167 |  |  | -25.0828 |  |  | -125.3741 |  |  | -301.1901 |  |  | -559.9612 |  |  | -848.4623 |  |  | -1154.0988 |  |  | -1598.135
[13 empty] | Press drop ratio this iteration |  |  | 0.33347 |  |  | 0.31628 |  |  | 0.20653 |  |  | -0.71835 |  |  | 1.9178 |  |  | 1.2488 |  |  | 1.12 |  |  | 1.0761 |  |  | 1.0548 |  |  | 1.039
[13 empty] | Expansion factor | 12 |  | 0.82633 |  |  | 0.83532 |  |  | 0.89144 |  |  | 1.3829 |  |  | -0.053999 |  |  | 0.27251 |  |  | 0.29802 |  |  | 0.2459 |  |  | 0.40459 |  |  | 0.08058
[13 empty] | C Non choked w/ reducers | 7 |  | 12.2689 |  |  | 48.7578 |  |  | 161.0387 |  |  | #NUM! |  |  | 3358.0953 |  |  | -333.5677 |  |  | -214.8405 |  |  | -218.0664 |  |  | -127.4746 |  |  | -720.4532
[13 empty] | C Choked w/ reducers | 7 |  | 10.9713 |  |  | 42.9195 |  |  | 122.8262 |  |  | 524.821 |  |  | -483.4317 |  |  | -201.3321 |  |  | -139.3021 |  |  | -120.9195 |  |  | -103.3435 |  |  | -144.5531
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 12.2689 |  |  | 48.7578 |  |  | 161.0387 |  |  | #NUM! |  |  | -483.4317 |  |  | -201.3321 |  |  | -139.3021 |  |  | -120.9195 |  |  | -103.3435 |  |  | -144.5531
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7.5389 | 30291.8759 |  | 37.1578 | 115460.6224 |  | 138.0387 | 282720.6526 |  | 236393 | 550667.6682 |  | 236393 | 923849.0463 |  | 236393 | 1348382.8451 |  | 236393 | 1799422.1339 |  | 236393 | 2195636.9655 |  | 236393 | 2549066.3542 |  | 236393 | 2988980.7714
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 30897.7134 | C_100 - C this iteration | iteration | 116615.2286 | C_100 - C this iteration | iteration | 285547.8591 | C_100 - C this iteration | iteration | 556174.3448 | C_100 - C this iteration | iteration | 933087.5367 | C_100 - C this iteration | iteration | 1361866.6736 | C_100 - C this iteration | iteration | 1817416.3553 | C_100 - C this iteration | iteration | 2217593.3351 | C_100 - C this iteration | iteration | 2574557.0177 | C_100 - C this iteration | iteration | 3018870.5791 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.011 |  |  | 87.7065 |  |  | 75.3239 |  |  | 33.8063 |  |  | -68.5009 |  |  | -247.8508 |  |  | -511.8232 |  |  | -806.1231 |  |  | -1117.9029 |  |  | -1570.8643
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.011 |  |  | 27.7065 |  |  | 15.3239 |  |  | -26.1937 |  |  | -128.5009 |  |  | -307.8508 |  |  | -571.8232 |  |  | -866.1231 |  |  | -1177.9029 |  |  | -1630.8643
[13 empty] | Press drop ratio this iteration |  |  | 0.33342 |  |  | 0.3159 |  |  | 0.20344 |  |  | -0.77482 |  |  | 1.8759 |  |  | 1.2421 |  |  | 1.1172 |  |  | 1.0744 |  |  | 1.0537 |  |  | 1.0382
[13 empty] | Expansion factor | 12 |  | 0.82635 |  |  | 0.83551 |  |  | 0.89306 |  |  | 1.413 |  |  | -0.030975 |  |  | 0.2764 |  |  | 0.29976 |  |  | 0.24707 |  |  | 0.40525 |  |  | 0.0813
[13 empty] | C Non choked w/ reducers | 7 |  | 12.5158 |  |  | 49.2908 |  |  | 164.2159 |  |  | #NUM! |  |  | 5705.4836 |  |  | -324.0988 |  |  | -210.9895 |  |  | -214.5694 |  |  | -125.8726 |  |  | -706.4703
[13 empty] | C Choked w/ reducers | 7 |  | 11.1916 |  |  | 43.3729 |  |  | 124.5367 |  |  | 547.4874 |  |  | -465.979 |  |  | -197.8808 |  |  | -137.4344 |  |  | -119.453 |  |  | -102.1544 |  |  | -142.9567
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 12.5158 |  |  | 49.2908 |  |  | 164.2159 |  |  | #NUM! |  |  | -465.979 |  |  | -197.8808 |  |  | -137.4344 |  |  | -119.453 |  |  | -102.1544 |  |  | -142.9567
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7.7858 | 30897.7134 |  | 37.6908 | 116615.2286 |  | 141.2159 | 285547.8591 |  | 236393 | 556174.3448 |  | 236393 | 933087.5367 |  | 236393 | 1361866.6736 |  | 236393 | 1817416.3553 |  | 236393 | 2217593.3351 |  | 236393 | 2574557.0177 |  | 236393 | 3018870.5791
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 31515.6677 | C_100 - C this iteration | iteration | 117781.3809 | C_100 - C this iteration | iteration | 288403.3377 | C_100 - C this iteration | iteration | 561736.0883 | C_100 - C this iteration | iteration | 942418.4121 | C_100 - C this iteration | iteration | 1375485.3403 | C_100 - C this iteration | iteration | 1835590.5188 | C_100 - C this iteration | iteration | 2239769.2685 | C_100 - C this iteration | iteration | 2600302.5879 | C_100 - C this iteration | iteration | 3049059.2849 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.004 |  |  | 87.6566 |  |  | 75.0252 |  |  | 32.6731 |  |  | -71.6904 |  |  | -254.6453 |  |  | -523.9235 |  |  | -824.1389 |  |  | -1142.1855 |  |  | -1604.2514
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 30.004 |  |  | 27.6566 |  |  | 15.0252 |  |  | -27.3269 |  |  | -131.6904 |  |  | -314.6453 |  |  | -583.9235 |  |  | -884.1389 |  |  | -1202.1855 |  |  | -1664.2514
[13 empty] | Press drop ratio this iteration |  |  | 0.33336 |  |  | 0.31551 |  |  | 0.20027 |  |  | -0.83637 |  |  | 1.8369 |  |  | 1.2356 |  |  | 1.1145 |  |  | 1.0728 |  |  | 1.0525 |  |  | 1.0374
[13 empty] | Expansion factor | 12 |  | 0.82638 |  |  | 0.83572 |  |  | 0.89473 |  |  | 1.4458 |  |  | -0.0095579 |  |  | 0.28017 |  |  | 0.30146 |  |  | 0.24821 |  |  | 0.4059 |  |  | 0.082003
[13 empty] | C Non choked w/ reducers | 7 |  | 12.7677 |  |  | 49.8306 |  |  | 167.519 |  |  | #NUM! |  |  | 18032.7147 |  |  | -315.1469 |  |  | -207.2571 |  |  | -211.1638 |  |  | -124.2984 |  |  | -692.9572
[13 empty] | C Choked w/ reducers | 7 |  | 11.4163 |  |  | 43.8315 |  |  | 126.2829 |  |  | 572.1409 |  |  | -449.6996 |  |  | -194.5269 |  |  | -135.6029 |  |  | -118.0102 |  |  | -100.9824 |  |  | -141.3814
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 12.7677 |  |  | 49.8306 |  |  | 167.519 |  |  | #NUM! |  |  | -449.6996 |  |  | -194.5269 |  |  | -135.6029 |  |  | -118.0102 |  |  | -100.9824 |  |  | -141.3814
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 8.0377 | 31515.6677 |  | 38.2306 | 117781.3809 |  | 144.519 | 288403.3377 |  | 236393 | 561736.0883 |  | 236393 | 942418.4121 |  | 236393 | 1375485.3403 |  | 236393 | 1835590.5188 |  | 236393 | 2239769.2685 |  | 236393 | 2600302.5879 |  | 236393 | 3049059.2849
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 32145.981 | C_100 - C this iteration | iteration | 118959.1947 | C_100 - C this iteration | iteration | 291287.3711 | C_100 - C this iteration | iteration | 567353.4492 | C_100 - C this iteration | iteration | 951842.5962 | C_100 - C this iteration | iteration | 1389240.1937 | C_100 - C this iteration | iteration | 1853946.424 | C_100 - C this iteration | iteration | 2262166.9612 | C_100 - C this iteration | iteration | 2626305.6138 | C_100 - C this iteration | iteration | 3079549.8777 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9967 |  |  | 87.6058 |  |  | 74.7205 |  |  | 31.5171 |  |  | -74.9441 |  |  | -261.5764 |  |  | -536.2671 |  |  | -842.5168 |  |  | -1166.9562 |  |  | -1638.3095
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9967 |  |  | 27.6058 |  |  | 14.7205 |  |  | -28.4829 |  |  | -134.9441 |  |  | -321.5764 |  |  | -596.2671 |  |  | -902.5168 |  |  | -1226.9562 |  |  | -1698.3095
[13 empty] | Press drop ratio this iteration |  |  | 0.33331 |  |  | 0.31511 |  |  | 0.19701 |  |  | -0.90373 |  |  | 1.8006 |  |  | 1.2294 |  |  | 1.1119 |  |  | 1.0712 |  |  | 1.0514 |  |  | 1.0366
[13 empty] | Expansion factor | 12 |  | 0.82641 |  |  | 0.83592 |  |  | 0.89644 |  |  | 1.4817 |  |  | 0.010412 |  |  | 0.2838 |  |  | 0.30311 |  |  | 0.24932 |  |  | 0.40652 |  |  | 0.082691
[13 empty] | C Non choked w/ reducers | 7 |  | 13.0247 |  |  | 50.3774 |  |  | 170.957 |  |  | #NUM! |  |  | -16154.2003 |  |  | -306.6688 |  |  | -203.6377 |  |  | -207.846 |  |  | -122.7513 |  |  | -679.8897
[13 empty] | C Choked w/ reducers | 7 |  | 11.6456 |  |  | 44.2955 |  |  | 128.0659 |  |  | 599.0572 |  |  | -434.4776 |  |  | -191.2662 |  |  | -133.8064 |  |  | -116.5904 |  |  | -99.8273 |  |  | -139.8267
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 13.0247 |  |  | 50.3774 |  |  | 170.957 |  |  | #NUM! |  |  | -434.4776 |  |  | -191.2662 |  |  | -133.8064 |  |  | -116.5904 |  |  | -99.8273 |  |  | -139.8267
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 8.2947 | 32145.981 |  | 38.7774 | 118959.1947 |  | 147.957 | 291287.3711 |  | 236393 | 567353.4492 |  | 236393 | 951842.5962 |  | 236393 | 1389240.1937 |  | 236393 | 1853946.424 |  | 236393 | 2262166.9612 |  | 236393 | 2626305.6138 |  | 236393 | 3079549.8777
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 32788.9007 | C_100 - C this iteration | iteration | 120148.7867 | C_100 - C this iteration | iteration | 294200.2448 | C_100 - C this iteration | iteration | 573026.9837 | C_100 - C this iteration | iteration | 961361.0222 | C_100 - C this iteration | iteration | 1403132.5957 | C_100 - C this iteration | iteration | 1872485.8882 | C_100 - C this iteration | iteration | 2284788.6308 | C_100 - C this iteration | iteration | 2652568.6699 | C_100 - C this iteration | iteration | 3110345.3765 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9891 |  |  | 87.554 |  |  | 74.4097 |  |  | 30.3379 |  |  | -78.2632 |  |  | -268.6468 |  |  | -548.8588 |  |  | -861.2641 |  |  | -1192.2247 |  |  | -1673.0523
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9891 |  |  | 27.554 |  |  | 14.4097 |  |  | -29.6621 |  |  | -138.2632 |  |  | -328.6468 |  |  | -608.8588 |  |  | -921.2641 |  |  | -1252.2247 |  |  | -1733.0523
[13 empty] | Press drop ratio this iteration |  |  | 0.33325 |  |  | 0.31471 |  |  | 0.19365 |  |  | -0.97773 |  |  | 1.7666 |  |  | 1.2233 |  |  | 1.1093 |  |  | 1.0697 |  |  | 1.0503 |  |  | 1.0359
[13 empty] | Expansion factor | 12 |  | 0.82644 |  |  | 0.83614 |  |  | 0.89821 |  |  | 1.5212 |  |  | 0.029072 |  |  | 0.28732 |  |  | 0.30472 |  |  | 0.25041 |  |  | 0.40714 |  |  | 0.083364
[13 empty] | C Non choked w/ reducers | 7 |  | 13.287 |  |  | 50.9312 |  |  | 174.5398 |  |  | #NUM! |  |  | -5648.9672 |  |  | -298.6263 |  |  | -200.1258 |  |  | -204.6122 |  |  | -121.2307 |  |  | -667.2452
[13 empty] | C Choked w/ reducers | 7 |  | 11.8795 |  |  | 44.7649 |  |  | 129.8868 |  |  | 628.5659 |  |  | -420.2122 |  |  | -188.0947 |  |  | -132.0441 |  |  | -115.193 |  |  | -98.6886 |  |  | -138.2922
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 13.287 |  |  | 50.9312 |  |  | 174.5398 |  |  | #NUM! |  |  | -420.2122 |  |  | -188.0947 |  |  | -132.0441 |  |  | -115.193 |  |  | -98.6886 |  |  | -138.2922
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 8.557 | 32788.9007 |  | 39.3312 | 120148.7867 |  | 151.5398 | 294200.2448 |  | 236393 | 573026.9837 |  | 236393 | 961361.0222 |  | 236393 | 1403132.5957 |  | 236393 | 1872485.8882 |  | 236393 | 2284788.6308 |  | 236393 | 2652568.6699 |  | 236393 | 3110345.3765
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 33444.6787 | C_100 - C this iteration | iteration | 121350.2745 | C_100 - C this iteration | iteration | 297142.2473 | C_100 - C this iteration | iteration | 578757.2535 | C_100 - C this iteration | iteration | 970974.6324 | C_100 - C this iteration | iteration | 1417163.9216 | C_100 - C this iteration | iteration | 1891210.7471 | C_100 - C this iteration | iteration | 2307636.5171 | C_100 - C this iteration | iteration | 2679094.3566 | C_100 - C this iteration | iteration | 3141448.8303 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9812 |  |  | 87.5011 |  |  | 74.0926 |  |  | 29.1349 |  |  | -81.649 |  |  | -275.8593 |  |  | -561.7036 |  |  | -880.3883 |  |  | -1218.0011 |  |  | -1708.4934
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9812 |  |  | 27.5011 |  |  | 14.0926 |  |  | -30.8651 |  |  | -141.649 |  |  | -335.8593 |  |  | -621.7036 |  |  | -940.3883 |  |  | -1278.0011 |  |  | -1768.4934
[13 empty] | Press drop ratio this iteration |  |  | 0.33319 |  |  | 0.31429 |  |  | 0.1902 |  |  | -1.0594 |  |  | 1.7349 |  |  | 1.2175 |  |  | 1.1068 |  |  | 1.0682 |  |  | 1.0493 |  |  | 1.0351
[13 empty] | Expansion factor | 12 |  | 0.82647 |  |  | 0.83635 |  |  | 0.90002 |  |  | 1.5647 |  |  | 0.046544 |  |  | 0.29072 |  |  | 0.30629 |  |  | 0.25147 |  |  | 0.40774 |  |  | 0.084022
[13 empty] | C Non choked w/ reducers | 7 |  | 13.5546 |  |  | 51.4922 |  |  | 178.2784 |  |  | #NUM! |  |  | -3447.0685 |  |  | -290.985 |  |  | -196.7163 |  |  | -201.4592 |  |  | -119.7358 |  |  | -655.0026
[13 empty] | C Choked w/ reducers | 7 |  | 12.1181 |  |  | 45.2399 |  |  | 131.7471 |  |  | 661.0634 |  |  | -406.8148 |  |  | -185.0086 |  |  | -130.3148 |  |  | -113.8177 |  |  | -97.5661 |  |  | -136.7777
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 13.5546 |  |  | 51.4922 |  |  | 178.2784 |  |  | #NUM! |  |  | -406.8148 |  |  | -185.0086 |  |  | -130.3148 |  |  | -113.8177 |  |  | -97.5661 |  |  | -136.7777
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 8.8246 | 33444.6787 |  | 39.8922 | 121350.2745 |  | 155.2784 | 297142.2473 |  | 236393 | 578757.2535 |  | 236393 | 970974.6324 |  | 236393 | 1417163.9216 |  | 236393 | 1891210.7471 |  | 236393 | 2307636.5171 |  | 236393 | 2679094.3566 |  | 236393 | 3141448.8303
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 34113.5722 | C_100 - C this iteration | iteration | 122563.7773 | C_100 - C this iteration | iteration | 300113.6697 | C_100 - C this iteration | iteration | 584544.826 | C_100 - C this iteration | iteration | 980684.3787 | C_100 - C this iteration | iteration | 1431335.5608 | C_100 - C this iteration | iteration | 1910122.8546 | C_100 - C this iteration | iteration | 2330712.8822 | C_100 - C this iteration | iteration | 2705885.3002 | C_100 - C this iteration | iteration | 3172863.3186 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9729 |  |  | 87.4471 |  |  | 73.7691 |  |  | 27.9078 |  |  | -85.1029 |  |  | -283.2168 |  |  | -574.8065 |  |  | -899.8968 |  |  | -1244.2957 |  |  | -1744.6468
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9729 |  |  | 27.4471 |  |  | 13.7691 |  |  | -32.0922 |  |  | -145.1029 |  |  | -343.2168 |  |  | -634.8065 |  |  | -959.8968 |  |  | -1304.2957 |  |  | -1804.6468
[13 empty] | Press drop ratio this iteration |  |  | 0.33313 |  |  | 0.31387 |  |  | 0.18665 |  |  | -1.1499 |  |  | 1.705 |  |  | 1.2119 |  |  | 1.1044 |  |  | 1.0667 |  |  | 1.0482 |  |  | 1.0344
[13 empty] | Expansion factor | 12 |  | 0.8265 |  |  | 0.83657 |  |  | 0.90189 |  |  | 1.613 |  |  | 0.062935 |  |  | 0.29401 |  |  | 0.30781 |  |  | 0.2525 |  |  | 0.40833 |  |  | 0.084666
[13 empty] | C Non choked w/ reducers | 7 |  | 13.8277 |  |  | 52.0606 |  |  | 182.185 |  |  | #NUM! |  |  | -2491.8157 |  |  | -283.7142 |  |  | -193.4046 |  |  | -198.3838 |  |  | -118.2659 |  |  | -643.1421
[13 empty] | C Choked w/ reducers | 7 |  | 12.3616 |  |  | 45.7205 |  |  | 133.6481 |  |  | 697.0317 |  |  | -394.2074 |  |  | -182.0044 |  |  | -128.6177 |  |  | -112.4638 |  |  | -96.4593 |  |  | -135.2828
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 13.8277 |  |  | 52.0606 |  |  | 182.185 |  |  | #NUM! |  |  | -394.2074 |  |  | -182.0044 |  |  | -128.6177 |  |  | -112.4638 |  |  | -96.4593 |  |  | -135.2828
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 9.0977 | 34113.5722 |  | 40.4606 | 122563.7773 |  | 159.185 | 300113.6697 |  | 236393 | 584544.826 |  | 236393 | 980684.3787 |  | 236393 | 1431335.5608 |  | 236393 | 1910122.8546 |  | 236393 | 2330712.8822 |  | 236393 | 2705885.3002 |  | 236393 | 3172863.3186
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 34795.8437 | C_100 - C this iteration | iteration | 123789.415 | C_100 - C this iteration | iteration | 303114.8064 | C_100 - C this iteration | iteration | 590390.2743 | C_100 - C this iteration | iteration | 990491.2225 | C_100 - C this iteration | iteration | 1445648.9164 | C_100 - C this iteration | iteration | 1929224.0831 | C_100 - C this iteration | iteration | 2354020.0111 | C_100 - C this iteration | iteration | 2732944.1532 | C_100 - C this iteration | iteration | 3204591.9518 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9644 |  |  | 87.3921 |  |  | 73.4392 |  |  | 26.6561 |  |  | -88.6262 |  |  | -290.7222 |  |  | -588.1729 |  |  | -919.7974 |  |  | -1271.1187 |  |  | -1781.5269
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9644 |  |  | 27.3921 |  |  | 13.4392 |  |  | -33.3439 |  |  | -148.6262 |  |  | -350.7222 |  |  | -648.1729 |  |  | -979.7974 |  |  | -1331.1187 |  |  | -1841.5269
[13 empty] | Press drop ratio this iteration |  |  | 0.33307 |  |  | 0.31344 |  |  | 0.183 |  |  | -1.2509 |  |  | 1.677 |  |  | 1.2064 |  |  | 1.102 |  |  | 1.0652 |  |  | 1.0472 |  |  | 1.0337
[13 empty] | Expansion factor | 12 |  | 0.82653 |  |  | 0.8368 |  |  | 0.90381 |  |  | 1.6668 |  |  | 0.078338 |  |  | 0.2972 |  |  | 0.3093 |  |  | 0.25351 |  |  | 0.4089 |  |  | 0.085296
[13 empty] | C Non choked w/ reducers | 7 |  | 14.1063 |  |  | 52.6364 |  |  | 186.2732 |  |  | #NUM! |  |  | -1957.6403 |  |  | -276.7862 |  |  | -190.1863 |  |  | -195.3829 |  |  | -116.8204 |  |  | -631.6454
[13 empty] | C Choked w/ reducers | 7 |  | 12.6101 |  |  | 46.2068 |  |  | 135.591 |  |  | 737.062 |  |  | -382.3213 |  |  | -179.0788 |  |  | -126.9517 |  |  | -111.1308 |  |  | -95.3681 |  |  | -133.8071
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 14.1063 |  |  | 52.6364 |  |  | 186.2732 |  |  | #NUM! |  |  | -382.3213 |  |  | -179.0788 |  |  | -126.9517 |  |  | -111.1308 |  |  | -95.3681 |  |  | -133.8071
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 9.3763 | 34795.8437 |  | 41.0364 | 123789.415 |  | 163.2732 | 303114.8064 |  | 236393 | 590390.2743 |  | 236393 | 990491.2225 |  | 236393 | 1445648.9164 |  | 236393 | 1929224.0831 |  | 236393 | 2354020.0111 |  | 236393 | 2732944.1532 |  | 236393 | 3204591.9518
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 35491.7606 | C_100 - C this iteration | iteration | 125027.3092 | C_100 - C this iteration | iteration | 306145.9545 | C_100 - C this iteration | iteration | 596294.177 | C_100 - C this iteration | iteration | 1000396.1347 | C_100 - C this iteration | iteration | 1460105.4056 | C_100 - C this iteration | iteration | 1948516.324 | C_100 - C this iteration | iteration | 2377560.2112 | C_100 - C this iteration | iteration | 2760273.5947 | C_100 - C this iteration | iteration | 3236637.8713 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9555 |  |  | 87.336 |  |  | 73.1026 |  |  | 25.3791 |  |  | -92.2203 |  |  | -298.3784 |  |  | -601.8079 |  |  | -940.0981 |  |  | -1298.4809 |  |  | -1819.1483
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9555 |  |  | 27.336 |  |  | 13.1026 |  |  | -34.6209 |  |  | -152.2203 |  |  | -358.3784 |  |  | -661.8079 |  |  | -1000.0981 |  |  | -1358.4809 |  |  | -1879.1483
[13 empty] | Press drop ratio this iteration |  |  | 0.333 |  |  | 0.313 |  |  | 0.17924 |  |  | -1.3641 |  |  | 1.6506 |  |  | 1.2011 |  |  | 1.0997 |  |  | 1.0638 |  |  | 1.0462 |  |  | 1.033
[13 empty] | Expansion factor | 12 |  | 0.82657 |  |  | 0.83703 |  |  | 0.90579 |  |  | 1.7272 |  |  | 0.092839 |  |  | 0.30029 |  |  | 0.31075 |  |  | 0.2545 |  |  | 0.40946 |  |  | 0.085913
[13 empty] | C Non choked w/ reducers | 7 |  | 14.3907 |  |  | 53.2198 |  |  | 190.5584 |  |  | #NUM! |  |  | -1616.1321 |  |  | -270.1761 |  |  | -187.0572 |  |  | -192.4539 |  |  | -115.3988 |  |  | -620.4953
[13 empty] | C Choked w/ reducers | 7 |  | 12.8635 |  |  | 46.6989 |  |  | 137.5775 |  |  | 781.8882 |  |  | -371.0953 |  |  | -176.2285 |  |  | -125.3162 |  |  | -109.8184 |  |  | -94.292 |  |  | -132.3502
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 14.3907 |  |  | 53.2198 |  |  | 190.5584 |  |  | #NUM! |  |  | -371.0953 |  |  | -176.2285 |  |  | -125.3162 |  |  | -109.8184 |  |  | -94.292 |  |  | -132.3502
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 9.6607 | 35491.7606 |  | 41.6198 | 125027.3092 |  | 167.5584 | 306145.9545 |  | 236393 | 596294.177 |  | 236393 | 1000396.1347 |  | 236393 | 1460105.4056 |  | 236393 | 1948516.324 |  | 236393 | 2377560.2112 |  | 236393 | 2760273.5947 |  | 236393 | 3236637.8713
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 36201.5958 | C_100 - C this iteration | iteration | 126277.5823 | C_100 - C this iteration | iteration | 309207.4141 | C_100 - C this iteration | iteration | 602257.1188 | C_100 - C this iteration | iteration | 1010400.0961 | C_100 - C this iteration | iteration | 1474706.4597 | C_100 - C this iteration | iteration | 1968001.4872 | C_100 - C this iteration | iteration | 2401335.8133 | C_100 - C this iteration | iteration | 2787876.3306 | C_100 - C this iteration | iteration | 3269004.25 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9462 |  |  | 87.2787 |  |  | 72.7592 |  |  | 24.0765 |  |  | -95.8866 |  |  | -306.1885 |  |  | -615.7169 |  |  | -960.8068 |  |  | -1326.3931 |  |  | -1857.5259
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9462 |  |  | 27.2787 |  |  | 12.7592 |  |  | -35.9235 |  |  | -155.8866 |  |  | -366.1885 |  |  | -675.7169 |  |  | -1020.8068 |  |  | -1386.3931 |  |  | -1917.5259
[13 empty] | Press drop ratio this iteration |  |  | 0.33293 |  |  | 0.31255 |  |  | 0.17536 |  |  | -1.4921 |  |  | 1.6257 |  |  | 1.196 |  |  | 1.0974 |  |  | 1.0624 |  |  | 1.0452 |  |  | 1.0323
[13 empty] | Expansion factor | 12 |  | 0.8266 |  |  | 0.83726 |  |  | 0.90782 |  |  | 1.7953 |  |  | 0.10651 |  |  | 0.30327 |  |  | 0.31216 |  |  | 0.25547 |  |  | 0.41001 |  |  | 0.086516
[13 empty] | C Non choked w/ reducers | 7 |  | 14.6809 |  |  | 53.8109 |  |  | 195.0577 |  |  | #NUM! |  |  | -1378.7946 |  |  | -263.8614 |  |  | -184.0134 |  |  | -189.5938 |  |  | -114.0003 |  |  | -609.6756
[13 empty] | C Choked w/ reducers | 7 |  | 13.1222 |  |  | 47.1968 |  |  | 139.609 |  |  | 832.4322 |  |  | -360.475 |  |  | -173.4507 |  |  | -123.7101 |  |  | -108.5259 |  |  | -93.2309 |  |  | -130.912
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 14.6809 |  |  | 53.8109 |  |  | 195.0577 |  |  | #NUM! |  |  | -360.475 |  |  | -173.4507 |  |  | -123.7101 |  |  | -108.5259 |  |  | -93.2309 |  |  | -130.912
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 9.9509 | 36201.5958 |  | 42.2109 | 126277.5823 |  | 172.0577 | 309207.4141 |  | 236393 | 602257.1188 |  | 236393 | 1010400.0961 |  | 236393 | 1474706.4597 |  | 236393 | 1968001.4872 |  | 236393 | 2401335.8133 |  | 236393 | 2787876.3306 |  | 236393 | 3269004.25
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 36925.6277 | C_100 - C this iteration | iteration | 127540.3581 | C_100 - C this iteration | iteration | 312299.4882 | C_100 - C this iteration | iteration | 608279.69 | C_100 - C this iteration | iteration | 1020504.0971 | C_100 - C this iteration | iteration | 1489453.5242 | C_100 - C this iteration | iteration | 1987681.5021 | C_100 - C this iteration | iteration | 2425349.1714 | C_100 - C this iteration | iteration | 2815755.094 | C_100 - C this iteration | iteration | 3301694.2925 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9365 |  |  | 87.2203 |  |  | 72.409 |  |  | 22.7477 |  |  | -99.6267 |  |  | -314.1557 |  |  | -629.9055 |  |  | -981.9317 |  |  | -1354.8664 |  |  | -1896.6749
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9365 |  |  | 27.2203 |  |  | 12.409 |  |  | -37.2523 |  |  | -159.6267 |  |  | -374.1557 |  |  | -689.9055 |  |  | -1041.9317 |  |  | -1414.8664 |  |  | -1956.6749
[13 empty] | Press drop ratio this iteration |  |  | 0.33286 |  |  | 0.31209 |  |  | 0.17137 |  |  | -1.6376 |  |  | 1.6022 |  |  | 1.191 |  |  | 1.0953 |  |  | 1.0611 |  |  | 1.0443 |  |  | 1.0316
[13 empty] | Expansion factor | 12 |  | 0.82664 |  |  | 0.8375 |  |  | 0.90992 |  |  | 1.8729 |  |  | 0.11942 |  |  | 0.30617 |  |  | 0.31354 |  |  | 0.25641 |  |  | 0.41055 |  |  | 0.087106
[13 empty] | C Non choked w/ reducers | 7 |  | 14.9771 |  |  | 54.41 |  |  | 199.7904 |  |  | #NUM! |  |  | -1204.1406 |  |  | -257.8216 |  |  | -181.0512 |  |  | -186.8003 |  |  | -112.6245 |  |  | -599.1712
[13 empty] | C Choked w/ reducers | 7 |  | 13.386 |  |  | 47.7007 |  |  | 141.6872 |  |  | 889.8683 |  |  | -350.412 |  |  | -170.7425 |  |  | -122.1328 |  |  | -107.253 |  |  | -92.1843 |  |  | -129.4919
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 14.9771 |  |  | 54.41 |  |  | 199.7904 |  |  | #NUM! |  |  | -350.412 |  |  | -170.7425 |  |  | -122.1328 |  |  | -107.253 |  |  | -92.1843 |  |  | -129.4919
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 10.2471 | 36925.6277 |  | 42.81 | 127540.3581 |  | 176.7904 | 312299.4882 |  | 236393 | 608279.69 |  | 236393 | 1020504.0971 |  | 236393 | 1489453.5242 |  | 236393 | 1987681.5021 |  | 236393 | 2425349.1714 |  | 236393 | 2815755.094 |  | 236393 | 3301694.2925
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 37664.1402 | C_100 - C this iteration | iteration | 128815.7617 | C_100 - C this iteration | iteration | 315422.4831 | C_100 - C this iteration | iteration | 614362.4869 | C_100 - C this iteration | iteration | 1030709.138 | C_100 - C this iteration | iteration | 1504348.0595 | C_100 - C this iteration | iteration | 2007558.3171 | C_100 - C this iteration | iteration | 2449602.6631 | C_100 - C this iteration | iteration | 2843912.6449 | C_100 - C this iteration | iteration | 3334711.2354 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9265 |  |  | 87.1607 |  |  | 72.0517 |  |  | 21.3923 |  |  | -103.4419 |  |  | -322.2829 |  |  | -644.3794 |  |  | -1003.4813 |  |  | -1383.9119 |  |  | -1936.6108
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9265 |  |  | 27.1607 |  |  | 12.0517 |  |  | -38.6077 |  |  | -163.4419 |  |  | -382.2829 |  |  | -704.3794 |  |  | -1063.4813 |  |  | -1443.9119 |  |  | -1996.6108
[13 empty] | Press drop ratio this iteration |  |  | 0.33279 |  |  | 0.31162 |  |  | 0.16726 |  |  | -1.8048 |  |  | 1.58 |  |  | 1.1862 |  |  | 1.0931 |  |  | 1.0598 |  |  | 1.0434 |  |  | 1.031
[13 empty] | Expansion factor | 12 |  | 0.82668 |  |  | 0.83775 |  |  | 0.91208 |  |  | 1.962 |  |  | 0.13163 |  |  | 0.30897 |  |  | 0.31488 |  |  | 0.25733 |  |  | 0.41107 |  |  | 0.087683
[13 empty] | C Non choked w/ reducers | 7 |  | 15.2793 |  |  | 55.017 |  |  | 204.7787 |  |  | #NUM! |  |  | -1070.1368 |  |  | -252.0381 |  |  | -178.1671 |  |  | -184.0708 |  |  | -111.2707 |  |  | -588.9678
[13 empty] | C Choked w/ reducers | 7 |  | 13.6553 |  |  | 48.2106 |  |  | 143.8137 |  |  | 955.7161 |  |  | -340.8628 |  |  | -168.1011 |  |  | -120.5834 |  |  | -105.9993 |  |  | -91.152 |  |  | -128.0898
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 15.2793 |  |  | 55.017 |  |  | 204.7787 |  |  | #NUM! |  |  | -340.8628 |  |  | -168.1011 |  |  | -120.5834 |  |  | -105.9993 |  |  | -91.152 |  |  | -128.0898
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 10.5493 | 37664.1402 |  | 43.417 | 128815.7617 |  | 181.7787 | 315422.4831 |  | 236393 | 614362.4869 |  | 236393 | 1030709.138 |  | 236393 | 1504348.0595 |  | 236393 | 2007558.3171 |  | 236393 | 2449602.6631 |  | 236393 | 2843912.6449 |  | 236393 | 3334711.2354
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 38417.423 | C_100 - C this iteration | iteration | 130103.9193 | C_100 - C this iteration | iteration | 318576.7079 | C_100 - C this iteration | iteration | 620506.1118 | C_100 - C this iteration | iteration | 1041016.2294 | C_100 - C this iteration | iteration | 1519391.5401 | C_100 - C this iteration | iteration | 2027633.9003 | C_100 - C this iteration | iteration | 2474098.6898 | C_100 - C this iteration | iteration | 2872351.7713 | C_100 - C this iteration | iteration | 3368058.3478 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.916 |  |  | 87.0999 |  |  | 71.6872 |  |  | 20.0095 |  |  | -107.3338 |  |  | -330.5735 |  |  | -659.1441 |  |  | -1025.4639 |  |  | -1413.5412 |  |  | -1977.3494
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.916 |  |  | 27.0999 |  |  | 11.6872 |  |  | -39.9905 |  |  | -167.3338 |  |  | -390.5735 |  |  | -719.1441 |  |  | -1085.4639 |  |  | -1473.5412 |  |  | -2037.3494
[13 empty] | Press drop ratio this iteration |  |  | 0.33271 |  |  | 0.31114 |  |  | 0.16303 |  |  | -1.9986 |  |  | 1.559 |  |  | 1.1815 |  |  | 1.091 |  |  | 1.0585 |  |  | 1.0424 |  |  | 1.0303
[13 empty] | Expansion factor | 12 |  | 0.82672 |  |  | 0.838 |  |  | 0.9143 |  |  | 2.0654 |  |  | 0.14319 |  |  | 0.31169 |  |  | 0.31618 |  |  | 0.25822 |  |  | 0.41159 |  |  | 0.088248
[13 empty] | C Non choked w/ reducers | 7 |  | 15.5878 |  |  | 55.6323 |  |  | 210.0475 |  |  | #NUM! |  |  | -963.9972 |  |  | -246.4942 |  |  | -175.358 |  |  | -181.4031 |  |  | -109.9385 |  |  | -579.0521
[13 empty] | C Choked w/ reducers | 7 |  | 13.93 |  |  | 48.7267 |  |  | 145.9903 |  |  | 1031.9773 |  |  | -331.7882 |  |  | -165.524 |  |  | -119.0612 |  |  | -104.7643 |  |  | -90.1338 |  |  | -126.7053
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 15.5878 |  |  | 55.6323 |  |  | 210.0475 |  |  | #NUM! |  |  | -331.7882 |  |  | -165.524 |  |  | -119.0612 |  |  | -104.7643 |  |  | -90.1338 |  |  | -126.7053
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 10.8578 | 38417.423 |  | 44.0323 | 130103.9193 |  | 187.0475 | 318576.7079 |  | 236393 | 620506.1118 |  | 236393 | 1041016.2294 |  | 236393 | 1519391.5401 |  | 236393 | 2027633.9003 |  | 236393 | 2474098.6898 |  | 236393 | 2872351.7713 |  | 236393 | 3368058.3478
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 39185.7715 | C_100 - C this iteration | iteration | 131404.9585 | C_100 - C this iteration | iteration | 321762.475 | C_100 - C this iteration | iteration | 626711.1729 | C_100 - C this iteration | iteration | 1051426.3917 | C_100 - C this iteration | iteration | 1534585.4555 | C_100 - C this iteration | iteration | 2047910.2393 | C_100 - C this iteration | iteration | 2498839.6767 | C_100 - C this iteration | iteration | 2901075.2891 | C_100 - C this iteration | iteration | 3401738.9313 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9052 |  |  | 87.0379 |  |  | 71.3154 |  |  | 18.599 |  |  | -111.3039 |  |  | -339.0308 |  |  | -674.2056 |  |  | -1047.8885 |  |  | -1443.7661 |  |  | -2018.9068
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9052 |  |  | 27.0379 |  |  | 11.3154 |  |  | -41.401 |  |  | -171.3039 |  |  | -399.0308 |  |  | -734.2056 |  |  | -1107.8885 |  |  | -1503.7661 |  |  | -2078.9068
[13 empty] | Press drop ratio this iteration |  |  | 0.33263 |  |  | 0.31065 |  |  | 0.15867 |  |  | -2.226 |  |  | 1.5391 |  |  | 1.177 |  |  | 1.089 |  |  | 1.0573 |  |  | 1.0416 |  |  | 1.0297
[13 empty] | Expansion factor | 12 |  | 0.82676 |  |  | 0.83825 |  |  | 0.9166 |  |  | 2.1866 |  |  | 0.15415 |  |  | 0.31433 |  |  | 0.31746 |  |  | 0.2591 |  |  | 0.41209 |  |  | 0.088801
[13 empty] | C Non choked w/ reducers | 7 |  | 15.9026 |  |  | 56.2559 |  |  | 215.6256 |  |  | #NUM! |  |  | -877.792 |  |  | -241.1743 |  |  | -172.6208 |  |  | -178.7949 |  |  | -108.6273 |  |  | -569.4116
[13 empty] | C Choked w/ reducers | 7 |  | 14.2103 |  |  | 49.2491 |  |  | 148.219 |  |  | 1121.3438 |  |  | -323.1531 |  |  | -163.0089 |  |  | -117.5654 |  |  | -103.5476 |  |  | -89.1293 |  |  | -125.3382
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 15.9026 |  |  | 56.2559 |  |  | 215.6256 |  |  | #NUM! |  |  | -323.1531 |  |  | -163.0089 |  |  | -117.5654 |  |  | -103.5476 |  |  | -89.1293 |  |  | -125.3382
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 11.1726 | 39185.7715 |  | 44.6559 | 131404.9585 |  | 192.6256 | 321762.475 |  | 236393 | 626711.1729 |  | 236393 | 1051426.3917 |  | 236393 | 1534585.4555 |  | 236393 | 2047910.2393 |  | 236393 | 2498839.6767 |  | 236393 | 2901075.2891 |  | 236393 | 3401738.9313
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 39969.4869 | C_100 - C this iteration | iteration | 132719.0081 | C_100 - C this iteration | iteration | 324980.0997 | C_100 - C this iteration | iteration | 632978.2846 | C_100 - C this iteration | iteration | 1061940.6556 | C_100 - C this iteration | iteration | 1549931.31 | C_100 - C this iteration | iteration | 2068389.3417 | C_100 - C this iteration | iteration | 2523828.0734 | C_100 - C this iteration | iteration | 2930086.0419 | C_100 - C this iteration | iteration | 3435756.3206 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.8939 |  |  | 86.9746 |  |  | 70.9361 |  |  | 17.1601 |  |  | -115.3539 |  |  | -347.658 |  |  | -689.5699 |  |  | -1070.7638 |  |  | -1474.5986 |  |  | -2061.2996
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8939 |  |  | 26.9746 |  |  | 10.9361 |  |  | -42.8399 |  |  | -175.3539 |  |  | -407.658 |  |  | -749.5699 |  |  | -1130.7638 |  |  | -1534.5986 |  |  | -2121.2996
[13 empty] | Press drop ratio this iteration |  |  | 0.33255 |  |  | 0.31014 |  |  | 0.15417 |  |  | -2.4965 |  |  | 1.5201 |  |  | 1.1726 |  |  | 1.087 |  |  | 1.056 |  |  | 1.0407 |  |  | 1.0291
[13 empty] | Expansion factor | 12 |  | 0.82681 |  |  | 0.83851 |  |  | 0.91896 |  |  | 2.3308 |  |  | 0.16455 |  |  | 0.31689 |  |  | 0.3187 |  |  | 0.25996 |  |  | 0.41258 |  |  | 0.089341
[13 empty] | C Non choked w/ reducers | 7 |  | 16.2239 |  |  | 56.888 |  |  | 221.5461 |  |  | #NUM! |  |  | -806.3422 |  |  | -236.0644 |  |  | -169.9524 |  |  | -176.2442 |  |  | -107.3367 |  |  | -560.0343
[13 empty] | C Choked w/ reducers | 7 |  | 14.4963 |  |  | 49.7777 |  |  | 150.5016 |  |  | 1227.5225 |  |  | -314.9256 |  |  | -160.5535 |  |  | -116.0954 |  |  | -102.3488 |  |  | -88.1384 |  |  | -123.9881
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 16.2239 |  |  | 56.888 |  |  | 221.5461 |  |  | #NUM! |  |  | -314.9256 |  |  | -160.5535 |  |  | -116.0954 |  |  | -102.3488 |  |  | -88.1384 |  |  | -123.9881
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 11.4939 | 39969.4869 |  | 45.288 | 132719.0081 |  | 198.5461 | 324980.0997 |  | 236393 | 632978.2846 |  | 236393 | 1061940.6556 |  | 236393 | 1549931.31 |  | 236393 | 2068389.3417 |  | 236393 | 2523828.0734 |  | 236393 | 2930086.0419 |  | 236393 | 3435756.3206
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 40768.8767 | C_100 - C this iteration | iteration | 134046.1982 | C_100 - C this iteration | iteration | 328229.9007 | C_100 - C this iteration | iteration | 639308.0675 | C_100 - C this iteration | iteration | 1072560.0622 | C_100 - C this iteration | iteration | 1565430.6231 | C_100 - C this iteration | iteration | 2089073.2351 | C_100 - C this iteration | iteration | 2549066.3542 | C_100 - C this iteration | iteration | 2959386.9024 | C_100 - C this iteration | iteration | 3470113.8838 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.8821 |  |  | 86.9101 |  |  | 70.5492 |  |  | 15.6923 |  |  | -119.4852 |  |  | -356.4586 |  |  | -705.2429 |  |  | -1094.0988 |  |  | -1506.0507 |  |  | -2104.5444
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8821 |  |  | 26.9101 |  |  | 10.5492 |  |  | -44.3077 |  |  | -179.4852 |  |  | -416.4586 |  |  | -765.2429 |  |  | -1154.0988 |  |  | -1566.0507 |  |  | -2164.5444
[13 empty] | Press drop ratio this iteration |  |  | 0.33246 |  |  | 0.30963 |  |  | 0.14953 |  |  | -2.8235 |  |  | 1.5022 |  |  | 1.1683 |  |  | 1.0851 |  |  | 1.0548 |  |  | 1.0398 |  |  | 1.0285
[13 empty] | Expansion factor | 12 |  | 0.82685 |  |  | 0.83878 |  |  | 0.9214 |  |  | 2.5051 |  |  | 0.17443 |  |  | 0.31937 |  |  | 0.31991 |  |  | 0.2608 |  |  | 0.41306 |  |  | 0.089871
[13 empty] | C Non choked w/ reducers | 7 |  | 16.5518 |  |  | 57.5288 |  |  | 227.8473 |  |  | #NUM! |  |  | -746.1216 |  |  | -231.1515 |  |  | -167.3503 |  |  | -173.749 |  |  | -106.0661 |  |  | -550.9092
[13 empty] | C Choked w/ reducers | 7 |  | 14.7882 |  |  | 50.3128 |  |  | 152.8402 |  |  | 1355.7639 |  |  | -307.0771 |  |  | -158.1554 |  |  | -114.6505 |  |  | -101.1675 |  |  | -87.1607 |  |  | -122.6547
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 16.5518 |  |  | 57.5288 |  |  | 227.8473 |  |  | #NUM! |  |  | -307.0771 |  |  | -158.1554 |  |  | -114.6505 |  |  | -101.1675 |  |  | -87.1607 |  |  | -122.6547
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 11.8218 | 40768.8767 |  | 45.9288 | 134046.1982 |  | 204.8473 | 328229.9007 |  | 236393 | 639308.0675 |  | 236393 | 1072560.0622 |  | 236393 | 1565430.6231 |  | 236393 | 2089073.2351 |  | 236393 | 2549066.3542 |  | 236393 | 2959386.9024 |  | 236393 | 3470113.8838
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 41584.2542 | C_100 - C this iteration | iteration | 135386.6601 | C_100 - C this iteration | iteration | 331512.1997 | C_100 - C this iteration | iteration | 645701.1481 | C_100 - C this iteration | iteration | 1083285.6628 | C_100 - C this iteration | iteration | 1581084.9294 | C_100 - C this iteration | iteration | 2109963.9674 | C_100 - C this iteration | iteration | 2574557.0177 | C_100 - C this iteration | iteration | 2988980.7714 | C_100 - C this iteration | iteration | 3504815.0226 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.8699 |  |  | 86.8443 |  |  | 70.1545 |  |  | 14.195 |  |  | -123.6996 |  |  | -365.4362 |  |  | -721.231 |  |  | -1117.9029 |  |  | -1538.135 |  |  | -2148.6585
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8699 |  |  | 26.8443 |  |  | 10.1545 |  |  | -45.805 |  |  | -183.6996 |  |  | -425.4362 |  |  | -781.231 |  |  | -1177.9029 |  |  | -1598.135 |  |  | -2208.6585
[13 empty] | Press drop ratio this iteration |  |  | 0.33237 |  |  | 0.30911 |  |  | 0.14474 |  |  | -3.2268 |  |  | 1.485 |  |  | 1.1642 |  |  | 1.0832 |  |  | 1.0537 |  |  | 1.039 |  |  | 1.0279
[13 empty] | Expansion factor | 12 |  | 0.8269 |  |  | 0.83905 |  |  | 0.92392 |  |  | 2.7201 |  |  | 0.18383 |  |  | 0.32178 |  |  | 0.3211 |  |  | 0.26162 |  |  | 0.41353 |  |  | 0.090389
[13 empty] | C Non choked w/ reducers | 7 |  | 16.8865 |  |  | 58.1784 |  |  | 234.5739 |  |  | #NUM! |  |  | -694.646 |  |  | -226.4239 |  |  | -164.8118 |  |  | -171.3074 |  |  | -104.8151 |  |  | -542.0257
[13 empty] | C Choked w/ reducers | 7 |  | 15.086 |  |  | 50.8545 |  |  | 155.2371 |  |  | 1513.759 |  |  | -299.5813 |  |  | -155.8128 |  |  | -113.23 |  |  | -100.0035 |  |  | -86.196 |  |  | -121.3379
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 16.8865 |  |  | 58.1784 |  |  | 234.5739 |  |  | #NUM! |  |  | -299.5813 |  |  | -155.8128 |  |  | -113.23 |  |  | -100.0035 |  |  | -86.196 |  |  | -121.3379
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 12.1565 | 41584.2542 |  | 46.5784 | 135386.6601 |  | 211.5739 | 331512.1997 |  | 236393 | 645701.1481 |  | 236393 | 1083285.6628 |  | 236393 | 1581084.9294 |  | 236393 | 2109963.9674 |  | 236393 | 2574557.0177 |  | 236393 | 2988980.7714 |  | 236393 | 3504815.0226
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 42415.9393 | C_100 - C this iteration | iteration | 136740.5267 | C_100 - C this iteration | iteration | 334827.3217 | C_100 - C this iteration | iteration | 652158.1596 | C_100 - C this iteration | iteration | 1094118.5194 | C_100 - C this iteration | iteration | 1596895.7787 | C_100 - C this iteration | iteration | 2131063.6071 | C_100 - C this iteration | iteration | 2600302.5879 | C_100 - C this iteration | iteration | 3018870.5791 | C_100 - C this iteration | iteration | 3539863.1728 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.8571 |  |  | 86.7771 |  |  | 69.7519 |  |  | 12.6676 |  |  | -127.9986 |  |  | -374.5942 |  |  | -737.5405 |  |  | -1142.1855 |  |  | -1570.8643 |  |  | -2193.6592
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8571 |  |  | 26.7771 |  |  | 9.7519 |  |  | -47.3324 |  |  | -187.9986 |  |  | -434.5942 |  |  | -797.5405 |  |  | -1202.1855 |  |  | -1630.8643 |  |  | -2253.6592
[13 empty] | Press drop ratio this iteration |  |  | 0.33227 |  |  | 0.30857 |  |  | 0.13981 |  |  | -3.7365 |  |  | 1.4688 |  |  | 1.1602 |  |  | 1.0814 |  |  | 1.0525 |  |  | 1.0382 |  |  | 1.0274
[13 empty] | Expansion factor | 12 |  | 0.82695 |  |  | 0.83933 |  |  | 0.92651 |  |  | 2.9918 |  |  | 0.19279 |  |  | 0.32412 |  |  | 0.32225 |  |  | 0.26241 |  |  | 0.41399 |  |  | 0.090896
[13 empty] | C Non choked w/ reducers | 7 |  | 17.228 |  |  | 58.8371 |  |  | 241.7786 |  |  | #NUM! |  |  | -650.1149 |  |  | -221.8704 |  |  | -162.3344 |  |  | -168.9176 |  |  | -103.5832 |  |  | -533.3739
[13 empty] | C Choked w/ reducers | 7 |  | 15.3899 |  |  | 51.4028 |  |  | 157.6945 |  |  | 1713.2437 |  |  | -292.4145 |  |  | -153.5236 |  |  | -111.8334 |  |  | -98.8562 |  |  | -85.2441 |  |  | -120.0372
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 17.228 |  |  | 58.8371 |  |  | 241.7786 |  |  | #NUM! |  |  | -292.4145 |  |  | -153.5236 |  |  | -111.8334 |  |  | -98.8562 |  |  | -85.2441 |  |  | -120.0372
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 12.498 | 42415.9393 |  | 47.2371 | 136740.5267 |  | 218.7786 | 334827.3217 |  | 236393 | 652158.1596 |  | 236393 | 1094118.5194 |  | 236393 | 1596895.7787 |  | 236393 | 2131063.6071 |  | 236393 | 2600302.5879 |  | 236393 | 3018870.5791 |  | 236393 | 3539863.1728
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 43264.2581 | C_100 - C this iteration | iteration | 138107.932 | C_100 - C this iteration | iteration | 338175.595 | C_100 - C this iteration | iteration | 658679.7412 | C_100 - C this iteration | iteration | 1105059.7046 | C_100 - C this iteration | iteration | 1612864.7365 | C_100 - C this iteration | iteration | 2152374.2432 | C_100 - C this iteration | iteration | 2626305.6138 | C_100 - C this iteration | iteration | 3049059.2849 | C_100 - C this iteration | iteration | 3575261.8046 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.8439 |  |  | 86.7086 |  |  | 69.3412 |  |  | 11.1095 |  |  | -132.3841 |  |  | -383.9362 |  |  | -754.1778 |  |  | -1166.9562 |  |  | -1604.2514 |  |  | -2239.5645
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8439 |  |  | 26.7086 |  |  | 9.3412 |  |  | -48.8905 |  |  | -192.3841 |  |  | -443.9362 |  |  | -814.1778 |  |  | -1226.9562 |  |  | -1664.2514 |  |  | -2299.5645
[13 empty] | Press drop ratio this iteration |  |  | 0.33217 |  |  | 0.30803 |  |  | 0.13471 |  |  | -4.4008 |  |  | 1.4532 |  |  | 1.1563 |  |  | 1.0796 |  |  | 1.0514 |  |  | 1.0374 |  |  | 1.0268
[13 empty] | Expansion factor | 12 |  | 0.827 |  |  | 0.83961 |  |  | 0.92919 |  |  | 3.3459 |  |  | 0.20132 |  |  | 0.32639 |  |  | 0.32337 |  |  | 0.2632 |  |  | 0.41444 |  |  | 0.091392
[13 empty] | C Non choked w/ reducers | 7 |  | 17.5767 |  |  | 59.5049 |  |  | 249.5235 |  |  | #NUM! |  |  | -611.1912 |  |  | -217.4812 |  |  | -159.9158 |  |  | -166.5778 |  |  | -102.37 |  |  | -524.9444
[13 empty] | C Choked w/ reducers | 7 |  | 15.7 |  |  | 51.9578 |  |  | 160.2148 |  |  | 1973.0602 |  |  | -285.555 |  |  | -151.2858 |  |  | -110.46 |  |  | -97.7254 |  |  | -84.3047 |  |  | -118.7526
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 17.5767 |  |  | 59.5049 |  |  | 249.5235 |  |  | #NUM! |  |  | -285.555 |  |  | -151.2858 |  |  | -110.46 |  |  | -97.7254 |  |  | -84.3047 |  |  | -118.7526
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 12.8467 | 43264.2581 |  | 47.9049 | 138107.932 |  | 226.5235 | 338175.595 |  | 236393 | 658679.7412 |  | 236393 | 1105059.7046 |  | 236393 | 1612864.7365 |  | 236393 | 2152374.2432 |  | 236393 | 2626305.6138 |  | 236393 | 3049059.2849 |  | 236393 | 3575261.8046
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 44129.5432 | C_100 - C this iteration | iteration | 139489.0113 | C_100 - C this iteration | iteration | 341557.3509 | C_100 - C this iteration | iteration | 665266.5386 | C_100 - C this iteration | iteration | 1116110.3017 | C_100 - C this iteration | iteration | 1628993.3838 | C_100 - C this iteration | iteration | 2173897.9856 | C_100 - C this iteration | iteration | 2652568.6699 | C_100 - C this iteration | iteration | 3079549.8777 | C_100 - C this iteration | iteration | 3611014.4226 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.8301 |  |  | 86.6388 |  |  | 68.9222 |  |  | 9.5201 |  |  | -136.8578 |  |  | -393.4661 |  |  | -771.1495 |  |  | -1192.2247 |  |  | -1638.3095 |  |  | -2286.3925
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8301 |  |  | 26.6388 |  |  | 8.9222 |  |  | -50.4799 |  |  | -196.8578 |  |  | -453.4661 |  |  | -831.1495 |  |  | -1252.2247 |  |  | -1698.3095 |  |  | -2346.3925
[13 empty] | Press drop ratio this iteration |  |  | 0.33207 |  |  | 0.30747 |  |  | 0.12945 |  |  | -5.3025 |  |  | 1.4384 |  |  | 1.1525 |  |  | 1.0778 |  |  | 1.0503 |  |  | 1.0366 |  |  | 1.0262
[13 empty] | Expansion factor | 12 |  | 0.82705 |  |  | 0.8399 |  |  | 0.93195 |  |  | 3.8265 |  |  | 0.20946 |  |  | 0.3286 |  |  | 0.32447 |  |  | 0.26396 |  |  | 0.41487 |  |  | 0.091877
[13 empty] | C Non choked w/ reducers | 7 |  | 17.9326 |  |  | 60.1822 |  |  | 257.8831 |  |  | #NUM! |  |  | -576.8613 |  |  | -213.2469 |  |  | -157.5539 |  |  | -164.2865 |  |  | -101.1751 |  |  | -516.7284
[13 empty] | C Choked w/ reducers | 7 |  | 16.0165 |  |  | 52.5197 |  |  | 162.8006 |  |  | 2325.4957 |  |  | -278.9829 |  |  | -149.0979 |  |  | -109.1092 |  |  | -96.6107 |  |  | -83.3777 |  |  | -117.4836
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 17.9326 |  |  | 60.1822 |  |  | 257.8831 |  |  | #NUM! |  |  | -278.9829 |  |  | -149.0979 |  |  | -109.1092 |  |  | -96.6107 |  |  | -83.3777 |  |  | -117.4836
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 13.2026 | 44129.5432 |  | 48.5822 | 139489.0113 |  | 234.8831 | 341557.3509 |  | 236393 | 665266.5386 |  | 236393 | 1116110.3017 |  | 236393 | 1628993.3838 |  | 236393 | 2173897.9856 |  | 236393 | 2652568.6699 |  | 236393 | 3079549.8777 |  | 236393 | 3611014.4226
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 45012.1341 | C_100 - C this iteration | iteration | 140883.9014 | C_100 - C this iteration | iteration | 344972.9244 | C_100 - C this iteration | iteration | 671919.204 | C_100 - C this iteration | iteration | 1127271.4047 | C_100 - C this iteration | iteration | 1645283.3177 | C_100 - C this iteration | iteration | 2195636.9655 | C_100 - C this iteration | iteration | 2679094.3566 | C_100 - C this iteration | iteration | 3110345.3765 | C_100 - C this iteration | iteration | 3647124.5668 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.8158 |  |  | 86.5675 |  |  | 68.4948 |  |  | 7.8987 |  |  | -141.4213 |  |  | -403.1874 |  |  | -788.4623 |  |  | -1218.0011 |  |  | -1673.0523 |  |  | -2334.1617
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8158 |  |  | 26.5675 |  |  | 8.4948 |  |  | -52.1013 |  |  | -201.4213 |  |  | -463.1874 |  |  | -848.4623 |  |  | -1278.0011 |  |  | -1733.0523 |  |  | -2394.1617
[13 empty] | Press drop ratio this iteration |  |  | 0.33197 |  |  | 0.3069 |  |  | 0.12402 |  |  | -6.5962 |  |  | 1.4243 |  |  | 1.1488 |  |  | 1.0761 |  |  | 1.0493 |  |  | 1.0359 |  |  | 1.0257
[13 empty] | Expansion factor | 12 |  | 0.82711 |  |  | 0.8402 |  |  | 0.93481 |  |  | 4.5161 |  |  | 0.21724 |  |  | 0.33074 |  |  | 0.32554 |  |  | 0.26471 |  |  | 0.4153 |  |  | 0.092352
[13 empty] | C Non choked w/ reducers | 7 |  | 18.2959 |  |  | 60.869 |  |  | 266.9472 |  |  | #NUM! |  |  | -546.3424 |  |  | -209.159 |  |  | -155.2465 |  |  | -162.042 |  |  | -99.9981 |  |  | -508.7174
[13 empty] | C Choked w/ reducers | 7 |  | 16.3394 |  |  | 53.0886 |  |  | 165.4545 |  |  | 2830.8773 |  |  | -272.6801 |  |  | -146.958 |  |  | -107.7806 |  |  | -95.5118 |  |  | -82.4627 |  |  | -116.23
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 18.2959 |  |  | 60.869 |  |  | 266.9472 |  |  | #NUM! |  |  | -272.6801 |  |  | -146.958 |  |  | -107.7806 |  |  | -95.5118 |  |  | -82.4627 |  |  | -116.23
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 13.5659 | 45012.1341 |  | 49.269 | 140883.9014 |  | 243.9472 | 344972.9244 |  | 236393 | 671919.204 |  | 236393 | 1127271.4047 |  | 236393 | 1645283.3177 |  | 236393 | 2195636.9655 |  | 236393 | 2679094.3566 |  | 236393 | 3110345.3765 |  | 236393 | 3647124.5668
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 45912.3768 | C_100 - C this iteration | iteration | 142292.7405 | C_100 - C this iteration | iteration | 348422.6537 | C_100 - C this iteration | iteration | 678638.396 | C_100 - C this iteration | iteration | 1138544.1187 | C_100 - C this iteration | iteration | 1661736.1508 | C_100 - C this iteration | iteration | 2217593.3351 | C_100 - C this iteration | iteration | 2705885.3002 | C_100 - C this iteration | iteration | 3141448.8303 | C_100 - C this iteration | iteration | 3683595.8125 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.8008 |  |  | 86.4948 |  |  | 68.0589 |  |  | 6.2448 |  |  | -146.0766 |  |  | -413.1042 |  |  | -806.1231 |  |  | -1244.2957 |  |  | -1708.4934 |  |  | -2382.891
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8008 |  |  | 26.4948 |  |  | 8.0589 |  |  | -53.7552 |  |  | -206.0766 |  |  | -473.1042 |  |  | -866.1231 |  |  | -1304.2957 |  |  | -1768.4934 |  |  | -2442.891
[13 empty] | Press drop ratio this iteration |  |  | 0.33185 |  |  | 0.30632 |  |  | 0.11841 |  |  | -8.608 |  |  | 1.4107 |  |  | 1.1452 |  |  | 1.0744 |  |  | 1.0482 |  |  | 1.0351 |  |  | 1.0252
[13 empty] | Expansion factor | 12 |  | 0.82717 |  |  | 0.8405 |  |  | 0.93776 |  |  | 5.5886 |  |  | 0.22467 |  |  | 0.33282 |  |  | 0.32659 |  |  | 0.26544 |  |  | 0.41572 |  |  | 0.092818
[13 empty] | C Non choked w/ reducers | 7 |  | 18.6667 |  |  | 61.5657 |  |  | 276.8253 |  |  | #NUM! |  |  | -519.0208 |  |  | -205.2094 |  |  | -152.9916 |  |  | -159.843 |  |  | -98.8386 |  |  | -500.9035
[13 empty] | C Choked w/ reducers | 7 |  | 16.669 |  |  | 53.6645 |  |  | 168.1796 |  |  | 3616.4548 |  |  | -266.63 |  |  | -144.8645 |  |  | -106.4735 |  |  | -94.4283 |  |  | -81.5596 |  |  | -114.9917
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 18.6667 |  |  | 61.5657 |  |  | 276.8253 |  |  | #NUM! |  |  | -266.63 |  |  | -144.8645 |  |  | -106.4735 |  |  | -94.4283 |  |  | -81.5596 |  |  | -114.9917
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 13.9367 | 45912.3768 |  | 49.9657 | 142292.7405 |  | 253.8253 | 348422.6537 |  | 236393 | 678638.396 |  | 236393 | 1138544.1187 |  | 236393 | 1661736.1508 |  | 236393 | 2217593.3351 |  | 236393 | 2705885.3002 |  | 236393 | 3141448.8303 |  | 236393 | 3683595.8125
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 46830.6243 | C_100 - C this iteration | iteration | 143715.6679 | C_100 - C this iteration | iteration | 351906.8802 | C_100 - C this iteration | iteration | 685424.78 | C_100 - C this iteration | iteration | 1149929.5599 | C_100 - C this iteration | iteration | 1678353.5123 | C_100 - C this iteration | iteration | 2239769.2685 | C_100 - C this iteration | iteration | 2732944.1532 | C_100 - C this iteration | iteration | 3172863.3186 | C_100 - C this iteration | iteration | 3720431.7706 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.7853 |  |  | 86.4206 |  |  | 67.6141 |  |  | 4.5576 |  |  | -150.8255 |  |  | -423.2203 |  |  | -824.1389 |  |  | -1271.1187 |  |  | -1744.6468 |  |  | -2432.5999
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.7853 |  |  | 26.4206 |  |  | 7.6141 |  |  | -55.4424 |  |  | -210.8255 |  |  | -483.2203 |  |  | -884.1389 |  |  | -1331.1187 |  |  | -1804.6468 |  |  | -2492.5999
[13 empty] | Press drop ratio this iteration |  |  | 0.33174 |  |  | 0.30572 |  |  | 0.11261 |  |  | -12.1649 |  |  | 1.3978 |  |  | 1.1418 |  |  | 1.0728 |  |  | 1.0472 |  |  | 1.0344 |  |  | 1.0247
[13 empty] | Expansion factor | 12 |  | 0.82723 |  |  | 0.84081 |  |  | 0.94081 |  |  | 7.4846 |  |  | 0.23178 |  |  | 0.33484 |  |  | 0.32761 |  |  | 0.26615 |  |  | 0.41613 |  |  | 0.093273
[13 empty] | C Non choked w/ reducers | 7 |  | 19.0453 |  |  | 62.2723 |  |  | 287.6526 |  |  | #NUM! |  |  | -494.4081 |  |  | -201.3909 |  |  | -150.7874 |  |  | -157.6878 |  |  | -97.6962 |  |  | -493.2792
[13 empty] | C Choked w/ reducers | 7 |  | 17.0053 |  |  | 54.2477 |  |  | 170.9786 |  |  | 5004.8102 |  |  | -260.8173 |  |  | -142.8158 |  |  | -105.1874 |  |  | -93.3601 |  |  | -80.6682 |  |  | -113.7683
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 19.0453 |  |  | 62.2723 |  |  | 287.6526 |  |  | #NUM! |  |  | -260.8173 |  |  | -142.8158 |  |  | -105.1874 |  |  | -93.3601 |  |  | -80.6682 |  |  | -113.7683
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 14.3153 | 46830.6243 |  | 50.6723 | 143715.6679 |  | 264.6526 | 351906.8802 |  | 236393 | 685424.78 |  | 236393 | 1149929.5599 |  | 236393 | 1678353.5123 |  | 236393 | 2239769.2685 |  | 236393 | 2732944.1532 |  | 236393 | 3172863.3186 |  | 236393 | 3720431.7706
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 47767.2368 | C_100 - C this iteration | iteration | 145152.8245 | C_100 - C this iteration | iteration | 355425.949 | C_100 - C this iteration | iteration | 692279.0278 | C_100 - C this iteration | iteration | 1161428.8555 | C_100 - C this iteration | iteration | 1695137.0475 | C_100 - C this iteration | iteration | 2262166.9612 | C_100 - C this iteration | iteration | 2760273.5947 | C_100 - C this iteration | iteration | 3204591.9518 | C_100 - C this iteration | iteration | 3757636.0883 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.7692 |  |  | 86.3449 |  |  | 67.1605 |  |  | 2.8365 |  |  | -155.6698 |  |  | -433.5398 |  |  | -842.5168 |  |  | -1298.4809 |  |  | -1781.5269 |  |  | -2483.3079
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.7692 |  |  | 26.3449 |  |  | 7.1605 |  |  | -57.1635 |  |  | -215.6698 |  |  | -493.5398 |  |  | -902.5168 |  |  | -1358.4809 |  |  | -1841.5269 |  |  | -2543.3079
[13 empty] | Press drop ratio this iteration |  |  | 0.33162 |  |  | 0.30511 |  |  | 0.10662 |  |  | -20.1532 |  |  | 1.3854 |  |  | 1.1384 |  |  | 1.0712 |  |  | 1.0462 |  |  | 1.0337 |  |  | 1.0242
[13 empty] | Expansion factor | 12 |  | 0.82729 |  |  | 0.84113 |  |  | 0.94396 |  |  | 11.7428 |  |  | 0.23858 |  |  | 0.33681 |  |  | 0.3286 |  |  | 0.26685 |  |  | 0.41654 |  |  | 0.093719
[13 empty] | C Non choked w/ reducers | 7 |  | 19.4317 |  |  | 62.9891 |  |  | 299.5982 |  |  | #NUM! |  |  | -472.1111 |  |  | -197.6966 |  |  | -148.6321 |  |  | -155.5752 |  |  | -96.5705 |  |  | -485.8373
[13 empty] | C Choked w/ reducers | 7 |  | 17.3485 |  |  | 54.8382 |  |  | 173.8549 |  |  | 8122.062 |  |  | -255.2279 |  |  | -140.8106 |  |  | -103.9219 |  |  | -92.3067 |  |  | -79.7882 |  |  | -112.5597
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 19.4317 |  |  | 62.9891 |  |  | 299.5982 |  |  | #NUM! |  |  | -255.2279 |  |  | -140.8106 |  |  | -103.9219 |  |  | -92.3067 |  |  | -79.7882 |  |  | -112.5597
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 14.7017 | 47767.2368 |  | 51.3891 | 145152.8245 |  | 276.5982 | 355425.949 |  | 236393 | 692279.0278 |  | 236393 | 1161428.8555 |  | 236393 | 1695137.0475 |  | 236393 | 2262166.9612 |  | 236393 | 2760273.5947 |  | 236393 | 3204591.9518 |  | 236393 | 3757636.0883
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 48722.5815 | C_100 - C this iteration | iteration | 146604.3528 | C_100 - C this iteration | iteration | 358980.2085 | C_100 - C this iteration | iteration | 699201.8181 | C_100 - C this iteration | iteration | 1173043.1441 | C_100 - C this iteration | iteration | 1712088.4179 | C_100 - C this iteration | iteration | 2284788.6308 | C_100 - C this iteration | iteration | 2787876.3306 | C_100 - C this iteration | iteration | 3236637.8713 | C_100 - C this iteration | iteration | 3795212.4492 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.7524 |  |  | 86.2677 |  |  | 66.6977 |  |  | 1.0807 |  |  | -160.6115 |  |  | -444.0667 |  |  | -861.2641 |  |  | -1326.3931 |  |  | -1819.1483 |  |  | -2535.0351
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.7524 |  |  | 26.2677 |  |  | 6.6977 |  |  | -58.9193 |  |  | -220.6115 |  |  | -504.0667 |  |  | -921.2641 |  |  | -1386.3931 |  |  | -1879.1483 |  |  | -2595.0351
[13 empty] | Press drop ratio this iteration |  |  | 0.33149 |  |  | 0.30449 |  |  | 0.10042 |  |  | -54.5172 |  |  | 1.3736 |  |  | 1.1351 |  |  | 1.0697 |  |  | 1.0452 |  |  | 1.033 |  |  | 1.0237
[13 empty] | Expansion factor | 12 |  | 0.82735 |  |  | 0.84146 |  |  | 0.94722 |  |  | 30.0608 |  |  | 0.2451 |  |  | 0.33872 |  |  | 0.32957 |  |  | 0.26753 |  |  | 0.41693 |  |  | 0.094155
[13 empty] | C Non choked w/ reducers | 7 |  | 19.8263 |  |  | 63.7164 |  |  | 312.8775 |  |  | #NUM! |  |  | -451.8094 |  |  | -194.1201 |  |  | -146.5239 |  |  | -153.5039 |  |  | -95.4611 |  |  | -478.571
[13 empty] | C Choked w/ reducers | 7 |  | 17.6988 |  |  | 55.4361 |  |  | 176.8119 |  |  | 21529.7761 |  |  | -249.8488 |  |  | -138.8473 |  |  | -102.6764 |  |  | -91.2679 |  |  | -78.9195 |  |  | -111.3655
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 19.8263 |  |  | 63.7164 |  |  | 312.8775 |  |  | #NUM! |  |  | -249.8488 |  |  | -138.8473 |  |  | -102.6764 |  |  | -91.2679 |  |  | -78.9195 |  |  | -111.3655
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 15.0963 | 48722.5815 |  | 52.1164 | 146604.3528 |  | 289.8775 | 358980.2085 |  | 236393 | 699201.8181 |  | 236393 | 1173043.1441 |  | 236393 | 1712088.4179 |  | 236393 | 2284788.6308 |  | 236393 | 2787876.3306 |  | 236393 | 3236637.8713 |  | 236393 | 3795212.4492
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 49697.0332 | C_100 - C this iteration | iteration | 148070.3963 | C_100 - C this iteration | iteration | 362570.0106 | C_100 - C this iteration | iteration | 706193.8363 | C_100 - C this iteration | iteration | 1184773.5755 | C_100 - C this iteration | iteration | 1729209.3021 | C_100 - C this iteration | iteration | 2307636.5171 | C_100 - C this iteration | iteration | 2815755.094 | C_100 - C this iteration | iteration | 3269004.25 | C_100 - C this iteration | iteration | 3833164.5737 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.7349 |  |  | 86.189 |  |  | 66.2256 |  |  | -0.71025 |  |  | -165.6525 |  |  | -454.8051 |  |  | -880.3883 |  |  | -1354.8664 |  |  | -1857.5259 |  |  | -2587.802
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.7349 |  |  | 26.189 |  |  | 6.2256 |  |  | -60.7103 |  |  | -225.6525 |  |  | -514.8051 |  |  | -940.3883 |  |  | -1414.8664 |  |  | -1917.5259 |  |  | -2647.802
[13 empty] | Press drop ratio this iteration |  |  | 0.33136 |  |  | 0.30386 |  |  | 0.094005 |  |  | 85.4773 |  |  | 1.3622 |  |  | 1.1319 |  |  | 1.0682 |  |  | 1.0443 |  |  | 1.0323 |  |  | 1.0232
[13 empty] | Expansion factor | 12 |  | 0.82742 |  |  | 0.84179 |  |  | 0.95059 |  |  | -44.5643 |  |  | 0.25135 |  |  | 0.34058 |  |  | 0.33052 |  |  | 0.26819 |  |  | 0.41731 |  |  | 0.094582
[13 empty] | C Non choked w/ reducers | 7 |  | 20.229 |  |  | 64.4543 |  |  | 327.7688 |  |  | 42.3584 |  |  | -433.2395 |  |  | -190.6556 |  |  | -144.4612 |  |  | -151.4726 |  |  | -94.3678 |  |  | -471.4739
[13 empty] | C Choked w/ reducers | 7 |  | 18.0563 |  |  | 56.0417 |  |  | 179.853 |  |  | -33088.2138 |  |  | -244.6681 |  |  | -136.9247 |  |  | -101.4505 |  |  | -90.2433 |  |  | -78.0619 |  |  | -110.1857
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 20.229 |  |  | 64.4543 |  |  | 327.7688 |  |  | -33088.2138 |  |  | -244.6681 |  |  | -136.9247 |  |  | -101.4505 |  |  | -90.2433 |  |  | -78.0619 |  |  | -110.1857
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 15.499 | 49697.0332 |  | 52.8543 | 148070.3963 |  | 304.7688 | 362570.0106 |  | 236393 | 706193.8363 |  | 236393 | 1184773.5755 |  | 236393 | 1729209.3021 |  | 236393 | 2307636.5171 |  | 236393 | 2815755.094 |  | 236393 | 3269004.25 |  | 236393 | 3833164.5737
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 50690.9738 | C_100 - C this iteration | iteration | 149551.1003 | C_100 - C this iteration | iteration | 366195.7107 | C_100 - C this iteration | iteration | 713255.7746 | C_100 - C this iteration | iteration | 1196621.3113 | C_100 - C this iteration | iteration | 1746501.3951 | C_100 - C this iteration | iteration | 2330712.8822 | C_100 - C this iteration | iteration | 2843912.6449 | C_100 - C this iteration | iteration | 3301694.2925 | C_100 - C this iteration | iteration | 3871496.2195 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.7167 |  |  | 86.1087 |  |  | 65.744 |  |  | -2.5372 |  |  | -170.7948 |  |  | -465.7594 |  |  | -899.8968 |  |  | -1383.9119 |  |  | -1896.6749 |  |  | -2641.6295
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.7167 |  |  | 26.1087 |  |  | 5.744 |  |  | -62.5372 |  |  | -230.7948 |  |  | -525.7594 |  |  | -959.8968 |  |  | -1443.9119 |  |  | -1956.6749 |  |  | -2701.6295
[13 empty] | Press drop ratio this iteration |  |  | 0.33123 |  |  | 0.30321 |  |  | 0.087369 |  |  | 24.6477 |  |  | 1.3513 |  |  | 1.1288 |  |  | 1.0667 |  |  | 1.0434 |  |  | 1.0316 |  |  | 1.0227
[13 empty] | Expansion factor | 12 |  | 0.82749 |  |  | 0.84212 |  |  | 0.95407 |  |  | -12.1386 |  |  | 0.25734 |  |  | 0.34238 |  |  | 0.33145 |  |  | 0.26884 |  |  | 0.41769 |  |  | 0.095
[13 empty] | C Non choked w/ reducers | 7 |  | 20.6403 |  |  | 65.2031 |  |  | 344.6402 |  |  | 81.8775 |  |  | -416.1824 |  |  | -187.2974 |  |  | -142.4425 |  |  | -149.4801 |  |  | -93.2902 |  |  | -464.5399
[13 empty] | C Choked w/ reducers | 7 |  | 18.4212 |  |  | 56.6549 |  |  | 182.9822 |  |  | -9354.994 |  |  | -239.6746 |  |  | -135.0413 |  |  | -100.2437 |  |  | -89.2328 |  |  | -77.2151 |  |  | -109.0199
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 20.6403 |  |  | 65.2031 |  |  | 344.6402 |  |  | -9354.994 |  |  | -239.6746 |  |  | -135.0413 |  |  | -100.2437 |  |  | -89.2328 |  |  | -77.2151 |  |  | -109.0199
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 15.9103 | 50690.9738 |  | 53.6031 | 149551.1003 |  | 321.6402 | 366195.7107 |  | 236393 | 713255.7746 |  | 236393 | 1196621.3113 |  | 236393 | 1746501.3951 |  | 236393 | 2330712.8822 |  | 236393 | 2843912.6449 |  | 236393 | 3301694.2925 |  | 236393 | 3871496.2195
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 51704.7933 | C_100 - C this iteration | iteration | 151046.6113 | C_100 - C this iteration | iteration | 369857.6678 | C_100 - C this iteration | iteration | 720388.3324 | C_100 - C this iteration | iteration | 1208587.5244 | C_100 - C this iteration | iteration | 1763966.4091 | C_100 - C this iteration | iteration | 2354020.0111 | C_100 - C this iteration | iteration | 2872351.7713 | C_100 - C this iteration | iteration | 3334711.2354 | C_100 - C this iteration | iteration | 3910211.1817 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.6978 |  |  | 86.0267 |  |  | 65.2527 |  |  | -4.401 |  |  | -176.0405 |  |  | -476.9339 |  |  | -919.7974 |  |  | -1413.5412 |  |  | -1936.6108 |  |  | -2696.539
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.6978 |  |  | 26.0267 |  |  | 5.2527 |  |  | -64.401 |  |  | -236.0405 |  |  | -536.9339 |  |  | -979.7974 |  |  | -1473.5412 |  |  | -1996.6108 |  |  | -2756.539
[13 empty] | Press drop ratio this iteration |  |  | 0.33109 |  |  | 0.30254 |  |  | 0.080498 |  |  | 14.6334 |  |  | 1.3408 |  |  | 1.1258 |  |  | 1.0652 |  |  | 1.0424 |  |  | 1.031 |  |  | 1.0223
[13 empty] | Expansion factor | 12 |  | 0.82757 |  |  | 0.84247 |  |  | 0.95769 |  |  | -6.8004 |  |  | 0.26309 |  |  | 0.34414 |  |  | 0.33235 |  |  | 0.26948 |  |  | 0.41806 |  |  | 0.095409
[13 empty] | C Non choked w/ reducers | 7 |  | 21.0601 |  |  | 65.9631 |  |  | 363.9901 |  |  | 110.4459 |  |  | -400.455 |  |  | -184.0405 |  |  | -140.4664 |  |  | -147.5253 |  |  | -92.228 |  |  | -457.7632
[13 empty] | C Choked w/ reducers | 7 |  | 18.7936 |  |  | 57.2759 |  |  | 186.2034 |  |  | -5447.2789 |  |  | -234.858 |  |  | -133.1961 |  |  | -99.0556 |  |  | -88.236 |  |  | -76.3791 |  |  | -107.8679
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 21.0601 |  |  | 65.9631 |  |  | 363.9901 |  |  | -5447.2789 |  |  | -234.858 |  |  | -133.1961 |  |  | -99.0556 |  |  | -88.236 |  |  | -76.3791 |  |  | -107.8679
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 16.3301 | 51704.7933 |  | 54.3631 | 151046.6113 |  | 340.9901 | 369857.6678 |  | 236393 | 720388.3324 |  | 236393 | 1208587.5244 |  | 236393 | 1763966.4091 |  | 236393 | 2354020.0111 |  | 236393 | 2872351.7713 |  | 236393 | 3334711.2354 |  | 236393 | 3910211.1817
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 52738.8892 | C_100 - C this iteration | iteration | 152557.0774 | C_100 - C this iteration | iteration | 373556.2445 | C_100 - C this iteration | iteration | 727592.2157 | C_100 - C this iteration | iteration | 1220673.3996 | C_100 - C this iteration | iteration | 1781606.0732 | C_100 - C this iteration | iteration | 2377560.2112 | C_100 - C this iteration | iteration | 2901075.2891 | C_100 - C this iteration | iteration | 3368058.3478 | C_100 - C this iteration | iteration | 3949313.2935 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.6781 |  |  | 85.9432 |  |  | 64.7516 |  |  | -6.3021 |  |  | -181.3917 |  |  | -488.333 |  |  | -940.0981 |  |  | -1443.7661 |  |  | -1977.3494 |  |  | -2752.5522
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.6781 |  |  | 25.9432 |  |  | 4.7516 |  |  | -66.3021 |  |  | -241.3917 |  |  | -548.333 |  |  | -1000.0981 |  |  | -1503.7661 |  |  | -2037.3494 |  |  | -2812.5522
[13 empty] | Press drop ratio this iteration |  |  | 0.33094 |  |  | 0.30186 |  |  | 0.073382 |  |  | 10.5206 |  |  | 1.3308 |  |  | 1.1229 |  |  | 1.0638 |  |  | 1.0416 |  |  | 1.0303 |  |  | 1.0218
[13 empty] | Expansion factor | 12 |  | 0.82764 |  |  | 0.84282 |  |  | 0.96143 |  |  | -4.6081 |  |  | 0.26862 |  |  | 0.34585 |  |  | 0.33323 |  |  | 0.2701 |  |  | 0.41842 |  |  | 0.09581
[13 empty] | C Non choked w/ reducers | 7 |  | 21.4888 |  |  | 66.7344 |  |  | 386.5139 |  |  | 135.5816 |  |  | -385.9025 |  |  | -180.8799 |  |  | -138.5313 |  |  | -145.607 |  |  | -91.1808 |  |  | -451.1381
[13 empty] | C Choked w/ reducers | 7 |  | 19.1736 |  |  | 57.9049 |  |  | 189.5209 |  |  | -3842.0282 |  |  | -230.2089 |  |  | -131.3878 |  |  | -97.8857 |  |  | -87.2527 |  |  | -75.5535 |  |  | -106.7296
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 21.4888 |  |  | 66.7344 |  |  | 386.5139 |  |  | -3842.0282 |  |  | -230.2089 |  |  | -131.3878 |  |  | -97.8857 |  |  | -87.2527 |  |  | -75.5535 |  |  | -106.7296
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 16.7588 | 52738.8892 |  | 55.1344 | 152557.0774 |  | 363.5139 | 373556.2445 |  | 236393 | 727592.2157 |  | 236393 | 1220673.3996 |  | 236393 | 1781606.0732 |  | 236393 | 2377560.2112 |  | 236393 | 2901075.2891 |  | 236393 | 3368058.3478 |  | 236393 | 3949313.2935
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 53793.667 | C_100 - C this iteration | iteration | 154082.6482 | C_100 - C this iteration | iteration | 377291.8069 | C_100 - C this iteration | iteration | 734868.1379 | C_100 - C this iteration | iteration | 1232880.1336 | C_100 - C this iteration | iteration | 1799422.1339 | C_100 - C this iteration | iteration | 2401335.8133 | C_100 - C this iteration | iteration | 2930086.0419 | C_100 - C this iteration | iteration | 3401738.9313 | C_100 - C this iteration | iteration | 3988806.4264 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.6576 |  |  | 85.8579 |  |  | 64.2404 |  |  | -8.2415 |  |  | -186.8503 |  |  | -499.9612 |  |  | -960.8068 |  |  | -1474.5986 |  |  | -2018.9068 |  |  | -2809.6912
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.6576 |  |  | 25.8579 |  |  | 4.2404 |  |  | -68.2415 |  |  | -246.8503 |  |  | -559.9612 |  |  | -1020.8068 |  |  | -1534.5986 |  |  | -2078.9068 |  |  | -2869.6912
[13 empty] | Press drop ratio this iteration |  |  | 0.33079 |  |  | 0.30117 |  |  | 0.066008 |  |  | 8.2802 |  |  | 1.3211 |  |  | 1.12 |  |  | 1.0624 |  |  | 1.0407 |  |  | 1.0297 |  |  | 1.0214
[13 empty] | Expansion factor | 12 |  | 0.82772 |  |  | 0.84318 |  |  | 0.9653 |  |  | -3.4138 |  |  | 0.27393 |  |  | 0.34752 |  |  | 0.3341 |  |  | 0.27071 |  |  | 0.41877 |  |  | 0.096202
[13 empty] | C Non choked w/ reducers | 7 |  | 21.9266 |  |  | 67.5174 |  |  | 413.2165 |  |  | 159.3235 |  |  | -372.3936 |  |  | -177.8113 |  |  | -136.636 |  |  | -143.7242 |  |  | -90.1484 |  |  | -444.6596
[13 empty] | C Choked w/ reducers | 7 |  | 19.5616 |  |  | 58.5421 |  |  | 192.9394 |  |  | -2967.304 |  |  | -225.7184 |  |  | -129.6153 |  |  | -96.7337 |  |  | -86.2826 |  |  | -74.7383 |  |  | -105.6047
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 21.9266 |  |  | 67.5174 |  |  | 413.2165 |  |  | -2967.304 |  |  | -225.7184 |  |  | -129.6153 |  |  | -96.7337 |  |  | -86.2826 |  |  | -74.7383 |  |  | -105.6047
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 17.1966 | 53793.667 |  | 55.9174 | 154082.6482 |  | 390.2165 | 377291.8069 |  | 236393 | 734868.1379 |  | 236393 | 1232880.1336 |  | 236393 | 1799422.1339 |  | 236393 | 2401335.8133 |  | 236393 | 2930086.0419 |  | 236393 | 3401738.9313 |  | 236393 | 3988806.4264
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 54869.5403 | C_100 - C this iteration | iteration | 155623.4747 | C_100 - C this iteration | iteration | 381064.725 | C_100 - C this iteration | iteration | 742216.8192 | C_100 - C this iteration | iteration | 1245208.935 | C_100 - C this iteration | iteration | 1817416.3553 | C_100 - C this iteration | iteration | 2425349.1714 | C_100 - C this iteration | iteration | 2959386.9024 | C_100 - C this iteration | iteration | 3435756.3206 | C_100 - C this iteration | iteration | 4028694.4907 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.6363 |  |  | 85.7709 |  |  | 63.7189 |  |  | -10.2199 |  |  | -192.4188 |  |  | -511.8232 |  |  | -981.9317 |  |  | -1506.0507 |  |  | -2061.2996 |  |  | -2867.9787
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.6363 |  |  | 25.7709 |  |  | 3.7189 |  |  | -70.2199 |  |  | -252.4188 |  |  | -571.8232 |  |  | -1041.9317 |  |  | -1566.0507 |  |  | -2121.2996 |  |  | -2927.9787
[13 empty] | Press drop ratio this iteration |  |  | 0.33063 |  |  | 0.30046 |  |  | 0.058364 |  |  | 6.8709 |  |  | 1.3118 |  |  | 1.1172 |  |  | 1.0611 |  |  | 1.0398 |  |  | 1.0291 |  |  | 1.0209
[13 empty] | Expansion factor | 12 |  | 0.82781 |  |  | 0.84355 |  |  | 0.96932 |  |  | -2.6626 |  |  | 0.27904 |  |  | 0.34914 |  |  | 0.33494 |  |  | 0.27131 |  |  | 0.41912 |  |  | 0.096586
[13 empty] | C Non choked w/ reducers | 7 |  | 22.3735 |  |  | 68.3123 |  |  | 445.6159 |  |  | 182.6476 |  |  | -359.816 |  |  | -174.8304 |  |  | -134.7792 |  |  | -141.8759 |  |  | -89.1304 |  |  | -438.3224
[13 empty] | C Choked w/ reducers | 7 |  | 19.9576 |  |  | 59.1874 |  |  | 196.4636 |  |  | -2416.8209 |  |  | -221.3781 |  |  | -127.8774 |  |  | -95.5991 |  |  | -85.3255 |  |  | -73.9332 |  |  | -104.493
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 22.3735 |  |  | 68.3123 |  |  | 445.6159 |  |  | -2416.8209 |  |  | -221.3781 |  |  | -127.8774 |  |  | -95.5991 |  |  | -85.3255 |  |  | -73.9332 |  |  | -104.493
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 17.6435 | 54869.5403 |  | 56.7123 | 155623.4747 |  | 422.6159 | 381064.725 |  | 236393 | 742216.8192 |  | 236393 | 1245208.935 |  | 236393 | 1817416.3553 |  | 236393 | 2425349.1714 |  | 236393 | 2959386.9024 |  | 236393 | 3435756.3206 |  | 236393 | 4028694.4907
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 55966.9311 | C_100 - C this iteration | iteration | 157179.7094 | C_100 - C this iteration | iteration | 384875.3722 | C_100 - C this iteration | iteration | 749638.9874 | C_100 - C this iteration | iteration | 1257661.0243 | C_100 - C this iteration | iteration | 1835590.5188 | C_100 - C this iteration | iteration | 2449602.6631 | C_100 - C this iteration | iteration | 2988980.7714 | C_100 - C this iteration | iteration | 3470113.8838 | C_100 - C this iteration | iteration | 4068981.4356 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.6141 |  |  | 85.6822 |  |  | 63.1869 |  |  | -12.238 |  |  | -198.0991 |  |  | -523.9235 |  |  | -1003.4813 |  |  | -1538.135 |  |  | -2104.5444 |  |  | -2927.4378
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.6141 |  |  | 25.6822 |  |  | 3.1869 |  |  | -72.238 |  |  | -258.0991 |  |  | -583.9235 |  |  | -1063.4813 |  |  | -1598.135 |  |  | -2164.5444 |  |  | -2987.4378
[13 empty] | Press drop ratio this iteration |  |  | 0.33046 |  |  | 0.29974 |  |  | 0.050436 |  |  | 5.9027 |  |  | 1.3029 |  |  | 1.1145 |  |  | 1.0598 |  |  | 1.039 |  |  | 1.0285 |  |  | 1.0205
[13 empty] | Expansion factor | 12 |  | 0.82789 |  |  | 0.84393 |  |  | 0.97349 |  |  | -2.1465 |  |  | 0.28395 |  |  | 0.35072 |  |  | 0.33576 |  |  | 0.27189 |  |  | 0.41945 |  |  | 0.096962
[13 empty] | C Non choked w/ reducers | 7 |  | 22.83 |  |  | 69.1193 |  |  | 486.1394 |  |  | 206.1682 |  |  | -348.073 |  |  | -171.9331 |  |  | -132.9596 |  |  | -140.0611 |  |  | -88.1265 |  |  | -432.1219
[13 empty] | C Choked w/ reducers | 7 |  | 20.3617 |  |  | 59.8412 |  |  | 200.0988 |  |  | -2038.453 |  |  | -217.1806 |  |  | -126.1733 |  |  | -94.4816 |  |  | -84.3811 |  |  | -73.1382 |  |  | -103.3943
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 22.83 |  |  | 69.1193 |  |  | 486.1394 |  |  | -2038.453 |  |  | -217.1806 |  |  | -126.1733 |  |  | -94.4816 |  |  | -84.3811 |  |  | -73.1382 |  |  | -103.3943
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18.1 | 55966.9311 |  | 57.5193 | 157179.7094 |  | 463.1394 | 384875.3722 |  | 236393 | 749638.9874 |  | 236393 | 1257661.0243 |  | 236393 | 1835590.5188 |  | 236393 | 2449602.6631 |  | 236393 | 2988980.7714 |  | 236393 | 3470113.8838 |  | 236393 | 4068981.4356
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 57086.2697 | C_100 - C this iteration | iteration | 158751.5065 | C_100 - C this iteration | iteration | 388724.126 | C_100 - C this iteration | iteration | 757135.3773 | C_100 - C this iteration | iteration | 1270237.6345 | C_100 - C this iteration | iteration | 1853946.424 | C_100 - C this iteration | iteration | 2474098.6898 | C_100 - C this iteration | iteration | 3018870.5791 | C_100 - C this iteration | iteration | 3504815.0226 | C_100 - C this iteration | iteration | 4109671.2499 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.5911 |  |  | 85.5917 |  |  | 62.6442 |  |  | -14.2968 |  |  | -203.8936 |  |  | -536.2671 |  |  | -1025.4639 |  |  | -1570.8643 |  |  | -2148.6585 |  |  | -2988.092
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.5911 |  |  | 25.5917 |  |  | 2.6442 |  |  | -74.2968 |  |  | -263.8936 |  |  | -596.2671 |  |  | -1085.4639 |  |  | -1630.8643 |  |  | -2208.6585 |  |  | -3048.092
[13 empty] | Press drop ratio this iteration |  |  | 0.33029 |  |  | 0.299 |  |  | 0.04221 |  |  | 5.1968 |  |  | 1.2943 |  |  | 1.1119 |  |  | 1.0585 |  |  | 1.0382 |  |  | 1.0279 |  |  | 1.0201
[13 empty] | Expansion factor | 12 |  | 0.82798 |  |  | 0.84432 |  |  | 0.97781 |  |  | -1.7702 |  |  | 0.28868 |  |  | 0.35225 |  |  | 0.33656 |  |  | 0.27246 |  |  | 0.41978 |  |  | 0.09733
[13 empty] | C Non choked w/ reducers | 7 |  | 23.2962 |  |  | 69.9389 |  |  | 538.9697 |  |  | 230.3534 |  |  | -337.081 |  |  | -169.1159 |  |  | -131.1762 |  |  | -138.2789 |  |  | -87.1366 |  |  | -426.0534
[13 empty] | C Choked w/ reducers | 7 |  | 20.7743 |  |  | 60.5035 |  |  | 203.8505 |  |  | -1762.369 |  |  | -213.1186 |  |  | -124.5018 |  |  | -93.3808 |  |  | -83.4492 |  |  | -72.3529 |  |  | -102.3085
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 23.2962 |  |  | 69.9389 |  |  | 538.9697 |  |  | -1762.369 |  |  | -213.1186 |  |  | -124.5018 |  |  | -93.3808 |  |  | -83.4492 |  |  | -72.3529 |  |  | -102.3085
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18.5662 | 57086.2697 |  | 58.3389 | 158751.5065 |  | 515.9697 | 388724.126 |  | 236393 | 757135.3773 |  | 236393 | 1270237.6345 |  | 236393 | 1853946.424 |  | 236393 | 2474098.6898 |  | 236393 | 3018870.5791 |  | 236393 | 3504815.0226 |  | 236393 | 4109671.2499
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 58227.9951 | C_100 - C this iteration | iteration | 160339.0216 | C_100 - C this iteration | iteration | 392611.3672 | C_100 - C this iteration | iteration | 764706.7311 | C_100 - C this iteration | iteration | 1282940.0109 | C_100 - C this iteration | iteration | 1872485.8882 | C_100 - C this iteration | iteration | 2498839.6767 | C_100 - C this iteration | iteration | 3049059.2849 | C_100 - C this iteration | iteration | 3539863.1728 | C_100 - C this iteration | iteration | 4150767.9624 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.5671 |  |  | 85.4994 |  |  | 62.0907 |  |  | -16.3968 |  |  | -209.8046 |  |  | -548.8588 |  |  | -1047.8885 |  |  | -1604.2514 |  |  | -2193.6592 |  |  | -3049.9654
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.5671 |  |  | 25.4994 |  |  | 2.0907 |  |  | -76.3968 |  |  | -269.8046 |  |  | -608.8588 |  |  | -1107.8885 |  |  | -1664.2514 |  |  | -2253.6592 |  |  | -3109.9654
[13 empty] | Press drop ratio this iteration |  |  | 0.33011 |  |  | 0.29824 |  |  | 0.033671 |  |  | 4.6592 |  |  | 1.286 |  |  | 1.1093 |  |  | 1.0573 |  |  | 1.0374 |  |  | 1.0274 |  |  | 1.0197
[13 empty] | Expansion factor | 12 |  | 0.82808 |  |  | 0.84471 |  |  | 0.9823 |  |  | -1.4836 |  |  | 0.29324 |  |  | 0.35375 |  |  | 0.33735 |  |  | 0.27302 |  |  | 0.42011 |  |  | 0.097691
[13 empty] | C Non choked w/ reducers | 7 |  | 23.7722 |  |  | 70.7712 |  |  | 612.1132 |  |  | 255.6156 |  |  | -326.7672 |  |  | -166.3752 |  |  | -129.4277 |  |  | -136.5283 |  |  | -86.1602 |  |  | -420.1127
[13 empty] | C Choked w/ reducers | 7 |  | 21.1955 |  |  | 61.1746 |  |  | 207.7246 |  |  | -1552.0137 |  |  | -209.1854 |  |  | -122.8619 |  |  | -92.2963 |  |  | -82.5297 |  |  | -71.5774 |  |  | -101.2354
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 23.7722 |  |  | 70.7712 |  |  | 612.1132 |  |  | -1552.0137 |  |  | -209.1854 |  |  | -122.8619 |  |  | -92.2963 |  |  | -82.5297 |  |  | -71.5774 |  |  | -101.2354
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 19.0422 | 58227.9951 |  | 59.1712 | 160339.0216 |  | 589.1132 | 392611.3672 |  | 236393 | 764706.7311 |  | 236393 | 1282940.0109 |  | 236393 | 1872485.8882 |  | 236393 | 2498839.6767 |  | 236393 | 3049059.2849 |  | 236393 | 3539863.1728 |  | 236393 | 4150767.9624
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 59392.555 | C_100 - C this iteration | iteration | 161942.4118 | C_100 - C this iteration | iteration | 396537.4809 | C_100 - C this iteration | iteration | 772353.7984 | C_100 - C this iteration | iteration | 1295769.411 | C_100 - C this iteration | iteration | 1891210.7471 | C_100 - C this iteration | iteration | 2523828.0734 | C_100 - C this iteration | iteration | 3079549.8777 | C_100 - C this iteration | iteration | 3575261.8046 | C_100 - C this iteration | iteration | 4192275.6421 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.5421 |  |  | 85.4052 |  |  | 61.526 |  |  | -18.5391 |  |  | -215.8344 |  |  | -561.7036 |  |  | -1070.7638 |  |  | -1638.3095 |  |  | -2239.5645 |  |  | -3113.0824
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.5421 |  |  | 25.4052 |  |  | 1.526 |  |  | -78.5391 |  |  | -275.8344 |  |  | -621.7036 |  |  | -1130.7638 |  |  | -1698.3095 |  |  | -2299.5645 |  |  | -3173.0824
[13 empty] | Press drop ratio this iteration |  |  | 0.32992 |  |  | 0.29747 |  |  | 0.024802 |  |  | 4.2364 |  |  | 1.278 |  |  | 1.1068 |  |  | 1.056 |  |  | 1.0366 |  |  | 1.0268 |  |  | 1.0193
[13 empty] | Expansion factor | 12 |  | 0.82817 |  |  | 0.84511 |  |  | 0.98696 |  |  | -1.2582 |  |  | 0.29763 |  |  | 0.3552 |  |  | 0.33812 |  |  | 0.27356 |  |  | 0.42042 |  |  | 0.098044
[13 empty] | C Non choked w/ reducers | 7 |  | 24.2584 |  |  | 71.6166 |  |  | 723.519 |  |  | 282.3604 |  |  | -317.0681 |  |  | -163.7076 |  |  | -127.7131 |  |  | -134.8086 |  |  | -85.1972 |  |  | -414.2955
[13 empty] | C Choked w/ reducers | 7 |  | 21.6254 |  |  | 61.8544 |  |  | 211.7275 |  |  | -1386.3969 |  |  | -205.3747 |  |  | -121.2529 |  |  | -91.2278 |  |  | -81.6221 |  |  | -70.8113 |  |  | -100.1747
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 24.2584 |  |  | 71.6166 |  |  | 723.519 |  |  | -1386.3969 |  |  | -205.3747 |  |  | -121.2529 |  |  | -91.2278 |  |  | -81.6221 |  |  | -70.8113 |  |  | -100.1747
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 19.5284 | 59392.555 |  | 60.0166 | 161942.4118 |  | 700.519 | 396537.4809 |  | 236393 | 772353.7984 |  | 236393 | 1295769.411 |  | 236393 | 1891210.7471 |  | 236393 | 2523828.0734 |  | 236393 | 3079549.8777 |  | 236393 | 3575261.8046 |  | 236393 | 4192275.6421
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 60580.4061 | C_100 - C this iteration | iteration | 163561.8359 | C_100 - C this iteration | iteration | 400502.8557 | C_100 - C this iteration | iteration | 780077.3364 | C_100 - C this iteration | iteration | 1308727.1051 | C_100 - C this iteration | iteration | 1910122.8546 | C_100 - C this iteration | iteration | 2549066.3542 | C_100 - C this iteration | iteration | 3110345.3765 | C_100 - C this iteration | iteration | 3611014.4226 | C_100 - C this iteration | iteration | 4234198.3985 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.5161 |  |  | 85.3091 |  |  | 60.9499 |  |  | -20.7245 |  |  | -221.9854 |  |  | -574.8065 |  |  | -1094.0988 |  |  | -1673.0523 |  |  | -2286.3925 |  |  | -3177.4681
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.5161 |  |  | 25.3091 |  |  | 0.94993 |  |  | -80.7245 |  |  | -281.9854 |  |  | -634.8065 |  |  | -1154.0988 |  |  | -1733.0523 |  |  | -2346.3925 |  |  | -3237.4681
[13 empty] | Press drop ratio this iteration |  |  | 0.32973 |  |  | 0.29668 |  |  | 0.015585 |  |  | 3.8951 |  |  | 1.2703 |  |  | 1.1044 |  |  | 1.0548 |  |  | 1.0359 |  |  | 1.0262 |  |  | 1.0189
[13 empty] | Expansion factor | 12 |  | 0.82827 |  |  | 0.84552 |  |  | 0.99181 |  |  | -1.0763 |  |  | 0.30186 |  |  | 0.35662 |  |  | 0.33887 |  |  | 0.2741 |  |  | 0.42073 |  |  | 0.098389
[13 empty] | C Non choked w/ reducers | 7 |  | 24.7551 |  |  | 72.4754 |  |  | 926.0102 |  |  | 311.0207 |  |  | -307.9281 |  |  | -161.1102 |  |  | -126.0314 |  |  | -133.1188 |  |  | -84.2472 |  |  | -408.5978
[13 empty] | C Choked w/ reducers | 7 |  | 22.0643 |  |  | 62.5433 |  |  | 215.8659 |  |  | -1252.6062 |  |  | -201.6809 |  |  | -119.6738 |  |  | -90.1749 |  |  | -80.7264 |  |  | -70.0546 |  |  | -99.1263
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 24.7551 |  |  | 72.4754 |  |  | 926.0102 |  |  | -1252.6062 |  |  | -201.6809 |  |  | -119.6738 |  |  | -90.1749 |  |  | -80.7264 |  |  | -70.0546 |  |  | -99.1263
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 20.0251 | 60580.4061 |  | 60.8754 | 163561.8359 |  | 903.0102 | 400502.8557 |  | 236393 | 780077.3364 |  | 236393 | 1308727.1051 |  | 236393 | 1910122.8546 |  | 236393 | 2549066.3542 |  | 236393 | 3110345.3765 |  | 236393 | 3611014.4226 |  | 236393 | 4234198.3985
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 61792.0142 | C_100 - C this iteration | iteration | 165197.4543 | C_100 - C this iteration | iteration | 404507.8842 | C_100 - C this iteration | iteration | 787878.1097 | C_100 - C this iteration | iteration | 1321814.3762 | C_100 - C this iteration | iteration | 1929224.0831 | C_100 - C this iteration | iteration | 2574557.0177 | C_100 - C this iteration | iteration | 3141448.8303 | C_100 - C this iteration | iteration | 3647124.5668 | C_100 - C this iteration | iteration | 4276540.3825 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.4891 |  |  | 85.2111 |  |  | 60.3623 |  |  | -22.9538 |  |  | -228.26 |  |  | -588.1729 |  |  | -1117.9029 |  |  | -1708.4934 |  |  | -2334.1617 |  |  | -3243.1479
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.4891 |  |  | 25.2111 |  |  | 0.3623 |  |  | -82.9538 |  |  | -288.26 |  |  | -648.1729 |  |  | -1177.9029 |  |  | -1768.4934 |  |  | -2394.1617 |  |  | -3303.1479
[13 empty] | Press drop ratio this iteration |  |  | 0.32953 |  |  | 0.29587 |  |  | 0.0060021 |  |  | 3.6139 |  |  | 1.2629 |  |  | 1.102 |  |  | 1.0537 |  |  | 1.0351 |  |  | 1.0257 |  |  | 1.0185
[13 empty] | Expansion factor | 12 |  | 0.82838 |  |  | 0.84595 |  |  | 0.99684 |  |  | -0.92644 |  |  | 0.30595 |  |  | 0.358 |  |  | 0.3396 |  |  | 0.27462 |  |  | 0.42104 |  |  | 0.098728
[13 empty] | C Non choked w/ reducers | 7 |  | 25.2623 |  |  | 73.3479 |  |  | 1514.0859 |  |  | 342.0861 |  |  | -299.2978 |  |  | -158.58 |  |  | -124.3816 |  |  | -131.4582 |  |  | -83.3101 |  |  | -403.016
[13 empty] | C Choked w/ reducers | 7 |  | 22.5124 |  |  | 63.2414 |  |  | 220.147 |  |  | -1142.262 |  |  | -198.0982 |  |  | -118.1237 |  |  | -89.1373 |  |  | -79.8423 |  |  | -69.3072 |  |  | -98.09
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 25.2623 |  |  | 73.3479 |  |  | 1514.0859 |  |  | -1142.262 |  |  | -198.0982 |  |  | -118.1237 |  |  | -89.1373 |  |  | -79.8423 |  |  | -69.3072 |  |  | -98.09
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 20.5323 | 61792.0142 |  | 61.7479 | 165197.4543 |  | 1491.0859 | 404507.8842 |  | 236393 | 787878.1097 |  | 236393 | 1321814.3762 |  | 236393 | 1929224.0831 |  | 236393 | 2574557.0177 |  | 236393 | 3141448.8303 |  | 236393 | 3647124.5668 |  | 236393 | 4276540.3825
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 63027.8545 | C_100 - C this iteration | iteration | 166849.4288 | C_100 - C this iteration | iteration | 408552.9631 | C_100 - C this iteration | iteration | 795756.8908 | C_100 - C this iteration | iteration | 1335032.5199 | C_100 - C this iteration | iteration | 1948516.324 | C_100 - C this iteration | iteration | 2600302.5879 | C_100 - C this iteration | iteration | 3172863.3186 | C_100 - C this iteration | iteration | 3683595.8125 | C_100 - C this iteration | iteration | 4319305.7863 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.461 |  |  | 85.1111 |  |  | 59.7629 |  |  | -25.2279 |  |  | -234.6607 |  |  | -601.8079 |  |  | -1142.1855 |  |  | -1744.6468 |  |  | -2382.891 |  |  | -3310.1479
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.461 |  |  | 25.1111 |  |  | -0.23713 |  |  | -85.2279 |  |  | -294.6607 |  |  | -661.8079 |  |  | -1202.1855 |  |  | -1804.6468 |  |  | -2442.891 |  |  | -3370.1479
[13 empty] | Press drop ratio this iteration |  |  | 0.32932 |  |  | 0.29504 |  |  | -0.0039679 |  |  | 3.3783 |  |  | 1.2557 |  |  | 1.0997 |  |  | 1.0525 |  |  | 1.0344 |  |  | 1.0252 |  |  | 1.0181
[13 empty] | Expansion factor | 12 |  | 0.82849 |  |  | 0.84638 |  |  | 1.0021 |  |  | -0.80084 |  |  | 0.30989 |  |  | 0.35935 |  |  | 0.34031 |  |  | 0.27513 |  |  | 0.42133 |  |  | 0.099059
[13 empty] | C Non choked w/ reducers | 7 |  | 25.7805 |  |  | 74.2345 |  |  | #NUM! |  |  | 376.1349 |  |  | -291.1339 |  |  | -156.1143 |  |  | -122.7628 |  |  | -129.8261 |  |  | -82.3856 |  |  | -397.5462
[13 empty] | C Choked w/ reducers | 7 |  | 22.9699 |  |  | 63.9489 |  |  | 224.5787 |  |  | -1049.6891 |  |  | -194.6217 |  |  | -116.6019 |  |  | -88.1147 |  |  | -78.9697 |  |  | -68.5688 |  |  | -97.0656
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 25.7805 |  |  | 74.2345 |  |  | #NUM! |  |  | -1049.6891 |  |  | -194.6217 |  |  | -116.6019 |  |  | -88.1147 |  |  | -78.9697 |  |  | -68.5688 |  |  | -97.0656
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 21.0505 | 63027.8545 |  | 62.6345 | 166849.4288 |  | 236393 | 408552.9631 |  | 236393 | 795756.8908 |  | 236393 | 1335032.5199 |  | 236393 | 1948516.324 |  | 236393 | 2600302.5879 |  | 236393 | 3172863.3186 |  | 236393 | 3683595.8125 |  | 236393 | 4319305.7863
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 64288.4116 | C_100 - C this iteration | iteration | 168517.9231 | C_100 - C this iteration | iteration | 412638.4927 | C_100 - C this iteration | iteration | 803714.4597 | C_100 - C this iteration | iteration | 1348382.8451 | C_100 - C this iteration | iteration | 1968001.4872 | C_100 - C this iteration | iteration | 2626305.6138 | C_100 - C this iteration | iteration | 3204591.9518 | C_100 - C this iteration | iteration | 3720431.7706 | C_100 - C this iteration | iteration | 4362498.8441 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.4318 |  |  | 85.0091 |  |  | 59.1514 |  |  | -27.5477 |  |  | -241.1901 |  |  | -615.7169 |  |  | -1166.9562 |  |  | -1781.5269 |  |  | -2432.5999 |  |  | -3378.4946
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.4318 |  |  | 25.0091 |  |  | -0.84862 |  |  | -87.5477 |  |  | -301.1901 |  |  | -675.7169 |  |  | -1226.9562 |  |  | -1841.5269 |  |  | -2492.5999 |  |  | -3438.4946
[13 empty] | Press drop ratio this iteration |  |  | 0.3291 |  |  | 0.29419 |  |  | -0.014347 |  |  | 3.178 |  |  | 1.2488 |  |  | 1.0974 |  |  | 1.0514 |  |  | 1.0337 |  |  | 1.0247 |  |  | 1.0178
[13 empty] | Expansion factor | 12 |  | 0.8286 |  |  | 0.84682 |  |  | 1.0075 |  |  | -0.69408 |  |  | 0.31369 |  |  | 0.36066 |  |  | 0.34101 |  |  | 0.27563 |  |  | 0.42162 |  |  | 0.099384
[13 empty] | C Non choked w/ reducers | 7 |  | 26.3098 |  |  | 75.1355 |  |  | #NUM! |  |  | 413.8739 |  |  | -283.3978 |  |  | -153.7103 |  |  | -121.174 |  |  | -128.2216 |  |  | -81.4734 |  |  | -392.1851
[13 empty] | C Choked w/ reducers | 7 |  | 23.4369 |  |  | 64.6659 |  |  | 229.1693 |  |  | -970.9073 |  |  | -191.2465 |  |  | -115.1075 |  |  | -87.1067 |  |  | -78.1083 |  |  | -67.8393 |  |  | -96.053
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 26.3098 |  |  | 75.1355 |  |  | #NUM! |  |  | -970.9073 |  |  | -191.2465 |  |  | -115.1075 |  |  | -87.1067 |  |  | -78.1083 |  |  | -67.8393 |  |  | -96.053
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 21.5798 | 64288.4116 |  | 63.5355 | 168517.9231 |  | 236393 | 412638.4927 |  | 236393 | 803714.4597 |  | 236393 | 1348382.8451 |  | 236393 | 1968001.4872 |  | 236393 | 2626305.6138 |  | 236393 | 3204591.9518 |  | 236393 | 3720431.7706 |  | 236393 | 4362498.8441
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 65574.1799 | C_100 - C this iteration | iteration | 170203.1023 | C_100 - C this iteration | iteration | 416764.8776 | C_100 - C this iteration | iteration | 811751.6043 | C_100 - C this iteration | iteration | 1361866.6736 | C_100 - C this iteration | iteration | 1987681.5021 | C_100 - C this iteration | iteration | 2652568.6699 | C_100 - C this iteration | iteration | 3236637.8713 | C_100 - C this iteration | iteration | 3757636.0883 | C_100 - C this iteration | iteration | 4406123.8326 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.4013 |  |  | 84.9051 |  |  | 58.5276 |  |  | -29.9141 |  |  | -247.8508 |  |  | -629.9055 |  |  | -1192.2247 |  |  | -1819.1483 |  |  | -2483.3079 |  |  | -3448.215
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.4013 |  |  | 24.9051 |  |  | -1.4724 |  |  | -89.9141 |  |  | -307.8508 |  |  | -689.9055 |  |  | -1252.2247 |  |  | -1879.1483 |  |  | -2543.3079 |  |  | -3508.215
[13 empty] | Press drop ratio this iteration |  |  | 0.32887 |  |  | 0.29333 |  |  | -0.025157 |  |  | 3.0057 |  |  | 1.2421 |  |  | 1.0953 |  |  | 1.0503 |  |  | 1.033 |  |  | 1.0242 |  |  | 1.0174
[13 empty] | Expansion factor | 12 |  | 0.82872 |  |  | 0.84727 |  |  | 1.0132 |  |  | -0.60223 |  |  | 0.31737 |  |  | 0.36194 |  |  | 0.34169 |  |  | 0.27611 |  |  | 0.42191 |  |  | 0.099701
[13 empty] | C Non choked w/ reducers | 7 |  | 26.8506 |  |  | 76.0513 |  |  | #NUM! |  |  | 456.1905 |  |  | -276.0549 |  |  | -151.3658 |  |  | -119.6144 |  |  | -126.644 |  |  | -80.5733 |  |  | -386.9294
[13 empty] | C Choked w/ reducers | 7 |  | 23.9138 |  |  | 65.3925 |  |  | 233.9278 |  |  | -903.0423 |  |  | -187.9681 |  |  | -113.6399 |  |  | -86.1132 |  |  | -77.2578 |  |  | -67.1186 |  |  | -95.052
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 26.8506 |  |  | 76.0513 |  |  | #NUM! |  |  | -903.0423 |  |  | -187.9681 |  |  | -113.6399 |  |  | -86.1132 |  |  | -77.2578 |  |  | -67.1186 |  |  | -95.052
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 22.1206 | 65574.1799 |  | 64.4513 | 170203.1023 |  | 236393 | 416764.8776 |  | 236393 | 811751.6043 |  | 236393 | 1361866.6736 |  | 236393 | 1987681.5021 |  | 236393 | 2652568.6699 |  | 236393 | 3236637.8713 |  | 236393 | 3757636.0883 |  | 236393 | 4406123.8326
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 66885.6635 | C_100 - C this iteration | iteration | 171905.1333 | C_100 - C this iteration | iteration | 420932.5264 | C_100 - C this iteration | iteration | 819869.1204 | C_100 - C this iteration | iteration | 1375485.3403 | C_100 - C this iteration | iteration | 2007558.3171 | C_100 - C this iteration | iteration | 2679094.3566 | C_100 - C this iteration | iteration | 3269004.25 | C_100 - C this iteration | iteration | 3795212.4492 | C_100 - C this iteration | iteration | 4450185.0709 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.3697 |  |  | 84.799 |  |  | 57.8913 |  |  | -32.3281 |  |  | -254.6453 |  |  | -644.3794 |  |  | -1218.0011 |  |  | -1857.5259 |  |  | -2535.0351 |  |  | -3519.3369
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.3697 |  |  | 24.799 |  |  | -2.1087 |  |  | -92.3281 |  |  | -314.6453 |  |  | -704.3794 |  |  | -1278.0011 |  |  | -1917.5259 |  |  | -2595.0351 |  |  | -3579.3369
[13 empty] | Press drop ratio this iteration |  |  | 0.32863 |  |  | 0.29244 |  |  | -0.036425 |  |  | 2.856 |  |  | 1.2356 |  |  | 1.0931 |  |  | 1.0493 |  |  | 1.0323 |  |  | 1.0237 |  |  | 1.017
[13 empty] | Expansion factor | 12 |  | 0.82885 |  |  | 0.84773 |  |  | 1.0191 |  |  | -0.5224 |  |  | 0.32092 |  |  | 0.36319 |  |  | 0.34236 |  |  | 0.27659 |  |  | 0.42219 |  |  | 0.10001
[13 empty] | C Non choked w/ reducers | 7 |  | 27.4032 |  |  | 76.9823 |  |  | #NUM! |  |  | 504.2285 |  |  | -269.0746 |  |  | -149.0783 |  |  | -118.0831 |  |  | -125.0928 |  |  | -79.6852 |  |  | -381.7757
[13 empty] | C Choked w/ reducers | 7 |  | 24.4007 |  |  | 66.1291 |  |  | 238.8641 |  |  | -843.9667 |  |  | -184.7822 |  |  | -112.1982 |  |  | -85.1337 |  |  | -76.4183 |  |  | -66.4065 |  |  | -94.0624
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 27.4032 |  |  | 76.9823 |  |  | #NUM! |  |  | -843.9667 |  |  | -184.7822 |  |  | -112.1982 |  |  | -85.1337 |  |  | -76.4183 |  |  | -66.4065 |  |  | -94.0624
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 22.6732 | 66885.6635 |  | 65.3823 | 171905.1333 |  | 236393 | 420932.5264 |  | 236393 | 819869.1204 |  | 236393 | 1375485.3403 |  | 236393 | 2007558.3171 |  | 236393 | 2679094.3566 |  | 236393 | 3269004.25 |  | 236393 | 3795212.4492 |  | 236393 | 4450185.0709
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 68223.3767 | C_100 - C this iteration | iteration | 173624.1847 | C_100 - C this iteration | iteration | 425141.8517 | C_100 - C this iteration | iteration | 828067.8116 | C_100 - C this iteration | iteration | 1389240.1937 | C_100 - C this iteration | iteration | 2027633.9003 | C_100 - C this iteration | iteration | 2705885.3002 | C_100 - C this iteration | iteration | 3301694.2925 | C_100 - C this iteration | iteration | 3833164.5737 | C_100 - C this iteration | iteration | 4494686.9216 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.3367 |  |  | 84.6907 |  |  | 57.2422 |  |  | -34.7906 |  |  | -261.5764 |  |  | -659.1441 |  |  | -1244.2957 |  |  | -1896.6749 |  |  | -2587.802 |  |  | -3591.8883
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.3367 |  |  | 24.6907 |  |  | -2.7578 |  |  | -94.7906 |  |  | -321.5764 |  |  | -719.1441 |  |  | -1304.2957 |  |  | -1956.6749 |  |  | -2647.802 |  |  | -3651.8883
[13 empty] | Press drop ratio this iteration |  |  | 0.32838 |  |  | 0.29154 |  |  | -0.048178 |  |  | 2.7246 |  |  | 1.2294 |  |  | 1.091 |  |  | 1.0482 |  |  | 1.0316 |  |  | 1.0232 |  |  | 1.0167
[13 empty] | Expansion factor | 12 |  | 0.82897 |  |  | 0.8482 |  |  | 1.0253 |  |  | -0.45237 |  |  | 0.32435 |  |  | 0.3644 |  |  | 0.34301 |  |  | 0.27706 |  |  | 0.42246 |  |  | 0.10032
[13 empty] | C Non choked w/ reducers | 7 |  | 27.9677 |  |  | 77.9289 |  |  | #NUM! |  |  | 559.4981 |  |  | -262.4293 |  |  | -146.8457 |  |  | -116.5795 |  |  | -123.5671 |  |  | -78.8087 |  |  | -376.7212
[13 empty] | C Choked w/ reducers | 7 |  | 24.8979 |  |  | 66.8758 |  |  | 243.9884 |  |  | -792.0722 |  |  | -181.6849 |  |  | -110.7818 |  |  | -84.168 |  |  | -75.5893 |  |  | -65.703 |  |  | -93.0841
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 27.9677 |  |  | 77.9289 |  |  | #NUM! |  |  | -792.0722 |  |  | -181.6849 |  |  | -110.7818 |  |  | -84.168 |  |  | -75.5893 |  |  | -65.703 |  |  | -93.0841
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 23.2377 | 68223.3767 |  | 66.3289 | 173624.1847 |  | 236393 | 425141.8517 |  | 236393 | 828067.8116 |  | 236393 | 1389240.1937 |  | 236393 | 2027633.9003 |  | 236393 | 2705885.3002 |  | 236393 | 3301694.2925 |  | 236393 | 3833164.5737 |  | 236393 | 4494686.9216
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 69587.8443 | C_100 - C this iteration | iteration | 175360.4265 | C_100 - C this iteration | iteration | 429393.2702 | C_100 - C this iteration | iteration | 836348.4897 | C_100 - C this iteration | iteration | 1403132.5957 | C_100 - C this iteration | iteration | 2047910.2393 | C_100 - C this iteration | iteration | 2732944.1532 | C_100 - C this iteration | iteration | 3334711.2354 | C_100 - C this iteration | iteration | 3871496.2195 | C_100 - C this iteration | iteration | 4539633.7908 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.3024 |  |  | 84.5803 |  |  | 56.58 |  |  | -37.3026 |  |  | -268.6468 |  |  | -674.2056 |  |  | -1271.1187 |  |  | -1936.6108 |  |  | -2641.6295 |  |  | -3665.8979
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.3024 |  |  | 24.5803 |  |  | -3.42 |  |  | -97.3026 |  |  | -328.6468 |  |  | -734.2056 |  |  | -1331.1187 |  |  | -1996.6108 |  |  | -2701.6295 |  |  | -3725.8979
[13 empty] | Press drop ratio this iteration |  |  | 0.32813 |  |  | 0.29061 |  |  | -0.060445 |  |  | 2.6085 |  |  | 1.2233 |  |  | 1.089 |  |  | 1.0472 |  |  | 1.031 |  |  | 1.0227 |  |  | 1.0164
[13 empty] | Expansion factor | 12 |  | 0.82911 |  |  | 0.84868 |  |  | 1.0318 |  |  | -0.39046 |  |  | 0.32766 |  |  | 0.36559 |  |  | 0.34365 |  |  | 0.27752 |  |  | 0.42273 |  |  | 0.10062
[13 empty] | C Non choked w/ reducers | 7 |  | 28.5446 |  |  | 78.8915 |  |  | #NUM! |  |  | 624.0461 |  |  | -256.0941 |  |  | -144.6659 |  |  | -115.1026 |  |  | -122.0664 |  |  | -77.9437 |  |  | -371.7627
[13 empty] | C Choked w/ reducers | 7 |  | 25.4056 |  |  | 67.6327 |  |  | 249.3122 |  |  | -746.1203 |  |  | -178.6722 |  |  | -109.3901 |  |  | -83.2158 |  |  | -74.7709 |  |  | -65.0078 |  |  | -92.1169
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 28.5446 |  |  | 78.8915 |  |  | #NUM! |  |  | -746.1203 |  |  | -178.6722 |  |  | -109.3901 |  |  | -83.2158 |  |  | -74.7709 |  |  | -65.0078 |  |  | -92.1169
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 23.8146 | 69587.8443 |  | 67.2915 | 175360.4265 |  | 236393 | 429393.2702 |  | 236393 | 836348.4897 |  | 236393 | 1403132.5957 |  | 236393 | 2047910.2393 |  | 236393 | 2732944.1532 |  | 236393 | 3334711.2354 |  | 236393 | 3871496.2195 |  | 236393 | 4539633.7908
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 70979.6011 | C_100 - C this iteration | iteration | 177114.0308 | C_100 - C this iteration | iteration | 433687.2029 | C_100 - C this iteration | iteration | 844711.9746 | C_100 - C this iteration | iteration | 1417163.9216 | C_100 - C this iteration | iteration | 2068389.3417 | C_100 - C this iteration | iteration | 2760273.5947 | C_100 - C this iteration | iteration | 3368058.3478 | C_100 - C this iteration | iteration | 3910211.1817 | C_100 - C this iteration | iteration | 4585030.1288 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.2668 |  |  | 84.4676 |  |  | 55.9046 |  |  | -39.8651 |  |  | -275.8593 |  |  | -689.5699 |  |  | -1298.4809 |  |  | -1977.3494 |  |  | -2696.539 |  |  | -3741.3952
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.2668 |  |  | 24.4676 |  |  | -4.0954 |  |  | -99.8651 |  |  | -335.8593 |  |  | -749.5699 |  |  | -1358.4809 |  |  | -2037.3494 |  |  | -2756.539 |  |  | -3801.3952
[13 empty] | Press drop ratio this iteration |  |  | 0.32786 |  |  | 0.28967 |  |  | -0.073257 |  |  | 2.5051 |  |  | 1.2175 |  |  | 1.087 |  |  | 1.0462 |  |  | 1.0303 |  |  | 1.0223 |  |  | 1.016
[13 empty] | Expansion factor | 12 |  | 0.82925 |  |  | 0.84917 |  |  | 1.0385 |  |  | -0.33535 |  |  | 0.33087 |  |  | 0.36674 |  |  | 0.34428 |  |  | 0.27796 |  |  | 0.42299 |  |  | 0.10091
[13 empty] | C Non choked w/ reducers | 7 |  | 29.1341 |  |  | 79.8705 |  |  | #NUM! |  |  | 700.727 |  |  | -250.0466 |  |  | -142.5369 |  |  | -113.6518 |  |  | -120.59 |  |  | -77.0899 |  |  | -366.8977
[13 empty] | C Choked w/ reducers | 7 |  | 25.9241 |  |  | 68.4002 |  |  | 254.8478 |  |  | -705.1418 |  |  | -175.7407 |  |  | -108.0223 |  |  | -82.2768 |  |  | -73.9627 |  |  | -64.3209 |  |  | -91.1606
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 29.1341 |  |  | 79.8705 |  |  | #NUM! |  |  | -705.1418 |  |  | -175.7407 |  |  | -108.0223 |  |  | -82.2768 |  |  | -73.9627 |  |  | -64.3209 |  |  | -91.1606
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 24.4041 | 70979.6011 |  | 68.2705 | 177114.0308 |  | 236393 | 433687.2029 |  | 236393 | 844711.9746 |  | 236393 | 1417163.9216 |  | 236393 | 2068389.3417 |  | 236393 | 2760273.5947 |  | 236393 | 3368058.3478 |  | 236393 | 3910211.1817 |  | 236393 | 4585030.1288
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 72399.1932 | C_100 - C this iteration | iteration | 178885.1711 | C_100 - C this iteration | iteration | 438024.0749 | C_100 - C this iteration | iteration | 853159.0943 | C_100 - C this iteration | iteration | 1431335.5608 | C_100 - C this iteration | iteration | 2089073.2351 | C_100 - C this iteration | iteration | 2787876.3306 | C_100 - C this iteration | iteration | 3401738.9313 | C_100 - C this iteration | iteration | 3949313.2935 | C_100 - C this iteration | iteration | 4630880.43 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.2297 |  |  | 84.3527 |  |  | 55.2155 |  |  | -42.4791 |  |  | -283.2168 |  |  | -705.2429 |  |  | -1326.3931 |  |  | -2018.9068 |  |  | -2752.5522 |  |  | -3818.41
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.2297 |  |  | 24.3527 |  |  | -4.7845 |  |  | -102.4791 |  |  | -343.2168 |  |  | -765.2429 |  |  | -1386.3931 |  |  | -2078.9068 |  |  | -2812.5522 |  |  | -3878.41
[13 empty] | Press drop ratio this iteration |  |  | 0.32758 |  |  | 0.2887 |  |  | -0.086651 |  |  | 2.4125 |  |  | 1.2119 |  |  | 1.0851 |  |  | 1.0452 |  |  | 1.0297 |  |  | 1.0218 |  |  | 1.0157
[13 empty] | Expansion factor | 12 |  | 0.82939 |  |  | 0.84968 |  |  | 1.0455 |  |  | -0.28598 |  |  | 0.33398 |  |  | 0.36787 |  |  | 0.34488 |  |  | 0.2784 |  |  | 0.42324 |  |  | 0.10119
[13 empty] | C Non choked w/ reducers | 7 |  | 29.7366 |  |  | 80.8664 |  |  | #NUM! |  |  | 793.6542 |  |  | -244.2666 |  |  | -140.4569 |  |  | -112.2263 |  |  | -119.1374 |  |  | -76.2472 |  |  | -362.1232
[13 empty] | C Choked w/ reducers | 7 |  | 26.4536 |  |  | 69.1783 |  |  | 260.6083 |  |  | -668.3675 |  |  | -172.887 |  |  | -106.6779 |  |  | -81.3509 |  |  | -73.1646 |  |  | -63.6421 |  |  | -90.2152
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 29.7366 |  |  | 80.8664 |  |  | #NUM! |  |  | -668.3675 |  |  | -172.887 |  |  | -106.6779 |  |  | -81.3509 |  |  | -73.1646 |  |  | -63.6421 |  |  | -90.2152
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 25.0066 | 72399.1932 |  | 69.2664 | 178885.1711 |  | 236393 | 438024.0749 |  | 236393 | 853159.0943 |  | 236393 | 1431335.5608 |  | 236393 | 2089073.2351 |  | 236393 | 2787876.3306 |  | 236393 | 3401738.9313 |  | 236393 | 3949313.2935 |  | 236393 | 4630880.43
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 73847.177 | C_100 - C this iteration | iteration | 180674.0228 | C_100 - C this iteration | iteration | 442404.3157 | C_100 - C this iteration | iteration | 861690.6853 | C_100 - C this iteration | iteration | 1445648.9164 | C_100 - C this iteration | iteration | 2109963.9674 | C_100 - C this iteration | iteration | 2815755.094 | C_100 - C this iteration | iteration | 3435756.3206 | C_100 - C this iteration | iteration | 3988806.4264 | C_100 - C this iteration | iteration | 4677189.2343 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.1911 |  |  | 84.2355 |  |  | 54.5126 |  |  | -45.1457 |  |  | -290.7222 |  |  | -721.231 |  |  | -1354.8664 |  |  | -2061.2996 |  |  | -2809.6912 |  |  | -3896.9727
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.1911 |  |  | 24.2355 |  |  | -5.4874 |  |  | -105.1457 |  |  | -350.7222 |  |  | -781.231 |  |  | -1414.8664 |  |  | -2121.2996 |  |  | -2869.6912 |  |  | -3956.9727
[13 empty] | Press drop ratio this iteration |  |  | 0.32729 |  |  | 0.28771 |  |  | -0.10066 |  |  | 2.329 |  |  | 1.2064 |  |  | 1.0832 |  |  | 1.0443 |  |  | 1.0291 |  |  | 1.0214 |  |  | 1.0154
[13 empty] | Expansion factor | 12 |  | 0.82955 |  |  | 0.85019 |  |  | 1.0529 |  |  | -0.24151 |  |  | 0.33699 |  |  | 0.36897 |  |  | 0.34548 |  |  | 0.27883 |  |  | 0.42349 |  |  | 0.10147
[13 empty] | C Non choked w/ reducers | 7 |  | 30.3524 |  |  | 81.8797 |  |  | #NUM! |  |  | 908.9887 |  |  | -238.7357 |  |  | -138.4239 |  |  | -110.8255 |  |  | -117.708 |  |  | -75.4153 |  |  | -357.4368
[13 empty] | C Choked w/ reducers | 7 |  | 26.9943 |  |  | 69.9673 |  |  | 266.6083 |  |  | -635.1789 |  |  | -170.1079 |  |  | -105.3562 |  |  | -80.4377 |  |  | -72.3765 |  |  | -62.9713 |  |  | -89.2804
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 30.3524 |  |  | 81.8797 |  |  | #NUM! |  |  | -635.1789 |  |  | -170.1079 |  |  | -105.3562 |  |  | -80.4377 |  |  | -72.3765 |  |  | -62.9713 |  |  | -89.2804
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 25.6224 | 73847.177 |  | 70.2797 | 180674.0228 |  | 236393 | 442404.3157 |  | 236393 | 861690.6853 |  | 236393 | 1445648.9164 |  | 236393 | 2109963.9674 |  | 236393 | 2815755.094 |  | 236393 | 3435756.3206 |  | 236393 | 3988806.4264 |  | 236393 | 4677189.2343
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 75324.1206 | C_100 - C this iteration | iteration | 182480.763 | C_100 - C this iteration | iteration | 446828.3588 | C_100 - C this iteration | iteration | 870307.5921 | C_100 - C this iteration | iteration | 1460105.4056 | C_100 - C this iteration | iteration | 2131063.6071 | C_100 - C this iteration | iteration | 2843912.6449 | C_100 - C this iteration | iteration | 3470113.8838 | C_100 - C this iteration | iteration | 4028694.4907 | C_100 - C this iteration | iteration | 4723961.1267 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.1509 |  |  | 84.1159 |  |  | 53.7956 |  |  | -47.8658 |  |  | -298.3784 |  |  | -737.5405 |  |  | -1383.9119 |  |  | -2104.5444 |  |  | -2867.9787 |  |  | -3977.1146
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.1509 |  |  | 24.1159 |  |  | -6.2044 |  |  | -107.8658 |  |  | -358.3784 |  |  | -797.5405 |  |  | -1443.9119 |  |  | -2164.5444 |  |  | -2927.9787 |  |  | -4037.1146
[13 empty] | Press drop ratio this iteration |  |  | 0.32698 |  |  | 0.2867 |  |  | -0.11533 |  |  | 2.2535 |  |  | 1.2011 |  |  | 1.0814 |  |  | 1.0434 |  |  | 1.0285 |  |  | 1.0209 |  |  | 1.0151
[13 empty] | Expansion factor | 12 |  | 0.8297 |  |  | 0.85072 |  |  | 1.0606 |  |  | -0.20125 |  |  | 0.3399 |  |  | 0.37004 |  |  | 0.34606 |  |  | 0.27925 |  |  | 0.42374 |  |  | 0.10175
[13 empty] | C Non choked w/ reducers | 7 |  | 30.9819 |  |  | 82.9108 |  |  | #NUM! |  |  | 1056.4037 |  |  | -233.4372 |  |  | -136.4365 |  |  | -109.4487 |  |  | -116.3013 |  |  | -74.5942 |  |  | -352.836
[13 empty] | C Choked w/ reducers | 7 |  | 27.5466 |  |  | 70.7675 |  |  | 272.8634 |  |  | -605.0734 |  |  | -167.4005 |  |  | -104.0567 |  |  | -79.5369 |  |  | -71.5982 |  |  | -62.3084 |  |  | -88.3562
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 30.9819 |  |  | 82.9108 |  |  | #NUM! |  |  | -605.0734 |  |  | -167.4005 |  |  | -104.0567 |  |  | -79.5369 |  |  | -71.5982 |  |  | -62.3084 |  |  | -88.3562
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 26.2519 | 75324.1206 |  | 71.3108 | 182480.763 |  | 236393 | 446828.3588 |  | 236393 | 870307.5921 |  | 236393 | 1460105.4056 |  | 236393 | 2131063.6071 |  | 236393 | 2843912.6449 |  | 236393 | 3470113.8838 |  | 236393 | 4028694.4907 |  | 236393 | 4723961.1267
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 76830.603 | C_100 - C this iteration | iteration | 184305.5707 | C_100 - C this iteration | iteration | 451296.6424 | C_100 - C this iteration | iteration | 879010.6681 | C_100 - C this iteration | iteration | 1474706.4597 | C_100 - C this iteration | iteration | 2152374.2432 | C_100 - C this iteration | iteration | 2872351.7713 | C_100 - C this iteration | iteration | 3504815.0226 | C_100 - C this iteration | iteration | 4068981.4356 | C_100 - C this iteration | iteration | 4771200.7379 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.1092 |  |  | 83.9939 |  |  | 53.0642 |  |  | -50.6406 |  |  | -306.1885 |  |  | -754.1778 |  |  | -1413.5412 |  |  | -2148.6585 |  |  | -2927.4378 |  |  | -4058.8673
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.1092 |  |  | 23.9939 |  |  | -6.9358 |  |  | -110.6406 |  |  | -366.1885 |  |  | -814.1778 |  |  | -1473.5412 |  |  | -2208.6585 |  |  | -2987.4378 |  |  | -4118.8673
[13 empty] | Press drop ratio this iteration |  |  | 0.32667 |  |  | 0.28566 |  |  | -0.13071 |  |  | 2.1848 |  |  | 1.196 |  |  | 1.0796 |  |  | 1.0424 |  |  | 1.0279 |  |  | 1.0205 |  |  | 1.0148
[13 empty] | Expansion factor | 12 |  | 0.82987 |  |  | 0.85126 |  |  | 1.0687 |  |  | -0.16463 |  |  | 0.34271 |  |  | 0.37108 |  |  | 0.34663 |  |  | 0.27966 |  |  | 0.42398 |  |  | 0.10202
[13 empty] | C Non choked w/ reducers | 7 |  | 31.6253 |  |  | 83.9602 |  |  | #NUM! |  |  | 1252.0146 |  |  | -228.3559 |  |  | -134.4929 |  |  | -108.0954 |  |  | -114.9166 |  |  | -73.7835 |  |  | -348.3183
[13 empty] | C Choked w/ reducers | 7 |  | 28.1107 |  |  | 71.5789 |  |  | 279.3907 |  |  | -577.638 |  |  | -164.7618 |  |  | -102.7788 |  |  | -78.6484 |  |  | -70.8295 |  |  | -61.6533 |  |  | -87.4423
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 31.6253 |  |  | 83.9602 |  |  | #NUM! |  |  | -577.638 |  |  | -164.7618 |  |  | -102.7788 |  |  | -78.6484 |  |  | -70.8295 |  |  | -61.6533 |  |  | -87.4423
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 26.8953 | 76830.603 |  | 72.3602 | 184305.5707 |  | 236393 | 451296.6424 |  | 236393 | 879010.6681 |  | 236393 | 1474706.4597 |  | 236393 | 2152374.2432 |  | 236393 | 2872351.7713 |  | 236393 | 3504815.0226 |  | 236393 | 4068981.4356 |  | 236393 | 4771200.7379
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 78367.215 | C_100 - C this iteration | iteration | 186148.6264 | C_100 - C this iteration | iteration | 455809.6089 | C_100 - C this iteration | iteration | 887800.7747 | C_100 - C this iteration | iteration | 1489453.5242 | C_100 - C this iteration | iteration | 2173897.9856 | C_100 - C this iteration | iteration | 2901075.2891 | C_100 - C this iteration | iteration | 3539863.1728 | C_100 - C this iteration | iteration | 4109671.2499 | C_100 - C this iteration | iteration | 4818912.7453 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.0657 |  |  | 83.8695 |  |  | 52.3181 |  |  | -53.4712 |  |  | -314.1557 |  |  | -771.1495 |  |  | -1443.7661 |  |  | -2193.6592 |  |  | -2988.092 |  |  | -4142.2633
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.0657 |  |  | 23.8695 |  |  | -7.6819 |  |  | -113.4712 |  |  | -374.1557 |  |  | -831.1495 |  |  | -1503.7661 |  |  | -2253.6592 |  |  | -3048.092 |  |  | -4202.2633
[13 empty] | Press drop ratio this iteration |  |  | 0.32634 |  |  | 0.2846 |  |  | -0.14683 |  |  | 2.1221 |  |  | 1.191 |  |  | 1.0778 |  |  | 1.0416 |  |  | 1.0274 |  |  | 1.0201 |  |  | 1.0145
[13 empty] | Expansion factor | 12 |  | 0.83004 |  |  | 0.85181 |  |  | 1.0772 |  |  | -0.1312 |  |  | 0.34545 |  |  | 0.3721 |  |  | 0.34719 |  |  | 0.28006 |  |  | 0.42421 |  |  | 0.10228
[13 empty] | C Non choked w/ reducers | 7 |  | 32.2832 |  |  | 85.0285 |  |  | #NUM! |  |  | 1524.8243 |  |  | -223.4779 |  |  | -132.5917 |  |  | -106.7648 |  |  | -113.5534 |  |  | -72.9831 |  |  | -343.8815
[13 empty] | C Choked w/ reducers | 7 |  | 28.6869 |  |  | 72.402 |  |  | 286.209 |  |  | -552.5303 |  |  | -162.1892 |  |  | -101.522 |  |  | -77.772 |  |  | -70.0703 |  |  | -61.0059 |  |  | -86.5386
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 32.2832 |  |  | 85.0285 |  |  | #NUM! |  |  | -552.5303 |  |  | -162.1892 |  |  | -101.522 |  |  | -77.772 |  |  | -70.0703 |  |  | -61.0059 |  |  | -86.5386
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 27.5532 | 78367.215 |  | 73.4285 | 186148.6264 |  | 236393 | 455809.6089 |  | 236393 | 887800.7747 |  | 236393 | 1489453.5242 |  | 236393 | 2173897.9856 |  | 236393 | 2901075.2891 |  | 236393 | 3539863.1728 |  | 236393 | 4109671.2499 |  | 236393 | 4818912.7453
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 79934.5593 | C_100 - C this iteration | iteration | 188010.1126 | C_100 - C this iteration | iteration | 460367.7049 | C_100 - C this iteration | iteration | 896678.7825 | C_100 - C this iteration | iteration | 1504348.0595 | C_100 - C this iteration | iteration | 2195636.9655 | C_100 - C this iteration | iteration | 2930086.0419 | C_100 - C this iteration | iteration | 3575261.8046 | C_100 - C this iteration | iteration | 4150767.9624 | C_100 - C this iteration | iteration | 4867101.8728 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.0205 |  |  | 83.7425 |  |  | 51.557 |  |  | -56.3587 |  |  | -322.2829 |  |  | -788.4623 |  |  | -1474.5986 |  |  | -2239.5645 |  |  | -3049.9654 |  |  | -4227.3355
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 29.0205 |  |  | 23.7425 |  |  | -8.443 |  |  | -116.3587 |  |  | -382.2829 |  |  | -848.4623 |  |  | -1534.5986 |  |  | -2299.5645 |  |  | -3109.9654 |  |  | -4287.3355
[13 empty] | Press drop ratio this iteration |  |  | 0.326 |  |  | 0.28352 |  |  | -0.16376 |  |  | 2.0646 |  |  | 1.1862 |  |  | 1.0761 |  |  | 1.0407 |  |  | 1.0268 |  |  | 1.0197 |  |  | 1.0142
[13 empty] | Expansion factor | 12 |  | 0.83022 |  |  | 0.85238 |  |  | 1.0861 |  |  | -0.10055 |  |  | 0.34809 |  |  | 0.3731 |  |  | 0.34773 |  |  | 0.28045 |  |  | 0.42444 |  |  | 0.10254
[13 empty] | C Non choked w/ reducers | 7 |  | 32.9558 |  |  | 86.1162 |  |  | #NUM! |  |  | 1932.8416 |  |  | -218.7904 |  |  | -130.7314 |  |  | -105.4564 |  |  | -112.2114 |  |  | -72.1928 |  |  | -339.5234
[13 empty] | C Choked w/ reducers | 7 |  | 29.2755 |  |  | 73.2369 |  |  | 293.3386 |  |  | -529.4641 |  |  | -159.6802 |  |  | -100.2857 |  |  | -76.9073 |  |  | -69.3204 |  |  | -60.3659 |  |  | -85.6451
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 32.9558 |  |  | 86.1162 |  |  | #NUM! |  |  | -529.4641 |  |  | -159.6802 |  |  | -100.2857 |  |  | -76.9073 |  |  | -69.3204 |  |  | -60.3659 |  |  | -85.6451
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 28.2258 | 79934.5593 |  | 74.5162 | 188010.1126 |  | 236393 | 460367.7049 |  | 236393 | 896678.7825 |  | 236393 | 1504348.0595 |  | 236393 | 2195636.9655 |  | 236393 | 2930086.0419 |  | 236393 | 3575261.8046 |  | 236393 | 4150767.9624 |  | 236393 | 4867101.8728
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 81533.2505 | C_100 - C this iteration | iteration | 189890.2138 | C_100 - C this iteration | iteration | 464971.382 | C_100 - C this iteration | iteration | 905645.5703 | C_100 - C this iteration | iteration | 1519391.5401 | C_100 - C this iteration | iteration | 2217593.3351 | C_100 - C this iteration | iteration | 2959386.9024 | C_100 - C this iteration | iteration | 3611014.4226 | C_100 - C this iteration | iteration | 4192275.6421 | C_100 - C this iteration | iteration | 4915772.8915 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.9734 |  |  | 83.613 |  |  | 50.7805 |  |  | -59.3042 |  |  | -330.5735 |  |  | -806.1231 |  |  | -1506.0507 |  |  | -2286.3925 |  |  | -3113.0824 |  |  | -4314.1176
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.9734 |  |  | 23.613 |  |  | -9.2195 |  |  | -119.3042 |  |  | -390.5735 |  |  | -866.1231 |  |  | -1566.0507 |  |  | -2346.3925 |  |  | -3173.0824 |  |  | -4374.1176
[13 empty] | Press drop ratio this iteration |  |  | 0.32564 |  |  | 0.28241 |  |  | -0.18156 |  |  | 2.0117 |  |  | 1.1815 |  |  | 1.0744 |  |  | 1.0398 |  |  | 1.0262 |  |  | 1.0193 |  |  | 1.0139
[13 empty] | Expansion factor | 12 |  | 0.8304 |  |  | 0.85295 |  |  | 1.0954 |  |  | -0.072368 |  |  | 0.35066 |  |  | 0.37407 |  |  | 0.34827 |  |  | 0.28084 |  |  | 0.42467 |  |  | 0.10279
[13 empty] | C Non choked w/ reducers | 7 |  | 33.6435 |  |  | 87.2239 |  |  | #NUM! |  |  | 2611.4547 |  |  | -214.2819 |  |  | -128.9105 |  |  | -104.1697 |  |  | -110.8899 |  |  | -71.4125 |  |  | -335.2418
[13 empty] | C Choked w/ reducers | 7 |  | 29.8768 |  |  | 74.0838 |  |  | 300.8019 |  |  | -508.1983 |  |  | -157.2322 |  |  | -99.0695 |  |  | -76.0542 |  |  | -68.5796 |  |  | -59.7335 |  |  | -84.7615
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 33.6435 |  |  | 87.2239 |  |  | #NUM! |  |  | -508.1983 |  |  | -157.2322 |  |  | -99.0695 |  |  | -76.0542 |  |  | -68.5796 |  |  | -59.7335 |  |  | -84.7615
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 28.9135 | 81533.2505 |  | 75.6239 | 189890.2138 |  | 236393 | 464971.382 |  | 236393 | 905645.5703 |  | 236393 | 1519391.5401 |  | 236393 | 2217593.3351 |  | 236393 | 2959386.9024 |  | 236393 | 3611014.4226 |  | 236393 | 4192275.6421 |  | 236393 | 4915772.8915
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 83163.9155 | C_100 - C this iteration | iteration | 191789.1159 | C_100 - C this iteration | iteration | 469621.0958 | C_100 - C this iteration | iteration | 914702.026 | C_100 - C this iteration | iteration | 1534585.4555 | C_100 - C this iteration | iteration | 2239769.2685 | C_100 - C this iteration | iteration | 2988980.7714 | C_100 - C this iteration | iteration | 3647124.5668 | C_100 - C this iteration | iteration | 4234198.3985 | C_100 - C this iteration | iteration | 4964930.6204 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.9245 |  |  | 83.4809 |  |  | 49.9885 |  |  | -62.309 |  |  | -339.0308 |  |  | -824.1389 |  |  | -1538.135 |  |  | -2334.1617 |  |  | -3177.4681 |  |  | -4402.6441
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.9245 |  |  | 23.4809 |  |  | -10.0115 |  |  | -122.309 |  |  | -399.0308 |  |  | -884.1389 |  |  | -1598.135 |  |  | -2394.1617 |  |  | -3237.4681 |  |  | -4462.6441
[13 empty] | Press drop ratio this iteration |  |  | 0.32527 |  |  | 0.28127 |  |  | -0.20028 |  |  | 1.9629 |  |  | 1.177 |  |  | 1.0728 |  |  | 1.039 |  |  | 1.0257 |  |  | 1.0189 |  |  | 1.0136
[13 empty] | Expansion factor | 12 |  | 0.8306 |  |  | 0.85354 |  |  | 1.1053 |  |  | -0.04636 |  |  | 0.35315 |  |  | 0.37502 |  |  | 0.34879 |  |  | 0.28121 |  |  | 0.42489 |  |  | 0.10304
[13 empty] | C Non choked w/ reducers | 7 |  | 34.3469 |  |  | 88.3522 |  |  | #NUM! |  |  | 3967.0511 |  |  | -209.9417 |  |  | -127.1278 |  |  | -102.904 |  |  | -109.5886 |  |  | -70.642 |  |  | -331.0348
[13 empty] | C Choked w/ reducers | 7 |  | 30.4911 |  |  | 74.943 |  |  | 308.6235 |  |  | -488.5282 |  |  | -154.8431 |  |  | -97.8729 |  |  | -75.2124 |  |  | -67.8479 |  |  | -59.1083 |  |  | -83.8877
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 34.3469 |  |  | 88.3522 |  |  | #NUM! |  |  | -488.5282 |  |  | -154.8431 |  |  | -97.8729 |  |  | -75.2124 |  |  | -67.8479 |  |  | -59.1083 |  |  | -83.8877
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 29.6169 | 83163.9155 |  | 76.7522 | 191789.1159 |  | 236393 | 469621.0958 |  | 236393 | 914702.026 |  | 236393 | 1534585.4555 |  | 236393 | 2239769.2685 |  | 236393 | 2988980.7714 |  | 236393 | 3647124.5668 |  | 236393 | 4234198.3985 |  | 236393 | 4964930.6204
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 84827.1938 | C_100 - C this iteration | iteration | 193707.0071 | C_100 - C this iteration | iteration | 474317.3068 | C_100 - C this iteration | iteration | 923849.0463 | C_100 - C this iteration | iteration | 1549931.31 | C_100 - C this iteration | iteration | 2262166.9612 | C_100 - C this iteration | iteration | 3018870.5791 | C_100 - C this iteration | iteration | 3683595.8125 | C_100 - C this iteration | iteration | 4276540.3825 | C_100 - C this iteration | iteration | 5014579.9266 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.8736 |  |  | 83.3462 |  |  | 49.1805 |  |  | -65.3741 |  |  | -347.658 |  |  | -842.5168 |  |  | -1570.8643 |  |  | -2382.891 |  |  | -3243.1479 |  |  | -4492.95
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.8736 |  |  | 23.3462 |  |  | -10.8195 |  |  | -125.3741 |  |  | -407.658 |  |  | -902.5168 |  |  | -1630.8643 |  |  | -2442.891 |  |  | -3303.1479 |  |  | -4552.95
[13 empty] | Press drop ratio this iteration |  |  | 0.32488 |  |  | 0.28011 |  |  | -0.21999 |  |  | 1.9178 |  |  | 1.1726 |  |  | 1.0712 |  |  | 1.0382 |  |  | 1.0252 |  |  | 1.0185 |  |  | 1.0134
[13 empty] | Expansion factor | 12 |  | 0.8308 |  |  | 0.85415 |  |  | 1.1156 |  |  | -0.022294 |  |  | 0.35556 |  |  | 0.37594 |  |  | 0.3493 |  |  | 0.28158 |  |  | 0.4251 |  |  | 0.10328
[13 empty] | C Non choked w/ reducers | 7 |  | 35.0663 |  |  | 89.5018 |  |  | #NUM! |  |  | 8034.3988 |  |  | -205.7598 |  |  | -125.3821 |  |  | -101.659 |  |  | -108.307 |  |  | -69.8811 |  |  | -326.9002
[13 empty] | C Choked w/ reducers | 7 |  | 31.1188 |  |  | 75.8148 |  |  | 316.8306 |  |  | -470.2794 |  |  | -152.5106 |  |  | -96.6953 |  |  | -74.3818 |  |  | -67.125 |  |  | -58.4904 |  |  | -83.0236
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 35.0663 |  |  | 89.5018 |  |  | #NUM! |  |  | -470.2794 |  |  | -152.5106 |  |  | -96.6953 |  |  | -74.3818 |  |  | -67.125 |  |  | -58.4904 |  |  | -83.0236
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 30.3363 | 84827.1938 |  | 77.9018 | 193707.0071 |  | 236393 | 474317.3068 |  | 236393 | 923849.0463 |  | 236393 | 1549931.31 |  | 236393 | 2262166.9612 |  | 236393 | 3018870.5791 |  | 236393 | 3683595.8125 |  | 236393 | 4276540.3825 |  | 236393 | 5014579.9266
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 86523.7377 | C_100 - C this iteration | iteration | 195644.0771 | C_100 - C this iteration | iteration | 479060.4798 | C_100 - C this iteration | iteration | 933087.5367 | C_100 - C this iteration | iteration | 1565430.6231 | C_100 - C this iteration | iteration | 2284788.6308 | C_100 - C this iteration | iteration | 3049059.2849 | C_100 - C this iteration | iteration | 3720431.7706 | C_100 - C this iteration | iteration | 4319305.7863 | C_100 - C this iteration | iteration | 5064725.7259 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.8206 |  |  | 83.2087 |  |  | 48.3564 |  |  | -68.5009 |  |  | -356.4586 |  |  | -861.2641 |  |  | -1604.2514 |  |  | -2432.5999 |  |  | -3310.1479 |  |  | -4585.071
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.8206 |  |  | 23.2087 |  |  | -11.6436 |  |  | -128.5009 |  |  | -416.4586 |  |  | -921.2641 |  |  | -1664.2514 |  |  | -2492.5999 |  |  | -3370.1479 |  |  | -4645.071
[13 empty] | Press drop ratio this iteration |  |  | 0.32448 |  |  | 0.27892 |  |  | -0.24079 |  |  | 1.8759 |  |  | 1.1683 |  |  | 1.0697 |  |  | 1.0374 |  |  | 1.0247 |  |  | 1.0181 |  |  | 1.0131
[13 empty] | Expansion factor | 12 |  | 0.83101 |  |  | 0.85477 |  |  | 1.1266 |  |  | 3.7749e-05 |  |  | 0.3579 |  |  | 0.37685 |  |  | 0.3498 |  |  | 0.28194 |  |  | 0.42532 |  |  | 0.10352
[13 empty] | C Non choked w/ reducers | 7 |  | 35.8021 |  |  | 90.6732 |  |  | #NUM! |  |  | -4624337.9127 |  |  | -201.7272 |  |  | -123.6721 |  |  | -100.434 |  |  | -107.0445 |  |  | -69.1297 |  |  | -322.8363
[13 empty] | C Choked w/ reducers | 7 |  | 31.7601 |  |  | 76.6995 |  |  | 325.453 |  |  | -453.3015 |  |  | -150.2327 |  |  | -95.5364 |  |  | -73.5622 |  |  | -66.4109 |  |  | -57.8795 |  |  | -82.1691
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 35.8021 |  |  | 90.6732 |  |  | #NUM! |  |  | -453.3015 |  |  | -150.2327 |  |  | -95.5364 |  |  | -73.5622 |  |  | -66.4109 |  |  | -57.8795 |  |  | -82.1691
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 31.0721 | 86523.7377 |  | 79.0732 | 195644.0771 |  | 236393 | 479060.4798 |  | 236393 | 933087.5367 |  | 236393 | 1565430.6231 |  | 236393 | 2284788.6308 |  | 236393 | 3049059.2849 |  | 236393 | 3720431.7706 |  | 236393 | 4319305.7863 |  | 236393 | 5064725.7259
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 88254.2125 | C_100 - C this iteration | iteration | 197600.5179 | C_100 - C this iteration | iteration | 483851.0846 | C_100 - C this iteration | iteration | 942418.4121 | C_100 - C this iteration | iteration | 1581084.9294 | C_100 - C this iteration | iteration | 2307636.5171 | C_100 - C this iteration | iteration | 3079549.8777 | C_100 - C this iteration | iteration | 3757636.0883 | C_100 - C this iteration | iteration | 4362498.8441 | C_100 - C this iteration | iteration | 5115372.9832 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.7654 |  |  | 83.0685 |  |  | 47.5156 |  |  | -71.6904 |  |  | -365.4362 |  |  | -880.3883 |  |  | -1638.3095 |  |  | -2483.3079 |  |  | -3378.4946 |  |  | -4679.0437
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.7654 |  |  | 23.0685 |  |  | -12.4844 |  |  | -131.6904 |  |  | -425.4362 |  |  | -940.3883 |  |  | -1698.3095 |  |  | -2543.3079 |  |  | -3438.4946 |  |  | -4739.0437
[13 empty] | Press drop ratio this iteration |  |  | 0.32406 |  |  | 0.2777 |  |  | -0.26274 |  |  | 1.8369 |  |  | 1.1642 |  |  | 1.0682 |  |  | 1.0366 |  |  | 1.0242 |  |  | 1.0178 |  |  | 1.0128
[13 empty] | Expansion factor | 12 |  | 0.83123 |  |  | 0.8554 |  |  | 1.1381 |  |  | 0.020811 |  |  | 0.36018 |  |  | 0.37773 |  |  | 0.35028 |  |  | 0.2823 |  |  | 0.42552 |  |  | 0.10375
[13 empty] | C Non choked w/ reducers | 7 |  | 36.5548 |  |  | 91.8672 |  |  | #NUM! |  |  | -8180.5905 |  |  | -197.8356 |  |  | -121.9966 |  |  | -99.2286 |  |  | -105.8009 |  |  | -68.3875 |  |  | -318.8413
[13 empty] | C Choked w/ reducers | 7 |  | 32.4154 |  |  | 77.5972 |  |  | 334.5238 |  |  | -437.4649 |  |  | -148.0075 |  |  | -94.3958 |  |  | -72.7532 |  |  | -65.7054 |  |  | -57.2757 |  |  | -81.324
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 36.5548 |  |  | 91.8672 |  |  | #NUM! |  |  | -437.4649 |  |  | -148.0075 |  |  | -94.3958 |  |  | -72.7532 |  |  | -65.7054 |  |  | -57.2757 |  |  | -81.324
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 31.8248 | 88254.2125 |  | 80.2672 | 197600.5179 |  | 236393 | 483851.0846 |  | 236393 | 942418.4121 |  | 236393 | 1581084.9294 |  | 236393 | 2307636.5171 |  | 236393 | 3079549.8777 |  | 236393 | 3757636.0883 |  | 236393 | 4362498.8441 |  | 236393 | 5115372.9832
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 90019.2967 | C_100 - C this iteration | iteration | 199576.5231 | C_100 - C this iteration | iteration | 488689.5955 | C_100 - C this iteration | iteration | 951842.5962 | C_100 - C this iteration | iteration | 1596895.7787 | C_100 - C this iteration | iteration | 2330712.8822 | C_100 - C this iteration | iteration | 3110345.3765 | C_100 - C this iteration | iteration | 3795212.4492 | C_100 - C this iteration | iteration | 4406123.8326 | C_100 - C this iteration | iteration | 5166526.713 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.7081 |  |  | 82.9254 |  |  | 46.6579 |  |  | -74.9441 |  |  | -374.5942 |  |  | -899.8968 |  |  | -1673.0523 |  |  | -2535.0351 |  |  | -3448.215 |  |  | -4774.9051
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.7081 |  |  | 22.9254 |  |  | -13.3421 |  |  | -134.9441 |  |  | -434.5942 |  |  | -959.8968 |  |  | -1733.0523 |  |  | -2595.0351 |  |  | -3508.215 |  |  | -4834.9051
[13 empty] | Press drop ratio this iteration |  |  | 0.32362 |  |  | 0.27646 |  |  | -0.28595 |  |  | 1.8006 |  |  | 1.1602 |  |  | 1.0667 |  |  | 1.0359 |  |  | 1.0237 |  |  | 1.0174 |  |  | 1.0126
[13 empty] | Expansion factor | 12 |  | 0.83145 |  |  | 0.85605 |  |  | 1.1503 |  |  | 0.04018 |  |  | 0.36238 |  |  | 0.37859 |  |  | 0.35076 |  |  | 0.28264 |  |  | 0.42572 |  |  | 0.10398
[13 empty] | C Non choked w/ reducers | 7 |  | 37.325 |  |  | 93.0846 |  |  | #NUM! |  |  | -4134.7738 |  |  | -194.0772 |  |  | -120.3546 |  |  | -98.0422 |  |  | -104.5757 |  |  | -67.6546 |  |  | -314.9132
[13 empty] | C Choked w/ reducers | 7 |  | 33.0851 |  |  | 78.5084 |  |  | 344.0797 |  |  | -422.6571 |  |  | -145.8329 |  |  | -93.2729 |  |  | -71.9549 |  |  | -65.0083 |  |  | -56.6788 |  |  | -80.4883
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 37.325 |  |  | 93.0846 |  |  | #NUM! |  |  | -422.6571 |  |  | -145.8329 |  |  | -93.2729 |  |  | -71.9549 |  |  | -65.0083 |  |  | -56.6788 |  |  | -80.4883
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 32.595 | 90019.2967 |  | 81.4846 | 199576.5231 |  | 236393 | 488689.5955 |  | 236393 | 951842.5962 |  | 236393 | 1596895.7787 |  | 236393 | 2330712.8822 |  | 236393 | 3110345.3765 |  | 236393 | 3795212.4492 |  | 236393 | 4406123.8326 |  | 236393 | 5166526.713
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 91819.6827 | C_100 - C this iteration | iteration | 201572.2883 | C_100 - C this iteration | iteration | 493576.4914 | C_100 - C this iteration | iteration | 961361.0222 | C_100 - C this iteration | iteration | 1612864.7365 | C_100 - C this iteration | iteration | 2354020.0111 | C_100 - C this iteration | iteration | 3141448.8303 | C_100 - C this iteration | iteration | 3833164.5737 | C_100 - C this iteration | iteration | 4450185.0709 | C_100 - C this iteration | iteration | 5218191.9801 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.6484 |  |  | 82.7795 |  |  | 45.783 |  |  | -78.2632 |  |  | -383.9362 |  |  | -919.7974 |  |  | -1708.4934 |  |  | -2587.802 |  |  | -3519.3369 |  |  | -4872.6935
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.6484 |  |  | 22.7795 |  |  | -14.217 |  |  | -138.2632 |  |  | -443.9362 |  |  | -979.7974 |  |  | -1768.4934 |  |  | -2647.802 |  |  | -3579.3369 |  |  | -4932.6935
[13 empty] | Press drop ratio this iteration |  |  | 0.32317 |  |  | 0.27518 |  |  | -0.31053 |  |  | 1.7666 |  |  | 1.1563 |  |  | 1.0652 |  |  | 1.0351 |  |  | 1.0232 |  |  | 1.017 |  |  | 1.0123
[13 empty] | Expansion factor | 12 |  | 0.83169 |  |  | 0.85672 |  |  | 1.1632 |  |  | 0.058278 |  |  | 0.36452 |  |  | 0.37943 |  |  | 0.35123 |  |  | 0.28298 |  |  | 0.42592 |  |  | 0.1042
[13 empty] | C Non choked w/ reducers | 7 |  | 38.1131 |  |  | 94.326 |  |  | #NUM! |  |  | -2783.4614 |  |  | -190.4447 |  |  | -118.745 |  |  | -96.8746 |  |  | -103.3685 |  |  | -66.9306 |  |  | -311.0505
[13 empty] | C Choked w/ reducers | 7 |  | 33.7695 |  |  | 79.4333 |  |  | 354.1615 |  |  | -408.7798 |  |  | -143.7073 |  |  | -92.1674 |  |  | -71.1668 |  |  | -64.3196 |  |  | -56.0887 |  |  | -79.6617
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 38.1131 |  |  | 94.326 |  |  | #NUM! |  |  | -408.7798 |  |  | -143.7073 |  |  | -92.1674 |  |  | -71.1668 |  |  | -64.3196 |  |  | -56.0887 |  |  | -79.6617
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 33.3831 | 91819.6827 |  | 82.726 | 201572.2883 |  | 236393 | 493576.4914 |  | 236393 | 961361.0222 |  | 236393 | 1612864.7365 |  | 236393 | 2354020.0111 |  | 236393 | 3141448.8303 |  | 236393 | 3833164.5737 |  | 236393 | 4450185.0709 |  | 236393 | 5218191.9801
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 93656.0763 | C_100 - C this iteration | iteration | 203588.0112 | C_100 - C this iteration | iteration | 498512.2564 | C_100 - C this iteration | iteration | 970974.6324 | C_100 - C this iteration | iteration | 1628993.3838 | C_100 - C this iteration | iteration | 2377560.2112 | C_100 - C this iteration | iteration | 3172863.3186 | C_100 - C this iteration | iteration | 3871496.2195 | C_100 - C this iteration | iteration | 4494686.9216 | C_100 - C this iteration | iteration | 5270373.8999 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.5863 |  |  | 82.6307 |  |  | 44.8906 |  |  | -81.649 |  |  | -393.4661 |  |  | -940.0981 |  |  | -1744.6468 |  |  | -2641.6295 |  |  | -3591.8883 |  |  | -4972.4473
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.5863 |  |  | 22.6307 |  |  | -15.1094 |  |  | -141.649 |  |  | -453.4661 |  |  | -1000.0981 |  |  | -1804.6468 |  |  | -2701.6295 |  |  | -3651.8883 |  |  | -5032.4473
[13 empty] | Press drop ratio this iteration |  |  | 0.32269 |  |  | 0.27388 |  |  | -0.33658 |  |  | 1.7349 |  |  | 1.1525 |  |  | 1.0638 |  |  | 1.0344 |  |  | 1.0227 |  |  | 1.0167 |  |  | 1.0121
[13 empty] | Expansion factor | 12 |  | 0.83194 |  |  | 0.8574 |  |  | 1.1769 |  |  | 0.075225 |  |  | 0.3666 |  |  | 0.38025 |  |  | 0.35168 |  |  | 0.28331 |  |  | 0.42612 |  |  | 0.10442
[13 empty] | C Non choked w/ reducers | 7 |  | 38.9196 |  |  | 95.5922 |  |  | #NUM! |  |  | -2106.701 |  |  | -186.9316 |  |  | -117.1669 |  |  | -95.7252 |  |  | -102.1789 |  |  | -66.2155 |  |  | -307.2516
[13 empty] | C Choked w/ reducers | 7 |  | 34.469 |  |  | 80.3721 |  |  | 364.8147 |  |  | -395.7469 |  |  | -141.6289 |  |  | -91.0789 |  |  | -70.389 |  |  | -63.639 |  |  | -55.5054 |  |  | -78.8442
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 38.9196 |  |  | 95.5922 |  |  | #NUM! |  |  | -395.7469 |  |  | -141.6289 |  |  | -91.0789 |  |  | -70.389 |  |  | -63.639 |  |  | -55.5054 |  |  | -78.8442
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 34.1896 | 93656.0763 |  | 83.9922 | 203588.0112 |  | 236393 | 498512.2564 |  | 236393 | 970974.6324 |  | 236393 | 1628993.3838 |  | 236393 | 2377560.2112 |  | 236393 | 3172863.3186 |  | 236393 | 3871496.2195 |  | 236393 | 4494686.9216 |  | 236393 | 5270373.8999
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 95529.1978 | C_100 - C this iteration | iteration | 205623.8913 | C_100 - C this iteration | iteration | 503497.3789 | C_100 - C this iteration | iteration | 980684.3787 | C_100 - C this iteration | iteration | 1645283.3177 | C_100 - C this iteration | iteration | 2401335.8133 | C_100 - C this iteration | iteration | 3204591.9518 | C_100 - C this iteration | iteration | 3910211.1817 | C_100 - C this iteration | iteration | 4539633.7908 | C_100 - C this iteration | iteration | 5323077.6389 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.5218 |  |  | 82.4788 |  |  | 43.9801 |  |  | -85.1029 |  |  | -403.1874 |  |  | -960.8068 |  |  | -1781.5269 |  |  | -2696.539 |  |  | -3665.8979 |  |  | -5074.2062
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.5218 |  |  | 22.4788 |  |  | -16.0199 |  |  | -145.1029 |  |  | -463.1874 |  |  | -1020.8068 |  |  | -1841.5269 |  |  | -2756.539 |  |  | -3725.8979 |  |  | -5134.2062
[13 empty] | Press drop ratio this iteration |  |  | 0.3222 |  |  | 0.27254 |  |  | -0.36425 |  |  | 1.705 |  |  | 1.1488 |  |  | 1.0624 |  |  | 1.0337 |  |  | 1.0223 |  |  | 1.0164 |  |  | 1.0118
[13 empty] | Expansion factor | 12 |  | 0.8322 |  |  | 0.85809 |  |  | 1.1915 |  |  | 0.091123 |  |  | 0.36862 |  |  | 0.38105 |  |  | 0.35213 |  |  | 0.28363 |  |  | 0.42631 |  |  | 0.10464
[13 empty] | C Non choked w/ reducers | 7 |  | 39.7451 |  |  | 96.8842 |  |  | #NUM! |  |  | -1699.9332 |  |  | -183.5317 |  |  | -115.6192 |  |  | -94.5935 |  |  | -101.0065 |  |  | -65.509 |  |  | -303.5148
[13 empty] | C Choked w/ reducers | 7 |  | 35.1841 |  |  | 81.3253 |  |  | 376.0902 |  |  | -383.4825 |  |  | -139.5962 |  |  | -90.007 |  |  | -69.6212 |  |  | -62.9666 |  |  | -54.9286 |  |  | -78.0357
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 39.7451 |  |  | 96.8842 |  |  | #NUM! |  |  | -383.4825 |  |  | -139.5962 |  |  | -90.007 |  |  | -69.6212 |  |  | -62.9666 |  |  | -54.9286 |  |  | -78.0357
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 35.0151 | 95529.1978 |  | 85.2842 | 205623.8913 |  | 236393 | 503497.3789 |  | 236393 | 980684.3787 |  | 236393 | 1645283.3177 |  | 236393 | 2401335.8133 |  | 236393 | 3204591.9518 |  | 236393 | 3910211.1817 |  | 236393 | 4539633.7908 |  | 236393 | 5323077.6389
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 97439.7818 | C_100 - C this iteration | iteration | 207680.1302 | C_100 - C this iteration | iteration | 508532.3527 | C_100 - C this iteration | iteration | 990491.2225 | C_100 - C this iteration | iteration | 1661736.1508 | C_100 - C this iteration | iteration | 2425349.1714 | C_100 - C this iteration | iteration | 3236637.8713 | C_100 - C this iteration | iteration | 3949313.2935 | C_100 - C this iteration | iteration | 4585030.1288 | C_100 - C this iteration | iteration | 5376308.4153 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.4546 |  |  | 82.3239 |  |  | 43.0514 |  |  | -88.6262 |  |  | -413.1042 |  |  | -981.9317 |  |  | -1819.1483 |  |  | -2752.5522 |  |  | -3741.3952 |  |  | -5178.0105
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.4546 |  |  | 22.3239 |  |  | -16.9486 |  |  | -148.6262 |  |  | -473.1042 |  |  | -1041.9317 |  |  | -1879.1483 |  |  | -2812.5522 |  |  | -3801.3952 |  |  | -5238.0105
[13 empty] | Press drop ratio this iteration |  |  | 0.32169 |  |  | 0.27117 |  |  | -0.39368 |  |  | 1.677 |  |  | 1.1452 |  |  | 1.0611 |  |  | 1.033 |  |  | 1.0218 |  |  | 1.016 |  |  | 1.0116
[13 empty] | Expansion factor | 12 |  | 0.83246 |  |  | 0.8588 |  |  | 1.2069 |  |  | 0.10606 |  |  | 0.37059 |  |  | 0.38183 |  |  | 0.35256 |  |  | 0.28395 |  |  | 0.42649 |  |  | 0.10485
[13 empty] | C Non choked w/ reducers | 7 |  | 40.5902 |  |  | 98.2027 |  |  | #NUM! |  |  | -1428.2242 |  |  | -180.2392 |  |  | -114.1011 |  |  | -93.4793 |  |  | -99.851 |  |  | -64.8112 |  |  | -299.8386
[13 empty] | C Choked w/ reducers | 7 |  | 35.915 |  |  | 82.2931 |  |  | 388.0454 |  |  | -371.9197 |  |  | -137.6076 |  |  | -88.9513 |  |  | -68.8632 |  |  | -62.3021 |  |  | -54.3585 |  |  | -77.236
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 40.5902 |  |  | 98.2027 |  |  | #NUM! |  |  | -371.9197 |  |  | -137.6076 |  |  | -88.9513 |  |  | -68.8632 |  |  | -62.3021 |  |  | -54.3585 |  |  | -77.236
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 35.8602 | 97439.7818 |  | 86.6027 | 207680.1302 |  | 236393 | 508532.3527 |  | 236393 | 990491.2225 |  | 236393 | 1661736.1508 |  | 236393 | 2425349.1714 |  | 236393 | 3236637.8713 |  | 236393 | 3949313.2935 |  | 236393 | 4585030.1288 |  | 236393 | 5376308.4153
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 99388.5774 | C_100 - C this iteration | iteration | 209756.9315 | C_100 - C this iteration | iteration | 513617.6762 | C_100 - C this iteration | iteration | 1000396.1347 | C_100 - C this iteration | iteration | 1678353.5123 | C_100 - C this iteration | iteration | 2449602.6631 | C_100 - C this iteration | iteration | 3269004.25 | C_100 - C this iteration | iteration | 3988806.4264 | C_100 - C this iteration | iteration | 4630880.43 | C_100 - C this iteration | iteration | 5430071.4995 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.3847 |  |  | 82.1659 |  |  | 42.104 |  |  | -92.2203 |  |  | -423.2203 |  |  | -1003.4813 |  |  | -1857.5259 |  |  | -2809.6912 |  |  | -3818.41 |  |  | -5283.9012
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.3847 |  |  | 22.1659 |  |  | -17.896 |  |  | -152.2203 |  |  | -483.2203 |  |  | -1063.4813 |  |  | -1917.5259 |  |  | -2869.6912 |  |  | -3878.41 |  |  | -5343.9012
[13 empty] | Press drop ratio this iteration |  |  | 0.32115 |  |  | 0.26977 |  |  | -0.42504 |  |  | 1.6506 |  |  | 1.1418 |  |  | 1.0598 |  |  | 1.0323 |  |  | 1.0214 |  |  | 1.0157 |  |  | 1.0114
[13 empty] | Expansion factor | 12 |  | 0.83274 |  |  | 0.85953 |  |  | 1.2234 |  |  | 0.12013 |  |  | 0.3725 |  |  | 0.3826 |  |  | 0.35299 |  |  | 0.28426 |  |  | 0.42668 |  |  | 0.10505
[13 empty] | C Non choked w/ reducers | 7 |  | 41.4554 |  |  | 99.5487 |  |  | #NUM! |  |  | -1233.7244 |  |  | -177.0487 |  |  | -112.6117 |  |  | -92.382 |  |  | -98.7121 |  |  | -64.1218 |  |  | -296.2215
[13 empty] | C Choked w/ reducers | 7 |  | 36.6623 |  |  | 83.2759 |  |  | 400.7446 |  |  | -360.9991 |  |  | -135.6616 |  |  | -87.9115 |  |  | -68.1148 |  |  | -61.6454 |  |  | -53.7947 |  |  | -76.4451
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 41.4554 |  |  | 99.5487 |  |  | #NUM! |  |  | -360.9991 |  |  | -135.6616 |  |  | -87.9115 |  |  | -68.1148 |  |  | -61.6454 |  |  | -53.7947 |  |  | -76.4451
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 36.7254 | 99388.5774 |  | 87.9487 | 209756.9315 |  | 236393 | 513617.6762 |  | 236393 | 1000396.1347 |  | 236393 | 1678353.5123 |  | 236393 | 2449602.6631 |  | 236393 | 3269004.25 |  | 236393 | 3988806.4264 |  | 236393 | 4630880.43 |  | 236393 | 5430071.4995
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 101376.349 | C_100 - C this iteration | iteration | 211854.5008 | C_100 - C this iteration | iteration | 518753.853 | C_100 - C this iteration | iteration | 1010400.0961 | C_100 - C this iteration | iteration | 1695137.0475 | C_100 - C this iteration | iteration | 2474098.6898 | C_100 - C this iteration | iteration | 3301694.2925 | C_100 - C this iteration | iteration | 4028694.4907 | C_100 - C this iteration | iteration | 4677189.2343 | C_100 - C this iteration | iteration | 5484372.2145 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.3119 |  |  | 82.0047 |  |  | 41.1376 |  |  | -95.8866 |  |  | -433.5398 |  |  | -1025.4639 |  |  | -1896.6749 |  |  | -2867.9787 |  |  | -3896.9727 |  |  | -5391.9204
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.3119 |  |  | 22.0047 |  |  | -18.8624 |  |  | -155.8866 |  |  | -493.5398 |  |  | -1085.4639 |  |  | -1956.6749 |  |  | -2927.9787 |  |  | -3956.9727 |  |  | -5451.9204
[13 empty] | Press drop ratio this iteration |  |  | 0.32059 |  |  | 0.26834 |  |  | -0.45852 |  |  | 1.6257 |  |  | 1.1384 |  |  | 1.0585 |  |  | 1.0316 |  |  | 1.0209 |  |  | 1.0154 |  |  | 1.0111
[13 empty] | Expansion factor | 12 |  | 0.83303 |  |  | 0.86028 |  |  | 1.241 |  |  | 0.13339 |  |  | 0.37435 |  |  | 0.38335 |  |  | 0.35341 |  |  | 0.28457 |  |  | 0.42686 |  |  | 0.10525
[13 empty] | C Non choked w/ reducers | 7 |  | 42.3415 |  |  | 100.9231 |  |  | #NUM! |  |  | -1087.5017 |  |  | -173.9552 |  |  | -111.15 |  |  | -91.3014 |  |  | -97.5893 |  |  | -63.4407 |  |  | -292.6622
[13 empty] | C Choked w/ reducers | 7 |  | 37.4264 |  |  | 84.2739 |  |  | 414.2607 |  |  | -350.6678 |  |  | -133.7568 |  |  | -86.8873 |  |  | -67.376 |  |  | -60.9965 |  |  | -53.2373 |  |  | -75.6628
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 42.3415 |  |  | 100.9231 |  |  | #NUM! |  |  | -350.6678 |  |  | -133.7568 |  |  | -86.8873 |  |  | -67.376 |  |  | -60.9965 |  |  | -53.2373 |  |  | -75.6628
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 37.6115 | 101376.349 |  | 89.3231 | 211854.5008 |  | 236393 | 518753.853 |  | 236393 | 1010400.0961 |  | 236393 | 1695137.0475 |  | 236393 | 2474098.6898 |  | 236393 | 3301694.2925 |  | 236393 | 4028694.4907 |  | 236393 | 4677189.2343 |  | 236393 | 5484372.2145
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 103403.876 | C_100 - C this iteration | iteration | 213973.0458 | C_100 - C this iteration | iteration | 523941.3915 | C_100 - C this iteration | iteration | 1020504.0971 | C_100 - C this iteration | iteration | 1712088.4179 | C_100 - C this iteration | iteration | 2498839.6767 | C_100 - C this iteration | iteration | 3334711.2354 | C_100 - C this iteration | iteration | 4068981.4356 | C_100 - C this iteration | iteration | 4723961.1267 | C_100 - C this iteration | iteration | 5539215.9366 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.2362 |  |  | 81.8403 |  |  | 40.1518 |  |  | -99.6267 |  |  | -444.0667 |  |  | -1047.8885 |  |  | -1936.6108 |  |  | -2927.4378 |  |  | -3977.1146 |  |  | -5502.1107
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.2362 |  |  | 21.8403 |  |  | -19.8482 |  |  | -159.6267 |  |  | -504.0667 |  |  | -1107.8885 |  |  | -1996.6108 |  |  | -2987.4378 |  |  | -4037.1146 |  |  | -5562.1107
[13 empty] | Press drop ratio this iteration |  |  | 0.32001 |  |  | 0.26687 |  |  | -0.49433 |  |  | 1.6022 |  |  | 1.1351 |  |  | 1.0573 |  |  | 1.031 |  |  | 1.0205 |  |  | 1.0151 |  |  | 1.0109
[13 empty] | Expansion factor | 12 |  | 0.83334 |  |  | 0.86105 |  |  | 1.2598 |  |  | 0.14591 |  |  | 0.37615 |  |  | 0.38408 |  |  | 0.35382 |  |  | 0.28486 |  |  | 0.42703 |  |  | 0.10545
[13 empty] | C Non choked w/ reducers | 7 |  | 43.2489 |  |  | 102.327 |  |  | #NUM! |  |  | -973.4792 |  |  | -170.9541 |  |  | -109.7154 |  |  | -90.237 |  |  | -96.4824 |  |  | -62.7678 |  |  | -289.1593
[13 empty] | C Choked w/ reducers | 7 |  | 38.2076 |  |  | 85.2877 |  |  | 428.6764 |  |  | -340.8786 |  |  | -131.8918 |  |  | -85.8782 |  |  | -66.6464 |  |  | -60.3552 |  |  | -52.6862 |  |  | -74.8889
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 43.2489 |  |  | 102.327 |  |  | #NUM! |  |  | -340.8786 |  |  | -131.8918 |  |  | -85.8782 |  |  | -66.6464 |  |  | -60.3552 |  |  | -52.6862 |  |  | -74.8889
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 38.5189 | 103403.876 |  | 90.727 | 213973.0458 |  | 236393 | 523941.3915 |  | 236393 | 1020504.0971 |  | 236393 | 1712088.4179 |  | 236393 | 2498839.6767 |  | 236393 | 3334711.2354 |  | 236393 | 4068981.4356 |  | 236393 | 4723961.1267 |  | 236393 | 5539215.9366
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 105471.9535 | C_100 - C this iteration | iteration | 216112.7763 | C_100 - C this iteration | iteration | 529180.8054 | C_100 - C this iteration | iteration | 1030709.138 | C_100 - C this iteration | iteration | 1729209.3021 | C_100 - C this iteration | iteration | 2523828.0734 | C_100 - C this iteration | iteration | 3368058.3478 | C_100 - C this iteration | iteration | 4109671.2499 | C_100 - C this iteration | iteration | 4771200.7379 | C_100 - C this iteration | iteration | 5594608.096 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.1575 |  |  | 81.6726 |  |  | 39.1461 |  |  | -103.4419 |  |  | -454.8051 |  |  | -1070.7638 |  |  | -1977.3494 |  |  | -2988.092 |  |  | -4058.8673 |  |  | -5614.5158
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.1575 |  |  | 21.6726 |  |  | -20.8539 |  |  | -163.4419 |  |  | -514.8051 |  |  | -1130.7638 |  |  | -2037.3494 |  |  | -3048.092 |  |  | -4118.8673 |  |  | -5674.5158
[13 empty] | Press drop ratio this iteration |  |  | 0.3194 |  |  | 0.26536 |  |  | -0.53272 |  |  | 1.58 |  |  | 1.1319 |  |  | 1.056 |  |  | 1.0303 |  |  | 1.0201 |  |  | 1.0148 |  |  | 1.0107
[13 empty] | Expansion factor | 12 |  | 0.83365 |  |  | 0.86183 |  |  | 1.28 |  |  | 0.15775 |  |  | 0.37791 |  |  | 0.38479 |  |  | 0.35422 |  |  | 0.28516 |  |  | 0.4272 |  |  | 0.10564
[13 empty] | C Non choked w/ reducers | 7 |  | 44.1785 |  |  | 103.7614 |  |  | #NUM! |  |  | -882.009 |  |  | -168.041 |  |  | -108.3071 |  |  | -89.1884 |  |  | -95.391 |  |  | -62.103 |  |  | -285.7113
[13 empty] | C Choked w/ reducers | 7 |  | 39.0066 |  |  | 86.3175 |  |  | 444.0861 |  |  | -331.5892 |  |  | -130.0655 |  |  | -84.8839 |  |  | -65.9261 |  |  | -59.7214 |  |  | -52.1412 |  |  | -74.1235
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 44.1785 |  |  | 103.7614 |  |  | #NUM! |  |  | -331.5892 |  |  | -130.0655 |  |  | -84.8839 |  |  | -65.9261 |  |  | -59.7214 |  |  | -52.1412 |  |  | -74.1235
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 39.4485 | 105471.9535 |  | 92.1614 | 216112.7763 |  | 236393 | 529180.8054 |  | 236393 | 1030709.138 |  | 236393 | 1729209.3021 |  | 236393 | 2523828.0734 |  | 236393 | 3368058.3478 |  | 236393 | 4109671.2499 |  | 236393 | 4771200.7379 |  | 236393 | 5594608.096
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 107581.3926 | C_100 - C this iteration | iteration | 218273.9041 | C_100 - C this iteration | iteration | 534472.6135 | C_100 - C this iteration | iteration | 1041016.2294 | C_100 - C this iteration | iteration | 1746501.3951 | C_100 - C this iteration | iteration | 2549066.3542 | C_100 - C this iteration | iteration | 3401738.9313 | C_100 - C this iteration | iteration | 4150767.9624 | C_100 - C this iteration | iteration | 4818912.7453 | C_100 - C this iteration | iteration | 5650554.1769 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.0756 |  |  | 81.5015 |  |  | 38.1202 |  |  | -107.3338 |  |  | -465.7594 |  |  | -1094.0988 |  |  | -2018.9068 |  |  | -3049.9654 |  |  | -4142.2633 |  |  | -5729.1803
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 28.0756 |  |  | 21.5015 |  |  | -21.8798 |  |  | -167.3338 |  |  | -525.7594 |  |  | -1154.0988 |  |  | -2078.9068 |  |  | -3109.9654 |  |  | -4202.2633 |  |  | -5789.1803
[13 empty] | Press drop ratio this iteration |  |  | 0.31877 |  |  | 0.26382 |  |  | -0.57397 |  |  | 1.559 |  |  | 1.1288 |  |  | 1.0548 |  |  | 1.0297 |  |  | 1.0197 |  |  | 1.0145 |  |  | 1.0105
[13 empty] | Expansion factor | 12 |  | 0.83398 |  |  | 0.86263 |  |  | 1.3017 |  |  | 0.16896 |  |  | 0.37961 |  |  | 0.38548 |  |  | 0.35461 |  |  | 0.28544 |  |  | 0.42737 |  |  | 0.10583
[13 empty] | C Non choked w/ reducers | 7 |  | 45.1309 |  |  | 105.2275 |  |  | #NUM! |  |  | -806.9502 |  |  | -165.2118 |  |  | -106.9242 |  |  | -88.1554 |  |  | -94.3148 |  |  | -61.446 |  |  | -282.3171
[13 empty] | C Choked w/ reducers | 7 |  | 39.8237 |  |  | 87.3637 |  |  | 460.5976 |  |  | -322.7615 |  |  | -128.2765 |  |  | -83.9043 |  |  | -65.2147 |  |  | -59.0949 |  |  | -51.6024 |  |  | -73.3664
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 45.1309 |  |  | 105.2275 |  |  | #NUM! |  |  | -322.7615 |  |  | -128.2765 |  |  | -83.9043 |  |  | -65.2147 |  |  | -59.0949 |  |  | -51.6024 |  |  | -73.3664
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 40.4009 | 107581.3926 |  | 93.6275 | 218273.9041 |  | 236393 | 534472.6135 |  | 236393 | 1041016.2294 |  | 236393 | 1746501.3951 |  | 236393 | 2549066.3542 |  | 236393 | 3401738.9313 |  | 236393 | 4150767.9624 |  | 236393 | 4818912.7453 |  | 236393 | 5650554.1769
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 109733.0204 | C_100 - C this iteration | iteration | 220456.6431 | C_100 - C this iteration | iteration | 539817.3396 | C_100 - C this iteration | iteration | 1051426.3917 | C_100 - C this iteration | iteration | 1763966.4091 | C_100 - C this iteration | iteration | 2574557.0177 | C_100 - C this iteration | iteration | 3435756.3206 | C_100 - C this iteration | iteration | 4192275.6421 | C_100 - C this iteration | iteration | 4867101.8728 | C_100 - C this iteration | iteration | 5707059.7187 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.9904 |  |  | 81.327 |  |  | 37.0737 |  |  | -111.3039 |  |  | -476.9339 |  |  | -1117.9029 |  |  | -2061.2996 |  |  | -3113.0824 |  |  | -4227.3355 |  |  | -5846.1496
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 27.9904 |  |  | 21.327 |  |  | -22.9263 |  |  | -171.3039 |  |  | -536.9339 |  |  | -1177.9029 |  |  | -2121.2996 |  |  | -3173.0824 |  |  | -4287.3355 |  |  | -5906.1496
[13 empty] | Press drop ratio this iteration |  |  | 0.31811 |  |  | 0.26224 |  |  | -0.6184 |  |  | 1.5391 |  |  | 1.1258 |  |  | 1.0537 |  |  | 1.0291 |  |  | 1.0193 |  |  | 1.0142 |  |  | 1.0103
[13 empty] | Expansion factor | 12 |  | 0.83433 |  |  | 0.86346 |  |  | 1.3251 |  |  | 0.17959 |  |  | 0.38127 |  |  | 0.38616 |  |  | 0.35499 |  |  | 0.28572 |  |  | 0.42753 |  |  | 0.10602
[13 empty] | C Non choked w/ reducers | 7 |  | 46.1068 |  |  | 106.7265 |  |  | #NUM! |  |  | -744.2081 |  |  | -162.4627 |  |  | -105.5662 |  |  | -87.1376 |  |  | -93.2536 |  |  | -60.7969 |  |  | -278.9754
[13 empty] | C Choked w/ reducers | 7 |  | 40.6595 |  |  | 88.4267 |  |  | 478.3352 |  |  | -314.3613 |  |  | -126.5237 |  |  | -82.9388 |  |  | -64.5123 |  |  | -58.4757 |  |  | -51.0696 |  |  | -72.6175
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 46.1068 |  |  | 106.7265 |  |  | #NUM! |  |  | -314.3613 |  |  | -126.5237 |  |  | -82.9388 |  |  | -64.5123 |  |  | -58.4757 |  |  | -51.0696 |  |  | -72.6175
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 41.3768 | 109733.0204 |  | 95.1265 | 220456.6431 |  | 236393 | 539817.3396 |  | 236393 | 1051426.3917 |  | 236393 | 1763966.4091 |  | 236393 | 2574557.0177 |  | 236393 | 3435756.3206 |  | 236393 | 4192275.6421 |  | 236393 | 4867101.8728 |  | 236393 | 5707059.7187
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 111927.6808 | C_100 - C this iteration | iteration | 222661.2095 | C_100 - C this iteration | iteration | 545215.513 | C_100 - C this iteration | iteration | 1061940.6556 | C_100 - C this iteration | iteration | 1781606.0732 | C_100 - C this iteration | iteration | 2600302.5879 | C_100 - C this iteration | iteration | 3470113.8838 | C_100 - C this iteration | iteration | 4234198.3985 | C_100 - C this iteration | iteration | 4915772.8915 | C_100 - C this iteration | iteration | 5764130.3159 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.9017 |  |  | 81.1489 |  |  | 36.0062 |  |  | -115.3539 |  |  | -488.333 |  |  | -1142.1855 |  |  | -2104.5444 |  |  | -3177.4681 |  |  | -4314.1176 |  |  | -5965.4699
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 27.9017 |  |  | 21.1489 |  |  | -23.9938 |  |  | -175.3539 |  |  | -548.333 |  |  | -1202.1855 |  |  | -2164.5444 |  |  | -3237.4681 |  |  | -4374.1176 |  |  | -6025.4699
[13 empty] | Press drop ratio this iteration |  |  | 0.31742 |  |  | 0.26062 |  |  | -0.66638 |  |  | 1.5201 |  |  | 1.1229 |  |  | 1.0525 |  |  | 1.0285 |  |  | 1.0189 |  |  | 1.0139 |  |  | 1.0101
[13 empty] | Expansion factor | 12 |  | 0.83469 |  |  | 0.8643 |  |  | 1.3503 |  |  | 0.18968 |  |  | 0.38288 |  |  | 0.38683 |  |  | 0.35537 |  |  | 0.28599 |  |  | 0.4277 |  |  | 0.1062
[13 empty] | C Non choked w/ reducers | 7 |  | 47.1071 |  |  | 108.2595 |  |  | #NUM! |  |  | -690.9474 |  |  | -159.7901 |  |  | -104.2322 |  |  | -86.1346 |  |  | -92.207 |  |  | -60.1554 |  |  | -275.6851
[13 empty] | C Choked w/ reducers | 7 |  | 41.5145 |  |  | 89.5069 |  |  | 497.4424 |  |  | -306.3577 |  |  | -124.806 |  |  | -81.9873 |  |  | -63.8185 |  |  | -57.8638 |  |  | -50.5427 |  |  | -71.8767
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 47.1071 |  |  | 108.2595 |  |  | #NUM! |  |  | -306.3577 |  |  | -124.806 |  |  | -81.9873 |  |  | -63.8185 |  |  | -57.8638 |  |  | -50.5427 |  |  | -71.8767
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 42.3771 | 111927.6808 |  | 96.6595 | 222661.2095 |  | 236393 | 545215.513 |  | 236393 | 1061940.6556 |  | 236393 | 1781606.0732 |  | 236393 | 2600302.5879 |  | 236393 | 3470113.8838 |  | 236393 | 4234198.3985 |  | 236393 | 4915772.8915 |  | 236393 | 5764130.3159
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 114166.2344 | C_100 - C this iteration | iteration | 224887.8216 | C_100 - C this iteration | iteration | 550667.6682 | C_100 - C this iteration | iteration | 1072560.0622 | C_100 - C this iteration | iteration | 1799422.1339 | C_100 - C this iteration | iteration | 2626305.6138 | C_100 - C this iteration | iteration | 3504815.0226 | C_100 - C this iteration | iteration | 4276540.3825 | C_100 - C this iteration | iteration | 4964930.6204 | C_100 - C this iteration | iteration | 5821771.619 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.8095 |  |  | 80.9673 |  |  | 34.9172 |  |  | -119.4852 |  |  | -499.9612 |  |  | -1166.9562 |  |  | -2148.6585 |  |  | -3243.1479 |  |  | -4402.6441 |  |  | -6087.1885
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 27.8095 |  |  | 20.9673 |  |  | -25.0828 |  |  | -179.4852 |  |  | -559.9612 |  |  | -1226.9562 |  |  | -2208.6585 |  |  | -3303.1479 |  |  | -4462.6441 |  |  | -6147.1885
[13 empty] | Press drop ratio this iteration |  |  | 0.3167 |  |  | 0.25896 |  |  | -0.71835 |  |  | 1.5022 |  |  | 1.12 |  |  | 1.0514 |  |  | 1.0279 |  |  | 1.0185 |  |  | 1.0136 |  |  | 1.0099
[13 empty] | Expansion factor | 12 |  | 0.83506 |  |  | 0.86516 |  |  | 1.3776 |  |  | 0.19927 |  |  | 0.38445 |  |  | 0.38748 |  |  | 0.35573 |  |  | 0.28626 |  |  | 0.42785 |  |  | 0.10638
[13 empty] | C Non choked w/ reducers | 7 |  | 48.1327 |  |  | 109.828 |  |  | #NUM! |  |  | -645.1423 |  |  | -157.1906 |  |  | -102.9217 |  |  | -85.1462 |  |  | -91.1747 |  |  | -59.5216 |  |  | -272.4448
[13 empty] | C Choked w/ reducers | 7 |  | 42.3893 |  |  | 90.6047 |  |  | 518.0862 |  |  | -298.7227 |  |  | -123.1223 |  |  | -81.0495 |  |  | -63.1333 |  |  | -57.2588 |  |  | -50.0217 |  |  | -71.1438
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 48.1327 |  |  | 109.828 |  |  | #NUM! |  |  | -298.7227 |  |  | -123.1223 |  |  | -81.0495 |  |  | -63.1333 |  |  | -57.2588 |  |  | -50.0217 |  |  | -71.1438
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 43.4027 | 114166.2344 |  | 98.228 | 224887.8216 |  | 236393 | 550667.6682 |  | 236393 | 1072560.0622 |  | 236393 | 1799422.1339 |  | 236393 | 2626305.6138 |  | 236393 | 3504815.0226 |  | 236393 | 4276540.3825 |  | 236393 | 4964930.6204 |  | 236393 | 5821771.619
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 116449.5591 | C_100 - C this iteration | iteration | 227136.6998 | C_100 - C this iteration | iteration | 556174.3448 | C_100 - C this iteration | iteration | 1083285.6628 | C_100 - C this iteration | iteration | 1817416.3553 | C_100 - C this iteration | iteration | 2652568.6699 | C_100 - C this iteration | iteration | 3539863.1728 | C_100 - C this iteration | iteration | 4319305.7863 | C_100 - C this iteration | iteration | 5014579.9266 | C_100 - C this iteration | iteration | 5879989.3352 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.7135 |  |  | 80.782 |  |  | 33.8063 |  |  | -123.6996 |  |  | -511.8232 |  |  | -1192.2247 |  |  | -2193.6592 |  |  | -3310.1479 |  |  | -4492.95 |  |  | -6211.3537
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 27.7135 |  |  | 20.782 |  |  | -26.1937 |  |  | -183.6996 |  |  | -571.8232 |  |  | -1252.2247 |  |  | -2253.6592 |  |  | -3370.1479 |  |  | -4552.95 |  |  | -6271.3537
[13 empty] | Press drop ratio this iteration |  |  | 0.31595 |  |  | 0.25726 |  |  | -0.77482 |  |  | 1.485 |  |  | 1.1172 |  |  | 1.0503 |  |  | 1.0274 |  |  | 1.0181 |  |  | 1.0134 |  |  | 1.0097
[13 empty] | Expansion factor | 12 |  | 0.83545 |  |  | 0.86605 |  |  | 1.4073 |  |  | 0.20839 |  |  | 0.38598 |  |  | 0.38811 |  |  | 0.35609 |  |  | 0.28652 |  |  | 0.42801 |  |  | 0.10655
[13 empty] | C Non choked w/ reducers | 7 |  | 49.1842 |  |  | 111.4334 |  |  | #NUM! |  |  | -605.3069 |  |  | -154.661 |  |  | -101.634 |  |  | -84.172 |  |  | -90.1565 |  |  | -58.8951 |  |  | -269.2536
[13 empty] | C Choked w/ reducers | 7 |  | 43.2844 |  |  | 91.7207 |  |  | 540.4617 |  |  | -291.4308 |  |  | -121.4715 |  |  | -80.125 |  |  | -62.4566 |  |  | -56.6609 |  |  | -49.5064 |  |  | -70.4189
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 49.1842 |  |  | 111.4334 |  |  | #NUM! |  |  | -291.4308 |  |  | -121.4715 |  |  | -80.125 |  |  | -62.4566 |  |  | -56.6609 |  |  | -49.5064 |  |  | -70.4189
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 44.4542 | 116449.5591 |  | 99.8334 | 227136.6998 |  | 236393 | 556174.3448 |  | 236393 | 1083285.6628 |  | 236393 | 1817416.3553 |  | 236393 | 2652568.6699 |  | 236393 | 3539863.1728 |  | 236393 | 4319305.7863 |  | 236393 | 5014579.9266 |  | 236393 | 5879989.3352
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 118778.5503 | C_100 - C this iteration | iteration | 229408.0668 | C_100 - C this iteration | iteration | 561736.0883 | C_100 - C this iteration | iteration | 1094118.5194 | C_100 - C this iteration | iteration | 1835590.5188 | C_100 - C this iteration | iteration | 2679094.3566 | C_100 - C this iteration | iteration | 3575261.8046 | C_100 - C this iteration | iteration | 4362498.8441 | C_100 - C this iteration | iteration | 5064725.7259 | C_100 - C this iteration | iteration | 5938789.2286 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.6136 |  |  | 80.593 |  |  | 32.6731 |  |  | -127.9986 |  |  | -523.9235 |  |  | -1218.0011 |  |  | -2239.5645 |  |  | -3378.4946 |  |  | -4585.071 |  |  | -6338.0147
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 27.6136 |  |  | 20.593 |  |  | -27.3269 |  |  | -187.9986 |  |  | -583.9235 |  |  | -1278.0011 |  |  | -2299.5645 |  |  | -3438.4946 |  |  | -4645.071 |  |  | -6398.0147
[13 empty] | Press drop ratio this iteration |  |  | 0.31518 |  |  | 0.25552 |  |  | -0.83637 |  |  | 1.4688 |  |  | 1.1145 |  |  | 1.0493 |  |  | 1.0268 |  |  | 1.0178 |  |  | 1.0131 |  |  | 1.0095
[13 empty] | Expansion factor | 12 |  | 0.83585 |  |  | 0.86695 |  |  | 1.4396 |  |  | 0.21707 |  |  | 0.38747 |  |  | 0.38873 |  |  | 0.35645 |  |  | 0.28678 |  |  | 0.42816 |  |  | 0.10672
[13 empty] | C Non choked w/ reducers | 7 |  | 50.2627 |  |  | 113.0771 |  |  | #NUM! |  |  | -570.3265 |  |  | -152.1984 |  |  | -100.3684 |  |  | -83.2118 |  |  | -89.1521 |  |  | -58.2761 |  |  | -266.1104
[13 empty] | C Choked w/ reducers | 7 |  | 44.2004 |  |  | 92.8551 |  |  | 564.7988 |  |  | -284.459 |  |  | -119.8527 |  |  | -79.2136 |  |  | -61.7882 |  |  | -56.0698 |  |  | -48.9969 |  |  | -69.7017
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 50.2627 |  |  | 113.0771 |  |  | #NUM! |  |  | -284.459 |  |  | -119.8527 |  |  | -79.2136 |  |  | -61.7882 |  |  | -56.0698 |  |  | -48.9969 |  |  | -69.7017
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 45.5327 | 118778.5503 |  | 101.4771 | 229408.0668 |  | 236393 | 561736.0883 |  | 236393 | 1094118.5194 |  | 236393 | 1835590.5188 |  | 236393 | 2679094.3566 |  | 236393 | 3575261.8046 |  | 236393 | 4362498.8441 |  | 236393 | 5064725.7259 |  | 236393 | 5938789.2286
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 121154.1213 | C_100 - C this iteration | iteration | 231702.1475 | C_100 - C this iteration | iteration | 567353.4492 | C_100 - C this iteration | iteration | 1105059.7046 | C_100 - C this iteration | iteration | 1853946.424 | C_100 - C this iteration | iteration | 2705885.3002 | C_100 - C this iteration | iteration | 3611014.4226 | C_100 - C this iteration | iteration | 4406123.8326 | C_100 - C this iteration | iteration | 5115372.9832 | C_100 - C this iteration | iteration | 5998177.1209 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.5098 |  |  | 80.4002 |  |  | 31.5171 |  |  | -132.3841 |  |  | -536.2671 |  |  | -1244.2957 |  |  | -2286.3925 |  |  | -3448.215 |  |  | -4679.0437 |  |  | -6467.2215
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 27.5098 |  |  | 20.4002 |  |  | -28.4829 |  |  | -192.3841 |  |  | -596.2671 |  |  | -1304.2957 |  |  | -2346.3925 |  |  | -3508.215 |  |  | -4739.0437 |  |  | -6527.2215
[13 empty] | Press drop ratio this iteration |  |  | 0.31436 |  |  | 0.25373 |  |  | -0.90373 |  |  | 1.4532 |  |  | 1.1119 |  |  | 1.0482 |  |  | 1.0262 |  |  | 1.0174 |  |  | 1.0128 |  |  | 1.0093
[13 empty] | Expansion factor | 12 |  | 0.83628 |  |  | 0.86788 |  |  | 1.475 |  |  | 0.22535 |  |  | 0.38892 |  |  | 0.38934 |  |  | 0.35679 |  |  | 0.28703 |  |  | 0.42831 |  |  | 0.10689
[13 empty] | C Non choked w/ reducers | 7 |  | 51.3691 |  |  | 114.7608 |  |  | #NUM! |  |  | -539.3483 |  |  | -149.7999 |  |  | -99.1246 |  |  | -82.2653 |  |  | -88.1612 |  |  | -57.6642 |  |  | -263.014
[13 empty] | C Choked w/ reducers | 7 |  | 45.138 |  |  | 94.0086 |  |  | 591.3698 |  |  | -277.7861 |  |  | -118.2649 |  |  | -78.315 |  |  | -61.1279 |  |  | -55.4854 |  |  | -48.493 |  |  | -68.9922
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 51.3691 |  |  | 114.7608 |  |  | #NUM! |  |  | -277.7861 |  |  | -118.2649 |  |  | -78.315 |  |  | -61.1279 |  |  | -55.4854 |  |  | -48.493 |  |  | -68.9922
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 46.6391 | 121154.1213 |  | 103.1608 | 231702.1475 |  | 236393 | 567353.4492 |  | 236393 | 1105059.7046 |  | 236393 | 1853946.424 |  | 236393 | 2705885.3002 |  | 236393 | 3611014.4226 |  | 236393 | 4406123.8326 |  | 236393 | 5115372.9832 |  | 236393 | 5998177.1209
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 123577.2037 | C_100 - C this iteration | iteration | 234019.169 | C_100 - C this iteration | iteration | 573026.9837 | C_100 - C this iteration | iteration | 1116110.3017 | C_100 - C this iteration | iteration | 1872485.8882 | C_100 - C this iteration | iteration | 2732944.1532 | C_100 - C this iteration | iteration | 3647124.5668 | C_100 - C this iteration | iteration | 4450185.0709 | C_100 - C this iteration | iteration | 5166526.713 | C_100 - C this iteration | iteration | 6058158.8921 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.4017 |  |  | 80.2035 |  |  | 30.3379 |  |  | -136.8578 |  |  | -548.8588 |  |  | -1271.1187 |  |  | -2334.1617 |  |  | -3519.3369 |  |  | -4774.9051 |  |  | -6599.0254
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 27.4017 |  |  | 20.2035 |  |  | -29.6621 |  |  | -196.8578 |  |  | -608.8588 |  |  | -1331.1187 |  |  | -2394.1617 |  |  | -3579.3369 |  |  | -4834.9051 |  |  | -6659.0254
[13 empty] | Press drop ratio this iteration |  |  | 0.31351 |  |  | 0.2519 |  |  | -0.97773 |  |  | 1.4384 |  |  | 1.1093 |  |  | 1.0472 |  |  | 1.0257 |  |  | 1.017 |  |  | 1.0126 |  |  | 1.0091
[13 empty] | Expansion factor | 12 |  | 0.83672 |  |  | 0.86884 |  |  | 1.5139 |  |  | 0.23324 |  |  | 0.39033 |  |  | 0.38993 |  |  | 0.35713 |  |  | 0.28728 |  |  | 0.42845 |  |  | 0.10705
[13 empty] | C Non choked w/ reducers | 7 |  | 52.5045 |  |  | 116.486 |  |  | #NUM! |  |  | -511.7089 |  |  | -147.463 |  |  | -97.9017 |  |  | -81.3321 |  |  | -87.1836 |  |  | -57.0595 |  |  | -259.9634
[13 empty] | C Choked w/ reducers | 7 |  | 46.0976 |  |  | 95.1815 |  |  | 620.4998 |  |  | -271.3928 |  |  | -116.7073 |  |  | -77.4291 |  |  | -60.4757 |  |  | -54.9078 |  |  | -47.9946 |  |  | -68.2904
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 52.5045 |  |  | 116.486 |  |  | #NUM! |  |  | -271.3928 |  |  | -116.7073 |  |  | -77.4291 |  |  | -60.4757 |  |  | -54.9078 |  |  | -47.9946 |  |  | -68.2904
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 47.7745 | 123577.2037 |  | 104.886 | 234019.169 |  | 236393 | 573026.9837 |  | 236393 | 1116110.3017 |  | 236393 | 1872485.8882 |  | 236393 | 2732944.1532 |  | 236393 | 3647124.5668 |  | 236393 | 4450185.0709 |  | 236393 | 5166526.713 |  | 236393 | 6058158.8921
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 126048.7478 | C_100 - C this iteration | iteration | 236359.3607 | C_100 - C this iteration | iteration | 578757.2535 | C_100 - C this iteration | iteration | 1127271.4047 | C_100 - C this iteration | iteration | 1891210.7471 | C_100 - C this iteration | iteration | 2760273.5947 | C_100 - C this iteration | iteration | 3683595.8125 | C_100 - C this iteration | iteration | 4494686.9216 | C_100 - C this iteration | iteration | 5218191.9801 | C_100 - C this iteration | iteration | 6118740.481 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.2892 |  |  | 80.0029 |  |  | 29.1349 |  |  | -141.4213 |  |  | -561.7036 |  |  | -1298.4809 |  |  | -2382.891 |  |  | -3591.8883 |  |  | -4872.6935 |  |  | -6733.4785
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 27.2892 |  |  | 20.0029 |  |  | -30.8651 |  |  | -201.4213 |  |  | -621.7036 |  |  | -1358.4809 |  |  | -2442.891 |  |  | -3651.8883 |  |  | -4932.6935 |  |  | -6793.4785
[13 empty] | Press drop ratio this iteration |  |  | 0.31263 |  |  | 0.25003 |  |  | -1.0594 |  |  | 1.4243 |  |  | 1.1068 |  |  | 1.0462 |  |  | 1.0252 |  |  | 1.0167 |  |  | 1.0123 |  |  | 1.0089
[13 empty] | Expansion factor | 12 |  | 0.83718 |  |  | 0.86981 |  |  | 1.5569 |  |  | 0.24079 |  |  | 0.3917 |  |  | 0.39051 |  |  | 0.35746 |  |  | 0.28752 |  |  | 0.4286 |  |  | 0.10721
[13 empty] | C Non choked w/ reducers | 7 |  | 53.6698 |  |  | 118.2546 |  |  | #NUM! |  |  | -486.8844 |  |  | -145.185 |  |  | -96.6994 |  |  | -80.412 |  |  | -86.219 |  |  | -56.4618 |  |  | -256.9578
[13 empty] | C Choked w/ reducers | 7 |  | 47.0802 |  |  | 96.3744 |  |  | 652.5803 |  |  | -265.2615 |  |  | -115.1788 |  |  | -76.5554 |  |  | -59.8313 |  |  | -54.3367 |  |  | -47.5017 |  |  | -67.596
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 53.6698 |  |  | 118.2546 |  |  | #NUM! |  |  | -265.2615 |  |  | -115.1788 |  |  | -76.5554 |  |  | -59.8313 |  |  | -54.3367 |  |  | -47.5017 |  |  | -67.596
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 48.9398 | 126048.7478 |  | 106.6546 | 236359.3607 |  | 236393 | 578757.2535 |  | 236393 | 1127271.4047 |  | 236393 | 1891210.7471 |  | 236393 | 2760273.5947 |  | 236393 | 3683595.8125 |  | 236393 | 4494686.9216 |  | 236393 | 5218191.9801 |  | 236393 | 6118740.481
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 128569.7228 | C_100 - C this iteration | iteration | 238722.9543 | C_100 - C this iteration | iteration | 584544.826 | C_100 - C this iteration | iteration | 1138544.1187 | C_100 - C this iteration | iteration | 1910122.8546 | C_100 - C this iteration | iteration | 2787876.3306 | C_100 - C this iteration | iteration | 3720431.7706 | C_100 - C this iteration | iteration | 4539633.7908 | C_100 - C this iteration | iteration | 5270373.8999 | C_100 - C this iteration | iteration | 6179927.8858 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.1722 |  |  | 79.7982 |  |  | 27.9078 |  |  | -146.0766 |  |  | -574.8065 |  |  | -1326.3931 |  |  | -2432.5999 |  |  | -3665.8979 |  |  | -4972.4473 |  |  | -6870.6341
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 27.1722 |  |  | 19.7982 |  |  | -32.0922 |  |  | -206.0766 |  |  | -634.8065 |  |  | -1386.3931 |  |  | -2492.5999 |  |  | -3725.8979 |  |  | -5032.4473 |  |  | -6930.6341
[13 empty] | Press drop ratio this iteration |  |  | 0.31171 |  |  | 0.2481 |  |  | -1.1499 |  |  | 1.4107 |  |  | 1.1044 |  |  | 1.0452 |  |  | 1.0247 |  |  | 1.0164 |  |  | 1.0121 |  |  | 1.0087
[13 empty] | Expansion factor | 12 |  | 0.83766 |  |  | 0.87082 |  |  | 1.6045 |  |  | 0.24799 |  |  | 0.39304 |  |  | 0.39108 |  |  | 0.35778 |  |  | 0.28776 |  |  | 0.42874 |  |  | 0.10737
[13 empty] | C Non choked w/ reducers | 7 |  | 54.8662 |  |  | 120.0685 |  |  | #NUM! |  |  | -464.4553 |  |  | -142.9637 |  |  | -95.517 |  |  | -79.5047 |  |  | -85.2672 |  |  | -55.8711 |  |  | -253.996
[13 empty] | C Choked w/ reducers | 7 |  | 48.0862 |  |  | 97.5878 |  |  | 688.087 |  |  | -259.376 |  |  | -113.6788 |  |  | -75.6939 |  |  | -59.1948 |  |  | -53.7721 |  |  | -47.0143 |  |  | -66.9091
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 54.8662 |  |  | 120.0685 |  |  | #NUM! |  |  | -259.376 |  |  | -113.6788 |  |  | -75.6939 |  |  | -59.1948 |  |  | -53.7721 |  |  | -47.0143 |  |  | -66.9091
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 50.1362 | 128569.7228 |  | 108.4685 | 238722.9543 |  | 236393 | 584544.826 |  | 236393 | 1138544.1187 |  | 236393 | 1910122.8546 |  | 236393 | 2787876.3306 |  | 236393 | 3720431.7706 |  | 236393 | 4539633.7908 |  | 236393 | 5270373.8999 |  | 236393 | 6179927.8858
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 131141.1172 | C_100 - C this iteration | iteration | 241110.1838 | C_100 - C this iteration | iteration | 590390.2743 | C_100 - C this iteration | iteration | 1149929.5599 | C_100 - C this iteration | iteration | 1929224.0831 | C_100 - C this iteration | iteration | 2815755.094 | C_100 - C this iteration | iteration | 3757636.0883 | C_100 - C this iteration | iteration | 4585030.1288 | C_100 - C this iteration | iteration | 5323077.6389 | C_100 - C this iteration | iteration | 6241727.1647 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.0505 |  |  | 79.5895 |  |  | 26.6561 |  |  | -150.8255 |  |  | -588.1729 |  |  | -1354.8664 |  |  | -2483.3079 |  |  | -3741.3952 |  |  | -5074.2062 |  |  | -7010.5466
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 27.0505 |  |  | 19.5895 |  |  | -33.3439 |  |  | -210.8255 |  |  | -648.1729 |  |  | -1414.8664 |  |  | -2543.3079 |  |  | -3801.3952 |  |  | -5134.2062 |  |  | -7070.5466
[13 empty] | Press drop ratio this iteration |  |  | 0.31075 |  |  | 0.24613 |  |  | -1.2509 |  |  | 1.3978 |  |  | 1.102 |  |  | 1.0443 |  |  | 1.0242 |  |  | 1.016 |  |  | 1.0118 |  |  | 1.0086
[13 empty] | Expansion factor | 12 |  | 0.83816 |  |  | 0.87184 |  |  | 1.6575 |  |  | 0.25489 |  |  | 0.39435 |  |  | 0.39163 |  |  | 0.35809 |  |  | 0.28799 |  |  | 0.42887 |  |  | 0.10753
[13 empty] | C Non choked w/ reducers | 7 |  | 56.095 |  |  | 121.9297 |  |  | #NUM! |  |  | -444.082 |  |  | -140.7967 |  |  | -94.3541 |  |  | -78.6101 |  |  | -84.3279 |  |  | -55.2871 |  |  | -251.0773
[13 empty] | C Choked w/ reducers | 7 |  | 49.1165 |  |  | 98.8222 |  |  | 727.6036 |  |  | -253.7215 |  |  | -112.2064 |  |  | -74.8441 |  |  | -58.5659 |  |  | -53.2139 |  |  | -46.5322 |  |  | -66.2295
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 56.095 |  |  | 121.9297 |  |  | #NUM! |  |  | -253.7215 |  |  | -112.2064 |  |  | -74.8441 |  |  | -58.5659 |  |  | -53.2139 |  |  | -46.5322 |  |  | -66.2295
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 51.365 | 131141.1172 |  | 110.3297 | 241110.1838 |  | 236393 | 590390.2743 |  | 236393 | 1149929.5599 |  | 236393 | 1929224.0831 |  | 236393 | 2815755.094 |  | 236393 | 3757636.0883 |  | 236393 | 4585030.1288 |  | 236393 | 5323077.6389 |  | 236393 | 6241727.1647
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 133763.9396 | C_100 - C this iteration | iteration | 243521.2857 | C_100 - C this iteration | iteration | 596294.177 | C_100 - C this iteration | iteration | 1161428.8555 | C_100 - C this iteration | iteration | 1948516.324 | C_100 - C this iteration | iteration | 2843912.6449 | C_100 - C this iteration | iteration | 3795212.4492 | C_100 - C this iteration | iteration | 4630880.43 | C_100 - C this iteration | iteration | 5376308.4153 | C_100 - C this iteration | iteration | 6304144.4363 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.9239 |  |  | 79.3765 |  |  | 25.3791 |  |  | -155.6698 |  |  | -601.8079 |  |  | -1383.9119 |  |  | -2535.0351 |  |  | -3818.41 |  |  | -5178.0105 |  |  | -7153.2713
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 26.9239 |  |  | 19.3765 |  |  | -34.6209 |  |  | -215.6698 |  |  | -661.8079 |  |  | -1443.9119 |  |  | -2595.0351 |  |  | -3878.41 |  |  | -5238.0105 |  |  | -7213.2713
[13 empty] | Press drop ratio this iteration |  |  | 0.30974 |  |  | 0.24411 |  |  | -1.3641 |  |  | 1.3854 |  |  | 1.0997 |  |  | 1.0434 |  |  | 1.0237 |  |  | 1.0157 |  |  | 1.0116 |  |  | 1.0084
[13 empty] | Expansion factor | 12 |  | 0.83868 |  |  | 0.8729 |  |  | 1.7171 |  |  | 0.26149 |  |  | 0.39562 |  |  | 0.39217 |  |  | 0.3584 |  |  | 0.28822 |  |  | 0.42901 |  |  | 0.10768
[13 empty] | C Non choked w/ reducers | 7 |  | 57.3572 |  |  | 123.8403 |  |  | #NUM! |  |  | -425.4866 |  |  | -138.6821 |  |  | -93.2102 |  |  | -77.7278 |  |  | -83.401 |  |  | -54.7099 |  |  | -248.2006
[13 empty] | C Choked w/ reducers | 7 |  | 50.1718 |  |  | 100.0782 |  |  | 771.8546 |  |  | -248.2841 |  |  | -110.7608 |  |  | -74.0061 |  |  | -57.9446 |  |  | -52.662 |  |  | -46.0553 |  |  | -65.5572
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 57.3572 |  |  | 123.8403 |  |  | #NUM! |  |  | -248.2841 |  |  | -110.7608 |  |  | -74.0061 |  |  | -57.9446 |  |  | -52.662 |  |  | -46.0553 |  |  | -65.5572
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 52.6272 | 133763.9396 |  | 112.2403 | 243521.2857 |  | 236393 | 596294.177 |  | 236393 | 1161428.8555 |  | 236393 | 1948516.324 |  | 236393 | 2843912.6449 |  | 236393 | 3795212.4492 |  | 236393 | 4630880.43 |  | 236393 | 5376308.4153 |  | 236393 | 6304144.4363
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 136439.2184 | C_100 - C this iteration | iteration | 245956.4985 | C_100 - C this iteration | iteration | 602257.1188 | C_100 - C this iteration | iteration | 1173043.1441 | C_100 - C this iteration | iteration | 1968001.4872 | C_100 - C this iteration | iteration | 2872351.7713 | C_100 - C this iteration | iteration | 3833164.5737 | C_100 - C this iteration | iteration | 4677189.2343 | C_100 - C this iteration | iteration | 5430071.4995 | C_100 - C this iteration | iteration | 6367185.8807 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.7921 |  |  | 79.1592 |  |  | 24.0765 |  |  | -160.6115 |  |  | -615.7169 |  |  | -1413.5412 |  |  | -2587.802 |  |  | -3896.9727 |  |  | -5283.9012 |  |  | -7298.8648
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 26.7921 |  |  | 19.1592 |  |  | -35.9235 |  |  | -220.6115 |  |  | -675.7169 |  |  | -1473.5412 |  |  | -2647.802 |  |  | -3956.9727 |  |  | -5343.9012 |  |  | -7358.8648
[13 empty] | Press drop ratio this iteration |  |  | 0.30869 |  |  | 0.24203 |  |  | -1.4921 |  |  | 1.3736 |  |  | 1.0974 |  |  | 1.0424 |  |  | 1.0232 |  |  | 1.0154 |  |  | 1.0114 |  |  | 1.0082
[13 empty] | Expansion factor | 12 |  | 0.83923 |  |  | 0.87398 |  |  | 1.7843 |  |  | 0.26781 |  |  | 0.39685 |  |  | 0.3927 |  |  | 0.3587 |  |  | 0.28844 |  |  | 0.42914 |  |  | 0.10782
[13 empty] | C Non choked w/ reducers | 7 |  | 58.6544 |  |  | 125.8027 |  |  | #NUM! |  |  | -408.4393 |  |  | -136.6177 |  |  | -92.0849 |  |  | -76.8575 |  |  | -82.4862 |  |  | -54.1393 |  |  | -245.3652
[13 empty] | C Choked w/ reducers | 7 |  | 51.253 |  |  | 101.3564 |  |  | 821.75 |  |  | -243.0514 |  |  | -109.3413 |  |  | -73.1794 |  |  | -57.3307 |  |  | -52.1164 |  |  | -45.5837 |  |  | -64.892
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 58.6544 |  |  | 125.8027 |  |  | #NUM! |  |  | -243.0514 |  |  | -109.3413 |  |  | -73.1794 |  |  | -57.3307 |  |  | -52.1164 |  |  | -45.5837 |  |  | -64.892
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 53.9244 | 136439.2184 |  | 114.2027 | 245956.4985 |  | 236393 | 602257.1188 |  | 236393 | 1173043.1441 |  | 236393 | 1968001.4872 |  | 236393 | 2872351.7713 |  | 236393 | 3833164.5737 |  | 236393 | 4677189.2343 |  | 236393 | 5430071.4995 |  | 236393 | 6367185.8807
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 139168.0027 | C_100 - C this iteration | iteration | 248416.0635 | C_100 - C this iteration | iteration | 608279.69 | C_100 - C this iteration | iteration | 1184773.5755 | C_100 - C this iteration | iteration | 1987681.5021 | C_100 - C this iteration | iteration | 2901075.2891 | C_100 - C this iteration | iteration | 3871496.2195 | C_100 - C this iteration | iteration | 4723961.1267 | C_100 - C this iteration | iteration | 5484372.2145 | C_100 - C this iteration | iteration | 6430857.7395 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.6551 |  |  | 78.9376 |  |  | 22.7477 |  |  | -165.6525 |  |  | -629.9055 |  |  | -1443.7661 |  |  | -2641.6295 |  |  | -3977.1146 |  |  | -5391.9204 |  |  | -7447.3847
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 26.6551 |  |  | 18.9376 |  |  | -37.2523 |  |  | -225.6525 |  |  | -689.9055 |  |  | -1503.7661 |  |  | -2701.6295 |  |  | -4037.1146 |  |  | -5451.9204 |  |  | -7507.3847
[13 empty] | Press drop ratio this iteration |  |  | 0.3076 |  |  | 0.23991 |  |  | -1.6376 |  |  | 1.3622 |  |  | 1.0953 |  |  | 1.0416 |  |  | 1.0227 |  |  | 1.0151 |  |  | 1.0111 |  |  | 1.0081
[13 empty] | Expansion factor | 12 |  | 0.8398 |  |  | 0.87508 |  |  | 1.8608 |  |  | 0.27387 |  |  | 0.39806 |  |  | 0.39322 |  |  | 0.359 |  |  | 0.28865 |  |  | 0.42927 |  |  | 0.10797
[13 empty] | C Non choked w/ reducers | 7 |  | 59.9878 |  |  | 127.8192 |  |  | #NUM! |  |  | -392.7485 |  |  | -134.6017 |  |  | -90.9776 |  |  | -75.9992 |  |  | -81.5833 |  |  | -53.5753 |  |  | -242.5701
[13 empty] | C Choked w/ reducers | 7 |  | 52.3607 |  |  | 102.6574 |  |  | 878.449 |  |  | -238.0116 |  |  | -107.9472 |  |  | -72.3638 |  |  | -56.7241 |  |  | -51.5768 |  |  | -45.1172 |  |  | -64.2338
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 59.9878 |  |  | 127.8192 |  |  | #NUM! |  |  | -238.0116 |  |  | -107.9472 |  |  | -72.3638 |  |  | -56.7241 |  |  | -51.5768 |  |  | -45.1172 |  |  | -64.2338
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 55.2578 | 139168.0027 |  | 116.2192 | 248416.0635 |  | 236393 | 608279.69 |  | 236393 | 1184773.5755 |  | 236393 | 1987681.5021 |  | 236393 | 2901075.2891 |  | 236393 | 3871496.2195 |  | 236393 | 4723961.1267 |  | 236393 | 5484372.2145 |  | 236393 | 6430857.7395
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 141951.3628 | C_100 - C this iteration | iteration | 250900.2241 | C_100 - C this iteration | iteration | 614362.4869 | C_100 - C this iteration | iteration | 1196621.3113 | C_100 - C this iteration | iteration | 2007558.3171 | C_100 - C this iteration | iteration | 2930086.0419 | C_100 - C this iteration | iteration | 3910211.1817 | C_100 - C this iteration | iteration | 4771200.7379 | C_100 - C this iteration | iteration | 5539215.9366 | C_100 - C this iteration | iteration | 6495166.3169 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.5124 |  |  | 78.7115 |  |  | 21.3923 |  |  | -170.7948 |  |  | -644.3794 |  |  | -1474.5986 |  |  | -2696.539 |  |  | -4058.8673 |  |  | -5502.1107 |  |  | -7598.8898
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 26.5124 |  |  | 18.7115 |  |  | -38.6077 |  |  | -230.7948 |  |  | -704.3794 |  |  | -1534.5986 |  |  | -2756.539 |  |  | -4118.8673 |  |  | -5562.1107 |  |  | -7658.8898
[13 empty] | Press drop ratio this iteration |  |  | 0.30646 |  |  | 0.23772 |  |  | -1.8048 |  |  | 1.3513 |  |  | 1.0931 |  |  | 1.0407 |  |  | 1.0223 |  |  | 1.0148 |  |  | 1.0109 |  |  | 1.0079
[13 empty] | Expansion factor | 12 |  | 0.84039 |  |  | 0.87622 |  |  | 1.9487 |  |  | 0.27968 |  |  | 0.39924 |  |  | 0.39373 |  |  | 0.35929 |  |  | 0.28887 |  |  | 0.42939 |  |  | 0.10811
[13 empty] | C Non choked w/ reducers | 7 |  | 61.359 |  |  | 129.8926 |  |  | #NUM! |  |  | -378.2532 |  |  | -132.6323 |  |  | -89.8879 |  |  | -75.1525 |  |  | -80.692 |  |  | -53.0176 |  |  | -239.8145
[13 empty] | C Choked w/ reducers | 7 |  | 53.496 |  |  | 103.9818 |  |  | 943.4518 |  |  | -233.1539 |  |  | -106.5777 |  |  | -71.5593 |  |  | -56.1248 |  |  | -51.0434 |  |  | -44.6558 |  |  | -63.5827
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 61.359 |  |  | 129.8926 |  |  | #NUM! |  |  | -233.1539 |  |  | -106.5777 |  |  | -71.5593 |  |  | -56.1248 |  |  | -51.0434 |  |  | -44.6558 |  |  | -63.5827
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 56.629 | 141951.3628 |  | 118.2926 | 250900.2241 |  | 236393 | 614362.4869 |  | 236393 | 1196621.3113 |  | 236393 | 2007558.3171 |  | 236393 | 2930086.0419 |  | 236393 | 3910211.1817 |  | 236393 | 4771200.7379 |  | 236393 | 5539215.9366 |  | 236393 | 6495166.3169
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 144790.39 | C_100 - C this iteration | iteration | 253409.2264 | C_100 - C this iteration | iteration | 620506.1118 | C_100 - C this iteration | iteration | 1208587.5244 | C_100 - C this iteration | iteration | 2027633.9003 | C_100 - C this iteration | iteration | 2959386.9024 | C_100 - C this iteration | iteration | 3949313.2935 | C_100 - C this iteration | iteration | 4818912.7453 | C_100 - C this iteration | iteration | 5594608.096 | C_100 - C this iteration | iteration | 6560117.98 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.3641 |  |  | 78.4809 |  |  | 20.0095 |  |  | -176.0405 |  |  | -659.1441 |  |  | -1506.0507 |  |  | -2752.5522 |  |  | -4142.2633 |  |  | -5614.5158 |  |  | -7753.4402
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 26.3641 |  |  | 18.4809 |  |  | -39.9905 |  |  | -236.0405 |  |  | -719.1441 |  |  | -1566.0507 |  |  | -2812.5522 |  |  | -4202.2633 |  |  | -5674.5158 |  |  | -7813.4402
[13 empty] | Press drop ratio this iteration |  |  | 0.30527 |  |  | 0.23548 |  |  | -1.9986 |  |  | 1.3408 |  |  | 1.091 |  |  | 1.0398 |  |  | 1.0218 |  |  | 1.0145 |  |  | 1.0107 |  |  | 1.0077
[13 empty] | Expansion factor | 12 |  | 0.84101 |  |  | 0.87739 |  |  | 2.0505 |  |  | 0.28526 |  |  | 0.40038 |  |  | 0.39422 |  |  | 0.35957 |  |  | 0.28908 |  |  | 0.42951 |  |  | 0.10825
[13 empty] | C Non choked w/ reducers | 7 |  | 62.7696 |  |  | 132.0256 |  |  | #NUM! |  |  | -364.8171 |  |  | -130.7078 |  |  | -88.8154 |  |  | -74.3172 |  |  | -79.8122 |  |  | -52.4664 |  |  | -237.0977
[13 empty] | C Choked w/ reducers | 7 |  | 54.6596 |  |  | 105.3302 |  |  | 1018.7344 |  |  | -228.4684 |  |  | -105.2323 |  |  | -70.7655 |  |  | -55.5325 |  |  | -50.5159 |  |  | -44.1993 |  |  | -62.9384
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 62.7696 |  |  | 132.0256 |  |  | #NUM! |  |  | -228.4684 |  |  | -105.2323 |  |  | -70.7655 |  |  | -55.5325 |  |  | -50.5159 |  |  | -44.1993 |  |  | -62.9384
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 58.0396 | 144790.39 |  | 120.4256 | 253409.2264 |  | 236393 | 620506.1118 |  | 236393 | 1208587.5244 |  | 236393 | 2027633.9003 |  | 236393 | 2959386.9024 |  | 236393 | 3949313.2935 |  | 236393 | 4818912.7453 |  | 236393 | 5594608.096 |  | 236393 | 6560117.98
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 147686.1978 | C_100 - C this iteration | iteration | 255943.3186 | C_100 - C this iteration | iteration | 626711.1729 | C_100 - C this iteration | iteration | 1220673.3996 | C_100 - C this iteration | iteration | 2047910.2393 | C_100 - C this iteration | iteration | 2988980.7714 | C_100 - C this iteration | iteration | 3988806.4264 | C_100 - C this iteration | iteration | 4867101.8728 | C_100 - C this iteration | iteration | 5650554.1769 | C_100 - C this iteration | iteration | 6625719.1598 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.2097 |  |  | 78.2457 |  |  | 18.599 |  |  | -181.3917 |  |  | -674.2056 |  |  | -1538.135 |  |  | -2809.6912 |  |  | -4227.3355 |  |  | -5729.1803 |  |  | -7911.0971
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 26.2097 |  |  | 18.2457 |  |  | -41.401 |  |  | -241.3917 |  |  | -734.2056 |  |  | -1598.135 |  |  | -2869.6912 |  |  | -4287.3355 |  |  | -5789.1803 |  |  | -7971.0971
[13 empty] | Press drop ratio this iteration |  |  | 0.30402 |  |  | 0.23318 |  |  | -2.226 |  |  | 1.3308 |  |  | 1.089 |  |  | 1.039 |  |  | 1.0214 |  |  | 1.0142 |  |  | 1.0105 |  |  | 1.0076
[13 empty] | Expansion factor | 12 |  | 0.84166 |  |  | 0.87858 |  |  | 2.1701 |  |  | 0.29062 |  |  | 0.4015 |  |  | 0.39471 |  |  | 0.35985 |  |  | 0.28928 |  |  | 0.42964 |  |  | 0.10839
[13 empty] | C Non choked w/ reducers | 7 |  | 64.2213 |  |  | 134.2213 |  |  | #NUM! |  |  | -352.324 |  |  | -128.8266 |  |  | -87.7598 |  |  | -73.493 |  |  | -78.9436 |  |  | -51.9214 |  |  | -234.4188
[13 empty] | C Choked w/ reducers | 7 |  | 55.8527 |  |  | 106.7033 |  |  | 1106.9542 |  |  | -223.9458 |  |  | -103.9103 |  |  | -69.9823 |  |  | -54.9472 |  |  | -49.9943 |  |  | -43.7479 |  |  | -62.301
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 64.2213 |  |  | 134.2213 |  |  | #NUM! |  |  | -223.9458 |  |  | -103.9103 |  |  | -69.9823 |  |  | -54.9472 |  |  | -49.9943 |  |  | -43.7479 |  |  | -62.301
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 59.4913 | 147686.1978 |  | 122.6213 | 255943.3186 |  | 236393 | 626711.1729 |  | 236393 | 1220673.3996 |  | 236393 | 2047910.2393 |  | 236393 | 2988980.7714 |  | 236393 | 3988806.4264 |  | 236393 | 4867101.8728 |  | 236393 | 5650554.1769 |  | 236393 | 6625719.1598
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 150639.9218 | C_100 - C this iteration | iteration | 258502.7518 | C_100 - C this iteration | iteration | 632978.2846 | C_100 - C this iteration | iteration | 1232880.1336 | C_100 - C this iteration | iteration | 2068389.3417 | C_100 - C this iteration | iteration | 3018870.5791 | C_100 - C this iteration | iteration | 4028694.4907 | C_100 - C this iteration | iteration | 4915772.8915 | C_100 - C this iteration | iteration | 5707059.7187 | C_100 - C this iteration | iteration | 6691976.3514 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.0491 |  |  | 78.0057 |  |  | 17.1601 |  |  | -186.8503 |  |  | -689.5699 |  |  | -1570.8643 |  |  | -2867.9787 |  |  | -4314.1176 |  |  | -5846.1496 |  |  | -8071.9229
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 26.0491 |  |  | 18.0057 |  |  | -42.8399 |  |  | -246.8503 |  |  | -749.5699 |  |  | -1630.8643 |  |  | -2927.9787 |  |  | -4374.1176 |  |  | -5906.1496 |  |  | -8131.9229
[13 empty] | Press drop ratio this iteration |  |  | 0.30272 |  |  | 0.23083 |  |  | -2.4965 |  |  | 1.3211 |  |  | 1.087 |  |  | 1.0382 |  |  | 1.0209 |  |  | 1.0139 |  |  | 1.0103 |  |  | 1.0074
[13 empty] | Expansion factor | 12 |  | 0.84234 |  |  | 0.87981 |  |  | 2.3123 |  |  | 0.29577 |  |  | 0.40259 |  |  | 0.39518 |  |  | 0.36012 |  |  | 0.28948 |  |  | 0.42975 |  |  | 0.10852
[13 empty] | C Non choked w/ reducers | 7 |  | 65.7158 |  |  | 136.4829 |  |  | #NUM! |  |  | -340.6743 |  |  | -126.9871 |  |  | -86.7206 |  |  | -72.6799 |  |  | -78.0862 |  |  | -51.3825 |  |  | -231.7772
[13 empty] | C Choked w/ reducers | 7 |  | 57.076 |  |  | 108.1019 |  |  | 1211.7703 |  |  | -219.5774 |  |  | -102.611 |  |  | -69.2094 |  |  | -54.3688 |  |  | -49.4785 |  |  | -43.3013 |  |  | -61.6703
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 65.7158 |  |  | 136.4829 |  |  | #NUM! |  |  | -219.5774 |  |  | -102.611 |  |  | -69.2094 |  |  | -54.3688 |  |  | -49.4785 |  |  | -43.3013 |  |  | -61.6703
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 60.9858 | 150639.9218 |  | 124.8829 | 258502.7518 |  | 236393 | 632978.2846 |  | 236393 | 1232880.1336 |  | 236393 | 2068389.3417 |  | 236393 | 3018870.5791 |  | 236393 | 4028694.4907 |  | 236393 | 4915772.8915 |  | 236393 | 5707059.7187 |  | 236393 | 6691976.3514
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 153652.7202 | C_100 - C this iteration | iteration | 261087.7793 | C_100 - C this iteration | iteration | 639308.0675 | C_100 - C this iteration | iteration | 1245208.935 | C_100 - C this iteration | iteration | 2089073.2351 | C_100 - C this iteration | iteration | 3049059.2849 | C_100 - C this iteration | iteration | 4068981.4356 | C_100 - C this iteration | iteration | 4964930.6204 | C_100 - C this iteration | iteration | 5764130.3159 | C_100 - C this iteration | iteration | 6758896.115 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 85.882 |  |  | 77.7609 |  |  | 15.6923 |  |  | -192.4188 |  |  | -705.2429 |  |  | -1604.2514 |  |  | -2927.4378 |  |  | -4402.6441 |  |  | -5965.4699 |  |  | -8235.9812
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 25.882 |  |  | 17.7609 |  |  | -44.3077 |  |  | -252.4188 |  |  | -765.2429 |  |  | -1664.2514 |  |  | -2987.4378 |  |  | -4462.6441 |  |  | -6025.4699 |  |  | -8295.9812
[13 empty] | Press drop ratio this iteration |  |  | 0.30137 |  |  | 0.2284 |  |  | -2.8235 |  |  | 1.3118 |  |  | 1.0851 |  |  | 1.0374 |  |  | 1.0205 |  |  | 1.0136 |  |  | 1.0101 |  |  | 1.0073
[13 empty] | Expansion factor | 12 |  | 0.84305 |  |  | 0.88107 |  |  | 2.4842 |  |  | 0.30073 |  |  | 0.40365 |  |  | 0.39564 |  |  | 0.36039 |  |  | 0.28968 |  |  | 0.42987 |  |  | 0.10865
[13 empty] | C Non choked w/ reducers | 7 |  | 67.2551 |  |  | 138.8138 |  |  | #NUM! |  |  | -329.7819 |  |  | -125.1878 |  |  | -85.6973 |  |  | -71.8776 |  |  | -77.2396 |  |  | -50.8498 |  |  | -229.172
[13 empty] | C Choked w/ reducers | 7 |  | 58.3308 |  |  | 109.5267 |  |  | 1338.366 |  |  | -215.3553 |  |  | -101.3339 |  |  | -68.4468 |  |  | -53.7971 |  |  | -48.9684 |  |  | -42.8595 |  |  | -61.0463
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 67.2551 |  |  | 138.8138 |  |  | #NUM! |  |  | -215.3553 |  |  | -101.3339 |  |  | -68.4468 |  |  | -53.7971 |  |  | -48.9684 |  |  | -42.8595 |  |  | -61.0463
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 62.5251 | 153652.7202 |  | 127.2138 | 261087.7793 |  | 236393 | 639308.0675 |  | 236393 | 1245208.935 |  | 236393 | 2089073.2351 |  | 236393 | 3049059.2849 |  | 236393 | 4068981.4356 |  | 236393 | 4964930.6204 |  | 236393 | 5764130.3159 |  | 236393 | 6758896.115
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 156725.7746 | C_100 - C this iteration | iteration | 263698.6571 | C_100 - C this iteration | iteration | 645701.1481 | C_100 - C this iteration | iteration | 1257661.0243 | C_100 - C this iteration | iteration | 2109963.9674 | C_100 - C this iteration | iteration | 3079549.8777 | C_100 - C this iteration | iteration | 4109671.2499 | C_100 - C this iteration | iteration | 5014579.9266 | C_100 - C this iteration | iteration | 5821771.619 | C_100 - C this iteration | iteration | 6826485.0761 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 85.7082 |  |  | 77.5112 |  |  | 14.195 |  |  | -198.0991 |  |  | -721.231 |  |  | -1638.3095 |  |  | -2988.092 |  |  | -4492.95 |  |  | -6087.1885 |  |  | -8403.3372
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 25.7082 |  |  | 17.5112 |  |  | -45.805 |  |  | -258.0991 |  |  | -781.231 |  |  | -1698.3095 |  |  | -3048.092 |  |  | -4552.95 |  |  | -6147.1885 |  |  | -8463.3372
[13 empty] | Press drop ratio this iteration |  |  | 0.29995 |  |  | 0.22592 |  |  | -3.2268 |  |  | 1.3029 |  |  | 1.0832 |  |  | 1.0366 |  |  | 1.0201 |  |  | 1.0134 |  |  | 1.0099 |  |  | 1.0071
[13 empty] | Expansion factor | 12 |  | 0.84378 |  |  | 0.88237 |  |  | 2.6962 |  |  | 0.30549 |  |  | 0.40469 |  |  | 0.3961 |  |  | 0.36065 |  |  | 0.28987 |  |  | 0.42998 |  |  | 0.10878
[13 empty] | C Non choked w/ reducers | 7 |  | 68.8413 |  |  | 141.2179 |  |  | #NUM! |  |  | -319.5723 |  |  | -123.4275 |  |  | -84.6898 |  |  | -71.0858 |  |  | -76.4037 |  |  | -50.3231 |  |  | -226.6026
[13 empty] | C Choked w/ reducers | 7 |  | 59.6181 |  |  | 110.9783 |  |  | 1494.3336 |  |  | -211.2719 |  |  | -100.0784 |  |  | -67.6941 |  |  | -53.2322 |  |  | -48.464 |  |  | -42.4226 |  |  | -60.4288
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 68.8413 |  |  | 141.2179 |  |  | #NUM! |  |  | -211.2719 |  |  | -100.0784 |  |  | -67.6941 |  |  | -53.2322 |  |  | -48.464 |  |  | -42.4226 |  |  | -60.4288
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 64.1113 | 156725.7746 |  | 129.6179 | 263698.6571 |  | 236393 | 645701.1481 |  | 236393 | 1257661.0243 |  | 236393 | 2109963.9674 |  | 236393 | 3079549.8777 |  | 236393 | 4109671.2499 |  | 236393 | 5014579.9266 |  | 236393 | 5821771.619 |  | 236393 | 6826485.0761
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 159860.2901 | C_100 - C this iteration | iteration | 266335.6437 | C_100 - C this iteration | iteration | 652158.1596 | C_100 - C this iteration | iteration | 1270237.6345 | C_100 - C this iteration | iteration | 2131063.6071 | C_100 - C this iteration | iteration | 3110345.3765 | C_100 - C this iteration | iteration | 4150767.9624 | C_100 - C this iteration | iteration | 5064725.7259 | C_100 - C this iteration | iteration | 5879989.3352 | C_100 - C this iteration | iteration | 6894749.9269 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 85.5273 |  |  | 77.2564 |  |  | 12.6676 |  |  | -203.8936 |  |  | -737.5405 |  |  | -1673.0523 |  |  | -3049.9654 |  |  | -4585.071 |  |  | -6211.3537 |  |  | -8574.057
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 25.5273 |  |  | 17.2564 |  |  | -47.3324 |  |  | -263.8936 |  |  | -797.5405 |  |  | -1733.0523 |  |  | -3109.9654 |  |  | -4645.071 |  |  | -6271.3537 |  |  | -8634.057
[13 empty] | Press drop ratio this iteration |  |  | 0.29847 |  |  | 0.22337 |  |  | -3.7365 |  |  | 1.2943 |  |  | 1.0814 |  |  | 1.0359 |  |  | 1.0197 |  |  | 1.0131 |  |  | 1.0097 |  |  | 1.007
[13 empty] | Expansion factor | 12 |  | 0.84455 |  |  | 0.8837 |  |  | 2.9641 |  |  | 0.31008 |  |  | 0.4057 |  |  | 0.39654 |  |  | 0.36091 |  |  | 0.29006 |  |  | 0.43009 |  |  | 0.10891
[13 empty] | C Non choked w/ reducers | 7 |  | 70.4765 |  |  | 143.6993 |  |  | #NUM! |  |  | -309.9805 |  |  | -121.7046 |  |  | -83.6976 |  |  | -70.3044 |  |  | -75.5783 |  |  | -49.8023 |  |  | -224.0683
[13 empty] | C Choked w/ reducers | 7 |  | 60.9391 |  |  | 112.4577 |  |  | 1691.2584 |  |  | -207.3204 |  |  | -98.844 |  |  | -66.9512 |  |  | -52.6738 |  |  | -47.9652 |  |  | -41.9903 |  |  | -59.8179
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 70.4765 |  |  | 143.6993 |  |  | #NUM! |  |  | -207.3204 |  |  | -98.844 |  |  | -66.9512 |  |  | -52.6738 |  |  | -47.9652 |  |  | -41.9903 |  |  | -59.8179
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 65.7465 | 159860.2901 |  | 132.0993 | 266335.6437 |  | 236393 | 652158.1596 |  | 236393 | 1270237.6345 |  | 236393 | 2131063.6071 |  | 236393 | 3110345.3765 |  | 236393 | 4150767.9624 |  | 236393 | 5064725.7259 |  | 236393 | 5879989.3352 |  | 236393 | 6894749.9269
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 163057.4959 | C_100 - C this iteration | iteration | 268999.0001 | C_100 - C this iteration | iteration | 658679.7412 | C_100 - C this iteration | iteration | 1282940.0109 | C_100 - C this iteration | iteration | 2152374.2432 | C_100 - C this iteration | iteration | 3141448.8303 | C_100 - C this iteration | iteration | 4192275.6421 | C_100 - C this iteration | iteration | 5115372.9832 | C_100 - C this iteration | iteration | 5938789.2286 | C_100 - C this iteration | iteration | 6963697.4261 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 85.3391 |  |  | 76.9966 |  |  | 11.1095 |  |  | -209.8046 |  |  | -754.1778 |  |  | -1708.4934 |  |  | -3113.0824 |  |  | -4679.0437 |  |  | -6338.0147 |  |  | -8748.2082
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 25.3391 |  |  | 16.9966 |  |  | -48.8905 |  |  | -269.8046 |  |  | -814.1778 |  |  | -1768.4934 |  |  | -3173.0824 |  |  | -4739.0437 |  |  | -6398.0147 |  |  | -8808.2082
[13 empty] | Press drop ratio this iteration |  |  | 0.29692 |  |  | 0.22074 |  |  | -4.4008 |  |  | 1.286 |  |  | 1.0796 |  |  | 1.0351 |  |  | 1.0193 |  |  | 1.0128 |  |  | 1.0095 |  |  | 1.0069
[13 empty] | Expansion factor | 12 |  | 0.84536 |  |  | 0.88506 |  |  | 3.3133 |  |  | 0.3145 |  |  | 0.40669 |  |  | 0.39697 |  |  | 0.36116 |  |  | 0.29024 |  |  | 0.4302 |  |  | 0.10903
[13 empty] | C Non choked w/ reducers | 7 |  | 72.1631 |  |  | 146.2622 |  |  | #NUM! |  |  | -300.9495 |  |  | -120.0181 |  |  | -82.7203 |  |  | -69.5333 |  |  | -74.7632 |  |  | -49.2873 |  |  | -221.5684
[13 empty] | C Choked w/ reducers | 7 |  | 62.2949 |  |  | 113.9656 |  |  | 1947.7409 |  |  | -203.4942 |  |  | -97.6302 |  |  | -66.218 |  |  | -52.1219 |  |  | -47.4719 |  |  | -41.5626 |  |  | -59.2133
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 72.1631 |  |  | 146.2622 |  |  | #NUM! |  |  | -203.4942 |  |  | -97.6302 |  |  | -66.218 |  |  | -52.1219 |  |  | -47.4719 |  |  | -41.5626 |  |  | -59.2133
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 67.4331 | 163057.4959 |  | 134.6622 | 268999.0001 |  | 236393 | 658679.7412 |  | 236393 | 1282940.0109 |  | 236393 | 2152374.2432 |  | 236393 | 3141448.8303 |  | 236393 | 4192275.6421 |  | 236393 | 5115372.9832 |  | 236393 | 5938789.2286 |  | 236393 | 6963697.4261
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 166318.6458 | C_100 - C this iteration | iteration | 271688.9901 | C_100 - C this iteration | iteration | 665266.5386 | C_100 - C this iteration | iteration | 1295769.411 | C_100 - C this iteration | iteration | 2173897.9856 | C_100 - C this iteration | iteration | 3172863.3186 | C_100 - C this iteration | iteration | 4234198.3985 | C_100 - C this iteration | iteration | 5166526.713 | C_100 - C this iteration | iteration | 5998177.1209 | C_100 - C this iteration | iteration | 7033334.4004 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 85.1434 |  |  | 76.7315 |  |  | 9.5201 |  |  | -215.8344 |  |  | -771.1495 |  |  | -1744.6468 |  |  | -3177.4681 |  |  | -4774.9051 |  |  | -6467.2215 |  |  | -8925.8599
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 25.1434 |  |  | 16.7315 |  |  | -50.4799 |  |  | -275.8344 |  |  | -831.1495 |  |  | -1804.6468 |  |  | -3237.4681 |  |  | -4834.9051 |  |  | -6527.2215 |  |  | -8985.8599
[13 empty] | Press drop ratio this iteration |  |  | 0.29531 |  |  | 0.21805 |  |  | -5.3025 |  |  | 1.278 |  |  | 1.0778 |  |  | 1.0344 |  |  | 1.0189 |  |  | 1.0126 |  |  | 1.0093 |  |  | 1.0067
[13 empty] | Expansion factor | 12 |  | 0.8462 |  |  | 0.88646 |  |  | 3.7872 |  |  | 0.31876 |  |  | 0.40765 |  |  | 0.3974 |  |  | 0.3614 |  |  | 0.29042 |  |  | 0.43031 |  |  | 0.10915
[13 empty] | C Non choked w/ reducers | 7 |  | 73.9037 |  |  | 148.9116 |  |  | #NUM! |  |  | -292.4294 |  |  | -118.3667 |  |  | -81.7576 |  |  | -68.7721 |  |  | -73.9583 |  |  | -48.7781 |  |  | -219.1022
[13 empty] | C Choked w/ reducers | 7 |  | 63.6869 |  |  | 115.503 |  |  | 2295.6536 |  |  | -199.7873 |  |  | -96.4363 |  |  | -65.4943 |  |  | -51.5764 |  |  | -46.9841 |  |  | -41.1396 |  |  | -58.6152
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 73.9037 |  |  | 148.9116 |  |  | #NUM! |  |  | -199.7873 |  |  | -96.4363 |  |  | -65.4943 |  |  | -51.5764 |  |  | -46.9841 |  |  | -41.1396 |  |  | -58.6152
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 69.1737 | 166318.6458 |  | 137.3116 | 271688.9901 |  | 236393 | 665266.5386 |  | 236393 | 1295769.411 |  | 236393 | 2173897.9856 |  | 236393 | 3172863.3186 |  | 236393 | 4234198.3985 |  | 236393 | 5166526.713 |  | 236393 | 5998177.1209 |  | 236393 | 7033334.4004
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 169645.0188 | C_100 - C this iteration | iteration | 274405.8801 | C_100 - C this iteration | iteration | 671919.204 | C_100 - C this iteration | iteration | 1308727.1051 | C_100 - C this iteration | iteration | 2195636.9655 | C_100 - C this iteration | iteration | 3204591.9518 | C_100 - C this iteration | iteration | 4276540.3825 | C_100 - C this iteration | iteration | 5218191.9801 | C_100 - C this iteration | iteration | 6058158.8921 | C_100 - C this iteration | iteration | 7103667.7444 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 84.9397 |  |  | 76.4611 |  |  | 7.8987 |  |  | -221.9854 |  |  | -788.4623 |  |  | -1781.5269 |  |  | -3243.1479 |  |  | -4872.6935 |  |  | -6599.0254 |  |  | -9107.0825
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 24.9397 |  |  | 16.4611 |  |  | -52.1013 |  |  | -281.9854 |  |  | -848.4623 |  |  | -1841.5269 |  |  | -3303.1479 |  |  | -4932.6935 |  |  | -6659.0254 |  |  | -9167.0825
[13 empty] | Press drop ratio this iteration |  |  | 0.29362 |  |  | 0.21529 |  |  | -6.5962 |  |  | 1.2703 |  |  | 1.0761 |  |  | 1.0337 |  |  | 1.0185 |  |  | 1.0123 |  |  | 1.0091 |  |  | 1.0066
[13 empty] | Expansion factor | 12 |  | 0.84708 |  |  | 0.8879 |  |  | 4.4673 |  |  | 0.32286 |  |  | 0.40859 |  |  | 0.39781 |  |  | 0.36164 |  |  | 0.2906 |  |  | 0.43041 |  |  | 0.10927
[13 empty] | C Non choked w/ reducers | 7 |  | 75.7009 |  |  | 151.6526 |  |  | #NUM! |  |  | -284.376 |  |  | -116.7492 |  |  | -80.8093 |  |  | -68.0208 |  |  | -73.1634 |  |  | -48.2746 |  |  | -216.6692
[13 empty] | C Choked w/ reducers | 7 |  | 65.1164 |  |  | 117.0706 |  |  | 2794.5499 |  |  | -196.1939 |  |  | -95.262 |  |  | -64.7798 |  |  | -51.0372 |  |  | -46.5016 |  |  | -40.7211 |  |  | -58.0233
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 75.7009 |  |  | 151.6526 |  |  | #NUM! |  |  | -196.1939 |  |  | -95.262 |  |  | -64.7798 |  |  | -51.0372 |  |  | -46.5016 |  |  | -40.7211 |  |  | -58.0233
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 70.9709 | 169645.0188 |  | 140.0526 | 274405.8801 |  | 236393 | 671919.204 |  | 236393 | 1308727.1051 |  | 236393 | 2195636.9655 |  | 236393 | 3204591.9518 |  | 236393 | 4276540.3825 |  | 236393 | 5218191.9801 |  | 236393 | 6058158.8921 |  | 236393 | 7103667.7444
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 173037.9191 | C_100 - C this iteration | iteration | 277149.9389 | C_100 - C this iteration | iteration | 678638.396 | C_100 - C this iteration | iteration | 1321814.3762 | C_100 - C this iteration | iteration | 2217593.3351 | C_100 - C this iteration | iteration | 3236637.8713 | C_100 - C this iteration | iteration | 4319305.7863 | C_100 - C this iteration | iteration | 5270373.8999 | C_100 - C this iteration | iteration | 6118740.481 | C_100 - C this iteration | iteration | 7174704.4218 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 84.7278 |  |  | 76.1852 |  |  | 6.2448 |  |  | -228.26 |  |  | -806.1231 |  |  | -1819.1483 |  |  | -3310.1479 |  |  | -4972.4473 |  |  | -6733.4785 |  |  | -9291.9475
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 24.7278 |  |  | 16.1852 |  |  | -53.7552 |  |  | -288.26 |  |  | -866.1231 |  |  | -1879.1483 |  |  | -3370.1479 |  |  | -5032.4473 |  |  | -6793.4785 |  |  | -9351.9475
[13 empty] | Press drop ratio this iteration |  |  | 0.29185 |  |  | 0.21245 |  |  | -8.608 |  |  | 1.2629 |  |  | 1.0744 |  |  | 1.033 |  |  | 1.0181 |  |  | 1.0121 |  |  | 1.0089 |  |  | 1.0065
[13 empty] | Expansion factor | 12 |  | 0.848 |  |  | 0.88938 |  |  | 5.5248 |  |  | 0.32682 |  |  | 0.4095 |  |  | 0.39822 |  |  | 0.36188 |  |  | 0.29077 |  |  | 0.43052 |  |  | 0.10938
[13 empty] | C Non choked w/ reducers | 7 |  | 77.5577 |  |  | 154.4909 |  |  | #NUM! |  |  | -276.75 |  |  | -115.1645 |  |  | -79.8749 |  |  | -67.2792 |  |  | -72.3784 |  |  | -47.7767 |  |  | -214.2686
[13 empty] | C Choked w/ reducers | 7 |  | 66.5849 |  |  | 118.6694 |  |  | 3570.0465 |  |  | -192.7087 |  |  | -94.1067 |  |  | -64.0745 |  |  | -50.5042 |  |  | -46.0244 |  |  | -40.3071 |  |  | -57.4376
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 77.5577 |  |  | 154.4909 |  |  | #NUM! |  |  | -192.7087 |  |  | -94.1067 |  |  | -64.0745 |  |  | -50.5042 |  |  | -46.0244 |  |  | -40.3071 |  |  | -57.4376
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 72.8277 | 173037.9191 |  | 142.8909 | 277149.9389 |  | 236393 | 678638.396 |  | 236393 | 1321814.3762 |  | 236393 | 2217593.3351 |  | 236393 | 3236637.8713 |  | 236393 | 4319305.7863 |  | 236393 | 5270373.8999 |  | 236393 | 6118740.481 |  | 236393 | 7174704.4218
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 176498.6775 | C_100 - C this iteration | iteration | 279921.4382 | C_100 - C this iteration | iteration | 685424.78 | C_100 - C this iteration | iteration | 1335032.5199 | C_100 - C this iteration | iteration | 2239769.2685 | C_100 - C this iteration | iteration | 3269004.25 | C_100 - C this iteration | iteration | 4362498.8441 | C_100 - C this iteration | iteration | 5323077.6389 | C_100 - C this iteration | iteration | 6179927.8858 | C_100 - C this iteration | iteration | 7246451.4661 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 84.5073 |  |  | 75.9038 |  |  | 4.5576 |  |  | -234.6607 |  |  | -824.1389 |  |  | -1857.5259 |  |  | -3378.4946 |  |  | -5074.2062 |  |  | -6870.6341 |  |  | -9480.5284
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 24.5073 |  |  | 15.9038 |  |  | -55.4424 |  |  | -294.6607 |  |  | -884.1389 |  |  | -1917.5259 |  |  | -3438.4946 |  |  | -5134.2062 |  |  | -6930.6341 |  |  | -9540.5284
[13 empty] | Press drop ratio this iteration |  |  | 0.29 |  |  | 0.20953 |  |  | -12.1649 |  |  | 1.2557 |  |  | 1.0728 |  |  | 1.0323 |  |  | 1.0178 |  |  | 1.0118 |  |  | 1.0087 |  |  | 1.0063
[13 empty] | Expansion factor | 12 |  | 0.84896 |  |  | 0.8909 |  |  | 7.3945 |  |  | 0.33065 |  |  | 0.4104 |  |  | 0.39861 |  |  | 0.36211 |  |  | 0.29094 |  |  | 0.43062 |  |  | 0.1095
[13 empty] | C Non choked w/ reducers | 7 |  | 79.4773 |  |  | 157.4326 |  |  | #NUM! |  |  | -269.5165 |  |  | -113.6116 |  |  | -78.9543 |  |  | -66.547 |  |  | -71.6029 |  |  | -47.2843 |  |  | -211.8999
[13 empty] | C Choked w/ reducers | 7 |  | 68.0938 |  |  | 120.3004 |  |  | 4940.5858 |  |  | -189.3268 |  |  | -92.97 |  |  | -63.3782 |  |  | -49.9773 |  |  | -45.5524 |  |  | -39.8974 |  |  | -56.858
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 79.4773 |  |  | 157.4326 |  |  | #NUM! |  |  | -189.3268 |  |  | -92.97 |  |  | -63.3782 |  |  | -49.9773 |  |  | -45.5524 |  |  | -39.8974 |  |  | -56.858
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 74.7473 | 176498.6775 |  | 145.8326 | 279921.4382 |  | 236393 | 685424.78 |  | 236393 | 1335032.5199 |  | 236393 | 2239769.2685 |  | 236393 | 3269004.25 |  | 236393 | 4362498.8441 |  | 236393 | 5323077.6389 |  | 236393 | 6179927.8858 |  | 236393 | 7246451.4661
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 180028.6511 | C_100 - C this iteration | iteration | 282720.6526 | C_100 - C this iteration | iteration | 692279.0278 | C_100 - C this iteration | iteration | 1348382.8451 | C_100 - C this iteration | iteration | 2262166.9612 | C_100 - C this iteration | iteration | 3301694.2925 | C_100 - C this iteration | iteration | 4406123.8326 | C_100 - C this iteration | iteration | 5376308.4153 | C_100 - C this iteration | iteration | 6241727.1647 | C_100 - C this iteration | iteration | 7318915.9807 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 84.2779 |  |  | 75.6167 |  |  | 2.8365 |  |  | -241.1901 |  |  | -842.5168 |  |  | -1896.6749 |  |  | -3448.215 |  |  | -5178.0105 |  |  | -7010.5466 |  |  | -9672.8997
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 24.2779 |  |  | 15.6167 |  |  | -57.1635 |  |  | -301.1901 |  |  | -902.5168 |  |  | -1956.6749 |  |  | -3508.215 |  |  | -5238.0105 |  |  | -7070.5466 |  |  | -9732.8997
[13 empty] | Press drop ratio this iteration |  |  | 0.28807 |  |  | 0.20653 |  |  | -20.1532 |  |  | 1.2488 |  |  | 1.0712 |  |  | 1.0316 |  |  | 1.0174 |  |  | 1.0116 |  |  | 1.0086 |  |  | 1.0062
[13 empty] | Expansion factor | 12 |  | 0.84997 |  |  | 0.89246 |  |  | 11.5935 |  |  | 0.33434 |  |  | 0.41127 |  |  | 0.399 |  |  | 0.36233 |  |  | 0.29111 |  |  | 0.43072 |  |  | 0.10961
[13 empty] | C Non choked w/ reducers | 7 |  | 81.4632 |  |  | 160.4845 |  |  | #NUM! |  |  | -262.6446 |  |  | -112.0895 |  |  | -78.047 |  |  | -65.8242 |  |  | -70.837 |  |  | -46.7974 |  |  | -209.5625
[13 empty] | C Choked w/ reducers | 7 |  | 69.6447 |  |  | 121.9647 |  |  | 8017.8353 |  |  | -186.0434 |  |  | -91.8514 |  |  | -62.6907 |  |  | -49.4565 |  |  | -45.0856 |  |  | -39.4922 |  |  | -56.2845
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 81.4632 |  |  | 160.4845 |  |  | #NUM! |  |  | -186.0434 |  |  | -91.8514 |  |  | -62.6907 |  |  | -49.4565 |  |  | -45.0856 |  |  | -39.4922 |  |  | -56.2845
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 76.7332 | 180028.6511 |  | 148.8845 | 282720.6526 |  | 236393 | 692279.0278 |  | 236393 | 1348382.8451 |  | 236393 | 2262166.9612 |  | 236393 | 3301694.2925 |  | 236393 | 4406123.8326 |  | 236393 | 5376308.4153 |  | 236393 | 6241727.1647 |  | 236393 | 7318915.9807
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 183629.2241 | C_100 - C this iteration | iteration | 285547.8591 | C_100 - C this iteration | iteration | 699201.8181 | C_100 - C this iteration | iteration | 1361866.6736 | C_100 - C this iteration | iteration | 2284788.6308 | C_100 - C this iteration | iteration | 3334711.2354 | C_100 - C this iteration | iteration | 4450185.0709 | C_100 - C this iteration | iteration | 5430071.4995 | C_100 - C this iteration | iteration | 6304144.4363 | C_100 - C this iteration | iteration | 7392105.1405 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 84.0393 |  |  | 75.3239 |  |  | 1.0807 |  |  | -247.8508 |  |  | -861.2641 |  |  | -1936.6108 |  |  | -3519.3369 |  |  | -5283.9012 |  |  | -7153.2713 |  |  | -9869.1377
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 24.0393 |  |  | 15.3239 |  |  | -58.9193 |  |  | -307.8508 |  |  | -921.2641 |  |  | -1996.6108 |  |  | -3579.3369 |  |  | -5343.9012 |  |  | -7213.2713 |  |  | -9929.1377
[13 empty] | Press drop ratio this iteration |  |  | 0.28605 |  |  | 0.20344 |  |  | -54.5172 |  |  | 1.2421 |  |  | 1.0697 |  |  | 1.031 |  |  | 1.017 |  |  | 1.0114 |  |  | 1.0084 |  |  | 1.0061
[13 empty] | Expansion factor | 12 |  | 0.85102 |  |  | 0.89407 |  |  | 29.6568 |  |  | 0.3379 |  |  | 0.41212 |  |  | 0.39938 |  |  | 0.36255 |  |  | 0.29127 |  |  | 0.43081 |  |  | 0.10972
[13 empty] | C Non choked w/ reducers | 7 |  | 83.5189 |  |  | 163.6539 |  |  | #NUM! |  |  | -256.1062 |  |  | -110.5972 |  |  | -77.1529 |  |  | -65.1106 |  |  | -70.0805 |  |  | -46.3158 |  |  | -207.2559
[13 empty] | C Choked w/ reducers | 7 |  | 71.2393 |  |  | 123.6632 |  |  | 21253.4942 |  |  | -182.8542 |  |  | -90.7506 |  |  | -62.0119 |  |  | -48.9416 |  |  | -44.6239 |  |  | -39.0913 |  |  | -55.717
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 83.5189 |  |  | 163.6539 |  |  | #NUM! |  |  | -182.8542 |  |  | -90.7506 |  |  | -62.0119 |  |  | -48.9416 |  |  | -44.6239 |  |  | -39.0913 |  |  | -55.717
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 78.7889 | 183629.2241 |  | 152.0539 | 285547.8591 |  | 236393 | 699201.8181 |  | 236393 | 1361866.6736 |  | 236393 | 2284788.6308 |  | 236393 | 3334711.2354 |  | 236393 | 4450185.0709 |  | 236393 | 5430071.4995 |  | 236393 | 6304144.4363 |  | 236393 | 7392105.1405
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 187301.8086 | C_100 - C this iteration | iteration | 288403.3377 | C_100 - C this iteration | iteration | 706193.8363 | C_100 - C this iteration | iteration | 1375485.3403 | C_100 - C this iteration | iteration | 2307636.5171 | C_100 - C this iteration | iteration | 3368058.3478 | C_100 - C this iteration | iteration | 4494686.9216 | C_100 - C this iteration | iteration | 5484372.2145 | C_100 - C this iteration | iteration | 6367185.8807 | C_100 - C this iteration | iteration | 7466026.1919 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 83.791 |  |  | 75.0252 |  |  | -0.71025 |  |  | -254.6453 |  |  | -880.3883 |  |  | -1977.3494 |  |  | -3591.8883 |  |  | -5391.9204 |  |  | -7298.8648 |  |  | -10069.3201
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 23.791 |  |  | 15.0252 |  |  | -60.7103 |  |  | -314.6453 |  |  | -940.3883 |  |  | -2037.3494 |  |  | -3651.8883 |  |  | -5451.9204 |  |  | -7358.8648 |  |  | -10129.3201
[13 empty] | Press drop ratio this iteration |  |  | 0.28393 |  |  | 0.20027 |  |  | 85.4773 |  |  | 1.2356 |  |  | 1.0682 |  |  | 1.0303 |  |  | 1.0167 |  |  | 1.0111 |  |  | 1.0082 |  |  | 1.006
[13 empty] | Expansion factor | 12 |  | 0.85213 |  |  | 0.89572 |  |  | -43.9309 |  |  | 0.34134 |  |  | 0.41296 |  |  | 0.39975 |  |  | 0.36277 |  |  | 0.29143 |  |  | 0.43091 |  |  | 0.10983
[13 empty] | C Non choked w/ reducers | 7 |  | 85.6485 |  |  | 166.949 |  |  | 42.7156 |  |  | -249.8764 |  |  | -109.1339 |  |  | -76.2716 |  |  | -64.4059 |  |  | -69.3332 |  |  | -45.8396 |  |  | -204.9794
[13 empty] | C Choked w/ reducers | 7 |  | 72.8794 |  |  | 125.3971 |  |  | -32663.6078 |  |  | -179.755 |  |  | -89.6671 |  |  | -61.3417 |  |  | -48.4326 |  |  | -44.1672 |  |  | -38.6946 |  |  | -55.1554
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 85.6485 |  |  | 166.949 |  |  | -32663.6078 |  |  | -179.755 |  |  | -89.6671 |  |  | -61.3417 |  |  | -48.4326 |  |  | -44.1672 |  |  | -38.6946 |  |  | -55.1554
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 80.9185 | 187301.8086 |  | 155.349 | 288403.3377 |  | 236393 | 706193.8363 |  | 236393 | 1375485.3403 |  | 236393 | 2307636.5171 |  | 236393 | 3368058.3478 |  | 236393 | 4494686.9216 |  | 236393 | 5484372.2145 |  | 236393 | 6367185.8807 |  | 236393 | 7466026.1919
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 191047.8447 | C_100 - C this iteration | iteration | 291287.3711 | C_100 - C this iteration | iteration | 713255.7746 | C_100 - C this iteration | iteration | 1389240.1937 | C_100 - C this iteration | iteration | 2330712.8822 | C_100 - C this iteration | iteration | 3401738.9313 | C_100 - C this iteration | iteration | 4539633.7908 | C_100 - C this iteration | iteration | 5539215.9366 | C_100 - C this iteration | iteration | 6430857.7395 | C_100 - C this iteration | iteration | 7540686.4539 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 83.5326 |  |  | 74.7205 |  |  | -2.5372 |  |  | -261.5764 |  |  | -899.8968 |  |  | -2018.9068 |  |  | -3665.8979 |  |  | -5502.1107 |  |  | -7447.3847 |  |  | -10273.5262
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 23.5326 |  |  | 14.7205 |  |  | -62.5372 |  |  | -321.5764 |  |  | -959.8968 |  |  | -2078.9068 |  |  | -3725.8979 |  |  | -5562.1107 |  |  | -7507.3847 |  |  | -10333.5262
[13 empty] | Press drop ratio this iteration |  |  | 0.28172 |  |  | 0.19701 |  |  | 24.6477 |  |  | 1.2294 |  |  | 1.0667 |  |  | 1.0297 |  |  | 1.0164 |  |  | 1.0109 |  |  | 1.0081 |  |  | 1.0058
[13 empty] | Expansion factor | 12 |  | 0.85328 |  |  | 0.89742 |  |  | -11.956 |  |  | 0.34467 |  |  | 0.41377 |  |  | 0.40012 |  |  | 0.36298 |  |  | 0.29159 |  |  | 0.431 |  |  | 0.10993
[13 empty] | C Non choked w/ reducers | 7 |  | 87.8565 |  |  | 170.3787 |  |  | 82.6378 |  |  | -243.9327 |  |  | -107.6986 |  |  | -75.4029 |  |  | -63.7102 |  |  | -68.5949 |  |  | -45.3687 |  |  | -202.7326
[13 empty] | C Choked w/ reducers | 7 |  | 74.5669 |  |  | 127.1676 |  |  | -9234.9456 |  |  | -176.7419 |  |  | -88.6005 |  |  | -60.6798 |  |  | -47.9293 |  |  | -43.7155 |  |  | -38.3022 |  |  | -54.5997
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 87.8565 |  |  | 170.3787 |  |  | -9234.9456 |  |  | -176.7419 |  |  | -88.6005 |  |  | -60.6798 |  |  | -47.9293 |  |  | -43.7155 |  |  | -38.3022 |  |  | -54.5997
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 83.1265 | 191047.8447 |  | 158.7787 | 291287.3711 |  | 236393 | 713255.7746 |  | 236393 | 1389240.1937 |  | 236393 | 2330712.8822 |  | 236393 | 3401738.9313 |  | 236393 | 4539633.7908 |  | 236393 | 5539215.9366 |  | 236393 | 6430857.7395 |  | 236393 | 7540686.4539
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 194868.8016 | C_100 - C this iteration | iteration | 294200.2448 | C_100 - C this iteration | iteration | 720388.3324 | C_100 - C this iteration | iteration | 1403132.5957 | C_100 - C this iteration | iteration | 2354020.0111 | C_100 - C this iteration | iteration | 3435756.3206 | C_100 - C this iteration | iteration | 4585030.1288 | C_100 - C this iteration | iteration | 5594608.096 | C_100 - C this iteration | iteration | 6495166.3169 | C_100 - C this iteration | iteration | 7616093.3184 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 83.2639 |  |  | 74.4097 |  |  | -4.401 |  |  | -268.6468 |  |  | -919.7974 |  |  | -2061.2996 |  |  | -3741.3952 |  |  | -5614.5158 |  |  | -7598.8898 |  |  | -10481.8368
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 23.2639 |  |  | 14.4097 |  |  | -64.401 |  |  | -328.6468 |  |  | -979.7974 |  |  | -2121.2996 |  |  | -3801.3952 |  |  | -5674.5158 |  |  | -7658.8898 |  |  | -10541.8368
[13 empty] | Press drop ratio this iteration |  |  | 0.2794 |  |  | 0.19365 |  |  | 14.6334 |  |  | 1.2233 |  |  | 1.0652 |  |  | 1.0291 |  |  | 1.016 |  |  | 1.0107 |  |  | 1.0079 |  |  | 1.0057
[13 empty] | Expansion factor | 12 |  | 0.85449 |  |  | 0.89917 |  |  | -6.692 |  |  | 0.34789 |  |  | 0.41456 |  |  | 0.40047 |  |  | 0.36319 |  |  | 0.29174 |  |  | 0.43109 |  |  | 0.11003
[13 empty] | C Non choked w/ reducers | 7 |  | 90.1475 |  |  | 173.953 |  |  | 111.5733 |  |  | -238.2545 |  |  | -106.2905 |  |  | -74.5465 |  |  | -63.0231 |  |  | -67.8655 |  |  | -44.9029 |  |  | -200.5149
[13 empty] | C Choked w/ reducers | 7 |  | 76.3037 |  |  | 128.9758 |  |  | -5377.3764 |  |  | -173.8112 |  |  | -87.5503 |  |  | -60.0262 |  |  | -47.4318 |  |  | -43.2687 |  |  | -37.9139 |  |  | -54.0497
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 90.1475 |  |  | 173.953 |  |  | -5377.3764 |  |  | -173.8112 |  |  | -87.5503 |  |  | -60.0262 |  |  | -47.4318 |  |  | -43.2687 |  |  | -37.9139 |  |  | -54.0497
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 85.4175 | 194868.8016 |  | 162.353 | 294200.2448 |  | 236393 | 720388.3324 |  | 236393 | 1403132.5957 |  | 236393 | 2354020.0111 |  | 236393 | 3435756.3206 |  | 236393 | 4585030.1288 |  | 236393 | 5594608.096 |  | 236393 | 6495166.3169 |  | 236393 | 7616093.3184
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 198766.1777 | C_100 - C this iteration | iteration | 297142.2473 | C_100 - C this iteration | iteration | 727592.2157 | C_100 - C this iteration | iteration | 1417163.9216 | C_100 - C this iteration | iteration | 2377560.2112 | C_100 - C this iteration | iteration | 3470113.8838 | C_100 - C this iteration | iteration | 4630880.43 | C_100 - C this iteration | iteration | 5650554.1769 | C_100 - C this iteration | iteration | 6560117.98 | C_100 - C this iteration | iteration | 7692254.2516 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 82.9843 |  |  | 74.0926 |  |  | -6.3021 |  |  | -275.8593 |  |  | -940.0981 |  |  | -2104.5444 |  |  | -3818.41 |  |  | -5729.1803 |  |  | -7753.4402 |  |  | -10694.3344
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 22.9843 |  |  | 14.0926 |  |  | -66.3021 |  |  | -335.8593 |  |  | -1000.0981 |  |  | -2164.5444 |  |  | -3878.41 |  |  | -5789.1803 |  |  | -7813.4402 |  |  | -10754.3344
[13 empty] | Press drop ratio this iteration |  |  | 0.27697 |  |  | 0.1902 |  |  | 10.5206 |  |  | 1.2175 |  |  | 1.0638 |  |  | 1.0285 |  |  | 1.0157 |  |  | 1.0105 |  |  | 1.0077 |  |  | 1.0056
[13 empty] | Expansion factor | 12 |  | 0.85575 |  |  | 0.90096 |  |  | -4.5301 |  |  | 0.351 |  |  | 0.41533 |  |  | 0.40082 |  |  | 0.36339 |  |  | 0.29189 |  |  | 0.43118 |  |  | 0.11013
[13 empty] | C Non choked w/ reducers | 7 |  | 92.5269 |  |  | 177.6827 |  |  | 137.1011 |  |  | -232.8236 |  |  | -104.9088 |  |  | -73.7021 |  |  | -62.3446 |  |  | -67.1449 |  |  | -44.4422 |  |  | -198.3257
[13 empty] | C Choked w/ reducers | 7 |  | 78.092 |  |  | 130.823 |  |  | -3792.7252 |  |  | -170.9595 |  |  | -86.5164 |  |  | -59.3807 |  |  | -46.9399 |  |  | -42.8268 |  |  | -37.5297 |  |  | -53.5055
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 92.5269 |  |  | 177.6827 |  |  | -3792.7252 |  |  | -170.9595 |  |  | -86.5164 |  |  | -59.3807 |  |  | -46.9399 |  |  | -42.8268 |  |  | -37.5297 |  |  | -53.5055
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 87.7969 | 198766.1777 |  | 166.0827 | 297142.2473 |  | 236393 | 727592.2157 |  | 236393 | 1417163.9216 |  | 236393 | 2377560.2112 |  | 236393 | 3470113.8838 |  | 236393 | 4630880.43 |  | 236393 | 5650554.1769 |  | 236393 | 6560117.98 |  | 236393 | 7692254.2516
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 202741.5012 | C_100 - C this iteration | iteration | 300113.6697 | C_100 - C this iteration | iteration | 734868.1379 | C_100 - C this iteration | iteration | 1431335.5608 | C_100 - C this iteration | iteration | 2401335.8133 | C_100 - C this iteration | iteration | 3504815.0226 | C_100 - C this iteration | iteration | 4677189.2343 | C_100 - C this iteration | iteration | 5707059.7187 | C_100 - C this iteration | iteration | 6625719.1598 | C_100 - C this iteration | iteration | 7769176.7941 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 82.6934 |  |  | 73.7691 |  |  | -8.2415 |  |  | -283.2168 |  |  | -960.8068 |  |  | -2148.6585 |  |  | -3896.9727 |  |  | -5846.1496 |  |  | -7911.0971 |  |  | -10911.1033
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 22.6934 |  |  | 13.7691 |  |  | -68.2415 |  |  | -343.2168 |  |  | -1020.8068 |  |  | -2208.6585 |  |  | -3956.9727 |  |  | -5906.1496 |  |  | -7971.0971 |  |  | -10971.1033
[13 empty] | Press drop ratio this iteration |  |  | 0.27443 |  |  | 0.18665 |  |  | 8.2802 |  |  | 1.2119 |  |  | 1.0624 |  |  | 1.0279 |  |  | 1.0154 |  |  | 1.0103 |  |  | 1.0076 |  |  | 1.0055
[13 empty] | Expansion factor | 12 |  | 0.85708 |  |  | 0.90281 |  |  | -3.3525 |  |  | 0.35401 |  |  | 0.41609 |  |  | 0.40116 |  |  | 0.36359 |  |  | 0.29203 |  |  | 0.43127 |  |  | 0.11023
[13 empty] | C Non choked w/ reducers | 7 |  | 95.0003 |  |  | 181.5802 |  |  | 161.2822 |  |  | -227.6231 |  |  | -103.5527 |  |  | -72.8696 |  |  | -61.6746 |  |  | -66.433 |  |  | -43.9866 |  |  | -196.1647
[13 empty] | C Choked w/ reducers | 7 |  | 79.9341 |  |  | 132.7106 |  |  | -2929.2259 |  |  | -168.1834 |  |  | -85.4982 |  |  | -58.7431 |  |  | -46.4535 |  |  | -42.3896 |  |  | -37.1497 |  |  | -52.967
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 95.0003 |  |  | 181.5802 |  |  | -2929.2259 |  |  | -168.1834 |  |  | -85.4982 |  |  | -58.7431 |  |  | -46.4535 |  |  | -42.3896 |  |  | -37.1497 |  |  | -52.967
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 90.2703 | 202741.5012 |  | 169.9802 | 300113.6697 |  | 236393 | 734868.1379 |  | 236393 | 1431335.5608 |  | 236393 | 2401335.8133 |  | 236393 | 3504815.0226 |  | 236393 | 4677189.2343 |  | 236393 | 5707059.7187 |  | 236393 | 6625719.1598 |  | 236393 | 7769176.7941
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 206796.3312 | C_100 - C this iteration | iteration | 303114.8064 | C_100 - C this iteration | iteration | 742216.8192 | C_100 - C this iteration | iteration | 1445648.9164 | C_100 - C this iteration | iteration | 2425349.1714 | C_100 - C this iteration | iteration | 3539863.1728 | C_100 - C this iteration | iteration | 4723961.1267 | C_100 - C this iteration | iteration | 5764130.3159 | C_100 - C this iteration | iteration | 6691976.3514 | C_100 - C this iteration | iteration | 7846868.562 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 82.3907 |  |  | 73.4392 |  |  | -10.2199 |  |  | -290.7222 |  |  | -981.9317 |  |  | -2193.6592 |  |  | -3977.1146 |  |  | -5965.4699 |  |  | -8071.9229 |  |  | -11132.2291
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 22.3907 |  |  | 13.4392 |  |  | -70.2199 |  |  | -350.7222 |  |  | -1041.9317 |  |  | -2253.6592 |  |  | -4037.1146 |  |  | -6025.4699 |  |  | -8131.9229 |  |  | -11192.2291
[13 empty] | Press drop ratio this iteration |  |  | 0.27176 |  |  | 0.183 |  |  | 6.8709 |  |  | 1.2064 |  |  | 1.0611 |  |  | 1.0274 |  |  | 1.0151 |  |  | 1.0101 |  |  | 1.0074 |  |  | 1.0054
[13 empty] | Expansion factor | 12 |  | 0.85846 |  |  | 0.90472 |  |  | -2.6117 |  |  | 0.35693 |  |  | 0.41683 |  |  | 0.4015 |  |  | 0.36378 |  |  | 0.29218 |  |  | 0.43135 |  |  | 0.11033
[13 empty] | C Non choked w/ reducers | 7 |  | 97.574 |  |  | 185.659 |  |  | 185.1096 |  |  | -222.6378 |  |  | -102.2215 |  |  | -72.0486 |  |  | -61.0128 |  |  | -65.7296 |  |  | -43.536 |  |  | -194.0313
[13 empty] | C Choked w/ reducers | 7 |  | 81.8323 |  |  | 134.64 |  |  | -2385.807 |  |  | -165.4799 |  |  | -84.4954 |  |  | -58.1135 |  |  | -45.9726 |  |  | -41.9571 |  |  | -36.7736 |  |  | -52.434
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 97.574 |  |  | 185.659 |  |  | -2385.807 |  |  | -165.4799 |  |  | -84.4954 |  |  | -58.1135 |  |  | -45.9726 |  |  | -41.9571 |  |  | -36.7736 |  |  | -52.434
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 92.844 | 206796.3312 |  | 174.059 | 303114.8064 |  | 236393 | 742216.8192 |  | 236393 | 1445648.9164 |  | 236393 | 2425349.1714 |  | 236393 | 3539863.1728 |  | 236393 | 4723961.1267 |  | 236393 | 5764130.3159 |  | 236393 | 6691976.3514 |  | 236393 | 7846868.562
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 210932.2579 | C_100 - C this iteration | iteration | 306145.9545 | C_100 - C this iteration | iteration | 749638.9874 | C_100 - C this iteration | iteration | 1460105.4056 | C_100 - C this iteration | iteration | 2449602.6631 | C_100 - C this iteration | iteration | 3575261.8046 | C_100 - C this iteration | iteration | 4771200.7379 | C_100 - C this iteration | iteration | 5821771.619 | C_100 - C this iteration | iteration | 6758896.115 | C_100 - C this iteration | iteration | 7925337.2477 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 82.0758 |  |  | 73.1026 |  |  | -12.238 |  |  | -298.3784 |  |  | -1003.4813 |  |  | -2239.5645 |  |  | -4058.8673 |  |  | -6087.1885 |  |  | -8235.9812 |  |  | -11357.7997
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 22.0758 |  |  | 13.1026 |  |  | -72.238 |  |  | -358.3784 |  |  | -1063.4813 |  |  | -2299.5645 |  |  | -4118.8673 |  |  | -6147.1885 |  |  | -8295.9812 |  |  | -11417.7997
[13 empty] | Press drop ratio this iteration |  |  | 0.26897 |  |  | 0.17924 |  |  | 5.9027 |  |  | 1.2011 |  |  | 1.0598 |  |  | 1.0268 |  |  | 1.0148 |  |  | 1.0099 |  |  | 1.0073 |  |  | 1.0053
[13 empty] | Expansion factor | 12 |  | 0.85992 |  |  | 0.90667 |  |  | -2.1028 |  |  | 0.35975 |  |  | 0.41755 |  |  | 0.40182 |  |  | 0.36397 |  |  | 0.29232 |  |  | 0.43143 |  |  | 0.11042
[13 empty] | C Non choked w/ reducers | 7 |  | 100.2549 |  |  | 189.9344 |  |  | 209.2149 |  |  | -217.8538 |  |  | -100.9146 |  |  | -71.2391 |  |  | -60.3592 |  |  | -65.0345 |  |  | -43.0903 |  |  | -191.9249
[13 empty] | C Choked w/ reducers | 7 |  | 83.7892 |  |  | 136.6125 |  |  | -2012.2945 |  |  | -162.8462 |  |  | -83.5077 |  |  | -57.4915 |  |  | -45.4971 |  |  | -41.5293 |  |  | -36.4015 |  |  | -51.9066
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 100.2549 |  |  | 189.9344 |  |  | -2012.2945 |  |  | -162.8462 |  |  | -83.5077 |  |  | -57.4915 |  |  | -45.4971 |  |  | -41.5293 |  |  | -36.4015 |  |  | -51.9066
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 95.5249 | 210932.2579 |  | 178.3344 | 306145.9545 |  | 236393 | 749638.9874 |  | 236393 | 1460105.4056 |  | 236393 | 2449602.6631 |  | 236393 | 3575261.8046 |  | 236393 | 4771200.7379 |  | 236393 | 5821771.619 |  | 236393 | 6758896.115 |  | 236393 | 7925337.2477
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 215150.903 | C_100 - C this iteration | iteration | 309207.4141 | C_100 - C this iteration | iteration | 757135.3773 | C_100 - C this iteration | iteration | 1474706.4597 | C_100 - C this iteration | iteration | 2474098.6898 | C_100 - C this iteration | iteration | 3611014.4226 | C_100 - C this iteration | iteration | 4818912.7453 | C_100 - C this iteration | iteration | 5879989.3352 | C_100 - C this iteration | iteration | 6826485.0761 | C_100 - C this iteration | iteration | 8004590.6201 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 81.7482 |  |  | 72.7592 |  |  | -14.2968 |  |  | -306.1885 |  |  | -1025.4639 |  |  | -2286.3925 |  |  | -4142.2633 |  |  | -6211.3537 |  |  | -8403.3372 |  |  | -11587.9042
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 21.7482 |  |  | 12.7592 |  |  | -74.2968 |  |  | -366.1885 |  |  | -1085.4639 |  |  | -2346.3925 |  |  | -4202.2633 |  |  | -6271.3537 |  |  | -8463.3372 |  |  | -11647.9042
[13 empty] | Press drop ratio this iteration |  |  | 0.26604 |  |  | 0.17536 |  |  | 5.1968 |  |  | 1.196 |  |  | 1.0585 |  |  | 1.0262 |  |  | 1.0145 |  |  | 1.0097 |  |  | 1.0071 |  |  | 1.0052
[13 empty] | Expansion factor | 12 |  | 0.86144 |  |  | 0.90869 |  |  | -1.7317 |  |  | 0.36249 |  |  | 0.41825 |  |  | 0.40214 |  |  | 0.36416 |  |  | 0.29246 |  |  | 0.43152 |  |  | 0.11052
[13 empty] | C Non choked w/ reducers | 7 |  | 103.0507 |  |  | 194.4234 |  |  | 234.0865 |  |  | -213.2583 |  |  | -99.6311 |  |  | -70.4406 |  |  | -59.7136 |  |  | -64.3477 |  |  | -42.6494 |  |  | -189.8453
[13 empty] | C Choked w/ reducers | 7 |  | 85.8075 |  |  | 138.6297 |  |  | -1739.7533 |  |  | -160.2793 |  |  | -82.5347 |  |  | -56.8772 |  |  | -45.0269 |  |  | -41.1062 |  |  | -36.0333 |  |  | -51.3846
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 103.0507 |  |  | 194.4234 |  |  | -1739.7533 |  |  | -160.2793 |  |  | -82.5347 |  |  | -56.8772 |  |  | -45.0269 |  |  | -41.1062 |  |  | -36.0333 |  |  | -51.3846
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 98.3207 | 215150.903 |  | 182.8234 | 309207.4141 |  | 236393 | 757135.3773 |  | 236393 | 1474706.4597 |  | 236393 | 2474098.6898 |  | 236393 | 3611014.4226 |  | 236393 | 4818912.7453 |  | 236393 | 5879989.3352 |  | 236393 | 6826485.0761 |  | 236393 | 8004590.6201
[17 empty] | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this |  | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 219453.9211 | C_100 - C this iteration | iteration | 312299.4882 | C_100 - C this iteration | iteration | 764706.7311 | C_100 - C this iteration | iteration | 1489453.5242 | C_100 - C this iteration | iteration | 2498839.6767 | C_100 - C this iteration | iteration | 3647124.5668 | C_100 - C this iteration | iteration | 4867101.8728 | C_100 - C this iteration | iteration | 5938789.2286 | C_100 - C this iteration | iteration | 6894749.9269 | C_100 - C this iteration | iteration | 8084636.5263 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 81.4074 |  |  | 72.409 |  |  | -16.3968 |  |  | -314.1557 |  |  | -1047.8885 |  |  | -2334.1617 |  |  | -4227.3355 |  |  | -6338.0147 |  |  | -8574.057 |  |  | -11822.6338
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 21.4074 |  |  | 12.409 |  |  | -76.3968 |  |  | -374.1557 |  |  | -1107.8885 |  |  | -2394.1617 |  |  | -4287.3355 |  |  | -6398.0147 |  |  | -8634.057 |  |  | -11882.6338
[13 empty] | Press drop ratio this iteration |  |  | 0.26297 |  |  | 0.17137 |  |  | 4.6592 |  |  | 1.191 |  |  | 1.0573 |  |  | 1.0257 |  |  | 1.0142 |  |  | 1.0095 |  |  | 1.007 |  |  | 1.0051
[13 empty] | Expansion factor | 12 |  | 0.86304 |  |  | 0.91077 |  |  | -1.4491 |  |  | 0.36514 |  |  | 0.41894 |  |  | 0.40246 |  |  | 0.36434 |  |  | 0.29259 |  |  | 0.4316 |  |  | 0.11061
[13 empty] | C Non choked w/ reducers | 7 |  | 105.9699 |  |  | 199.1456 |  |  | 260.1614 |  |  | -208.8398 |  |  | -98.3704 |  |  | -69.6531 |  |  | -59.0758 |  |  | -63.669 |  |  | -42.2133 |  |  | -187.7918
[13 empty] | C Choked w/ reducers | 7 |  | 87.8901 |  |  | 140.6933 |  |  | -1532.0974 |  |  | -157.7767 |  |  | -81.5762 |  |  | -56.2703 |  |  | -44.562 |  |  | -40.6875 |  |  | -35.669 |  |  | -50.868
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 105.9699 |  |  | 199.1456 |  |  | -1532.0974 |  |  | -157.7767 |  |  | -81.5762 |  |  | -56.2703 |  |  | -44.562 |  |  | -40.6875 |  |  | -35.669 |  |  | -50.868
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 101.2399 | 219453.9211 |  | 187.5456 | 312299.4882 |  | 236393 | 764706.7311 |  | 236393 | 1489453.5242 |  | 236393 | 2498839.6767 |  | 236393 | 3647124.5668 |  | 236393 | 4867101.8728 |  | 236393 | 5938789.2286 |  | 236393 | 6894749.9269 |  | 236393 | 8084636.5263
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 223842.9995 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 81.0527
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 21.0527
[13 empty] | Press drop ratio this iteration |  |  | 0.25974
[13 empty] | Expansion factor | 12 |  | 0.86472
[13 empty] | C Non choked w/ reducers | 7 |  | 109.0219
[13 empty] | C Choked w/ reducers | 7 |  | 90.0401
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 109.0219
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 104.2919 | 223842.9995
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 228319.8595 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 80.6838
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 20.6838
[13 empty] | Press drop ratio this iteration |  |  | 0.25636
[13 empty] | Expansion factor | 12 |  | 0.86649
[13 empty] | C Non choked w/ reducers | 7 |  | 112.2172
[13 empty] | C Choked w/ reducers | 7 |  | 92.2609
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 112.2172
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 107.4872 | 228319.8595
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 232886.2567 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 80.2999
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 20.2999
[13 empty] | Press drop ratio this iteration |  |  | 0.2528
[13 empty] | Expansion factor | 12 |  | 0.86834
[13 empty] | C Non choked w/ reducers | 7 |  | 115.5675
[13 empty] | C Choked w/ reducers | 7 |  | 94.5559
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 115.5675
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 110.8375 | 232886.2567
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 237543.9818 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 79.9006
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 19.9006
[13 empty] | Press drop ratio this iteration |  |  | 0.24907
[13 empty] | Expansion factor | 12 |  | 0.87028
[13 empty] | C Non choked w/ reducers | 7 |  | 119.0862
[13 empty] | C Choked w/ reducers | 7 |  | 96.9291
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 119.0862
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 114.3562 | 237543.9818
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 242294.8615 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 79.4851
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 19.4851
[13 empty] | Press drop ratio this iteration |  |  | 0.24514
[13 empty] | Expansion factor | 12 |  | 0.87233
[13 empty] | C Non choked w/ reducers | 7 |  | 122.7881
[13 empty] | C Choked w/ reducers | 7 |  | 99.3845
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 122.7881
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 118.0581 | 242294.8615
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 247140.7587 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 79.0528
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 19.0528
[13 empty] | Press drop ratio this iteration |  |  | 0.24101
[13 empty] | Expansion factor | 12 |  | 0.87448
[13 empty] | C Non choked w/ reducers | 7 |  | 126.6903
[13 empty] | C Choked w/ reducers | 7 |  | 101.9265
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 126.6903
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 121.9603 | 247140.7587
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 252083.5739 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 78.6031
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 18.6031
[13 empty] | Press drop ratio this iteration |  |  | 0.23667
[13 empty] | Expansion factor | 12 |  | 0.87674
[13 empty] | C Non choked w/ reducers | 7 |  | 130.8121
[13 empty] | C Choked w/ reducers | 7 |  | 104.5599
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 130.8121
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 126.0821 | 252083.5739
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 257125.2453 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 78.1352
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 18.1352
[13 empty] | Press drop ratio this iteration |  |  | 0.2321
[13 empty] | Expansion factor | 12 |  | 0.87912
[13 empty] | C Non choked w/ reducers | 7 |  | 135.1757
[13 empty] | C Choked w/ reducers | 7 |  | 107.2898
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 135.1757
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 130.4457 | 257125.2453
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 262267.7502 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 77.6483
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 17.6483
[13 empty] | Press drop ratio this iteration |  |  | 0.22729
[13 empty] | Expansion factor | 12 |  | 0.88163
[13 empty] | C Non choked w/ reducers | 7 |  | 139.8066
[13 empty] | C Choked w/ reducers | 7 |  | 110.1217
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 139.8066
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 135.0766 | 262267.7502
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 267513.1052 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 77.1419
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 17.1419
[13 empty] | Press drop ratio this iteration |  |  | 0.22221
[13 empty] | Expansion factor | 12 |  | 0.88427
[13 empty] | C Non choked w/ reducers | 7 |  | 144.7346
[13 empty] | C Choked w/ reducers | 7 |  | 113.0616
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 144.7346
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 140.0046 | 267513.1052
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 272863.3674 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 76.6149
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 16.6149
[13 empty] | Press drop ratio this iteration |  |  | 0.21686
[13 empty] | Expansion factor | 12 |  | 0.88706
[13 empty] | C Non choked w/ reducers | 7 |  | 149.9942
[13 empty] | C Choked w/ reducers | 7 |  | 116.116
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 149.9942
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 145.2642 | 272863.3674
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 278320.6347 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 76.0667
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 16.0667
[13 empty] | Press drop ratio this iteration |  |  | 0.21122
[13 empty] | Expansion factor | 12 |  | 0.89
[13 empty] | C Non choked w/ reducers | 7 |  | 155.6264
[13 empty] | C Choked w/ reducers | 7 |  | 119.2919
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 155.6264
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 150.8964 | 278320.6347
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 283887.0474 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 75.4963
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 15.4963
[13 empty] | Press drop ratio this iteration |  |  | 0.20526
[13 empty] | Expansion factor | 12 |  | 0.8931
[13 empty] | C Non choked w/ reducers | 7 |  | 161.6796
[13 empty] | C Choked w/ reducers | 7 |  | 122.5971
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 161.6796
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 156.9496 | 283887.0474
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 289564.7883 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 74.9029
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 14.9029
[13 empty] | Press drop ratio this iteration |  |  | 0.19896
[13 empty] | Expansion factor | 12 |  | 0.89638
[13 empty] | C Non choked w/ reducers | 7 |  | 168.2117
[13 empty] | C Choked w/ reducers | 7 |  | 126.0397
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 168.2117
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 163.4817 | 289564.7883
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 295356.0841 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 74.2855
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 14.2855
[13 empty] | Press drop ratio this iteration |  |  | 0.19231
[13 empty] | Expansion factor | 12 |  | 0.89985
[13 empty] | C Non choked w/ reducers | 7 |  | 175.293
[13 empty] | C Choked w/ reducers | 7 |  | 129.629
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 175.293
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 170.563 | 295356.0841
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 301263.2058 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 73.6431
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 13.6431
[13 empty] | Press drop ratio this iteration |  |  | 0.18526
[13 empty] | Expansion factor | 12 |  | 0.90351
[13 empty] | C Non choked w/ reducers | 7 |  | 183.0095
[13 empty] | C Choked w/ reducers | 7 |  | 133.3749
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 183.0095
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 178.2795 | 301263.2058
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 307288.4699 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 72.9748
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 12.9748
[13 empty] | Press drop ratio this iteration |  |  | 0.1778
[13 empty] | Expansion factor | 12 |  | 0.9074
[13 empty] | C Non choked w/ reducers | 7 |  | 191.4678
[13 empty] | C Choked w/ reducers | 7 |  | 137.2882
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 191.4678
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 186.7378 | 307288.4699
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 313434.2393 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 72.2795
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 12.2795
[13 empty] | Press drop ratio this iteration |  |  | 0.16989
[13 empty] | Expansion factor | 12 |  | 0.91152
[13 empty] | C Non choked w/ reducers | 7 |  | 200.8018
[13 empty] | C Choked w/ reducers | 7 |  | 141.381
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 200.8018
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 196.0718 | 313434.2393
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 319702.9241 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 71.5562
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 11.5562
[13 empty] | Press drop ratio this iteration |  |  | 0.1615
[13 empty] | Expansion factor | 12 |  | 0.91589
[13 empty] | C Non choked w/ reducers | 7 |  | 211.1829
[13 empty] | C Choked w/ reducers | 7 |  | 145.6665
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 211.1829
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 206.4529 | 319702.9241
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 326096.9826 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 70.8036
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 10.8036
[13 empty] | Press drop ratio this iteration |  |  | 0.15258
[13 empty] | Expansion factor | 12 |  | 0.92053
[13 empty] | C Non choked w/ reducers | 7 |  | 222.8347
[13 empty] | C Choked w/ reducers | 7 |  | 150.1592
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 222.8347
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 218.1047 | 326096.9826
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 332618.9222 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 70.0205
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 10.0205
[13 empty] | Press drop ratio this iteration |  |  | 0.14311
[13 empty] | Expansion factor | 12 |  | 0.92547
[13 empty] | C Non choked w/ reducers | 7 |  | 236.0551
[13 empty] | C Choked w/ reducers | 7 |  | 154.8751
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 236.0551
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 231.3251 | 332618.9222
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 339271.3007 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 69.2059
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 9.2059
[13 empty] | Press drop ratio this iteration |  |  | 0.13302
[13 empty] | Expansion factor | 12 |  | 0.93072
[13 empty] | C Non choked w/ reducers | 7 |  | 251.2517
[13 empty] | C Choked w/ reducers | 7 |  | 159.8322
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 251.2517
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 246.5217 | 339271.3007
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 346056.7267 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 68.3583
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 8.3583
[13 empty] | Press drop ratio this iteration |  |  | 0.12227
[13 empty] | Expansion factor | 12 |  | 0.93632
[13 empty] | C Non choked w/ reducers | 7 |  | 269.0008
[13 empty] | C Choked w/ reducers | 7 |  | 165.0502
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 269.0008
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 264.2708 | 346056.7267
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 352977.8612 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 67.4765
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 7.4765
[13 empty] | Press drop ratio this iteration |  |  | 0.1108
[13 empty] | Expansion factor | 12 |  | 0.94229
[13 empty] | C Non choked w/ reducers | 7 |  | 290.1487
[13 empty] | C Choked w/ reducers | 7 |  | 170.5512
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 290.1487
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 285.4187 | 352977.8612
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 360037.4184 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 66.5591
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 6.5591
[13 empty] | Press drop ratio this iteration |  |  | 0.098546
[13 empty] | Expansion factor | 12 |  | 0.94868
[13 empty] | C Non choked w/ reducers | 7 |  | 316.0015
[13 empty] | C Choked w/ reducers | 7 |  | 176.3601
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 316.0015
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 311.2715 | 360037.4184
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 367238.1668 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 65.6046
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 5.6046
[13 empty] | Press drop ratio this iteration |  |  | 0.08543
[13 empty] | Expansion factor | 12 |  | 0.95551
[13 empty] | C Non choked w/ reducers | 7 |  | 348.7059
[13 empty] | C Choked w/ reducers | 7 |  | 182.5045
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 348.7059
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 343.9759 | 367238.1668
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 374582.9301 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 64.6116
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 4.6116
[13 empty] | Press drop ratio this iteration |  |  | 0.071374
[13 empty] | Expansion factor | 12 |  | 0.96283
[13 empty] | C Non choked w/ reducers | 7 |  | 392.1077
[13 empty] | C Choked w/ reducers | 7 |  | 189.0156
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 392.1077
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 387.3777 | 374582.9301
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 382074.5887 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 63.5784
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 3.5784
[13 empty] | Press drop ratio this iteration |  |  | 0.056283
[13 empty] | Expansion factor | 12 |  | 0.97069
[13 empty] | C Non choked w/ reducers | 7 |  | 453.999
[13 empty] | C Choked w/ reducers | 7 |  | 195.929
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 453.999
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 449.269 | 382074.5887
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 389716.0805 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 62.5035
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 2.5035
[13 empty] | Press drop ratio this iteration |  |  | 0.040054
[13 empty] | Expansion factor | 12 |  | 0.97914
[13 empty] | C Non choked w/ reducers | 7 |  | 553.5583
[13 empty] | C Choked w/ reducers | 7 |  | 203.2844
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 553.5583
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 548.8283 | 389716.0805
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 397510.4021 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 61.3852
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 1.3852
[13 empty] | Press drop ratio this iteration |  |  | 0.022565
[13 empty] | Expansion factor | 12 |  | 0.98825
[13 empty] | C Non choked w/ reducers | 7 |  | 758.9014
[13 empty] | C Choked w/ reducers | 7 |  | 211.1277
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 758.9014
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 754.1714 | 397510.4021
[17 empty] | Abs Value of | Flow this
[13 empty] | Next iteration flow rate |  |  | 405460.6102 | C_100 - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 60.2217
[13 empty] | P2 at this iteration flow rate |  |  | 60
[13 empty] | Delta P at this iteration flow rate |  |  | 0.22166
[13 empty] | Press drop ratio this iteration |  |  | 0.0036807
[13 empty] | Expansion factor | 12 |  | 0.99808
[13 empty] | C Non choked w/ reducers | 7 |  | 1934.4277
[13 empty] | C Choked w/ reducers | 7 |  | 219.5109
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003
[13 empty] | Selected C this iteration |  |  | 1934.4277
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1929.6977 | 405460.6102

## Installed Gain
NO USER INPUT IS REQUIRED FOR THIS TAB.
BALL_SEG
3
PV123
Qmax = maximum
[8 empty] | design flow = | 236393
Qmin = minimum
[8 empty] | design flow = | 31863
[8 empty] | Flow units are | scfh
Graph Data
Valve relative travel, h | 0 | 0.05 | 0.1 | 0.15 | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.55 | 0.6 | 0.65 | 0.7 | 0.75 | 0.8 | 0.85 | 0.9 | 0.95 | 1
Relative flow Q/Qmax | 0 | 0.024766 | 0.049532 | 0.085408 | 0.12128 | 0.17876 | 0.23623 | 0.31628 | 0.39632 | 0.48738 | 0.57845 | 0.67519 | 0.77194 | 0.85692 | 0.94191 | 1.0177 | 1.0935 | 1.1879 | 1.2822 | 1.3354 | 1.3885 | 0.13479 | 0.13479 | 1 | 1
Gain = Delta Q / Delta h |  | 0.49532 | 0.60642 | 0.71753 | 0.9335 | 1.1495 | 1.3752 | 1.6009 | 1.7111 | 1.8212 | 1.8781 | 1.9349 | 1.8173 | 1.6997 | 1.608 | 1.5162 | 1.7017 | 1.8872 | 1.4748 | 1.0624
Qmin vertical line | [21 empty] | 0 | 4
Qmax vertical line | [23 empty] | 0 | 4
Delta Q |  | 0.049532 | 0.060642 | 0.071753 | 0.09335 | 0.11495 | 0.13752 | 0.16009 | 0.17111 | 0.18212 | 0.18781 | 0.19349 | 0.18173 | 0.16997 | 0.1608 | 0.15162 | 0.17017 | 0.18872 | 0.14748 | 0.10624
Delta h |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1

## xT Fd AEta Stp
Intermediate calculations
THE ONLY USER ACTION ON THIS TAB IS TO OPTIONALLY COPY xT VALLUES
[8 empty] | DESCRIPTION OF VARIABLE | NAME OF VARIABLE | FORMULA
Typical xT values based on the Reqired C and Valve size shown on the |  |  |  |  | For initial calculations (before |  |  | CALCULATED IN COLUMN "O" | CALCULATED IN COLUMN "O"
Valve Sizing tab. They can be copied to the the Valve Sizing tab. |  |  |  |  | the Cv is known), consider using
[5 empty] | the xT values listed below. |  |  | Capacity in units of Cv | C_v | 12.9194 | 39.4405 | 90.6476 | 136.9874
Flow | 31863 | 27000 | 65000 | 94000 | Minimum | Maximum |  | Valve size in units of inch | d_in | 3
Valve type | Choked press drop ratio factor, xT |  |  |  | Flow | Flow |  |  | Cv_over_d_Sq | 1.4355 | 4.3823 | 10.072 | 15.2208
INSTRUCTIONS FOR xT CALCULATIONS
Globe, 4 port cage | 0.7325 | 0.72087 | 0.7 | 0.7 | 0.74 | 0.72 | Perform initial valve sizing useing the suggested xT values in Columns H & I.
Fine tune xT values on Valve sizing tab as follows:
Globe, Parabolic plug | 0.60801 | 0.6 | 0.6 | 0.6 | 0.62 | 0.6
1. Copy xT values: Highlight all 4 columns in the row for the valve type
Rotary eccentric plug | 0.62 | 0.62 | 0.55011 | 0.399 | 0.62 | 0.52 | you are sizing.
2. Press Ctrl + C
Segment ball | 0.64 | 0.62307 | 0.55446 | 0.44972 | 0.64 | 0.4 | 3. Go to the Valve Sizing tab
4. Right Click on D9.
Butterfly | 0.693 | 0.66213 | 0.57217 | 0.49077 | 0.68 | 0.37 | 5. From "Paste Options" Select "Values"
Full ball (Full and reduced port) | 0.82 | 0.75905 | 0.62087 | 0.51853 | 0.82 | 0.3 | You may need to repeat Steps 1 through 5 one or two more times until
the xT values on this tab agree closely with what are on the Valve Sizing tab.
Typical FL values based on the Reqired C and Valve size shown
on the Valve Sizing tab. FL is only used in the IEC noise calculation.
This data is automaically copied to the Valve Sizing tab.
Flow | 31863 | 27000 | 65000 | 94000
Valve type | Liquid pressure recovery factor. FL
Globe, 4 port cage | 0.83838 | 0.84957 | 0.83058 | 0.81812
Globe, Parabolic plug | 0.91281 | 0.87865 | 0.84727 | 0.82348
Rotary eccentric plug | 0.90416 | 0.85297 | 0.79283 | 0.76
Segment ball | 0.92464 | 0.89311 | 0.83223 | 0.77714
Butterfly | 0.85795 | 0.82718 | 0.76826 | 0.7155
Full ball (Full and reduced port) | 0.8998 | 0.87625 | 0.83251 | 0.79481
Cv Table in current use | BALL_SEG
Values automatically copied to the | 0.92464 | 0.89311 | 0.83223 | 0.77714
Vlalve Sizing tab
Typical Fd values based on the Relative Travel on the Valve Sizing tab.
on the Valve Sizing tab. Fd is only used in the IEC noise calculation. | [8 empty] | Fd calculations
This data is automaically copied to the Valve Sizing tab. | [8 empty] | Valve travel from Valve Travel tab | 21.1574 | 40.0187 | 60.7462 | 73.6335
Valve type | Valve style modifier, Fd | [7 empty] | Relative travel | 0.21157 | 0.40019 | 0.60746 | 0.73633
Globe, 4 port cage =% | 0.43437 | 0.32972 | 0.31351 | 0.33241
[10 empty] | Case 1 | Case 2 | Case 3 | Case 4
Globe, 4 port cage Linear | 0.38505 | 0.34598 | 0.34681 | 0.37492
Globe, 4 port cage =%
Globe, Parabolic plug =% | 0.065621 | 0.13 | 0.24636 | 0.32999
[9 empty] | Relatve travel | 0.21157 | 0.40019 | 0.60746 | 0.73633
Globe, Parabolic plug Linear | 0.17468 | 0.25748 | 0.34848 | 0.40505 |  |  |  |  | Fd_GCE | 0.43437 | 0.32972 | 0.31351 | 0.33241
Rotary eccentric plug | 0.12162 | 0.12974 | 0.1649 | 0.19 |  |  |  |  | Globe, 4 port cage Linear
Segment ball | 0.77395 | 0.84824 | 0.92141 | 0.95597 |  |  |  |  | Relatve travel | 0.21157 | 0.40019 | 0.60746 | 0.73633
[9 empty] | Fd_GCL | 0.38505 | 0.34598 | 0.34681 | 0.37492
Butterfly | 0.15239 | 0.20095 | 0.26595 | 0.29976 |  | `
Globe Parabolic plug =%
Full ball (Standard port) | 0.68468 | 0.86038 | 0.95292 | 0.98342
[9 empty] | Relatve travel | 0.21157 | 0.40019 | 0.60746 | 0.73633
Full ball (Full port) | 0.68468 | 0.86038 | 0.95292 | 0.98342 |  |  |  |  | Fd_GPE | 0.065621 | 0.13 | 0.24636 | 0.32999
Globe Parabolic plug LIN
Values automatically copied to the | 0.77395 | 0.84824 | 0.92141 | 0.95597
Vlalve Sizing tab | [8 empty] | Relatve travel | 0.21157 | 0.40019 | 0.60746 | 0.73633
[9 empty] | Fd_GPL | 0.17468 | 0.25748 | 0.34848 | 0.40505
Typical values of Valve correction factor for acoustic efficiency, Aη | [8 empty] | Rotary eccentric plug
and Strouhal number for peak frequency calculation, Stp
This data is automaically copied to the Valve Sizing tab. | [8 empty] | Relatve travel
| Aη | Stp | [6 empty] | Relatve travel | 0.21157 | 0.40019 | 0.60746 | 0.73633
Globe parabolic Plug | -4.2 | 0.19 | [6 empty] | Fd_RP | 0.12162 | 0.12974 | 0.1649 | 0.19
Globe Cage | -3.8 | 0.2
Eccendtric rotary plug | -3.6 | 0.3 | [6 empty] | Segment ball
Ball, Segment ball | -3.6 | 0.3
Butterfly | -4.2 | 0.3 | [6 empty] | Relatve travel | 0.21157 | 0.40019 | 0.60746 | 0.73633
[9 empty] | Fd_SEG | 0.77395 | 0.84824 | 0.92141 | 0.95597
Values automatically copied to the | -3.6 | 0.3
Vlalve Sizing tab | [8 empty] | Butterfly
[9 empty] | Relatve travel | 0.21157 | 0.40019 | 0.60746 | 0.73633
[9 empty] | Fd_BF | 0.15239 | 0.20095 | 0.26595 | 0.29976
Full ball reduced Port
[9 empty] | Relatve travel | 0.21157 | 0.40019 | 0.60746 | 0.73633
[9 empty] | Fd_FB | 0.68468 | 0.86038 | 0.95292 | 0.98342
Full ball full Port
[9 empty] | Relatve travel | 0.21157 | 0.40019 | 0.60746 | 0.73633
[9 empty] | Fd_FB_FP | 0.68468 | 0.86038 | 0.95292 | 0.98342

## Mol Mass
This tab calculates MOLECULAR MASS for use on the Valve Sizing tab when Specific Gravity is know but not Molecular mass or when valve inlet Density, Pressure and Tempeerature are known, but not Molecular Mass.
Finall results fields remain blank until required data has been entered. |  |  |  |  | Intermediate Calculations
Inlet pressure converted to Pa (Pascal)
Conversion from specific gravity to Molecular Mass: |  |  |  | Inlet temperature coverted to Kelvin
Denisty converted to kg/m^3
| Specific gravity | G_ | 1 | Pa | P_1..L | 0
| Molecular Mass |  | 28.97 | R or K | Tabs_RorK | 459.67
|  |  |  | K | T_1..L | 255.3722
|  |  |  | kg/m^3 | DENS | 0
Conversion from Inlet Density, Pressure andTemperature to Molecular Mass
Engineering units shown here are those selected in B27 of the Valve Sizing tab.
Density (lbm/ft^3)
Pressure (psiA)
Temperature (F)
Molecular mass
| Input_Test |  | Data input
| 0 |  | Final results

## SPL Conv
Aerodynamic Noise - IEC 60534-8-3 Ed: 3.0 | Data imported from Valve Sizing tab | [5 empty] | Scroll to the right to view the conversion from user interface units to units required by the IEC Standard and to see the pipe reducer calculations. | Conversion from Valve Sizing tab units to |  |  | NO USER INPUT IS REQUIRED FOR THIS TAB
NO USER INPUT IS REQUIRED FOR THIS TAB. | [7 empty] | Units required by the IEC Standard. |  |  | Case 1 | Case 2 | Case 3 | Case 4 | DESCRIPTION OF VARIABLE | Eq | NAME OF VARIABLE
Process Parameters |  |  | Case 1 | Case 2 | Case 3 | Case 4 |  | (kg/s, Pa, K, kg/m3, m/s, m) | Units | [5 empty] | CALCULATED IN COLUMN "AA" |  | CALCULATED IN COLUMN "AA" | Case 1 | Case 2 | Case 3 | Case 4
Volumetric Flow (At standard pressure and temperature) | scfh | Q_S | 31863 | 93645 | 184894 | 236393 |  | Flow | kg/s | m_dot | 0.30713 | 0.90264 | 1.7822 | 2.2786
Inlet pressure | psiA | P_1 | 90 | 88.6 | 83.7 | 80 |  | Inlet pressure | Pa | P_1 | 620528.157 | 610875.4968 | 577091.186 | 551580.584
Inlet temperature | F | T_1 | 100 | 100 | 100 | 100 |  | Inlet temperature | K | T_1 | 310.9278 | 310.9278 | 310.9278 | 310.9278 | Calculation of FP and FLP
Pressure drop | psi | DELTA_P | 30 | 28.6 | 23.7 | 20 |  | Pressure drop | Pa | DELTA_P | 206842.719 | 197190.0588 | 163405.748 | 137895.146 | Reducer velocity head coefficients | S7501 18 | ZETA_1_REN | 0.28125 | 0.28125 | 0.28125 | 0.28125
[8 empty] | Inlet density 1 | kg/m3 | RHO_1 | 6.9541 | 6.8459 | 6.4673 | 6.1814 |  | S7501 17 | ZETA_B1_REN | 0.9375 | 0.9375 | 0.9375 | 0.9375
Molecular mass |  | M_ | 28.97 | =========> | =========> | =========> |  | Molecular mass |  | M_ | 28.97 | 28.97 | 28.97 | 28.97 |  | S7501 19 | ZETA_2_REN | 0.5625 | 0.5625 | 0.5625 | 0.5625
Specific heat ratio (g) |  | GAMMA | 1.4 | =========> | =========> | =========> |  | Specific heat ratio (g) |  | GAMMA | 1.4 | 1.4 | 1.4 | 1.4 |  | S7501 17 | ZETA_B2_REN | 0.9375 | 0.9375 | 0.9375 | 0.9375
Pipe/Valve Parameters | [14 empty] | Sum of velocity head coefficients | S7501 16 | SIGMA_ZETA_REN | 0.84375 | 0.84375 | 0.84375 | 0.84375
Flow coefficient (Kv or Cv) | Cv | C_ | 12.9194 | 39.4405 | 90.6476 | 136.9874 |  | Flow coefficient (Kv or Cv) | Cv | C_ | 12.9194 | 39.4405 | 90.6476 | 136.9874 | Sum of upstream velocity head coef | S7501 | SIGMA_ZETA_1_REN | 1.2188 | 1.2188 | 1.2188 | 1.2188
Liquid pressure recovery factor |  | F_L | 0.92464 | 0.89311 | 0.83223 | 0.77714 |  | Liquid pressure recovery factor |  | F_L | 0.92464 | 0.89311 | 0.83223 | 0.77714 | Piping geometry factor | S7501 15 | F_P | 0.99903 | 0.99103 | 0.95516 | 0.90556
Valve style modifier |  | F_D | 0.77395 | 0.84824 | 0.92141 | 0.95597 |  | Valve style modifier |  | F_D | 0.77395 | 0.84824 | 0.92141 | 0.95597 | Combined liquid pressure recovery
Valve correction - accoustic efficiency, Ah |  | A_ETA | -3.6 | =========> | =========> | =========> |  | Valve correction - accoustic efficiency, Ah |  | A_ETA | -3.6 | -3.6 | -3.6 | -3.6 | factor and piping geometry factor | S7501 21 | F_LP | 0.92353 | 0.88389 | 0.7949 | 0.71197
Strouhal number (peak) |  | St_P | 0.3 | =========> | =========> | =========> |  | Strouhal number (peak) |  | St_P | 0.3 | 0.3 | 0.3 | 0.3
Valve inlet internal diameter | inch | D_Vi | 3 | =========> | =========> | =========> |  | Valve inlet internatl diameter | m | D_Vi | 0.0762 | 0.0762 | 0.0762 | 0.0762
Valve outlet internal diameter | inch | D_Vo | 3 | =========> | =========> | =========> |  | Valve outlet internatl diameter | m | D_Vo | 0.0762 | 0.0762 | 0.0762 | 0.0762
Inlet pipe internal diameter | inch | D_1 | 6 | =========> | =========> | =========> |  | Inlet pipe internal diameter | m | D_1 | 0.1524 | 0.1524 | 0.1524 | 0.1524
Outlet pipe internal diameter | inch | D_2 | 6 | =========> | =========> | =========> |  | Outlet pipe internal diameter | m | D_2 | 0.1524 | 0.1524 | 0.1524 | 0.1524
Outlet pipe wall thickness | inch | T_S | 0.28 | =========> | =========> | =========> |  | Outlet pipe wall thickness | m | T_S | 0.007112 | 0.007112 | 0.007112 | 0.007112
[8 empty] | Speed of sound in pipe | m/s | C_S | 5000 | 5000 | 5000 | 5000
[8 empty] | Density of pipe material | kg/m3 | RHO_S | 8000 | 8000 | 8000 | 8000
Contraction coeff. for valve outlet or expander inlet*** |  | BETA | 0.75 | =========> | =========> | =========> |  | Beta (β)* |  | BETA | 0.75 | 0.75 | 0.75 | 0.75
Actual atmospheric pressure outside pipe | psiA | p_a | 14.696 | =========> | =========> | =========> |  | External speed of sound (atmospheric) | m/s | c_a | 343 | 343 | 343 | 343
[8 empty] | Actual atmospheric pressure outside pipe | Pa | p_a | 101325.3533 | 101325.3533 | 101325.3533 | 101325.3533
Convert volumetric flow to m dot in kg/s
[8 empty] | m^3/h to kg/s |  | m_dot_m3h | 10.844 | 31.8705 | 62.9256 | 80.4524
|  |  | Auto filled based on Flag # |  |  |  |  | scfh to kg/s |  | m_dot_scfh | 0.30713 | 0.90264 | 1.7822 | 2.2786
The conversion from standard volumetric flow to mass flow is based on Crane's Flow of Fluids book. W = ra G Q where W is the mass flow, ra is the density of air at standard temperature and pressure, G is the specific gravity of the flowing gas, and Q is the volumetric flow at standard conditions.
Density of air at standard temp. and press.
These flags are set by formulas that are controlled by user selections on lines 27, 28 & 29 of the Valve Sizing tab | [7 empty] | kg/m3 @ 15C, 1.01325 bar |  | RHO_air_kg_m3_15 | 1.2252
Unit Selection for user interface | Flag # | Flag Value | Options |  |  |  |  | kg/m3 @ 0C, 1.01325 bar |  | RHO_air_kg_m3_0 | 1.2925
[8 empty] | lbm/ft3 @ 15C, 1.01325 bar |  | RHO_air_lb_ft3_15 | 0.0765
Volumetric flow | IEC_1 | 2 | 1 = m3/h, 2 = scfh |  |  |  |  | lbm/ft3 @ 0C, 1.01325 bar |  | RHO_air_lb_ft3_0 | 0.0807
Pressure (absolute) | IEC_2 | 4 | 1 = Pa, 2 = kPa, 3 = bar, 4 = psiA
Temperature | IEC_3 | 3 | 1 = K, 2 = C, 3 = F
Density | IEC_4 | 2 | 1 = kg/m3, 2 = lbm/ft3 |  |  |  |  | 1 Inlet density is calculated from P_1, M, T_1 and Z
Length | IEC_5 | 3 | 1 = m, 2 = mm, 3 = in
Flow coefficient | IEC_6 | 1 | 1 = Cv, 2 = Kv
Ref temp for standard volumetric flow | REF_T | 1 | 1 = 15C (60F), 2 = 0C (32F)
Numerical Constants (Auto filled in based on Flag IEC_6)
N_14 |  | 0.0046
N_16 (Only used with multistage valves) |  | 48900
Universal gas constant | R_ | 8314 | J/kmol × K

## SPL Calcs
Calculations based on IEC 60534-8-3 Edition 3.0
NO USER INPUT IS REQUIRED FOR THIS TAB.
Lines 6 through 34, Columns D through G are automatically flled trom the SPL Conv tab
[7 empty] | DESCRIPTION OF VARIABLE |  | NAME OF VARIABLE
Process Parameters | Units | Name | Case 1 | Case 2 | Case 3 | Case 4 | CALCULATED IN COLUMN "K" | Eqn. # | CALCULATED IN COLUMN "K" | Case 1 | Case 2 | Case 3 | Case 4
Flow | kg/s | m_dot..D | 0.30713 | 0.90264 | 1.7822 | 2.2786
Inlet pressure | Pa | P_1..D | 620528.157 | 610875.4968 | 577091.186 | 551580.584 | Differential Pressure ratio | 1 | x | 0.33333 | 0.3228 | 0.28315 | 0.25
Inlet temperature | K | T_1..D | 310.9278 | 310.9278 | 310.9278 | 310.9278 | Absolute VC pressure at subsonic conditions | 2 | p_vc..K | 378484.7035 | 362988.0973 | 341153.7015 | 328500.1536 | does not have any dependents
Outlet pressure | Pa | P_2..D | 413685.438 | 413685.438 | 413685.438 | 413685.438 | VC diff. pressure ratio @ critical flow cond. | 3 | x_vcc..K | 0.47172 | 0.47172 | 0.47172 | 0.47172
Inlet density | kg/m3 | RHO_1..D | 6.9541 | 6.8459 | 6.4673 | 6.1814 | Diff press. ratio at critical flow conditions | 4 | x_c..K | 0.40312 | 0.37524 | 0.3267 | 0.29159
Molecular mass |  | M_..D | 28.97 | 28.97 | 28.97 | 28.97 | Recovery correction factor α | 5 | ALPHA..K | 0.88507 | 0.84558 | 0.78462 | 0.74573
Specific heat ratio (g) |  | GAMMA..D | 1.4 | 1.4 | 1.4 | 1.4 | Differential pressure ratio at break point | 6 | x_B..K | 0.652 | 0.63575 | 0.60745 | 0.58698
Pipe/Valve Parameters | [6 empty] | DP ratio where const acoustical efficiency begins | 7 | x_CE..K | 0.94864 | 0.94624 | 0.94207 | 0.93905
Flow coefficient (Kv or Cv) | Cv | C_..D | 12.9194 | 39.4405 | 90.6476 | 136.9874 | egime definition |  | Regime..K | Regime I | Regime I | Regime I | Regime I
Valve style modifier |  | F_D..D | 0.77395 | 0.84824 | 0.92141 | 0.95597 | Valve style modifier | 8a | F_d..K | 0.77395 | 0.84824 | 0.92141 | 0.95597
Valve correction - accoustic efficiency, Ah |  | A_ETA..D | -3.6 | -3.6 | -3.6 | -3.6 | Jet Diameter | 9 | D_ j..K | 0.012303 | 0.023142 | 0.036813 | 0.045637
Strouhal number (peak) |  | St_P..D | 0.3 | 0.3 | 0.3 | 0.3 | Mach Number at - Regime I Only | Table 3 | M_vc..K | 0.87097 | 0.8954 | 0.90015 | 0.8933
Valve outlet internatl diameter | m | D_Vo..D | 0.0762 | 0.0762 | 0.0762 | 0.0762 | Freely expanded jet Mach # in regimes II, III, IV | Table 3 | M_j..K | Regimes II-IV only | Regimes II-IV only | Regimes II-IV only | Regimes II-IV only
Outlet pipe internal diameter | m | D_2..D | 0.1524 | 0.1524 | 0.1524 | 0.1524 | Freely expanded jet Mach number in regime V | Table 3 | M_j5..K | Regime V only | Regime V only | Regime V only | Regime V only
[7 empty] | Absolute Temp at VC at subsonic flow conditions | Table 3 | T_vc..K | 269.9684 | 267.9605 | 267.567 | 268.1346
[7 empty] | Absolute Temperature at VC at critical flow cond. | Table 3 | T_vcc..K | Regimes II-V only | Regimes II-V only | Regimes II-V only | Regimes II-V only | does not have any dependents
Outlet pipe wall thickness | m | T_S..D | 0.007112 | 0.007112 | 0.007112 | 0.007112 | Speed of sound at VC at subsonic flow conditions | Table 3 | c_vc..K | 329.3451 | 328.1181 | 327.8771 | 328.2247
Speed of sound in pipe | m/s | C_S..D | 5000 | 5000 | 5000 | 5000 | Speed of sound at VC at critical flow conditions | Table 3 | c_vcc | Regimes II-V only | Regimes II-V only | Regimes II-V only | Regimes II-V only
Density of pipe material | kg/m3 | RHO_S..D | 8000 | 8000 | 8000 | 8000 | Acoustical eff. factor for noise created by valve flow, η | Table 3 | K24 | 0.00014183 | 0.00014344 | 0.00012689 | 0.00011068
Beta (β) |  | BETA..D | 0.75 | 0.75 | 0.75 | 0.75 | Generated peak frequency | Table 3 | f_p..K | 6994.4228 | 3808.5798 | 2405.1579 | 1927.415
Valve outlet temperature (assumed = Inlet temp) | K | T_2..D | 310.9278 | 310.9278 | 310.9278 | 310.9278 | Stream power of mass flow | Table 3 | W_m..K | 12635.7709 | 38956.8185 | 77621.3758 | 97942.4183
Smaller of valve outlet or expander inlet IDs | m | D_ViS..D | 0.0762 | 0.0762 | 0.0762 | 0.0762 | Sound Power for noise propagating downstream | 11 | W_a..K | 1.7921 | 5.5882 | 9.8493 | 10.8404
External speed of sound (atmospheric) | m/s | c_a..D | 343 | 343 | 343 | 343 | Outlet density | 13 | RHO_2..K | 4.6361 | 4.6361 | 4.6361 | 4.6361
Actual atmospheric pressure outside pipe | Pa | p_a..D | 101325.3533 | 101325.3533 | 101325.3533 | 101325.3533 | Speed of sound at downstream conditions | 14 | c_2..K | 353.4472 | 353.4472 | 353.4472 | 353.4472
Reducer corrected Recovery factor. F_LP |  | F_LP..D | 0.92353 | 0.88389 | 0.7949 | 0.71197 | Mach number at valve outlet | 15 | M_o..K | 0.0411 | 0.12079 | 0.2385 | 0.30493
Piping geometry factor, F_P |  | F_P..D | 0.99903 | 0.99103 | 0.95516 | 0.90556 | Mach number in downstream pipe ( limited to 0.3 for calculating L_g) | 17 | M_2..K | 0.010275 | 0.030198 | 0.059624 | 0.076231
Universal gas constant | J/kmol × K | R_..D | 8314 | 8314 | 8314 | 8314 | Correction for Mach number | 16 | L_g..K | 0.071768 | 0.21307 | 0.42718 | 0.55099
N14 |  | N14..D | 0.0046 | 0.0046 | 0.0046 | 0.0046 | Overall internal sound-pressure level | 18 | L_pi..K | 146.142 | 151.2223 | 153.8977 | 154.438
N16 (Only used with multistage valves) |  |  | 48900 | 48900 | 48900 | 48900 | Frequency dependent internal sound pressure level | 19 | L_pi_f_i | 96.5458 | 106.1135 | 112.1814 | 114.3557 |  | Table_5 Indexed |  | Table_7 - "A" weighting
[7 empty] | (third octave bands) |  | 2 | 98.3683 | 107.9356 | 114.003 | 116.1769 |  | Frequency bands |  | factor at frequency fi
Structural loss factor reference frequency | Hz | f_s..D | 1 | 1 | 1 | 1 |  |  | 3 | 100.0155 | 109.5825 | 115.6492 | 117.8224 |  | Index | Frequency | fi
Standard atmoshperic pressure | Ps | p_s..D | 101325 | 101325 | 101325 | 101325 |  |  | 4 | 101.6627 | 111.2291 | 117.2948 | 119.4672 |  | number | fi | (Hz) | ΔLA(fi)
[9 empty] | 5 | 103.3685 | 112.934 | 118.9982 | 121.1692 |  | 1 | 12.5 | 12.5 | -63.4
| Auto filled based on Flag IEC_6 | [7 empty] | 6 | 105.1315 | 114.6957 | 120.7575 | 122.9265 |  | 2 | 16 | 16 | -56.7
[9 empty] | 7 | 106.778 | 116.3404 | 122.3988 | 124.565 |  | 3 | 20 | 20 | -50.5
[9 empty] | 8 | 108.4828 | 118.0424 | 124.0957 | 126.2577 |  | 4 | 25 | 25 | -44.7
[9 empty] | 9 | 110.2441 | 119.7995 | 125.8451 | 128.0005 |  | 5 | 31.5 | 31.5 | -39.4
[9 empty] | 10 | 111.8884 | 121.4379 | 127.4727 | 129.6191 |  | 6 | 40 | 40 | -34.6
[9 empty] | 11 | 113.5311 | 123.072 | 129.0912 | 131.2248 |  | 7 | 50 | 50 | -30.2
[9 empty] | 12 | 115.3458 | 124.8726 | 130.8664 | 132.979 |  | 8 | 63 | 63 | -26.2
[9 empty] | 13 | 116.9827 | 126.4907 | 132.4508 | 134.5359 |  | 9 | 80 | 80 | -22.5
[9 empty] | 14 | 118.6148 | 128.0955 | 134.0074 | 136.0539 |  | 10 | 100 | 100 | -19.1
[9 empty] | 15 | 120.2977 | 129.7374 | 135.5783 | 137.5691 |  | 11 | 125 | 125 | -16.1
[9 empty] | 16 | 122.0256 | 131.4034 | 137.1404 | 139.0521 |  | 12 | 160 | 160 | -13.4
[9 empty] | 17 | 123.6239 | 132.9189 | 138.5221 | 140.336 |  | 13 | 200 | 200 | -10.9
[9 empty] | 18 | 125.2561 | 134.4306 | 139.8488 | 141.5344 |  | 14 | 250 | 250 | -8.6
[9 empty] | 19 | 126.9077 | 135.9086 | 141.0784 | 142.6019 |  | 15 | 315 | 315 | -6.6
[9 empty] | 20 | 128.4043 | 137.1865 | 142.0686 | 143.4156 |  | 16 | 400 | 400 | -4.8
[9 empty] | 21 | 129.8393 | 138.3386 | 142.8809 | 144.03 |  | 17 | 500 | 500 | -3.2
[9 empty] | 22 | 131.3298 | 139.435 | 143.5462 | 144.4507 |  | 18 | 630 | 630 | -1.9
[9 empty] | 23 | 132.5628 | 140.2385 | 143.9124 | 144.5657 |  | 19 | 800 | 800 | -0.8
[9 empty] | 24 | 133.6598 | 140.8415 | 144.0252 | 144.3873 |  | 20 | 1000 | 1000 | 0
[9 empty] | 25 | 134.6253 | 141.2309 | 143.8319 | 143.8426 |  | 21 | 1250 | 1250 | 0.6
[9 empty] | 26 | 135.4134 | 141.3483 | 143.2451 | 142.8522 |  | 22 | 1600 | 1600 | 1
[9 empty] | 27 | 135.9341 | 141.1527 | 142.3033 | 141.5333 |  | 23 | 2000 | 2000 | 1.2
[9 empty] | 28 | 136.228 | 140.5876 | 140.9279 | 139.8142 |  | 24 | 2500 | 2500 | 1.3
[9 empty] | 29 | 136.2306 | 139.5747 | 139.1316 | 137.7446 |  | 25 | 3150 | 3150 | 1.2
[9 empty] | 30 | 135.9093 | 138.2362 | 137.1887 | 135.6242 |  | 26 | 4000 | 4000 | 1
[9 empty] | 31 | 135.2281 | 136.5652 | 135.0672 | 133.3865 |  | 27 | 5000 | 5000 | 0.5
[9 empty] | 32 | 134.0258 | 134.4182 | 132.586 | 130.8267 |  | 28 | 6300 | 6300 | -0.1
[9 empty] | 33 | 132.5527 | 132.29 | 130.2685 | 128.4671 |  | 29 | 8000 | 8000 | -1.1
[7 empty] | Eqns. 34 through 43 apply only when MO > 0.3 | [7 empty] | 30 | 10000 | 10000 | -2.5
[7 empty] | Gas velocity in downstream pipe | 34 | U_p..K | N/A Mo<0.3 | N/A Mo<0.3 | N/A Mo<0.3 | 26.9437 |  | 31 | 12500 | 12500 | -4.3
[7 empty] | Gas velocity in the inlet diameter of expander | 35 | U_R | N/A Mo<0.3 | N/A Mo<0.3 | N/A Mo<0.3 | 143.6999 |  | 32 | 16000 | 16000 | -6.6
[7 empty] | Converted stream power in the expander | 36 | W_mR..K | N/A Mo<0.3 | N/A Mo<0.3 | N/A Mo<0.3 | 17938.6222 |  | 33 | 20000 | 20000 | -9.3
[7 empty] | Peak frequency in valve outlet or reduced diameter of expander | 37 | f_pR..K | N/A Mo<0.3 | N/A Mo<0.3 | N/A Mo<0.3 | 565.7474
[7 empty] | Mach number in the entrance to expander | 39 | M_R..K | N/A Mo<0.3 | N/A Mo<0.3 | N/A Mo<0.3 | 0.40657
[7 empty] | Acoustical eff. factor for noise created by outlet flow in expander | 38 | etta_r..K | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 1.6881e-05 | If you are trying to compare the Annex A Example 6
[7 empty] | Sound power for noise generated by the outlet flow and propagating downstream | 40 | W_Ar..K | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 0.30282 | calculations with this worksheet be aware that the
[7 empty] | Overall internal SPL at pipe wall for noise created by outlet flow in expander | 41 | L_piR..K | N/A Mo<0.3 | N/A Mo<0.3 | N/A Mo<0.3 | 138.8994 | value shown in Annex A for Equation 38 was based
[7 empty] | Frequency dependent internal SPL at pipe wall flow in expander | 42 | L_piR_f_i | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 107.8481 | on an old equation from the 2nd edition of the standard
[9 empty] | 2 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 109.6595 | (even thogh they show the correct equation in Annex A)
[9 empty] | 3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 111.2918 | and thus the values in the annex for Equation 38 and many
[9 empty] | 4 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 112.9173 | subsequent calculations are incorrect.
[9 empty] | 5 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 114.5902
[9 empty] | 6 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 116.3029
[9 empty] | 7 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 117.8806
[9 empty] | 8 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 119.4824
[9 empty] | 9 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 121.0892
[9 empty] | 10 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 122.5277
[9 empty] | 11 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 123.8849
[9 empty] | 12 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 125.2624
[9 empty] | 13 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 126.3667
[9 empty] | 14 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 127.3106
[9 empty] | 15 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 128.094
[9 empty] | 16 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 128.6711
[9 empty] | 17 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 128.9714
[9 empty] | 18 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 129.0046
[9 empty] | 19 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 128.6907
[9 empty] | 20 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 128.0281
[9 empty] | 21 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 126.9806
[9 empty] | 22 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 125.3906
[9 empty] | 23 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 123.6246
[9 empty] | 24 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 121.6259
[9 empty] | 25 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 119.3879
[9 empty] | 26 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 116.9604
[9 empty] | 27 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 114.6291
[9 empty] | 28 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 112.176
[9 empty] | 29 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 109.6161
[9 empty] | 30 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 107.2119
[9 empty] | 31 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 104.8003
[9 empty] | 32 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 102.1274
[9 empty] | 33 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 99.7085
[7 empty] | Combined internal sound-pressure level at pipe wall, caused by valve | 43 | L_piS_f_i | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 115.2317
[7 empty] | trim and expander (third octave bands: 12.5 Hz - 20,000 Hz) |  | 2 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 117.051
[9 empty] | 3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 118.6942
[9 empty] | 4 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 120.3354
[9 empty] | 5 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 122.0323
[9 empty] | 6 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 123.7815
[9 empty] | 7 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 125.4092
[9 empty] | 8 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 127.086
[9 empty] | 9 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 128.8055
[9 empty] | 10 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 130.3942
[9 empty] | 11 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 131.9601
[9 empty] | 12 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 133.6578
[9 empty] | 13 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 135.152
[9 empty] | 14 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 136.5983
[9 empty] | 15 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 138.0335
[9 empty] | 16 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 139.4327
[9 empty] | 17 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 140.6422
[9 empty] | 18 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 141.7704
[9 empty] | 19 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 142.7749
[9 empty] | 20 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 143.5395
[9 empty] | 21 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 144.1149
[9 empty] | 22 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 144.5043
[9 empty] | 23 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 144.6005
[9 empty] | 24 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 144.4102
[9 empty] | 25 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 143.8582
[9 empty] | 26 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 142.8634
[9 empty] | 27 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 141.5422
[9 empty] | 28 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 139.8216
[9 empty] | 29 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 137.7513
[9 empty] | 30 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 135.6305
[9 empty] | 31 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 133.3925
[9 empty] | 32 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 130.8325
[9 empty] | 33 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 128.4729
[7 empty] | Ring frequency | 21 | f_r..K | 10443.2377 | 10443.2377 | 10443.2377 | 10443.2377
[7 empty] | Internal coincidence pipe frequency | 22 | f_o..K | 2690.3303 | 2690.3303 | 2690.3303 | 2690.3303
[7 empty] | External coincidence frequency | 23 | f_g..K | 1824.0521 | 1824.0521 | 1824.0521 | 1824.0521
[7 empty] | Frequency factor (3rd octave bands: 12.5 Hz - 20,000 Hz) | Table 6 | G_x_f_i | 1.8868e-10 | 1.8868e-10 | 1.8868e-10 | 1.8868e-10
[9 empty] | 2 | 5.0649e-10 | 5.0649e-10 | 5.0649e-10 | 5.0649e-10
[9 empty] | 3 | 1.2365e-09 | 1.2365e-09 | 1.2365e-09 | 1.2365e-09
[9 empty] | 4 | 3.0189e-09 | 3.0189e-09 | 3.0189e-09 | 3.0189e-09
[9 empty] | 5 | 7.6091e-09 | 7.6091e-09 | 7.6091e-09 | 7.6091e-09
[9 empty] | 6 | 1.9785e-08 | 1.9785e-08 | 1.9785e-08 | 1.9785e-08
[9 empty] | 7 | 4.8303e-08 | 4.8303e-08 | 4.8303e-08 | 4.8303e-08
[9 empty] | 8 | 1.2175e-07 | 1.2175e-07 | 1.2175e-07 | 1.2175e-07
[9 empty] | 9 | 3.1656e-07 | 3.1656e-07 | 3.1656e-07 | 3.1656e-07
[9 empty] | 10 | 7.7284e-07 | 7.7284e-07 | 7.7284e-07 | 7.7284e-07
[9 empty] | 11 | 1.8868e-06 | 1.8868e-06 | 1.8868e-06 | 1.8868e-06
[9 empty] | 12 | 5.0649e-06 | 5.0649e-06 | 5.0649e-06 | 5.0649e-06
[9 empty] | 13 | 1.2365e-05 | 1.2365e-05 | 1.2365e-05 | 1.2365e-05
[9 empty] | 14 | 3.0189e-05 | 3.0189e-05 | 3.0189e-05 | 3.0189e-05
[9 empty] | 15 | 7.6091e-05 | 7.6091e-05 | 7.6091e-05 | 7.6091e-05
[9 empty] | 16 | 0.00019785 | 0.00019785 | 0.00019785 | 0.00019785
[9 empty] | 17 | 0.00048303 | 0.00048303 | 0.00048303 | 0.00048303
[9 empty] | 18 | 0.0012175 | 0.0012175 | 0.0012175 | 0.0012175
[9 empty] | 19 | 0.0031656 | 0.0031656 | 0.0031656 | 0.0031656
[9 empty] | 20 | 0.0077284 | 0.0077284 | 0.0077284 | 0.0077284
[9 empty] | 21 | 0.018868 | 0.018868 | 0.018868 | 0.018868
[9 empty] | 22 | 0.050649 | 0.050649 | 0.050649 | 0.050649
[9 empty] | 23 | 0.12365 | 0.12365 | 0.12365 | 0.12365
[9 empty] | 24 | 0.30189 | 0.30189 | 0.30189 | 0.30189
[9 empty] | 25 | 0.54921 | 0.54921 | 0.54921 | 0.54921
[9 empty] | 26 | 0.61889 | 0.61889 | 0.61889 | 0.61889
[9 empty] | 27 | 0.69194 | 0.69194 | 0.69194 | 0.69194
[9 empty] | 28 | 0.7767 | 0.7767 | 0.7767 | 0.7767
[9 empty] | 29 | 0.87524 | 0.87524 | 0.87524 | 0.87524
[9 empty] | 30 | 0.97855 | 0.97855 | 0.97855 | 0.97855
[9 empty] | 31 | 1 | 1 | 1 | 1
[9 empty] | 32 | 1 | 1 | 1 | 1
[9 empty] | 33 | 1 | 1 | 1 | 1
[7 empty] | Frequency factor (3rd octave bands: 12.5 Hz - 20,000 Hz) | Table 6 | G_y_f_i | 1 | 1 | 1 | 1
[9 empty] | 2 | 1 | 1 | 1 | 1
[9 empty] | 3 | 1 | 1 | 1 | 1
[9 empty] | 4 | 1 | 1 | 1 | 1
[9 empty] | 5 | 1 | 1 | 1 | 1
[9 empty] | 6 | 1 | 1 | 1 | 1
[9 empty] | 7 | 1 | 1 | 1 | 1
[9 empty] | 8 | 1 | 1 | 1 | 1
[9 empty] | 9 | 1 | 1 | 1 | 1
[9 empty] | 10 | 1 | 1 | 1 | 1
[9 empty] | 11 | 1 | 1 | 1 | 1
[9 empty] | 12 | 1 | 1 | 1 | 1
[9 empty] | 13 | 1 | 1 | 1 | 1
[9 empty] | 14 | 1 | 1 | 1 | 1
[9 empty] | 15 | 1 | 1 | 1 | 1
[9 empty] | 16 | 1 | 1 | 1 | 1
[9 empty] | 17 | 1 | 1 | 1 | 1
[9 empty] | 18 | 1 | 1 | 1 | 1
[9 empty] | 19 | 1 | 1 | 1 | 1
[9 empty] | 20 | 1 | 1 | 1 | 1
[9 empty] | 21 | 1 | 1 | 1 | 1
[9 empty] | 22 | 1 | 1 | 1 | 1
[9 empty] | 23 | 1 | 1 | 1 | 1
[9 empty] | 24 | 1 | 1 | 1 | 1
[9 empty] | 25 | 1 | 1 | 1 | 1
[9 empty] | 26 | 1 | 1 | 1 | 1
[9 empty] | 27 | 1 | 1 | 1 | 1
[9 empty] | 28 | 1 | 1 | 1 | 1
[9 empty] | 29 | 1 | 1 | 1 | 1
[9 empty] | 30 | 1 | 1 | 1 | 1
[9 empty] | 31 | 1 | 1 | 1 | 1
[9 empty] | 32 | 1 | 1 | 1 | 1
[9 empty] | 33 | 1 | 1 | 1 | 1
[7 empty] | Frequency-dependent structural loss factor third | 20c | η_s_f_i | 0.028284 | 0.028284 | 0.028284 | 0.028284
[7 empty] | octave bands: 12.5 Hz - 20,000 Hz) |  | 2 | 0.025 | 0.025 | 0.025 | 0.025
[9 empty] | 3 | 0.022361 | 0.022361 | 0.022361 | 0.022361
[9 empty] | 4 | 0.02 | 0.02 | 0.02 | 0.02
[9 empty] | 5 | 0.017817 | 0.017817 | 0.017817 | 0.017817
[9 empty] | 6 | 0.015811 | 0.015811 | 0.015811 | 0.015811
[9 empty] | 7 | 0.014142 | 0.014142 | 0.014142 | 0.014142
[9 empty] | 8 | 0.012599 | 0.012599 | 0.012599 | 0.012599
[9 empty] | 9 | 0.01118 | 0.01118 | 0.01118 | 0.01118
[9 empty] | 10 | 0.01 | 0.01 | 0.01 | 0.01
[9 empty] | 11 | 0.0089443 | 0.0089443 | 0.0089443 | 0.0089443
[9 empty] | 12 | 0.0079057 | 0.0079057 | 0.0079057 | 0.0079057
[9 empty] | 13 | 0.0070711 | 0.0070711 | 0.0070711 | 0.0070711
[9 empty] | 14 | 0.0063246 | 0.0063246 | 0.0063246 | 0.0063246
[9 empty] | 15 | 0.0056344 | 0.0056344 | 0.0056344 | 0.0056344
[9 empty] | 16 | 0.005 | 0.005 | 0.005 | 0.005
[9 empty] | 17 | 0.0044721 | 0.0044721 | 0.0044721 | 0.0044721
[9 empty] | 18 | 0.0039841 | 0.0039841 | 0.0039841 | 0.0039841
[9 empty] | 19 | 0.0035355 | 0.0035355 | 0.0035355 | 0.0035355
[9 empty] | 20 | 0.0031623 | 0.0031623 | 0.0031623 | 0.0031623
[9 empty] | 21 | 0.0028284 | 0.0028284 | 0.0028284 | 0.0028284
[9 empty] | 22 | 0.0025 | 0.0025 | 0.0025 | 0.0025
[9 empty] | 23 | 0.0022361 | 0.0022361 | 0.0022361 | 0.0022361
[9 empty] | 24 | 0.002 | 0.002 | 0.002 | 0.002
[9 empty] | 25 | 0.0017817 | 0.0017817 | 0.0017817 | 0.0017817
[9 empty] | 26 | 0.0015811 | 0.0015811 | 0.0015811 | 0.0015811
[9 empty] | 27 | 0.0014142 | 0.0014142 | 0.0014142 | 0.0014142
[9 empty] | 28 | 0.0012599 | 0.0012599 | 0.0012599 | 0.0012599
[9 empty] | 29 | 0.001118 | 0.001118 | 0.001118 | 0.001118
[9 empty] | 30 | 0.001 | 0.001 | 0.001 | 0.001
[9 empty] | 31 | 0.00089443 | 0.00089443 | 0.00089443 | 0.00089443
[9 empty] | 32 | 0.00079057 | 0.00079057 | 0.00079057 | 0.00079057
[9 empty] | 33 | 0.00070711 | 0.00070711 | 0.00070711 | 0.00070711
[7 empty] | Damping factor for transmission loss, ΔTL | 20b | DeltaTL..K | 3.4652 | 3.4652 | 3.4652 | 3.4652
[7 empty] | Frequency dependent transmission loss 3rd octave bands: | 20a | TL_f_i | -96.7589 | -96.7589 | -96.7589 | -96.7589
[7 empty] | 12.5 Hz - 20,000 Hz) |  | 2 | -94.6477 | -94.6477 | -94.6477 | -94.6477
[9 empty] | 3 | -92.7427 | -92.7427 | -92.7427 | -92.7427
[9 empty] | 4 | -90.8414 | -90.8414 | -90.8414 | -90.8414
[9 empty] | 5 | -88.8764 | -88.8764 | -88.8764 | -88.8764
[9 empty] | 6 | -86.8502 | -86.8502 | -86.8502 | -86.8502
[9 empty] | 7 | -84.9625 | -84.9625 | -84.9625 | -84.9625
[9 empty] | 8 | -83.013 | -83.013 | -83.013 | -83.013
[9 empty] | 9 | -81.0044 | -81.0044 | -81.0044 | -81.0044
[9 empty] | 10 | -79.1347 | -79.1347 | -79.1347 | -79.1347
[9 empty] | 11 | -77.2719 | -77.2719 | -77.2719 | -77.2719
[9 empty] | 12 | -75.2196 | -75.2196 | -75.2196 | -75.2196
[9 empty] | 13 | -73.373 | -73.373 | -73.373 | -73.373
[9 empty] | 14 | -71.5349 | -71.5349 | -71.5349 | -71.5349
[9 empty] | 15 | -69.6408 | -69.6408 | -69.6408 | -69.6408
[9 empty] | 16 | -67.694 | -67.694 | -67.694 | -67.694
[9 empty] | 17 | -65.8862 | -65.8862 | -65.8862 | -65.8862
[9 empty] | 18 | -64.0253 | -64.0253 | -64.0253 | -64.0253
[9 empty] | 19 | -62.1147 | -62.1147 | -62.1147 | -62.1147
[9 empty] | 20 | -60.3424 | -60.3424 | -60.3424 | -60.3424
[9 empty] | 21 | -58.5825 | -58.5825 | -58.5825 | -58.5825
[9 empty] | 22 | -56.6504 | -56.6504 | -56.6504 | -56.6504
[9 empty] | 23 | -54.9177 | -54.9177 | -54.9177 | -54.9177
[9 empty] | 24 | -53.1983 | -53.1983 | -53.1983 | -53.1983
[9 empty] | 25 | -52.8476 | -52.8476 | -52.8476 | -52.8476
[9 empty] | 26 | -54.6679 | -54.6679 | -54.6679 | -54.6679
[9 empty] | 27 | -56.3822 | -56.3822 | -56.3822 | -56.3822
[9 empty] | 28 | -58.1718 | -58.1718 | -58.1718 | -58.1718
[9 empty] | 29 | -60.0365 | -60.0365 | -60.0365 | -60.0365
[9 empty] | 30 | -61.7916 | -61.7916 | -61.7916 | -61.7916
[9 empty] | 31 | -63.9496 | -63.9496 | -63.9496 | -63.9496
[9 empty] | 32 | -66.4552 | -66.4552 | -66.4552 | -66.4552
[9 empty] | 33 | -68.7323 | -68.7323 | -68.7323 | -68.7323
[7 empty] | Frequency dependent external sound-pressure level | 24 | L_pe_1m_f_i | -11.3536 | -1.7859 | 4.282 | 7.3323
[7 empty] | (third octave bands: 12.5 Hz - 20,000 Hz) |  | 2 | -7.4199 | 2.1474 | 8.2149 | 11.2629
[9 empty] | 3 | -3.8677 | 5.6993 | 11.766 | 14.811
[9 empty] | 4 | -0.31918 | 9.2472 | 15.3129 | 18.3536
[9 empty] | 5 | 3.3517 | 12.9172 | 18.9814 | 22.0154
[9 empty] | 6 | 7.1409 | 16.7051 | 22.7669 | 25.7909
[9 empty] | 7 | 10.675 | 20.2374 | 26.2958 | 29.3063
[9 empty] | 8 | 14.3293 | 23.8889 | 29.9423 | 32.9325
[9 empty] | 9 | 18.0993 | 27.6547 | 33.7002 | 36.6606
[9 empty] | 10 | 21.6132 | 31.1627 | 37.1975 | 40.119
[9 empty] | 11 | 25.1187 | 34.6597 | 40.6789 | 43.5478
[9 empty] | 12 | 28.9857 | 38.5125 | 44.5063 | 47.2977
[9 empty] | 13 | 32.4693 | 41.9772 | 47.9373 | 50.6386
[9 empty] | 14 | 35.9394 | 45.4201 | 51.3321 | 53.923
[9 empty] | 15 | 39.5164 | 48.9561 | 54.7971 | 57.2522
[9 empty] | 16 | 43.1911 | 52.569 | 58.306 | 60.5983
[9 empty] | 17 | 46.5972 | 55.8923 | 61.4955 | 63.6155
[9 empty] | 18 | 50.0903 | 59.2648 | 64.6831 | 66.6046
[9 empty] | 19 | 53.6525 | 62.6534 | 67.8232 | 69.5197
[9 empty] | 20 | 56.9214 | 65.7036 | 70.5857 | 72.0566
[9 empty] | 21 | 60.1163 | 68.6156 | 73.1579 | 74.3919
[9 empty] | 22 | 63.539 | 71.6441 | 75.7553 | 76.7134
[9 empty] | 23 | 66.5046 | 74.1803 | 77.8542 | 78.5423
[9 empty] | 24 | 69.3211 | 76.5027 | 79.6865 | 80.0715
[9 empty] | 25 | 70.6372 | 77.2429 | 79.8439 | 79.8701
[9 empty] | 26 | 69.605 | 75.5399 | 77.4367 | 77.055
[9 empty] | 27 | 68.4114 | 73.63 | 74.7806 | 74.0195
[9 empty] | 28 | 66.9157 | 71.2753 | 71.6156 | 70.5093
[9 empty] | 29 | 65.0537 | 68.3977 | 67.9547 | 66.5743
[9 empty] | 30 | 62.9773 | 65.3041 | 64.2567 | 62.6984
[9 empty] | 31 | 60.1381 | 61.4751 | 59.9772 | 58.3025
[9 empty] | 32 | 56.4302 | 56.8225 | 54.9904 | 53.2369
[9 empty] | 33 | 52.6799 | 52.4172 | 50.3957 | 48.6001
[7 empty] | Summation of L_pe,1m(f_i) and DLA(fi),1m(f_i) and DLA(fi) | 25 | L_pe_fi_plus_delta_LA_fi | 3.3469e-08 | 3.0297e-07 | 1.2252e-06 | 2.473e-06
[9 empty] | 16 | 3.8727e-07 | 3.5054e-06 | 1.4174e-05 | 2.8595e-05
[7 empty] | Equation (25) has been divided into two parts. |  | 20 | 3.6579e-06 | 3.3108e-05 | 0.00013384 | 0.00026984
[7 empty] | This section calculates the portion shown in the red box below. |  | 25 | 3.1483e-05 | 0.00028492 | 0.0011516 | 0.0023193
[7 empty] | In the section below the quantities in this section are added |  | 31.5 | 0.00024841 | 0.0022476 | 0.009081 | 0.018262
[7 empty] | logarithmically and converted to dB(A) |  | 40 | 0.0017951 | 0.016237 | 0.065567 | 0.13155
[9 empty] | 50 | 0.011156 | 0.10087 | 0.40699 | 0.814
[9 empty] | 63 | 0.065002 | 0.58734 | 2.3672 | 4.7125
[9 empty] | 80 | 0.36302 | 3.2769 | 13.1832 | 26.0651
[9 empty] | 100 | 1.7837 | 16.0793 | 64.5281 | 126.4437
[9 empty] | 125 | 7.9776 | 71.7739 | 287.006 | 555.6247
[9 empty] | 160 | 36.1883 | 324.5276 | 1290.1234 | 2453.3927
[9 empty] | 200 | 143.5246 | 1281.5173 | 5055.14 | 9415.84
[9 empty] | 250 | 541.9303 | 4808.5337 | 18758.8519 | 34064.0358
[9 empty] | 315 | 1957.2322 | 17203.2612 | 66025.0396 | 116203.7161
[9 empty] | 400 | 6904.2089 | 59827.1125 | 224181.0696 | 380041.0577
[9 empty] | 500 | 21863.6678 | 185878.1183 | 675375.4801 | 1100407.2888
[9 empty] | 630 | 65922.1724 | 545108.248 | 1898040.0139 | 2954364.6541
[9 empty] | 800 | 192865.6208 | 1532291.9336 | 5038770.5342 | 7446767.5123
[9 empty] | 1000 | 492201.1302 | 3718416.9949 | 11443737.5644 | 16056783.9211
[9 empty] | 1250 | 1179323.4832 | 8347598.8516 | 23756985.0395 | 31563843.2326
[9 empty] | 1600 | 2843777.4067 | 18382644.9733 | 47373130.967 | 59066872.331
[9 empty] | 2000 | 5894715.5926 | 34516921.8936 | 80430567.6064 | 94239764.5292
[9 empty] | 2500 | 11537419.3163 | 60294050.0544 | 125501785.6946 | 137134811.9357
[9 empty] | 3150 | 15265841.455 | 69869464.9356 | 127171038.0448 | 127941914.2126
[9 empty] | 4000 | 11494846.6733 | 45080174.4895 | 69769790.9875 | 63900010.5746
[9 empty] | 5000 | 7782954.9225 | 25881880.263 | 33733586.3243 | 28310692.3139
[9 empty] | 6300 | 4803593.0026 | 13107720.5486 | 14176117.5956 | 10988411.0407
[9 empty] | 8000 | 2485231.742 | 5367534.789 | 4846920.5919 | 3527195.5014
[9 empty] | 10000 | 1116160.3592 | 1907268.5619 | 1498531.4085 | 1046751.8633
[9 empty] | 12500 | 383538.9287 | 521812.539 | 369591.1562 | 251333.2987
[9 empty] | 16000 | 96164.8975 | 105256.6827 | 69029.5679 | 46098.4472
[9 empty] | 20000 | 21776.676 | 20498.5671 | 12869.7524 | 8511.5967
[7 empty] | A-weighted overall SPL 1 m from pipe wall | 25 | L_pAe_1m..K | 78.1748 | 84.616 | 87.3885 | 87.6799
Note on L47: Jon:

## Valve Travel
VALVE TRAVEL AT GIVEN Cv | [6 empty] | Callculation of Valve capacity in units of Cv and size in units of inch
[9 empty] | Case 1 | Case 2 | Case 3 | Case 4
| Case 1 | Case 2 | Case 3 | Case 4 |  |  | Valve size in Inch | VS_IN | 3 | ===> | ===> | ===>
Valve size (inch) | 3 | [5 empty] | Valve cap. In Cv | VCAP_CV | 12.9194 | 39.4405 | 90.6476 | 136.9874
Calculated Cv | 12.9194 | 39.4405 | 90.6476 | 136.9874
NO USER INPUT IS REQUIRED FOR THIS TAB.
Travel % @ Cv | 21.1574 | 40.0187 | 60.7462 | 73.6335
TheTravel % @ Cv is calculated from the final Cv values on the
|  |  |  | Final results | Valve Sizing tab then copied to Line 24 of the Valve Sizing tab.
Cv table in use | BALL_SEG
[10 empty] | Case 1 | [12 empty] | Case 2 | [12 empty] | Case 3 | [13 empty] | Case 4
[6 empty] | Calc Cv | 12.9194 | [11 empty] | Calc Cv | 39.4405 | [11 empty] | Calc Cv | 90.6476 | [11 empty] | Calc Cv | 136.9874
[5 empty] | Travel, % | Cv @ travel % | 0 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420 | Travel, % | Cv @ travel % | 0 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420 | Travel, % | Cv @ travel % | 0 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420 | Travel, % | Cv @ travel % | 0 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420
[6 empty] | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
[6 empty] | M | 2.1142 | 1.4556 | 0.87719 | 0.60976 | 0.46296 | 0.36765 | 0.30488 | 0.22727 | 0.12346 | 0.057471 |  |  | M | 2.1142 | 1.4556 | 0.87719 | 0.60976 | 0.46296 | 0.36765 | 0.30488 | 0.22727 | 0.12346 | 0.057471 |  |  | M | 2.1142 | 1.4556 | 0.87719 | 0.60976 | 0.46296 | 0.36765 | 0.30488 | 0.22727 | 0.12346 | 0.057471 |  |  | M | 2.1142 | 1.4556 | 0.87719 | 0.60976 | 0.46296 | 0.36765 | 0.30488 | 0.22727 | 0.12346 | 0.057471
[7 empty] | 27.3137 | 21.9205 | 21.1574 | 23.8533 | 27.7405 | 32.3233 | 37.0486 | 45.4362 | 61.2246 | 76.6046 |  |  |  | 83.3837 | 60.5247 | 44.4215 | 40.0247 | 40.0187 | 42.0737 | 45.1343 | 51.4637 | 64.4988 | 78.1288 |  |  |  | 191.6439 | 135.062 | 89.34 | 71.2485 | 63.7257 | 60.8998 | 60.7462 | 63.1017 | 70.8207 | 81.0717 |  |  |  | 289.6139 | 202.5144 | 129.9889 | 99.5045 | 85.1793 | 77.9365 | 74.8742 | 73.6335 | 76.5416 | 83.7349
[6 empty] | Vlv Trav @ Cv | 0: 21.1574 |  | Vlv Trav @ Cv | 40.0187 | [11 empty] | Vlv Trav @ Cv | 60.7462 | [11 empty] | Vlv Trav @ Cv | 73.6335
VALVE Cv TABLES
|  |  | FULL PORT BALL VALVES |  |  | TABLE NAME: | 0: BALL_FP; 30: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 2 | 2.48 | 5.4 | 10.1 | 17.8 | 27.9 | 42.5 | 70.8 | 123 | 224 | 480
[6 empty] | 3 | 5.9 | 15.8 | 29.7 | 49.5 | 75.7 | 109 | 177 | 308 | 560 | 1200
[6 empty] | 4 | 9.7 | 25.9 | 48.6 | 81 | 124 | 179 | 313 | 545 | 989 | 2120
[6 empty] | 6 | 22 | 60 | 112 | 187 | 286 | 413 | 757 | 1318 | 2394 | 5100
[6 empty] | 8 | 40 | 106 | 199 | 331 | 506 | 732 | 1386 | 2413 | 4381 | 9300
[6 empty] | 10 | 63 | 167 | 314 | 523 | 800 | 1160 | 2244 | 3906 | 7092 | 15200
[6 empty] | 12 | 90 | 240 | 449 | 749 | 1150 | 1660 | 3306 | 5757 | 10452 | 22400
[6 empty] | 14 | 112 | 300 | 562 | 936 | 1430 | 2070 | 4177 | 7273 | 13205 | 28300
[6 empty] | 16 | 148 | 394 | 738 | 1230 | 1880 | 2720 | 5565 | 9689 | 17591 | 37700
[6 empty] | 18 | 188 | 502 | 942 | 1570 | 2400 | 3470 | 7085 | 12336 | 22397 | 48000
[6 empty] | 20 | 233 | 621 | 1160 | 1940 | 2790 | 4290 | 8782 | 15292 | 27763 | 59500
[6 empty] | 24 | 338 | 902 | 1690 | 2820 | 4310 | 6230 | 12738 | 22179 | 40268 | 86300
[6 empty] | 28 | 463 | 1240 | 2320 | 3860 | 5910 | 8530 | 17417 | 30326 | 55059 | 118000
[6 empty] | 30 | 533 | 1420 | 2660 | 4440 | 6790 | 9810 | 20074 | 34952 | 63458 | 136000
[6 empty] | 32 | 592 | 1580 | 2960 | 4942 | 7558 | 10915 | 22288 | 38807 | 70457 | 151000
[6 empty] | 36 | 752 | 2010 | 3760 | 6270 | 9590 | 13900 | 28339 | 49344 | 89587 | 192000
|  |  | REDUCED PORT BALL VALVES |  |  | TABLE NAME: | BALL_FP 10: BALL_RP; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  |  | Calc Cv | 39.4405 | [11 empty] | Calc Cv | 90.6476 | [11 empty] | Calc Cv | 136.9874
[6 empty] | Size, Inch | [11 empty] | Travel, % | Cv @ travel % | 0 | 3 | 7 | 15 | 26 | 45 | 74 | 105 | 165 | 245 | 350 | Travel, % | Cv @ travel % | 0 | 3 | 7 | 15 | 26 | 45 | 74 | 105 | 165 | 245 | 350 | Travel, % | Cv @ travel % | 0 | 3 | 7 | 15 | 26 | 45 | 74 | 105 | 165 | 245 | 350 | bar: Valve Travel, % 40
[6 empty] | 0.5 | 0.1 | 0.2 | 0.4 | 0.7 | 1.2 | 1.9 | 2.7 | 4.2 | 6.3 | 9 |  |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
[6 empty] | 0.75 | 0.2 | 0.4 | 0.9 | 1.4 | 2.5 | 4 | 5.7 | 9 | 13 | 19 |  |  | M | 3.3333 | 2.5 | 1.25 | 0.90909 | 0.52632 | 0.34483 | 0.32258 | 0.16667 | 0.125 | 0.095238 |  |  | M | 3.3333 | 2.5 | 1.25 | 0.90909 | 0.52632 | 0.34483 | 0.32258 | 0.16667 | 0.125 | 0.095238 |  |  | M | 3.3333 | 2.5 | 1.25 | 0.90909 | 0.52632 | 0.34483 | 0.32258 | 0.16667 | 0.125 | 0.095238
[6 empty] | 1 | 0.4 | 0.9 | 2 | 3.4 | 5.8 | 9.5 | 13.5 | 21 | 32 | 45 |  |  |  | 131.4683 | 101.1012 | 60.5506 | 52.2186 | 47.0739 | 48.0829 | 48.8518 | 59.0734 | 64.3051 | 70.4229 |  |  |  | 302.1586 | 229.1189 | 124.5595 | 98.7705 | 74.025 | 65.7405 | 65.3702 | 67.6079 | 70.7059 | 75.2998 |  |  |  | 456.6245 | 344.9684 | 182.4842 | 140.8976 | 98.4144 | 81.7198 | 80.3185 | 75.3312 | 76.4984 | 79.7131
[6 empty] | 1.5 | 1.1 | 2.4 | 5.6 | 9.4 | 16 | 26 | 38 | 58 | 88 | 125 |  |  | Vlv Trav @ Cv | 47.0739 | [11 empty] | Vlv Trav @ Cv | 65.3702 | [11 empty] | Vlv Trav @ Cv | 75.3312
[6 empty] | 2 | 1.5 | 3.1 | 7.5 | 12 | 21 | 35 | 50 | 78 | 115 | 165
[6 empty] | 3 | 3 | 7 | 15 | 26 | 45 | 74 | 105 | 165 | 245 | 350
[6 empty] | 4 | 2 | 5 | 17 | 32 | 54 | 90 | 135 | 201 | 301 | 550
[6 empty] | 6 | 7 | 15 | 35 | 57 | 100 | 160 | 230 | 360 | 535 | 765
[6 empty] | 8 | 17 | 36 | 85 | 140 | 245 | 395 | 570 | 890 | 1325 | 1890
[6 empty] | 10 | 35 | 74 | 175 | 290 | 505 | 815 | 1180 | 1840 | 2735 | 3900
[6 empty] | 12 | 60 | 127 | 300 | 505 | 870 | 1400 | 2010 | 3150 | 4690 | 6700
[6 empty] | 14 | 42 | 102 | 240 | 400 | 700 | 1130 | 1620 | 2540 | 3780 | 5400
[6 empty] | 16 | 70 | 155 | 375 | 630 | 1100 | 1785 | 2550 | 3990 | 5950 | 8500
[6 empty] | 18 | 100 | 200 | 440 | 760 | 1275 | 2050 | 2940 | 4600 | 6860 | 9800
[6 empty] | 20 | 125 | 260 | 610 | 990 | 1700 | 2750 | 3900 | 6110 | 9100 | 13000
|  |  | SEGMENT BALL VALVES |  |  | TABLE NAME: | BALL_RP 10: BALL_SEG; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 1 | 0.52 | 1.13 | 2.23 | 3.83 | 5.95 | 8.58 | 11.7 | 16.2 | 24.1 | 45
[6 empty] | 1.5 | 1.33 | 3.27 | 6.44 | 11.1 | 17.2 | 24.8 | 33.9 | 46.5 | 69.3 | 110
[6 empty] | 2 | 2.05 | 5.07 | 10 | 17.2 | 26.6 | 38.4 | 52.5 | 72.4 | 108 | 180
[6 empty] | 2.5 | 3.26 | 8.02 | 15.9 | 27.3 | 42.3 | 61 | 83.4 | 114 | 170 | 280
[6 empty] | 3 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420
[6 empty] | 4 | 7.57 | 18.6 | 36.8 | 63.1 | 97.7 | 141 | 193 | 264 | 393 | 620
[6 empty] | 6 | 13.9 | 34.1 | 67.2 | 115 | 178 | 258 | 352 | 484 | 719 | 1260
[6 empty] | 8 | 22.5 | 55.3 | 109 | 187 | 290 | 418 | 571 | 784 | 1164 | 2030
[6 empty] | 10 | 35.3 | 86.9 | 171 | 294 | 455 | 658 | 900 | 1236 | 1831 | 3210
[6 empty] | 12 | 49.8 | 123 | 243 | 418 | 648 | 937 | 1278 | 1754 | 2601 | 4490
[6 empty] | 14 | 63.9 | 158 | 311 | 534 | 827 | 1193 | 1628 | 2237 | 3320 | 6440
[6 empty] | 16 | 85.4 | 210 | 414 | 713 | 1106 | 1599 | 2180 | 2989 | 4432 | 8510
[6 empty] | 20 | 130.6 | 321 | 633 | 1090 | 1692 | 2446 | 3334 | 4571 | 6778 | 13020
[6 empty] | 24 | 198 | 486 | 958 | 1649 | 2560 | 3701 | 5045 | 6916 | 10255 | 19700
[6 empty] | 28 | 254 | 624 | 1230 | 2118 | 3288 | 4753 | 6479 | 8882 | 13171 | 25300
[6 empty] | 32 | 321 | 789 | 1556 | 2679 | 4159 | 6012 | 8195 | 11234 | 16659 | 32000
|  |  | HIGH PERFORMANCE BUTTERFLY |  |  | TABLE NAME: | BALL_SEG 10: HPBF_150; Valve Travel, % 40: Valve Travel, %
|  |  | VALVES CLASS 150 |  |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 2.5 | 4 | 7 | 11 | 16 | 22 | 30 | 43 | 59 | 71 | 78
[6 empty] | 3 | 4 | 12 | 21 | 35 | 46 | 66 | 90 | 125 | 153 | 165
[6 empty] | 4 | 8 | 12 | 55 | 87 | 120 | 165 | 225 | 310 | 380 | 400
[6 empty] | 5 | 10 | 38 | 87 | 143 | 193 | 263 | 356 | 482 | 606 | 650
[6 empty] | 6 | 10 | 58 | 137 | 235 | 310 | 415 | 560 | 745 | 960 | 1050
[6 empty] | 8 | 15 | 130 | 315 | 475 | 695 | 970 | 1370 | 1865 | 2015 | 2200
[6 empty] | 10 | 25 | 155 | 340 | 540 | 835 | 1210 | 1665 | 2225 | 3030 | 3300
[6 empty] | 12 | 55 | 310 | 590 | 895 | 1410 | 2020 | 2790 | 3855 | 4900 | 5100
[6 empty] | 14 | 100 | 435 | 755 | 1220 | 1625 | 2320 | 3190 | 4410 | 5395 | 5800
[6 empty] | 16 | 165 | 630 | 1050 | 1530 | 2190 | 3080 | 4350 | 6100 | 7600 | 8000
[6 empty] | 18 | 285 | 790 | 1365 | 2200 | 2940 | 4200 | 5760 | 7970 | 9750 | 10500
[6 empty] | 20 | 350 | 880 | 1570 | 2540 | 3400 | 5080 | 7150 | 9450 | 12650 | 14000
[6 empty] | 24 | 405 | 1070 | 1980 | 3050 | 4430 | 6500 | 9550 | 13950 | 19100 | 21600
[6 empty] | 28 | 570 | 1562 | 2779 | 4200 | 6000 | 8700 | 12900 | 18882 | 26400 | 30000
[6 empty] | 30 | 650 | 1770 | 3150 | 4760 | 6800 | 9860 | 14620 | 21400 | 29920 | 34000
[6 empty] | 32 | 784 | 2134 | 3799 | 5740 | 8200 | 11890 | 17630 | 25806 | 36080 | 41000
[6 empty] | 36 | 1220 | 2980 | 5230 | 7650 | 11150 | 16100 | 23500 | 34100 | 49200 | 55500
[6 empty] | 40 | 1452 | 3893 | 6987 | 10481 | 15018 | 21688 | 32123 | 47278 | 65880 | 75000
[6 empty] | 42 | 1600 | 4290 | 7700 | 11550 | 16550 | 23900 | 35400 | 52100 | 72600 | 82650
[6 empty] | 48 | 2100 | 5600 | 10100 | 15200 | 21700 | 31400 | 46600 | 68200 | 95300 | 108300
[6 empty] | 54 | 2540 | 6950 | 12400 | 18700 | 26700 | 38700 | 57400 | 84100 | 117500 | 133500
[6 empty] | 56 | 2740 | 7497 | 13375 | 20171 | 28800 | 41744 | 61915 | 90715 | 126742 | 144000
[6 empty] | 60 | 3020 | 8270 | 14800 | 22250 | 31800 | 46100 | 68370 | 100200 | 139900 | 159000
|  |  | HIGH PERFORMANCE BUTTERFLY |  |  | TABLE NAME: | HPBF_150 10: HPBF_300; Valve Travel, % 40: Valve Travel, %
|  |  | VALVES CLASS 300 |  |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 2.5 | 4 | 7 | 11 | 16 | 22 | 30 | 43 | 59 | 71 | 78
[6 empty] | 3 | 4 | 12 | 21 | 35 | 46 | 66 | 90 | 125 | 153 | 165
[6 empty] | 4 | 8 | 12 | 55 | 87 | 120 | 165 | 225 | 310 | 380 | 400
[6 empty] | 6 | 10 | 58 | 137 | 235 | 310 | 415 | 560 | 745 | 960 | 1050
[6 empty] | 8 | 12 | 115 | 260 | 390 | 570 | 795 | 1120 | 1525 | 1650 | 1800
[6 empty] | 10 | 20 | 145 | 325 | 515 | 795 | 1155 | 1590 | 2125 | 2890 | 3150
[6 empty] | 12 | 45 | 280 | 550 | 835 | 1315 | 1880 | 2600 | 3590 | 4570 | 4750
[6 empty] | 14 | 90 | 430 | 750 | 1200 | 1580 | 2250 | 3100 | 4300 | 5100 | 5200
[6 empty] | 16 | 150 | 620 | 1030 | 1500 | 2100 | 2950 | 4050 | 5450 | 6750 | 6900
[6 empty] | 18 | 280 | 780 | 1350 | 2100 | 2790 | 4000 | 5450 | 7350 | 8900 | 9300
[6 empty] | 20 | 340 | 870 | 1550 | 2510 | 3250 | 4800 | 6550 | 8250 | 10600 | 11300
[6 empty] | 24 | 400 | 1020 | 1920 | 2960 | 4300 | 6200 | 9000 | 12700 | 17400 | 18500
|  |  | HIGH PERFORMANCE BUTTERFLY |  |  | TABLE NAME: | HPBF_300 10: HPBF_600; Valve Travel, % 40: Valve Travel, %
|  |  | VALVES CLASS 600 |  |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 3 | 4 | 11 | 20 | 33 | 43 | 62 | 85 | 117 | 144 | 155
[6 empty] | 4 | 5 | 16 | 36 | 57 | 78 | 107 | 146 | 202 | 247 | 260
[6 empty] | 6 | 7 | 41 | 98 | 168 | 221 | 296 | 400 | 532 | 686 | 750
[6 empty] | 8 | 9 | 86 | 195 | 293 | 428 | 596 | 840 | 1144 | 1238 | 1350
[6 empty] | 10 | 13 | 97 | 217 | 343 | 530 | 770 | 1060 | 1417 | 1927 | 2100
[6 empty] | 12 | 27 | 171 | 336 | 510 | 803 | 1148 | 1587 | 2192 | 2790 | 2900
[6 empty] | 14 | 69 | 331 | 577 | 923 | 1215 | 1731 | 2385 | 3308 | 3923 | 4000
[6 empty] | 16 | 111 | 458 | 761 | 1109 | 1552 | 2180 | 2993 | 4028 | 4989 | 5100
[6 empty] | 18 | 166 | 461 | 798 | 1242 | 1650 | 2366 | 3223 | 4347 | 5263 | 5500
[6 empty] | 20 | 239 | 612 | 1090 | 1766 | 2287 | 3377 | 4608 | 5804 | 7458 | 7950
[6 empty] | 24 | 244 | 623 | 1173 | 1808 | 2626 | 3787 | 5497 | 7757 | 10628 | 11300
|  |  | GLOBE CAGE GUIDED EQUALL PERCENT |  |  | TABLE NAME: | HPBF_600 10: GC_EQ; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  | Decimal sizes N.01, N.02, N.03 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  | represent "N" inch valve , 1, 2, 3 |  |  | 2 | 2 | 4 | 6 | 9 | 14 | 21 | 33 | 50 | 66 | 71
|  |  | sizes reduced. |  |  | 2.01 | 1.1 | 3.3 | 5.5 | 7.6 | 9.8 | 12.8 | 17.9 | 26.3 | 39.7 | 50
[6 empty] | 2.02 | 0.6 | 1.2 | 1.6 | 2.5 | 4.6 | 8.2 | 12.9 | 17.7 | 21.6 | 24
[6 empty] | 2.03 | 0.3 | 0.7 | 0.9 | 1.5 | 2.7 | 4.8 | 7.5 | 10.4 | 12.6 | 14
[6 empty] | 3 | 4 | 8.5 | 14.5 | 22 | 33.5 | 51 | 75 | 108 | 128 | 138
[6 empty] | 3.01 | 2.5 | 3.7 | 6.6 | 11.1 | 18.4 | 29.4 | 45.6 | 67.7 | 92 | 110
[6 empty] | 3.02 | 1.2 | 2.5 | 3.3 | 5.2 | 9.5 | 17 | 26.8 | 37 | 45 | 50
[6 empty] | 3.03 | 0.8 | 1.6 | 2.1 | 3.3 | 6.1 | 10.9 | 17.2 | 23.7 | 28.8 | 32
[6 empty] | 4 | 5.6 | 12.9 | 23.4 | 36.9 | 59.6 | 86.5 | 128.2 | 163.9 | 188.6 | 210
[6 empty] | 4.01 | 2.8 | 6.7 | 11.7 | 17.9 | 28.6 | 46.2 | 71.9 | 105.8 | 141.2 | 160
[6 empty] | 4.02 | 2 | 4.1 | 5.5 | 8.5 | 15.6 | 27.9 | 44 | 60.6 | 73.8 | 82
[6 empty] | 4.03 | 1.2 | 2.5 | 3.3 | 5.2 | 9.5 | 17 | 26.8 | 37 | 45 | 50
[6 empty] | 6 | 6.5 | 15 | 27.7 | 47.1 | 77.1 | 123.8 | 198.5 | 265.2 | 316 | 340
[6 empty] | 6.01 | 3.4 | 11.1 | 22 | 32.3 | 50.4 | 81.7 | 126.8 | 187.4 | 246.3 | 270
[6 empty] | 6.02 | 3.3 | 6.8 | 9.1 | 14.1 | 25.9 | 46.2 | 73 | 100.5 | 122.3 | 136
[6 empty] | 6.03 | 2 | 4.1 | 5.5 | 8.5 | 15.6 | 27.9 | 44 | 60.6 | 73.8 | 82
[6 empty] | 8 | 6.5 | 23 | 45 | 83 | 138 | 220 | 325 | 445 | 510 | 560
[6 empty] | 8.01 | 5.6 | 19 | 39 | 58 | 94 | 148 | 222 | 310 | 405 | 450
[6 empty] | 8.02 | 4 | 11.7 | 15.8 | 24.4 | 44.9 | 80.2 | 126.6 | 174.5 | 212.3 | 236
[6 empty] | 8.03 | 3 | 7.1 | 9.5 | 14.7 | 27 | 48.3 | 76.2 | 105 | 127.7 | 142
[6 empty] | 10 | 8.1 | 33.2 | 65.7 | 124.4 | 216.8 | 350.1 | 493.2 | 619.9 | 747.6 | 830
[6 empty] | 10.01 | 6.5 | 26.5 | 47.1 | 76.2 | 126.3 | 219.8 | 343.2 | 460 | 566.2 | 655
[6 empty] | 10.02 | 6.1 | 18.6 | 25 | 38.7 | 71.2 | 127.2 | 200.6 | 276.5 | 336.4 | 374
[6 empty] | 10.03 | 5.5 | 11.1 | 15 | 23.2 | 42.6 | 76.2 | 120.2 | 165.6 | 201.5 | 224
[6 empty] | 12 | 22.4 | 64.3 | 111.1 | 179.8 | 303.1 | 546.8 | 795 | 996 | 1155 | 1240
[6 empty] | 12.01 | 15.5 | 44.7 | 73.7 | 110.5 | 174.2 | 277.6 | 441.3 | 650.5 | 837.5 | 960
[6 empty] | 12.02 | 12.8 | 26 | 35 | 54.2 | 99.7 | 178.1 | 281.1 | 387.4 | 471.4 | 524
[6 empty] | 12.03 | 7.7 | 15.6 | 21 | 32.5 | 59.8 | 106.8 | 168.4 | 232.1 | 282.5 | 314
[6 empty] | 14 | 24.7 | 82.3 | 158.3 | 266.7 | 427 | 693.9 | 1015.8 | 1277.2 | 1514.7 | 1650
[6 empty] | 14.01 | 18.9 | 60.2 | 103.2 | 164.8 | 260.6 | 405.5 | 630.9 | 903.9 | 1141.5 | 1275
[6 empty] | 14.02 | 16.2 | 37.1 | 49.8 | 77.1 | 142 | 253.6 | 400.2 | 551.5 | 671.1 | 746
[6 empty] | 14.03 | 10.9 | 22.2 | 29.8 | 46.1 | 84.9 | 151.6 | 239.2 | 329.7 | 401.2 | 446
[6 empty] | 16 | 35.1 | 100.4 | 167 | 268.4 | 471 | 849.3 | 1265.1 | 1603.9 | 1911.6 | 2090
[6 empty] | 16.01 | 26.3 | 73 | 119.6 | 175.7 | 287 | 477.7 | 773.1 | 1125.4 | 1432.4 | 1680
[6 empty] | 16.02 | 20.9 | 42.4 | 57 | 88.3 | 162.6 | 290.3 | 458.1 | 631.4 | 768.2 | 854
[6 empty] | 16.03 | 12.5 | 25.4 | 34.2 | 52.9 | 97.5 | 174.1 | 274.7 | 378.5 | 460.6 | 512
[6 empty] | 18 | 45.3 | 129.7 | 215.7 | 346.7 | 608.5 | 1097.2 | 1634.3 | 2072 | 2469.5 | 2700
[6 empty] | 18.01 | 29.8 | 82.6 | 135.2 | 198.7 | 324.6 | 540.3 | 874.3 | 1272.8 | 1620 | 1900
[6 empty] | 18.02 | 27.8 | 56.6 | 76.1 | 117.8 | 217 | 387.6 | 611.5 | 842.8 | 1025.5 | 1140
[6 empty] | 18.03 | 16.6 | 33.8 | 45.4 | 70.3 | 129.4 | 231.2 | 364.8 | 502.7 | 611.7 | 680
[6 empty] | 20 | 60.5 | 172.9 | 287.7 | 462.3 | 811.3 | 1462.9 | 2179.1 | 2762.7 | 3292.7 | 3600
[6 empty] | 20.01 | 39.2 | 108.7 | 177.9 | 261.5 | 427.1 | 710.9 | 1150.4 | 1674.7 | 2131.6 | 2500
[6 empty] | 20.02 | 36.6 | 74.5 | 100.2 | 155 | 285.5 | 509.9 | 804.6 | 1108.9 | 1349.3 | 1500
[6 empty] | 20.03 | 22 | 44.7 | 60.1 | 93 | 171.3 | 306 | 482.8 | 665.4 | 809.6 | 900
[6 empty] | 24 | 87.3 | 249.8 | 415.5 | 667.8 | 1171.9 | 2113.1 | 3147.6 | 3990.6 | 4756.1 | 5200
[6 empty] | 24.01 | 57.2 | 158.7 | 259.7 | 381.7 | 623.5 | 1037.9 | 1679.6 | 2445.1 | 3112.1 | 3650
[6 empty] | 24.03 | 53.7 | 109.3 | 146.9 | 227.4 | 418.7 | 747.9 | 1180.1 | 1626.4 | 1979 | 2200
[6 empty] | 24.03 | 31.7 | 64.6 | 86.8 | 134.4 | 247.5 | 441.9 | 697.4 | 961.1 | 1169.4 | 1300
|  |  | GLOBE CAGE GUIDED LINEAR |  |  | TABLE NAME: | GC_EQ 10: GC_LIN; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  | Decimal sizes N.01, N.02, N.03 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  | represent "N" inch valve , 1, 2, 3 |  |  | 2 | 4.9 | 13.9 | 22.2 | 30.3 | 39.5 | 48.6 | 57.3 | 64.7 | 69.5 | 74
|  |  | sizes reduced. |  |  | 2.01 | 3.5 | 7.6 | 12.5 | 17.3 | 22.4 | 27.6 | 33.1 | 38.5 | 43.6 | 48
[6 empty] | 2.02 | 2.6 | 5.2 | 7.7 | 10.3 | 12.9 | 15.4 | 18 | 20.6 | 23.2 | 26
[6 empty] | 2.03 | 1.6 | 3.2 | 4.8 | 6.3 | 7.9 | 9.5 | 11.1 | 12.7 | 14.3 | 16
[6 empty] | 3 | 8 | 22 | 39 | 59 | 75 | 90 | 105 | 119 | 130 | 142
[6 empty] | 3.01 | 6.2 | 16.6 | 26.9 | 36.9 | 46.6 | 56.8 | 67.4 | 78 | 87.8 | 98
[6 empty] | 3.02 | 4.5 | 11.1 | 16.6 | 22.2 | 27.7 | 33.3 | 38.8 | 44.4 | 49.9 | 56
[6 empty] | 3.03 | 3.4 | 6.7 | 10.1 | 13.5 | 16.8 | 20.2 | 23.6 | 26.9 | 30.3 | 34
[6 empty] | 4 | 19.3 | 41.5 | 74.4 | 105.3 | 133.4 | 164.5 | 187.6 | 206.4 | 219.3 | 230
[6 empty] | 4.01 | 8 | 25.4 | 43.1 | 60.4 | 77.2 | 93.8 | 110.7 | 127.6 | 143.9 | 160
[6 empty] | 4.02 | 6 | 17 | 25.5 | 34.1 | 42.6 | 51.1 | 59.6 | 68.1 | 76.6 | 86
[6 empty] | 4.03 | 5.2 | 10.3 | 15.4 | 20.6 | 25.7 | 30.9 | 36 | 41.2 | 46.3 | 52
[6 empty] | 6 | 23 | 62 | 123.5 | 181 | 229.1 | 269.3 | 315.2 | 349.9 | 370.1 | 380
[6 empty] | 6.01 | 12 | 40.9 | 71.4 | 101.4 | 130.6 | 158.9 | 186.7 | 214.7 | 242.2 | 275
[6 empty] | 6.02 | 9.5 | 29.7 | 44.6 | 59.4 | 74.3 | 89.1 | 104 | 118.8 | 133.7 | 150
[6 empty] | 6.03 | 8 | 17.8 | 26.7 | 35.6 | 44.6 | 53.5 | 62.4 | 71.3 | 80.2 | 90
[6 empty] | 8 | 28.2 | 94.2 | 185.6 | 288 | 377.1 | 449.1 | 514.1 | 571.9 | 590 | 600
[6 empty] | 8.01 | 14.5 | 52.5 | 108 | 172 | 232 | 299 | 365 | 417 | 430 | 455
[6 empty] | 8.02 | 10 | 45 | 75.4 | 100.6 | 125.7 | 150.9 | 176 | 201.2 | 226.3 | 254
[6 empty] | 8.03 | 9 | 30.1 | 45.1 | 60.2 | 75.2 | 90.3 | 105.3 | 120.4 | 135.4 | 152
[6 empty] | 10 | 45.9 | 189.3 | 329.3 | 461.8 | 583.3 | 689.9 | 778.5 | 847.7 | 897.9 | 950
[6 empty] | 10.01 | 25 | 103.6 | 183.3 | 260.7 | 337.5 | 414.1 | 489.4 | 562.3 | 631.5 | 700
[6 empty] | 10.02 | 17 | 78.8 | 118.2 | 157.6 | 197 | 236.4 | 275.8 | 315.2 | 354.6 | 398
[6 empty] | 10.03 | 12 | 46.7 | 70.1 | 93.5 | 116.8 | 140.2 | 163.6 | 186.9 | 210.3 | 238
[6 empty] | 12 | 93.2 | 250 | 463.3 | 660 | 840 | 990 | 1115 | 1205 | 1250 | 1270
[6 empty] | 12.01 | 66.7 | 167.8 | 276.8 | 382.9 | 485.5 | 586.9 | 692.1 | 796.9 | 893 | 970
[6 empty] | 12.02 | 25 | 108.9 | 163.4 | 218 | 272.3 | 326.7 | 381.2 | 435.6 | 490.1 | 550
[6 empty] | 12.03 | 17 | 67.3 | 101 | 134.6 | 168.3 | 202 | 235.6 | 269.3 | 302.9 | 340
[6 empty] | 14.01 | 127.4 | 407.5 | 673.4 | 915.6 | 1128.5 | 1316.5 | 1474.2 | 1593.1 | 1671.4 | 1740
[6 empty] | 14.01 | 91.3 | 233.3 | 393 | 548.1 | 696.8 | 838 | 976.4 | 1105.4 | 1221.2 | 1300
[6 empty] | 14.02 | 52 | 153.7 | 230.5 | 307.3 | 384.1 | 460.9 | 537.8 | 614.6 | 691.4 | 776
[6 empty] | 14.03 | 27 | 91.9 | 137.8 | 183.7 | 229.7 | 275.6 | 321.6 | 367.5 | 413.4 | 464
[6 empty] | 16 | 189 | 497 | 891.8 | 1248 | 1535.4 | 1791.5 | 1950 | 2063 | 2161.6 | 2215
[6 empty] | 16.01 | 101.3 | 276.5 | 448.1 | 615 | 779.1 | 941.9 | 1101.6 | 1255.7 | 1398.9 | 1530
[6 empty] | 16.02 | 71 | 186.1 | 279.2 | 372.2 | 465.3 | 558.4 | 651.4 | 744.5 | 837.5 | 940
[6 empty] | 16.03 | 47 | 112.5 | 168.7 | 224.9 | 281.2 | 337.4 | 393.6 | 449.9 | 506.1 | 568
[6 empty] | 18 | 230.4 | 605.8 | 1087.1 | 1521.3 | 1871.6 | 2183.8 | 2377 | 2514.7 | 2634.9 | 2700
[6 empty] | 18.01 | 125.8 | 343.4 | 556.4 | 763.8 | 967.6 | 1169.7 | 1368 | 1559.4 | 1737.2 | 1900
[6 empty] | 18.02 | 86.1 | 225.7 | 338.6 | 451.4 | 564.3 | 677.2 | 790 | 902.9 | 1015.7 | 1140
[6 empty] | 18.03 | 56.3 | 134.6 | 202 | 269.3 | 336.6 | 403.9 | 471.2 | 538.6 | 605.9 | 680
[6 empty] | 20 | 307.2 | 807.8 | 1449.4 | 2028.4 | 2495.5 | 2911.7 | 3169.3 | 3353 | 3513.2 | 3600
[6 empty] | 20.01 | 165.5 | 451.8 | 732.1 | 1005 | 1273.1 | 1539 | 1800 | 2051.8 | 2285.8 | 2500
[6 empty] | 20.02 | 113.3 | 297 | 445.5 | 594 | 742.5 | 891 | 1039.5 | 1188 | 1336.5 | 1500
[6 empty] | 20.03 | 74.5 | 178.2 | 267.3 | 356.4 | 445.5 | 534.6 | 623.7 | 712.8 | 801.9 | 900
[6 empty] | 24 | 443.7 | 1166.8 | 2093.6 | 2929.8 | 3604.6 | 4205.8 | 4577.9 | 4843.2 | 5074.6 | 5200
[6 empty] | 24.01 | 241.6 | 659.6 | 1068.9 | 1467.3 | 1858.7 | 2247 | 2628 | 2995.6 | 3337.2 | 3650
[6 empty] | 24.02 | 166.2 | 435.6 | 653.4 | 871.2 | 1089 | 1306.8 | 1524.6 | 1742.4 | 1960.2 | 2200
[6 empty] | 24.03 | 107.6 | 257.4 | 386.1 | 514.8 | 643.5 | 772.2 | 900.9 | 1029.6 | 1158.3 | 1300
|  |  | GLOBE PARABOLIC PLUG EQUAL % |  |  | 20.03: TABLE NAME:; 74.5: GP_EQ; 356.4: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  | Decimal sizes N.01, N.02, N.03 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  | represent "N" inch valve , 1, 2, 3 … |  |  | 0.5 | 0.164 | 0.355 | 0.562 | 0.888 | 1.378 | 2.163 | 3.417 | 4.842 | 6.441 | 7
|  |  | sizes reduced. |  |  | 0.501 | 0.057 | 0.159 | 0.307 | 0.488 | 0.78 | 1.456 | 2.173 | 2.884 | 3.533 | 4
[6 empty] | 0.502 | 0.083 | 0.155 | 0.228 | 0.336 | 0.585 | 0.941 | 1.37 | 1.702 | 2.005 | 2.3
[6 empty] | 0.503 | 0.048 | 0.092 | 0.137 | 0.202 | 0.35 | 0.56 | 0.818 | 1.113 | 1.329 | 1.5
[6 empty] | 0.504 | 0.02 | 0.037 | 0.057 | 0.083 | 0.161 | 0.28 | 0.413 | 0.538 | 0.656 | 0.8
[6 empty] | 0.505 | 0.009 | 0.022 | 0.035 | 0.054 | 0.096 | 0.168 | 0.253 | 0.334 | 0.414 | 0.5
[6 empty] | 0.506 | 0.005 | 0.011 | 0.02 | 0.033 | 0.063 | 0.105 | 0.15 | 0.197 | 0.245 | 0.3
[6 empty] | 0.75 | 0.239 | 0.452 | 0.668 | 1.069 | 1.849 | 2.928 | 4.022 | 5.229 | 7.131 | 9
[6 empty] | 0.751 | 0.057 | 0.198 | 0.399 | 0.669 | 1.109 | 1.785 | 2.787 | 3.712 | 4.739 | 5.5
[6 empty] | 0.752 | 0.05 | 0.169 | 0.276 | 0.453 | 0.776 | 1.204 | 1.802 | 2.352 | 2.723 | 3
[6 empty] | 0.753 | 0.044 | 0.093 | 0.15 | 0.214 | 0.405 | 0.684 | 0.999 | 1.299 | 1.667 | 2
[6 empty] | 0.754 | 0.034 | 0.061 | 0.086 | 0.131 | 0.248 | 0.418 | 0.62 | 0.817 | 1.011 | 1.2
[6 empty] | 0.755 | 0.012 | 0.029 | 0.051 | 0.082 | 0.142 | 0.234 | 0.34 | 0.451 | 0.58 | 0.7
[6 empty] | 0.756 | 0.009 | 0.019 | 0.03 | 0.044 | 0.082 | 0.141 | 0.207 | 0.271 | 0.333 | 0.4
[6 empty] | 1 | 0.268 | 0.568 | 0.913 | 1.549 | 2.754 | 4.657 | 7.075 | 9.487 | 11.626 | 13.5
[6 empty] | 1.001 | 0.118 | 0.287 | 0.507 | 0.825 | 1.557 | 2.695 | 4.14 | 5.605 | 7.028 | 8.5
[6 empty] | 1.002 | 0.073 | 0.185 | 0.331 | 0.525 | 0.966 | 1.672 | 2.647 | 3.588 | 4.366 | 5.4
[6 empty] | 1.003 | 0.027 | 0.09 | 0.186 | 0.317 | 0.583 | 0.997 | 1.52 | 2.05 | 2.54 | 3.1
[6 empty] | 1.004 | 0.03 | 0.075 | 0.134 | 0.215 | 0.397 | 0.67 | 1.002 | 1.354 | 1.701 | 2
[6 empty] | 1.005 | 0.025 | 0.053 | 0.077 | 0.131 | 0.248 | 0.433 | 0.643 | 0.853 | 1.056 | 1.2
[6 empty] | 1.006 | 0.011 | 0.025 | 0.041 | 0.073 | 0.143 | 0.239 | 0.345 | 0.462 | 0.589 | 0.8
[6 empty] | 1.5 | 0.453 | 1.124 | 2 | 3.071 | 5.909 | 10.566 | 16.175 | 21.567 | 25.661 | 28
[6 empty] | 1.501 | 0.226 | 0.582 | 1.056 | 1.694 | 3.155 | 5.364 | 7.974 | 10.692 | 13.438 | 16
[6 empty] | 1.502 | 0.203 | 0.437 | 0.705 | 1.021 | 1.877 | 3.245 | 4.93 | 6.712 | 8.593 | 10.5
[6 empty] | 1.503 | 0.086 | 0.219 | 0.398 | 0.617 | 1.131 | 2.022 | 3.169 | 4.256 | 5.211 | 6
[6 empty] | 1.504 | 0.053 | 0.141 | 0.262 | 0.412 | 0.789 | 1.363 | 2.078 | 2.828 | 3.453 | 4
[6 empty] | 1.505 | 0.031 | 0.076 | 0.134 | 0.21 | 0.391 | 0.691 | 1.071 | 1.431 | 1.736 | 2.2
[6 empty] | 1.506 | 0.027 | 0.056 | 0.085 | 0.128 | 0.234 | 0.396 | 0.588 | 0.784 | 0.981 | 1.2
[6 empty] | 2 | 1.209 | 2.459 | 3.305 | 5.116 | 9.421 | 16.828 | 26.55 | 36.591 | 44.523 | 49
[6 empty] | 2.01 | 0.315 | 0.817 | 1.505 | 2.87 | 5.482 | 9.305 | 13.774 | 18.306 | 23.17 | 28
[6 empty] | 2.02 | 0.171 | 0.467 | 0.882 | 1.633 | 3.179 | 5.473 | 8.207 | 11.089 | 13.683 | 17
[6 empty] | 2.03 | 0.146 | 0.369 | 0.662 | 1.023 | 1.894 | 3.286 | 5.007 | 6.711 | 8.407 | 10
[6 empty] | 3 | 2.007 | 4.467 | 7.366 | 12.276 | 22.522 | 38.624 | 62.018 | 79.573 | 90.094 | 100
[6 empty] | 3.01 | 1.004 | 2.505 | 4.499 | 6.963 | 12.945 | 23.649 | 36.145 | 47.819 | 58.698 | 70
[6 empty] | 3.02 | 0.727 | 1.606 | 2.636 | 3.946 | 7.53 | 13.569 | 21.257 | 28.974 | 34.99 | 42
[6 empty] | 3.03 | 0.355 | 0.887 | 1.588 | 2.455 | 4.505 | 8.075 | 12.547 | 16.822 | 20.779 | 25
[6 empty] | 4 | 2.896 | 6.719 | 11.479 | 17.159 | 29.352 | 56.255 | 86.653 | 120.896 | 153.844 | 190
[6 empty] | 4.01 | 1.558 | 3.765 | 6.626 | 10.108 | 18.418 | 32.827 | 55.269 | 77.526 | 98.631 | 120
[6 empty] | 4.02 | 1.45 | 3.05 | 4.822 | 8.099 | 14.857 | 24.2 | 35.222 | 49.808 | 61.142 | 72
[6 empty] | 4.03 | 0.882 | 1.818 | 2.839 | 4.443 | 8.424 | 14.384 | 21.124 | 27.793 | 34.167 | 42
[6 empty] | 6 | 4.225 | 9.715 | 16.432 | 25.732 | 49.583 | 89.691 | 140.008 | 195.766 | 256.778 | 295
[6 empty] | 6.01 | 2.829 | 6.733 | 11.683 | 17.723 | 31.528 | 53.903 | 88.375 | 113.113 | 140.553 | 165
[6 empty] | 6.02 | 1.364 | 3.606 | 6.678 | 10.62 | 17.821 | 28.656 | 42.883 | 57.38 | 71.534 | 85
[6 empty] | 6.03 | 0.911 | 1.895 | 2.949 | 4.261 | 7.768 | 13.68 | 21.418 | 29.715 | 37.963 | 50
|  |  | GLOBE PARABOLIC PLUG LINEAR |  |  | TABLE NAME: | GP_EQ 10: GP_LIN; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  | Decimal sizes N.01, N.02, N.03 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  | represent "N" inch valve , 1, 2, 3 … |  |  | 0.5 | 0.531 | 1.268 | 1.949 | 2.659 | 3.377 | 4.085 | 4.764 | 5.51 | 6.672 | 7
|  |  | sizes reduced. |  |  | 0.501 | 0.358 | 0.744 | 1.225 | 1.61 | 1.992 | 2.365 | 2.719 | 3.049 | 3.411 | 4
[6 empty] | 0.502 | 0.278 | 0.532 | 0.785 | 1.069 | 1.319 | 1.52 | 1.707 | 1.879 | 2.033 | 2.3
[6 empty] | 0.503 | 0.19 | 0.356 | 0.515 | 0.669 | 0.819 | 0.971 | 1.15 | 1.275 | 1.377 | 1.5
[6 empty] | 0.504 | 0.092 | 0.172 | 0.249 | 0.324 | 0.397 | 0.47 | 0.542 | 0.612 | 0.683 | 0.8
[6 empty] | 0.505 | 0.055 | 0.105 | 0.154 | 0.202 | 0.251 | 0.3 | 0.351 | 0.401 | 0.452 | 0.5
[6 empty] | 0.506 | 0.035 | 0.065 | 0.095 | 0.124 | 0.153 | 0.182 | 0.211 | 0.24 | 0.27 | 0.3
[6 empty] | 0.75 | 0.845 | 1.678 | 2.573 | 3.311 | 4.036 | 4.743 | 5.425 | 6.179 | 7.609 | 9
[6 empty] | 0.751 | 0.347 | 0.819 | 1.402 | 2.167 | 2.779 | 3.388 | 3.977 | 4.53 | 5.031 | 5.5
[6 empty] | 0.752 | 0.294 | 0.742 | 1.078 | 1.403 | 1.731 | 2.125 | 2.372 | 2.597 | 2.799 | 3
[6 empty] | 0.753 | 0.237 | 0.438 | 0.628 | 0.811 | 0.987 | 1.155 | 1.317 | 1.47 | 1.615 | 2
[6 empty] | 0.754 | 0.125 | 0.241 | 0.358 | 0.478 | 0.599 | 0.721 | 0.842 | 0.964 | 1.084 | 1.2
[6 empty] | 0.755 | 0.078 | 0.148 | 0.215 | 0.284 | 0.352 | 0.42 | 0.49 | 0.559 | 0.63 | 0.7
[6 empty] | 0.756 | 0.048 | 0.089 | 0.129 | 0.169 | 0.207 | 0.245 | 0.284 | 0.322 | 0.36 | 0.4
[6 empty] | 1 | 1.288 | 2.619 | 4.023 | 5.415 | 6.826 | 8.125 | 8.899 | 10.246 | 11.931 | 13.5
[6 empty] | 1.001 | 0.773 | 1.538 | 2.307 | 3.147 | 3.919 | 4.679 | 5.415 | 6.122 | 7.003 | 8.5
[6 empty] | 1.002 | 0.463 | 0.939 | 1.433 | 1.937 | 2.458 | 3.02 | 3.519 | 3.997 | 4.441 | 5.4
[6 empty] | 1.003 | 0.277 | 0.562 | 0.857 | 1.16 | 1.468 | 1.772 | 2.071 | 2.358 | 2.658 | 3.1
[6 empty] | 1.004 | 0.178 | 0.367 | 0.566 | 0.775 | 0.988 | 1.201 | 1.408 | 1.606 | 1.789 | 2
[6 empty] | 1.005 | 0.114 | 0.23 | 0.348 | 0.468 | 0.589 | 0.711 | 0.831 | 0.949 | 1.065 | 1.2
[6 empty] | 1.006 | 0.07 | 0.138 | 0.207 | 0.276 | 0.344 | 0.413 | 0.482 | 0.55 | 0.619 | 0.8
[6 empty] | 1.5 | 2.636 | 5.382 | 8.457 | 11.766 | 15.22 | 18.767 | 21.562 | 24.09 | 26.5 | 28
[6 empty] | 1.501 | 1.625 | 3.16 | 4.699 | 6.25 | 7.896 | 9.519 | 11.12 | 12.681 | 14.181 | 16
[6 empty] | 1.502 | 0.946 | 1.885 | 2.86 | 3.86 | 4.875 | 5.884 | 6.901 | 7.918 | 8.855 | 10.5
[6 empty] | 1.503 | 0.565 | 1.128 | 1.72 | 2.333 | 2.955 | 3.579 | 4.19 | 4.779 | 5.332 | 6
[6 empty] | 1.504 | 0.369 | 0.743 | 1.135 | 1.543 | 1.961 | 2.379 | 2.788 | 3.182 | 3.549 | 4
[6 empty] | 1.505 | 0.188 | 0.377 | 0.573 | 0.777 | 0.985 | 1.194 | 1.4 | 1.598 | 1.784 | 2.2
[6 empty] | 1.506 | 0.123 | 0.239 | 0.355 | 0.472 | 0.59 | 0.71 | 0.828 | 0.946 | 1.063 | 1.2
[6 empty] | 2 | 4.13 | 9.242 | 14.478 | 19.708 | 25.087 | 30.564 | 35.974 | 40.012 | 44.642 | 49
[6 empty] | 2.01 | 2.274 | 4.969 | 7.877 | 10.938 | 13.724 | 16.509 | 19.277 | 22.026 | 24.965 | 28
[6 empty] | 2.02 | 1.264 | 2.764 | 4.372 | 6.054 | 7.773 | 9.527 | 11.227 | 12.727 | 14.317 | 17
[6 empty] | 2.03 | 0.816 | 1.779 | 2.804 | 3.86 | 4.927 | 5.981 | 7.006 | 7.98 | 8.889 | 10
[6 empty] | 3 | 9.958 | 21.061 | 32.395 | 42.652 | 52.98 | 63.698 | 76.666 | 86.071 | 91.149 | 100
[6 empty] | 3.01 | 5.353 | 11.637 | 18.738 | 26.583 | 33.661 | 40.457 | 47.179 | 53.741 | 60.338 | 70
[6 empty] | 3.02 | 3.465 | 7.212 | 11.2 | 15.378 | 19.686 | 24.058 | 28.448 | 31.986 | 35.659 | 42
[6 empty] | 3.03 | 2.171 | 4.467 | 6.858 | 9.318 | 11.806 | 14.291 | 16.726 | 19.075 | 21.29 | 25
[6 empty] | 4 | 12.667 | 27.122 | 47.273 | 66.038 | 85.993 | 106.882 | 127.853 | 147.47 | 167.929 | 190
[6 empty] | 4.01 | 7.319 | 15.766 | 25.332 | 36.426 | 51.054 | 63.296 | 75.776 | 88.317 | 103.943 | 120
[6 empty] | 4.02 | 7.018 | 13.838 | 20.643 | 27.411 | 34.071 | 43.442 | 50.854 | 57.09 | 63.09 | 72
[6 empty] | 4.03 | 4.032 | 8.164 | 12.452 | 16.817 | 21.179 | 25.44 | 29.513 | 33.306 | 37.671 | 42
[6 empty] | 6 | 28.431 | 57.146 | 86.052 | 112.257 | 136.072 | 159.161 | 181.587 | 212.574 | 263.118 | 295
[6 empty] | 6.01 | 16.09 | 32.01 | 47.67 | 63.09 | 78.18 | 93.11 | 105.76 | 117.42 | 137.91 | 165
[6 empty] | 6.02 | 8.775 | 17.429 | 25.904 | 34.147 | 42.126 | 49.781 | 57.066 | 63.938 | 71.485 | 85
[6 empty] | 6.03 | 4.321 | 9.065 | 14.143 | 19.449 | 24.875 | 30.315 | 35.638 | 40.718 | 45.424 | 50
|  |  |  | ECCENTRIC ROTARY PLUG |  |  | GP_LIN 10: TABLE NAME:; GP_LIN 20: ROT_PLUG; Valve Travel, % 50: Valve Travel, %
[8 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  |  | Decimal sizes N.01 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  |  | represent "N" inch valve , 1 |  |  | 1 | 1.09 | 2.01 | 2.97 | 3.86 | 4.97 | 6.19 | 8.04 | 10.1 | 12.4 | 14.5
|  |  |  | size reduced. |  |  | 1.01 | 0.74 | 1.65 | 2.13 | 2.66 | 3.18 | 3.72 | 4.58 | 5.72 | 7.01 | 7.9
[7 empty] | 1.5 | 2.1 | 4.6 | 7.5 | 10.2 | 13.7 | 17.6 | 21.7 | 26 | 29.4 | 31
[7 empty] | 1.51 | 2.1 | 4.6 | 6.2 | 7.4 | 9.4 | 11.4 | 13.5 | 14.8 | 15.2 | 15.5
[7 empty] | 2 | 4.3 | 9 | 14 | 19 | 25 | 31 | 39 | 45 | 50 | 52
[7 empty] | 2.01 | 3.8 | 8 | 10 | 13 | 16 | 19 | 23 | 25 | 25.5 | 26
[7 empty] | 3 | 10 | 20 | 30 | 41 | 52 | 66 | 85 | 103 | 121 | 137
[7 empty] | 3.01 | 10 | 20 | 26 | 32 | 40 | 48 | 57 | 63 | 65 | 66
[7 empty] | 4 | 17 | 35 | 50 | 70 | 89 | 113 | 145 | 176 | 206 | 239
[7 empty] | 4.01 | 17 | 35 | 48 | 58 | 73 | 88 | 104 | 114 | 117 | 120
[7 empty] | 6 | 49 | 103 | 160 | 216 | 272 | 328 | 380 | 434 | 485 | 520
[7 empty] | 6.01 | 37 | 75 | 104 | 125 | 158 | 191 | 226 | 247 | 254 | 260
[7 empty] | 8 | 75 | 151 | 220 | 301 | 388 | 499 | 603 | 719 | 823 | 870
[7 empty] | 8.01 | 58 | 128 | 175 | 211 | 267 | 323 | 383 | 419 | 431 | 440
[7 empty] | 10 | 115 | 231 | 336 | 460 | 593 | 763 | 922 | 1099 | 1258 | 1330
[7 empty] | 10.01 | 85 | 188 | 271 | 326 | 412 | 500 | 592 | 647 | 666 | 680

## Wall Thck.
NO USER INPUT IS REQUIRED FOR THIS TAB.
PIPE WALL THICKNESS
Note: this data is believed to be accurate, but it is the user's responsibility to determine its applicability to their purpose.
| NPS | Outside Diameter | Schedule
| (in) | (in) (mm) | 10 | 20 | 30 | STD | 40 | 60 | XS | 80 | 100 | 120 | 140 | 160 | XXS
Wall Thickness (in) (mm)
| 1/8 | 0.405 |  |  |  | 0.068 | 0.068 |  | 0.095 | 0.095
|  | 10.3 |  |  |  | 1.73 | 1.73 |  | 2.41 | 2.41
| 1/4 | 0.54 |  |  |  | 0.088 | 0.088 |  | 0.119 | 0.119
|  | 13.7 |  |  |  | 2.24 | 2.24 |  | 3.02 | 3.02
| 3/8 | 0.675 |  |  |  | 0.091 | 0.091 |  | 0.126 | 0.126
|  | 17.1 |  |  |  | 2.31 | 2.31 |  | 3.2 | 3.2
| 1/2 | 0.84 |  |  |  | 0.109 | 0.109 |  | 0.147 | 0.147 |  |  |  | 0.187 | 0.294
|  | 21.3 |  |  |  | 2.77 | 2.77 |  | 3.73 | 3.73 |  |  |  | 4.75 | 7.47
| 3/4 | 1.05 |  |  |  | 0.113 | 0.113 |  | 0.154 | 0.154 |  |  |  | 0.219 | 0.308
|  | 26.7 |  |  |  | 2.87 | 2.87 |  | 3.91 | 3.91 |  |  |  | 5.56 | 7.82
| 1 | 1.315 |  |  |  | 0.133 | 0.133 |  | 0.179 | 0.179 |  |  |  | 0.25 | 0.358
|  | 33.4 |  |  |  | 3.38 | 3.38 |  | 4.55 | 4.55 |  |  |  | 6.35 | 9.09
| 1.25 | 1.66 |  |  |  | 0.14 | 0.14 |  | 0.191 | 0.191 |  |  |  | 0.25 | 0.382
|  | 42.2 |  |  |  | 3.56 | 3.56 |  | 4.85 | 4.85 |  |  |  | 6.35 | 9.7
| 1.5 | 1.9 |  |  |  | 0.145 | 0.145 |  | 0.2 | 0.2 |  |  |  | 0.281 | 0.4
|  | 48.3 |  |  |  | 3.68 | 3.68 |  | 5.08 | 5.08 |  |  |  | 7.14 | 10.2
| 2 | 2.375 |  |  |  | 0.154 | 0.154 |  | 0.218 | 0.218 |  |  |  | 0.344 | 0.436
|  | 60.3 |  |  |  | 3.91 | 3.91 |  | 5.54 | 5.54 |  |  |  | 8.74 | 11.1
| 2.5 | 2.875 |  |  |  | 0.203 | 0.203 |  | 0.276 | 0.276 |  |  |  | 0.375 | 0.552
|  | 73 |  |  |  | 5.16 | 5.16 |  | 7.01 | 7.01 |  |  |  | 9.52 | 14
| 3 | 3.5 |  |  |  | 0.216 | 0.216 |  | 0.3 | 0.3 |  |  |  | 0.438 | 0.6
|  | 88.9 |  |  |  | 5.49 | 5.49 |  | 7.62 | 7.62 |  |  |  | 11.1 | 15.2
| 3.5 | 4 |  |  |  | 0.226 | 0.226 |  | 0.318 | 0.318
|  | 102 |  |  |  | 5.74 | 5.74 |  | 8.08 | 8.08
| 4 | 4.5 |  |  |  | 0.237 | 0.237 |  | 0.337 | 0.337 |  | 0.438 |  | 0.531 | 0.674
|  | 114 |  |  |  | 6.02 | 6.02 |  | 8.56 | 8.56 |  | 11.1 |  | 13.5 | 17.1
| 5 | 5.563 |  |  |  | 0.258 | 0.258 |  | 0.375 | 0.375 |  | 0.5 |  | 0.625 | 0.75
|  | 141 |  |  |  | 6.55 | 6.55 |  | 9.52 | 9.52 |  | 12.7 |  | 15.9 | 19
| 6 | 6.625 |  |  |  | 0.28 | 0.28 |  | 0.432 | 0.432 |  | 0.562 |  | 0.719 | 0.864
|  | 168 |  |  |  | 7.11 | 7.11 |  | 11 | 11 |  | 14.3 |  | 18.3 | 21.9
| 8 | 8.625 |  | 0.25 | 0.277 | 0.322 | 0.322 | 0.406 | 0.5 | 0.5 | 0.594 | 0.719 | 0.812 | 0.906 | 0.875
|  | 219 |  | 6.35 | 7.04 | 8.18 | 8.18 | 10.3 | 12.7 | 12.7 | 15.1 | 18.3 | 20.6 | 23 | 22.2
| 10 | 10.75 |  | 0.25 | 0.307 | 0.365 | 0.365 | 0.5 | 0.5 | 0.594 | 0.719 | 0.844 | 1 | 1.125 | 1
|  | 273 |  | 6.35 | 7.8 | 9.27 | 9.27 | 12.7 | 12.7 | 15.1 | 18.3 | 21.4 | 25.4 | 28.6 | 25.4
| 12 | 12.75 |  | 0.25 | 0.33 | 0.375 | 0.406 | 0.562 | 0.5 | 0.688 | 0.844 | 1 | 1.125 | 1.312 | 1
|  | 324 |  | 6.35 | 8.38 | 9.52 | 10.3 | 14.3 | 12.7 | 17.5 | 21.4 | 25.4 | 28.6 | 33.3 | 25.4
| 14 | 14 | 0.25 | 0.312 | 0.375 | 0.375 | 0.438 | 0.594 | 0.5 | 0.75 | 0.938 | 1.094 | 1.25 | 1.406
|  | 356 | 6.35 | 7.92 | 9.52 | 9.52 | 11.1 | 15.1 | 12.7 | 19 | 23.8 | 27.8 | 31.8 | 35.7
| 16 | 16 | 0.25 | 0.312 | 0.375 | 0.375 | 0.5 | 0.656 | 0.5 | 0.844 | 1.031 | 1.219 | 1.438 | 1.594
|  | 406 | 6.35 | 7.92 | 9.52 | 9.52 | 12.7 | 16.7 | 12.7 | 21.4 | 26.2 | 31 | 36.5 | 40.5
| 18 | 18 | 0.25 | 0.312 | 0.438 | 0.375 | 0.562 | 0.75 | 0.5 | 0.938 | 1.156 | 1.375 | 1.562 | 1.781
|  | 457 | 6.35 | 7.92 | 11.1 | 9.52 | 14.3 | 19 | 12.7 | 23.8 | 29.4 | 34.9 | 39.7 | 45.2
| 20 | 20 | 0.25 | 0.375 | 0.5 | 0.375 | 0.594 | 0.812 | 0.5 | 1.031 | 1.281 | 1.5 | 1.75 | 1.969
|  | 508 | 6.35 | 9.52 | 12.7 | 9.52 | 15.1 | 20.6 | 12.7 | 26.2 | 32.5 | 38.1 | 44.4 | 50
| 22 | 22 | 0.25 | 0.375 | 0.5 | 0.375 |  | 0.875 | 0.5 | 1.125 | 1.375 | 1.625 | 1.875 | 2.125
|  | 559 | 6.35 | 9.52 | 12.7 | 9.52 |  | 22.2 | 12.7 | 28.6 | 34.9 | 41.3 | 47.6 | 54
| 24 | 24 | 0.25 | 0.375 | 0.562 | 0.375 | 0.688 | 0.969 | 0.5 | 1.219 | 1.531 | 1.812 | 2.062 | 2.344
|  | 610 | 6.35 | 9.52 | 14.3 | 9.52 | 17.5 | 24.6 | 12.7 | 31 | 38.9 | 46 | 52.4 | 59.5
| 30 | 30 | 0.312 | 0.5 | 0.625 | 0.375 |  |  | 0.5
|  | 762 | 7.92 | 12.7 | 15.9 | 9.52 |  |  | 12.7
| 32 | 32 | 0.312 | 0.5 | 0.625 | 0.375 | 0.688
|  | 813 | 7.92 | 12.7 | 15.9 | 9.52 | 17.5
| 34 | 34 | 0.312 | 0.5 | 0.625 | 0.375 | 0.688
|  | 864 | 7.92 | 12.7 | 15.9 | 9.52 | 17.5
| 36 | 36 | 0.312 | 0.5 | 0.625 | 0.375 | 0.75
|  | 914 | 7.92 | 12.7 | 15.9 | 9.52 | 19
| 42 | 42 |  | 0.5 | 0.625 | 0.375 | 0.75
|  | 1067 |  | 12.7 | 15.9 | 9.52 | 19