## Read Me
DOUBLE CLICK THE IMAGE TO THE LEFT TO READ THE
INSTRUCTIONS FOR THIS WORKBOOK.
The instruction booklet will open in a new Acrobat window.
The main user interface for this workbook is on the Vallve Sizing tab.
Your expereince with this workbook will be significantly enhanced it you read
the INTRODUCTION and USING THE WORKBOOK sections.

## Valve Sizing
CONTROL VALVE SIZING: LIQUID |  |  | TAG: | PV123 |  |  |  |  | Available Cv table names |  | Scroll to the right to view the intermediate calculations. | Valve sizing per ISA S75.01.01 2012
Flow | gpm | Q | 80 | 213 | 423 | 550 |  |  | BALL_FP | Full Port Ball Valve |  | DESCRIPTION OF VARIABLE | Eqn. | NAME OF VARIABLE | FORMULA
Inlet pressure | psiA | P_1 | 56.7 | 55.4 | 50.7 | 46.7 |  |  | BALL_RP | Reduced Port Ball Valve |  | CALCULATED IN COLUMN "S" |  | CALCULATED IN COLUMN "S"
Pressure drop | psi | DELTA_P | 32 | 30.4 | 24.9 | 20 |  |  | BALL_SEG | Segment Ball valve |  | Critical pressure ratio factor | 4 | F_F | 0.95665 | 0.95665 | 0.95665 | 0.95665
Specific gravity (r1/r0) |  | G | 1 | 1 | 1 | 1 |  |  | HPBF_150 | High Perf. Buttefly Cl 150 |  | WITHOUT REDUCERS
Vapor pressure | psiA | P_V | 0.46 | 0.46 | 0.46 | 0.46 |  |  | HPBF_300 | High Perf. Buttefly Cl 300 |  | Choked pressure drop | 3 | Delta_P_Ch | 48.6592 | 44.5176 | 32.1664 | 23.9812
Critical pressure | psiA | P_C | 3208 | [5 empty] | HPBF_600 | High Perf. Buttefly Cl 600 |  | C Non choked | 1 | C_NonCh | 14.1421 | 38.6316 | 84.7697 | 122.9837
Speed of sound in liquid | ft/s | c_1 | 4000 |  |  |  |  | 1 | GC_EQ | Globe Cage Guided =% |  | C Choked | 1 | C_Ch | 11.4685 | 31.9238 | 74.5829 | 112.3124
Recovery factor |  | F_L | 0.93 | 0.9 | 0.8 | 0.72 |  | 3 | GC_LIN | Globe Cage Guided linear |  | Select C Non choked or C choked | 2 | Applicable_C_NonCh_or_Ch | 14.1421 | 38.6316 | 84.7697 | 122.9837
Valve style modifier |  | F_D | 0.77929 | 0.84725 | 0.91936 | 0.95531 |  | 1, 2 | GP_EQ | Globe Parabolic Plug =% |  | (This is the initial guess for
DP ratio of incipient cavitation |  | x_Fz | 0.42716 | 0.38738 | 0.32461 | 0.28157 |  | 1, 2 | GP_LIN | Globe Parabolic Plug Linear |  | the following iterative calculations)
Valve correction - accoustic efficiency, Ah |  | A_ETA | -4.6 |  |  |  |  | 1, 2 | ROT_PLUG | Eccentric Rotary Plug
Inlet pipe diameter | inch | D_1 | 6 | [8 empty] | WITH REDUCERS
Outlet pipe diameter | inch | D_2 | 6 | [8 empty] | Reducer velocity head coefficients | 18 | ZETA_1 | 0.28125
Valve size | inch | d | 3 | [9 empty] | 17 | ZETA_B1 | 0.9375
Seat or Orifice Diameter | inch | d_o | 3 |  |  |  |  | 1, 6 |  |  |  |  | 19 | ZETA_2 | 0.5625
Valve Cv Table |  | Cv_Table | BALL_SEG |  |  |  |  | 5 |  |  |  |  | 17 | ZETA_B2 | 0.9375
Outlet pipe wall thickness | inch | T_S | 0.23 |  |  |  |  | 1 |  |  |  | Sum of velocity head coefficients | 16 | SIGMA_ZETA | 0.84375
For non-turbulent flow (valve Reynolds Number < 10,000) - Optional data if non-turbulent flow is suspected | [11 empty] | Sum of upstream velocity head coef |  | SIGMA_ZETA_1 | 1.2188
Kinematic viscosity, h | cS | nu_VS | [5 empty] | 7
Valve style modifier-for Non turbulent calcs. |  | F_D_NT | [5 empty] | 7, 8 |  |  |  | Beginning of iterative calculation |  | Total of 59 iterations
Reduced trim? C(Rated)<N18*0.016 (yes or no) |  | RED_TRM | NO | [8 empty] | Assumed C for this iteration |  | C_i | 14.1421 | 38.6316 | 84.7697 | 122.9837
Required flow coef. (Cv or Kv) | Cv | C_ | 14.1587 | 38.9735 | 88.5763 | 135.5671 |  | 1 = This entry is only used in the IEC noise calculation. |  |  |  | Piping geometry factor | 15 | F_P | 0.99883 | 0.99138 | 0.96043 | 0.92174
Flow calc from Cv or Kv | gpm |  | 80 | 213 | 423 | 550 |  | 2 = Values automatically copied from the "xT, FL, Fd, Aeta, Stp" tab after Cv is calculated. Can be overridden manually after unprotecting sheet. |  |  |  | Combined liquid pressure recovery
Choked delta p | psi |  | 48.6308 | 44.3858 | 32.3721 | 25.0972 |  | 3 = See "Typical FL, Fd, XfZ, AEta " tab for typical values. |  |  |  | factor and piping geometry factor | 21 | F_LP | 0.92864 | 0.89094 | 0.7706 | 0.67655
Sound pressure level | dB(A) |  | 64.5875 | 72.8683 | 77.812 | 78.2066 |  | 4 = See "Valve Travel" tab for supported valve sizes. |  |  |  | C Non choked w/ reducers | 1 | C_NonCh_W_Reducers | 14.1587 | 38.9675 | 88.2625 | 133.426
Valve inlet velocity | ft/s |  | 3.6311 | 9.6678 | 19.1995 | 24.9639 |  | 5 = A valid "Cv table" name must be entered for SPL and Travel results. |  |  |  | C Choked w/ reducers | 1 | C_Ch_W_Reducers | 11.4853 | 32.2483 | 77.4281 | 119.5247
Travel | % |  | 22.2445 | 39.7399 | 60.1147 | 73.3107 |  | 6 = If unknown, use valve size. |  |  |  | Choked pressure drop w/ reducers | 3 | Delta_P_Ch_W_Reducers | 48.6309 | 44.388 | 32.356 | 24.9227
[5 empty] | Data input | Calculated values |  | 7 = Only required if non-turbulent flow is suspected. |  |  |  | Select C Non choked or C choked |  |  | 14.1587 | 38.9675 | 88.2625 | 133.426
Unit selection: | 1 | 1 = US; 2 = SI (Cv, bar); 3 = SI (Cv, kPa); 4 = SI (Kv, bar); 5 = SI (Kv, kPa) | [5 empty] | 8 = Copy and paste (values) from "Valve style modifier" above after doing initial turbulent calc. |  |  |  | Ci/ C, this iteration |  | C_i divided by S29 | 0.99883 | 0.99138 | 0.96043 | 0.92174
Valve & pipe dia., wall thickness: | 1 | 1 = inch & Cv 2 = mm & Cv 3 = mm & Kv
[12 empty] | Assumed C for this iteration |  |  | 14.1587 | 38.9675 | 88.2625 | 133.426
VDMA Noise Calculaations based on Sch. 40 pipe. Used only for analysis of possible cavitation damage. | [11 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95731 | 0.90971
Valve Style Code |  | VSC | 2 | [8 empty] | Combined liquid pressure recovery
Sch 40 pipe wall attenuation |  | DeltaLp | -2 | Auto filled based on outlet pipe diameter | [7 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89079 | 0.76828 | 0.66965
|  | FLAG_1 | 1 | 1=flow coef is Cv 2=flow coef is Kv |  |  | Flag_1 is set with a formula based on B30 and only applies to the VDMA noise calculation |  |  |  |  | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9734 | 88.55 | 135.1905
Sound pressure level (VDMA) | dB(A) |  | 66.2314 | 71.4645 | 74.7282 | 75.3717 | [5 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.254 | 77.6626 | 120.7565
Cavitation Damage Warning |  |  | OK | OK | OK | OK |  |  | Valve Style Codes are automatically set based on the Valve Cv Table entered above. |  |  | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3707 | 25.0669
|  |  | "SEE NOTE !!" in the above row indicates that there is the potential for | [5 empty] | For reference, the the valve style codes configure the VDMA noise calculation for |  |  | Select C Non choked or C choked |  |  | 14.1587 | 38.9734 | 88.55 | 135.1905
|  |  | cavitation damage due to either fully choked flow (without flashing | [5 empty] | the valve types as listed below: |  |  | Ci / C, this iteration |  |  | 1 | 0.99985 | 0.99675 | 0.98695
conditions) or excessive noise being caused by cavitation.
[9 empty] | VSC | Valve type |  | Assumed C for this iteration |  |  | 14.1587 | 38.9734 | 88.55 | 135.1905
Intermedient calculations | [8 empty] | 0 | Globe Cage Guided |  | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95705 | 0.90763
Choked pressure drop |  | DP_CH | 48.6308 | 44.3858 | 32.3721 | 25.0972 |  |  | 1 | Eccentric Rotary Plug |  | Combined liquid pressure recovery
[9 empty] | 2 | Segment Ball valve |  | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76808 | 0.66845
[9 empty] | 3 | High Perf. Buttefly |  | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5741 | 135.5005
[9 empty] | 4 | Ball |  | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6823 | 120.9733
[9 empty] | 5 | Globe Parabolic Pludt |  | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.372 | 25.0919
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5741 | 135.5005
For Valve inlet velocitky calc: | [11 empty] | Ci / C, this iteration |  |  | 1 | 1 | 0.99973 | 0.99771
Valve size in units of INCH | Vsize_INCH | 3
[12 empty] | Assumed C for this iteration |  |  | 14.1587 | 38.9735 | 88.5741 | 135.5005
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95703 | 0.90726
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76807 | 0.66824
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5762 | 135.5553
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.684 | 121.0116
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0962
| The cells below detrmine if any input data is missing. | [10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5762 | 135.5553
| If it is, error messages are blanked out of the calculated results. | [10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 0.99998 | 0.9996
| TURB1 | TURB2 | TURB3 | TURB4
| 21514037413.4784 | 51454268448.5837 | 68085339533.1533 | 58946498012.16 | [7 empty] | Assumed C for this iteration |  |  | 14.1587 | 38.9735 | 88.5762 | 135.5553
| N_TURB1 | N_TURB2 | N_TURB3 | N_TURB4 | [7 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90719
Combined liquid pressure recovery
| N_DAT1 | N_DAT2 | N_DAT3 | N_DAT4 | [7 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
| -4226.262 | -4166.8962 | -3788.8431 | -3415.0834 | [7 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.565
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0184
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.097
These Numerical constants are set by the units choises set by the user above the user interface | [11 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.565
which incllude all the options for the ISA Standard | [11 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 0.99993
Numerical constants
N_1 | 1 | [10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.565
N_2 | 890 | [10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
N_4 | 17300 | [10 empty] | Combined liquid pressure recovery
N_18 | 645 | [10 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
N_32 | 17 | [10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5667
N_41 | 12.1 | 12.1=density lbm/ft^3, pressure psia | [9 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0196
|  | 39.0 =density kg/m^3, barA | [9 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
|  | 3.0=density kg/m^3, pressure kPaA | [9 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5667
[5 empty] | Flag_1 is used in the VDMA Noise Calc | [6 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 0.99999
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5667
NOTE: The above constants are set by formulas in those cells and are based on the unit selection made in Cells B30 or B31. | [11 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
FLAG_1 & N_41 only have an effect in the VDMA noise calculation | [11 empty] | Combined liquid pressure recovery
FLAG_3 only has an effect of the Inlet velocity calculation | [11 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
N_41 is a constant added by the Author for setting the noise calculation to use the appropriate units. | [11 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.567
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0198
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.567
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.567
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | CI / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor |  |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
[12 empty] | Combined liquid pressure recovery | 15
[12 empty] | factor and piping geometry factor |  |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 21 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 1 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked | 3 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | CI / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor |  |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
[12 empty] | Combined liquid pressure recovery | 15
[12 empty] | factor and piping geometry factor |  |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 21 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 1 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked | 3 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[12 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 |  | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | C Choked w/ reducers | 1 |  | 11.4853 | 32.2541 | 77.6841 | 121.0199
[12 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
Confirmation that the calculated C will
produce the given flow rate
[12 empty] | Final C calculated above |  | Final_Calculated_C | 14.1587 | 38.9735 | 88.5763 | 135.5671
[12 empty] | Piping geometry factor | 15 | Final_F_P | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[12 empty] | factor and piping geometry factor | 21 | Final_F_LP | 0.92864 | 0.89078 | 0.76806 | 0.6682
[12 empty] | Flow Non choked w/ reducers | 1 | Final_Flow_NonCh_W_Reducers | 80 | 213 | 423 | 550
[12 empty] | Flow Choked w/ reducers | 1 | Final_Flow_Ch_W_Reducers | 98.6213 | 257.374 | 482.3097 | 616.1128
[12 empty] | Choked pressure drop w/ reducers | 3 | Final_Delta_P_Ch_W_Reducers | 48.6308 | 44.3858 | 32.3721 | 25.0972
[12 empty] | Calculated flow from final calculated C |  | Calc_Flow_From_Final__ Calc_C | 80 | 213 | 423 | 550
Hydrodynamic noise calculation
Based on VDMA24422 1979
This is only used for optional determination of possible Cavitation damage.
[12 empty] | Valve nominal size in inches |  | d_in | 3 | ============> | ============> | ============>
[12 empty] | Cv/nominal size in inches squared |  | C_d | 1.5732 | 4.3304 | 9.8418 | 15.063
VALVE STYLE SPECIFIC
PRESSURE DROP RATIOS WHERE
CAVITATION NOISE IS FIRST
DETECTED
[12 empty] | For Cage globe valves |  | z_0 | 0.32213 | 0.22698 | 0.21782 | 0.20606
[12 empty] | For eccentric rotary plug valves |  | z_1 | 0.47973 | 0.38055 | 0.33092 | 0.22477
[12 empty] | For segment ball valves |  | z_2 | 0.42083 | 0.38889 | 0.33133 | 0.28453
[12 empty] | For butterfly valves |  | z_3 | 0.35391 | 0.32703 | 0.2783 | 0.2383
[12 empty] | For ball valves |  | z_4 | 0.48259 | 0.43507 | 0.35364 | 0.2906
[12 empty] | For Parabolic plug globe valves |  | z_5 | 0.65 | 0.62791 | 0.55265 | 0.45841
[12 empty] | For selected valve based on VSC |  | z | 0.42083 | 0.38889 | 0.33133 | 0.28453
(Valve Style Code)
[12 empty] | Pressure drop ratio |  | x_F | 0.56899 | 0.55333 | 0.49562 | 0.43253
[12 empty] | Scaled pressure drop ratio |  | x_R | 0.25581 | 0.26908 | 0.2457 | 0.20685
VALVE STYLE SPECIFIC NOISE
COEFFICIENT
[12 empty] | For globe valves |  | DeltaLf_0 | -6.9724 | -7.1578 | -6.8232 | -6.1867
[12 empty] | For eccentric rotary plug valves |  | DeltaLf_1 | -6.9724 | -7.1578 | -6.8232 | -6.1867
[12 empty] | For segment ball valves |  | DeltaLf_2 | 0 | 0 | 0 | 0
[12 empty] | For butterfly valves |  | DeltaLf_3 | 2 | 2 | 2 | 2
[12 empty] | For ball valves |  | DeltaLf_4 | 1.5349 | 1.6145 | 1.4742 | 1.2411
[12 empty] | For selected valve based on VSC |  | DeltaLf | 0 | 0 | 0 | 0
(Valve Style Code)
[12 empty] | Common portion of SPL Calculation |  | SPL_C | 44.1362 | 48.3508 | 51.2172 | 52.417
[12 empty] | SPL calculation if x_F is <=z |  | SPL_L | 46.4941 | 51.1076 | 54.3652 | 55.6909
[12 empty] | SPL calculation if x_F is >z |  | SPL_G | 66.2314 | 71.4645 | 74.7282 | 75.3717
[12 empty] | Selected SPL (SPL_L or SPL_G) |  | SPL_SELECTED | 66.2314 | 71.4645 | 74.7282 | 75.3717
[12 empty] | Non-Turbulent Calculation of C |  | Total of 12 iterations
[12 empty] | Viscosity limmited to no less than 1.0 |  | nu | 1 | 1 | 1 | 1
[12 empty] | Initial value of C for Non-turb Calculations |  | C_i_NT | 14.1421 | 38.6316 | 84.7697 | 122.9837
[12 empty] | Valve Reynolds Number | 23 | Re_V | 0 | 0 | 0 | 0
[12 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 360.45 | 48.3047 | 10.0321 | 4.7663
[12 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 23.9772 | 45.9003 | 76.8195 | 98.1671
[12 empty] | Select Eta, full or reduced trim |  |  | 360.45 | 48.3047 | 10.0321 | 4.7663
Reynolds Number Factor (FR)
[12 empty] | For laminar flow (Rev < 10) | A.6 |  | 0 | 0 | 0 | 0
[12 empty] | For transitional flow (Rev >= 10) | A.7 |  | #NUM! | #NUM! | #NUM! | #NUM!
[12 empty] | Selected based on actual Rev |  |  | 0 | 0 | 0 | 0
[12 empty] | Calculated flow from Initial Cv | A.2 |  | 0 | 0 | 0 | 0
[12 empty] | Assumed C for iterative purposes |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Valve Reynolds Number | 23 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Select Eta, full or reduced trim |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reynolds Number Factor (FR)
[12 empty] | For laminar flow (Rev < 10) | A.6 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | For transitional flow (Rev >= 10) | A.7 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Selected based on actual Rev |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Non-turbulent flow this iteration | A.2 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Change from previouse iteration |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Assumed C for iterative purposes |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Valve Reynolds Number | 23 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Select Eta, full or reduced trim |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reynolds Number Factor (FR)
[12 empty] | For laminar flow (Rev < 10) | A.6 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | For transitional flow (Rev >= 10) | A.7 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Selected based on actual Rev |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Non-turbulent flow this iteration | A.2 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Change from previouse iteration |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Assumed C for iterative purposes |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Valve Reynolds Number | 23 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Select Eta, full or reduced trim |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reynolds Number Factor (FR)
[12 empty] | For laminar flow (Rev < 10) | A.6 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | For transitional flow (Rev >= 10) | A.7 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Selected based on actual Rev |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Non-turbulent flow this iteration | A.2 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Change from previouse iteration |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Assumed C for iterative purposes |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Valve Reynolds Number | 23 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Select Eta, full or reduced trim |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reynolds Number Factor (FR)
[12 empty] | For laminar flow (Rev < 10) | A.6 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | For transitional flow (Rev >= 10) | A.7 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Selected based on actual Rev |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Non-turbulent flow this iteration | A.2 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Change from previouse iteration |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Assumed C for iterative purposes |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Valve Reynolds Number | 23 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Select Eta, full or reduced trim |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reynolds Number Factor (FR)
[12 empty] | For laminar flow (Rev < 10) | A.6 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | For transitional flow (Rev >= 10) | A.7 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Selected based on actual Rev |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Non-turbulent flow this iteration | A.2 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Change from previouse iteration |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Assumed C for iterative purposes |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Valve Reynolds Number | 23 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Select Eta, full or reduced trim |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reynolds Number Factor (FR)
[12 empty] | For laminar flow (Rev < 10) | A.6 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | For transitional flow (Rev >= 10) | A.7 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Selected based on actual Rev |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Non-turbulent flow this iteration | A.2 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Change from previouse iteration |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Assumed C for iterative purposes |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Valve Reynolds Number | 23 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Select Eta, full or reduced trim |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reynolds Number Factor (FR)
[12 empty] | For laminar flow (Rev < 10) | A.6 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | For transitional flow (Rev >= 10) | A.7 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Selected based on actual Rev |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Non-turbulent flow this iteration | A.2 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Change from previouse iteration |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Assumed C for iterative purposes |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Valve Reynolds Number | 23 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Select Eta, full or reduced trim |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reynolds Number Factor (FR)
[12 empty] | For laminar flow (Rev < 10) | A.6 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | For transitional flow (Rev >= 10) | A.7 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Selected based on actual Rev |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Non-turbulent flow this iteration | A.2 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Change from previouse iteration |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Assumed C for iterative purposes |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Valve Reynolds Number | 23 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Select Eta, full or reduced trim |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reynolds Number Factor (FR)
[12 empty] | For laminar flow (Rev < 10) | A.6 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | For transitional flow (Rev >= 10) | A.7 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Selected based on actual Rev |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Non-turbulent flow this iteration | A.2 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Change from previouse iteration |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Assumed C for iterative purposes |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Valve Reynolds Number | 23 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Select Eta, full or reduced trim |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reynolds Number Factor (FR)
[12 empty] | For laminar flow (Rev < 10) | A.6 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | For transitional flow (Rev >= 10) | A.7 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Selected based on actual Rev |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Non-turbulent flow this iteration | A.2 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Change from previouse iteration |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Assumed C for iterative purposes |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Valve Reynolds Number | 23
[12 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Select Eta, full or reduced trim |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Reynolds Number Factor (FR)
[12 empty] | For laminar flow (Rev < 10) | A.6 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | For transitional flow (Rev >= 10) | A.7 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Selected based on actual Rev |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Non-turbulent flow this iteration | A.2 |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | Change from previouse iteration |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Final Reynolds Number with error hidden

## Installed Flow
Intermediate Calculations
VALVE DATA | ` | [10 empty] | Scroll to the right to see the | DESCRIPTION OF VARIABLE | Eqn. | NAME OF VARIABLE | FORMULA
Valve Cv table | BALL_SEG | [10 empty] | intermediate calculations | CALCULATED IN COLUMN "P" |  | CALCULATED IN COLUMN "P"
Valve size, Inch, from Valve Travel tab | 3
Relative travel, h | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 |  |  | CALCULATE PARAMETERS FOR UPSTREAM AND DOWNSTREAM PROCESS PRESSURE MODEL
Cv from tables on Valve Travel tab | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420 |  |  | Minimum design flow (From Col D) |  | Q_min | 80
FL | 0.94 | 0.92621 | 0.91266 | 0.89316 | 0.86748 | 0.83514 | 0.79614 | 0.74383 | 0.64753 | 0.44067 |  |  | Maximum design flow (From Col F) |  | Q_max | 550
[13 empty] | Valve inlet pressure at minimum des. Flow |  | P_1_minQ | 56.7
[12 empty] | Scroll down for instructions for the Installed flow and gain graphs and | Valve inlet pressure at maximum des. flow |  | P_1_maxQ | 46.7
[12 empty] | the calculation of the fully open flow, Qf. The accuracy of the calculations | Pressure drop at minimum des. flow |  | DELTA_P_minQ | 32
| 3 0.7: BALL_SEG |  | on this and the Installed Gain tab depend on the accuracy of the process | Pressure drop at maximum des. flow |  | DELTA_P_maxQ | 20
| 3 0.7: 3 |  | data. | Valve outlet pressure at minimum des. Flow |  | P_2_minQ | 24.7
| 3 0.7: PV123 |  |  | Valve outlet pressure at maximum des. flow |  | P_2_maxQ | 26.7
[13 empty] | Upstream system drop |  | dp_up | 10
| 3 0.7: Fully open Flow, Qf |  | INSTALED FLOW AND GAIN ERRORS | Upstream system resistance factor |  | R_up | 3.3772e-05 |  | FLOW AT EACH INCREMENT OF RELATIVE VALVE TRAVEL
| 3 0.7: Qf=; 3 0.8: 746.4154 |  | If there are any error messages below, the graphs and Qf are not valid | Downstream system drop |  | dp_dn | 2
[13 empty] | Downstream system resistance factor |  | R_dn | 6.7545e-06 | Relative Travel, h | 0.1 |  |  | 0.2 |  |  | 0.3 |  |  | 0.4 |  |  | 0.5 |  |  | 0.6 |  |  | 0.7 |  |  | 0.8 |  |  | 0.9 |  |  | 1
[13 empty] | Upstream system press drop an min flow |  | dpup_minQ | 0.21614 | Min C_h - Ci | 0.039245 |  |  | 0.034973 |  |  | 0.11006 |  |  | 0.0082948 |  |  | 0.040324 |  |  | 0.238 |  |  | 0.28755 |  |  | 1.2577 |  |  | 2.167 |  |  | 0.027164
[13 empty] | Downstream system press drop an min flow |  | dpdn_minQ | 0.043229 | Flow at C_h | 26.6269 |  |  | 65.8515 |  |  | 128.2618 |  |  | 215.1835 |  |  | 317.2068 |  |  | 423.3137 |  |  | 516.5231 |  |  | 599.6673 |  |  | 682.4773 |  |  | 746.4154
| 3 0.7: Qmax = maximum | [6 empty] | Values found on Line | 1989 |  |  | 1043 |  |  | 779 |  |  | 614 |  |  | 471 |  |  | 361 |  |  | 262 |  |  | 207 |  |  | 185 |  |  | 141
[8 empty] | design flow = | 550
CALCULATE FLOW AT EACH INCREMENT OF h
[13 empty] | Valve C at travel h (Cv or Kv) |  | C_h | 4.73 |  |  | 11.6 |  |  | 23 |  |  | 39.4 |  |  | 61 |  |  | 88.2 |  |  | 121 |  |  | 165 |  |  | 246 |  |  | 420
Qmin = minimum
| 3 0.8: design flow =; 3 0.9: 80 |  |  | Caculation of flow conditions
[13 empty] | Piping geometry factor at relative travel, h | 15 | F_P_h | 0.99987 |  |  | 0.99921 |  |  | 0.99692 |  |  | 0.99104 |  |  | 0.97891 |  |  | 0.95737 |  |  | 0.92396 |  |  | 0.87084 |  |  | 0.7651 |  |  | 0.57123
Combined liquid pressure recovery factor
| 3 0.8: Flow units are; 3 0.9: gpm |  |  | and piping geometry factor at relative travel, h | 21 | F_LP_h | 0.93984 |  |  | 0.92531 |  |  | 0.90928 |  |  | 0.88395 |  |  | 0.84765 |  |  | 0.79929 |  |  | 0.74019 |  |  | 0.66407 |  |  | 0.54169 |  |  | 0.35067
Total iterations 421
[13 empty] | First iteration flow rate |  | Q_i | 0.8 | Abs Value of | Flow this | 26.6269 | Abs Value of | Flow this | 65.8515 | Abs Value of | Flow this | 128.2618 | Abs Value of | Flow this | 215.1835 | Abs Value of | Flow this | 317.2068 | Abs Value of | Flow this | 423.3137 | Abs Value of | Flow this | 516.5231 | Abs Value of | Flow this | 599.6673 | Abs Value of | Flow this | 682.4773 | Abs Value of | Flow this
Valve relative travel, h | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | The cell below prevents an error in M20 above when viscosity and F_D are |  |  |  |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
Relative Flow Q/Qf | 0 | 0.035673 | 0.088224 | 0.17184 | 0.28829 | 0.42497 | 0.56713 | 0.692 | 0.8034 | 0.91434 | 1 | not entered in Columns D and G of the Valve Sizing tab. | P1 at this iteration flow rate |  | P1_Qi | 56.9161 |  |  | 56.8922 |  |  | 56.7697 |  |  | 56.3606 |  |  | 55.3523 |  |  | 53.518 |  |  | 50.8643 |  |  | 47.9058 |  |  | 44.7716 |  |  | 41.1858
Minimum Flow | 0.10718 | 0.10718 | 0.10718 | 0.10718 | 0.10718 | 0.10718 | 0.10718 | 0.10718 | 0.10718 | 0.10718 | 0.10718 |  | P2 at this iteration flow rate |  | P2_Qi | 24.6568 |  |  | 24.6616 |  |  | 24.6861 |  |  | 24.7679 |  |  | 24.9695 |  |  | 25.3364 |  |  | 25.8671 |  |  | 26.4588 |  |  | 27.0857 |  |  | 27.8028
Maximum Flow | 0.73686 | 0.73686 | 0.73686 | 0.73686 | 0.73686 | 0.73686 | 0.73686 | 0.73686 | 0.73686 | 0.73686 | 0.73686 |  | Delta P at this iteration flow rate |  | DELTA_P_Qi | 32.2593 |  |  | 32.2306 |  |  | 32.0836 |  |  | 31.5927 |  |  | 30.3828 |  |  | 28.1816 |  |  | 24.9972 |  |  | 21.447 |  |  | 17.6859 |  |  | 13.383
[13 empty] | Choked pressure drop w/ reducers | 3 | DELTA_P_CH_W_Reducers | 49.8986 |  |  | 48.41 |  |  | 46.8606 |  |  | 44.4886 |  |  | 41.173 |  |  | 36.9967 |  |  | 32.361 |  |  | 27.6016 |  |  | 22.2214 |  |  | 15.3556
[13 empty] | C Non choked w/ reducers | 7 | C_N_Ch | 0.14087 |  |  | 4.6938 |  |  | 11.6618 |  |  | 23.0258 |  |  | 39.8797 |  |  | 62.414 |  |  | 91.6351 |  |  | 128.0769 |  |  | 186.3706 |  |  | 326.5874
[13 empty] | C Choked w/ reducers | 7 | C_Ch | 0.11327 |  |  | 3.83 |  |  | 9.6494 |  |  | 19.4036 |  |  | 34.2578 |  |  | 54.4732 |  |  | 80.5372 |  |  | 112.8981 |  |  | 166.2664 |  |  | 304.8896
INSTRUCTIONS FOR THE OPTIONAL INSTALLED FLOW AND GAIN GRAPHS AND FULLY OPEN FLOW CALCULATION The process pressure model is a curve fit based on the Flow, P1 and Delta P in Columns D and G on the Valve Sizing tab. The curve fit is based on the principle that piping pressure losses are approximately proportional to flow squared. This model is only valid for fully turbulent flow. The Vapor pressure and specific gravity used in the installed flow calculation are the values entered in Column G on the Valve Sizing tab. To calculate the fully open flow, Qf, the installed flow and the installed gain, on the Valve Sizing tab, enter the minimum design flow along with its associated values of P1 and Delta P in Column D and the maximum design flow along with its associated values of P1 and Delta P in Column G. The accuracy of these calculations depends on the accuracy of the process data that is used. Any process conditions entered in Columns E and F are not used in the calculation of the fully open flow, the installed flow and the installed gain. The process model, Qf, and the graphs are only valid if: 1. The flow in G2 on the Valve Sizing tab is greater than the flow in D2 2. P1 is either constant or decreasing with increasing flow 3. P2 is either constant or increasing with increasing flow 4. Flow is turbulent. NOTE: Extrapolating curve-fit data beyond the limits for which the curve fit was established can be uncertain. The farther beyond the limits, the greater is the potential for uncertainty. As such, the fully open flow, the Installed Flow and the Installed Gain should be treated as approximations. | [12 empty] | Selected C this iteration |  | C_i | 0.14087 |  |  | 4.6938 |  |  | 11.6618 |  |  | 23.0258 |  |  | 39.8797 |  |  | 62.414 |  |  | 91.6351 |  |  | 128.0769 |  |  | 186.3706 |  |  | 326.5874
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5891 | 0.8 |  | 6.9062 | 26.6269 |  | 11.3382 | 65.8515 |  | 16.3742 | 128.2618 |  | 21.1203 | 215.1835 |  | 25.786 | 317.2068 |  | 29.3649 | 423.3137 |  | 36.9231 | 516.5231 |  | 59.6294 | 599.6673 |  | 93.4126 | 682.4773
[13 empty] | Next iteration flow rate |  |  | 0.816 | Abs Value of | Flow this | 26.8932 | Abs Value of | Flow this | 66.51 | Abs Value of | Flow this | 129.5445 | Abs Value of | Flow this | 217.3353 | Abs Value of | Flow this | 320.3788 | Abs Value of | Flow this | 427.5468 | Abs Value of | Flow this | 521.6884 | Abs Value of | Flow this | 605.664 | Abs Value of | Flow this | 689.3021 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8917 |  |  | 56.7667 |  |  | 56.3494 |  |  | 55.3209 |  |  | 53.4497 |  |  | 50.7427 |  |  | 47.7247 |  |  | 44.5275 |  |  | 40.8696
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6617 |  |  | 24.6867 |  |  | 24.7701 |  |  | 24.9758 |  |  | 25.3501 |  |  | 25.8915 |  |  | 26.4951 |  |  | 27.1345 |  |  | 27.8661
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2301 |  |  | 32.0801 |  |  | 31.5793 |  |  | 30.3451 |  |  | 28.0996 |  |  | 24.8512 |  |  | 21.2296 |  |  | 17.393 |  |  | 13.0035
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4096 |  |  | 46.8582 |  |  | 44.4797 |  |  | 41.1495 |  |  | 36.9491 |  |  | 32.2829 |  |  | 27.4963 |  |  | 22.0991 |  |  | 15.2364
[13 empty] | C Non choked w/ reducers | 7 |  | 0.14369 |  |  | 4.7408 |  |  | 11.779 |  |  | 23.261 |  |  | 40.3035 |  |  | 63.13 |  |  | 92.8229 |  |  | 130.0181 |  |  | 189.8128 |  |  | 334.6309
[13 empty] | C Choked w/ reducers | 7 |  | 0.11553 |  |  | 3.8683 |  |  | 9.7462 |  |  | 19.5996 |  |  | 34.6103 |  |  | 55.0534 |  |  | 81.4409 |  |  | 114.2453 |  |  | 168.3934 |  |  | 309.1403
[13 empty] | Selected C this iteration |  |  | 0.14369 |  |  | 4.7408 |  |  | 11.779 |  |  | 23.261 |  |  | 40.3035 |  |  | 63.13 |  |  | 92.8229 |  |  | 130.0181 |  |  | 189.8128 |  |  | 334.6309
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5863 | 0.816 |  | 6.8592 | 26.8932 |  | 11.221 | 66.51 |  | 16.139 | 129.5445 |  | 20.6965 | 217.3353 |  | 25.07 | 320.3788 |  | 28.1771 | 427.5468 |  | 34.9819 | 521.6884 |  | 56.1872 | 605.664 |  | 85.3691 | 689.3021
[13 empty] | Next iteration flow rate |  |  | 0.83232 | Abs Value of | Flow this | 27.1621 | Abs Value of | Flow this | 67.1751 | Abs Value of | Flow this | 130.8399 | Abs Value of | Flow this | 219.5086 | Abs Value of | Flow this | 323.5826 | Abs Value of | Flow this | 431.8223 | Abs Value of | Flow this | 526.9052 | Abs Value of | Flow this | 611.7206 | Abs Value of | Flow this | 696.1951 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8912 |  |  | 56.7637 |  |  | 56.338 |  |  | 55.2889 |  |  | 53.38 |  |  | 50.6186 |  |  | 47.5399 |  |  | 44.2784 |  |  | 40.5471
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6618 |  |  | 24.6873 |  |  | 24.7724 |  |  | 24.9822 |  |  | 25.364 |  |  | 25.9163 |  |  | 26.532 |  |  | 27.1843 |  |  | 27.9306
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2295 |  |  | 32.0765 |  |  | 31.5656 |  |  | 30.3066 |  |  | 28.016 |  |  | 24.7023 |  |  | 21.0079 |  |  | 17.0941 |  |  | 12.6165
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4092 |  |  | 46.8557 |  |  | 44.4707 |  |  | 41.1254 |  |  | 36.9005 |  |  | 32.2033 |  |  | 27.3888 |  |  | 21.9743 |  |  | 15.1149
[13 empty] | C Non choked w/ reducers | 7 |  | 0.14656 |  |  | 4.7883 |  |  | 11.8975 |  |  | 23.4987 |  |  | 40.7324 |  |  | 63.8564 |  |  | 94.0333 |  |  | 132.0094 |  |  | 193.3793 |  |  | 343.1222
[13 empty] | C Choked w/ reducers | 7 |  | 0.11784 |  |  | 3.907 |  |  | 9.8439 |  |  | 19.7976 |  |  | 34.9666 |  |  | 55.6405 |  |  | 82.3569 |  |  | 115.6138 |  |  | 170.5597 |  |  | 313.4846
[13 empty] | Selected C this iteration |  |  | 0.14656 |  |  | 4.7883 |  |  | 11.8975 |  |  | 23.4987 |  |  | 40.7324 |  |  | 63.8564 |  |  | 94.0333 |  |  | 132.0094 |  |  | 193.3793 |  |  | 343.1222
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5834 | 0.83232 |  | 6.8117 | 27.1621 |  | 11.1025 | 67.1751 |  | 15.9013 | 130.8399 |  | 20.2676 | 219.5086 |  | 24.3436 | 323.5826 |  | 26.9667 | 431.8223 |  | 32.9906 | 526.9052 |  | 52.6207 | 611.7206 |  | 76.8778 | 696.1951
[13 empty] | Next iteration flow rate |  |  | 0.84897 | Abs Value of | Flow this | 27.4337 | Abs Value of | Flow this | 67.8468 | Abs Value of | Flow this | 132.1483 | Abs Value of | Flow this | 221.7037 | Abs Value of | Flow this | 326.8185 | Abs Value of | Flow this | 436.1405 | Abs Value of | Flow this | 532.1743 | Abs Value of | Flow this | 617.8378 | Abs Value of | Flow this | 703.1571 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8907 |  |  | 56.7607 |  |  | 56.3264 |  |  | 55.2561 |  |  | 53.3089 |  |  | 50.492 |  |  | 47.3515 |  |  | 44.0244 |  |  | 40.2181
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6619 |  |  | 24.6879 |  |  | 24.7747 |  |  | 24.9888 |  |  | 25.3782 |  |  | 25.9416 |  |  | 26.5697 |  |  | 27.2351 |  |  | 27.9964
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2289 |  |  | 32.0728 |  |  | 31.5516 |  |  | 30.2674 |  |  | 27.9307 |  |  | 24.5504 |  |  | 20.7818 |  |  | 16.7893 |  |  | 12.2217
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4087 |  |  | 46.8531 |  |  | 44.4614 |  |  | 41.1009 |  |  | 36.851 |  |  | 32.1221 |  |  | 27.2792 |  |  | 21.8469 |  |  | 14.9909
[13 empty] | C Non choked w/ reducers | 7 |  | 0.14949 |  |  | 4.8362 |  |  | 12.0171 |  |  | 23.7389 |  |  | 41.1664 |  |  | 64.5934 |  |  | 95.2669 |  |  | 134.053 |  |  | 197.0781 |  |  | 352.1066
[13 empty] | C Choked w/ reducers | 7 |  | 0.1202 |  |  | 3.9461 |  |  | 9.9426 |  |  | 19.9977 |  |  | 35.3268 |  |  | 56.2347 |  |  | 83.2856 |  |  | 117.0043 |  |  | 172.7665 |  |  | 317.9262
FL for characteritics calculation | 0: Using the same curve fit equations in the Cv table |  | Selected C this iteration |  |  | 0.14949 |  |  | 4.8362 |  |  | 12.0171 |  |  | 23.7389 |  |  | 41.1664 |  |  | 64.5934 |  |  | 95.2669 |  |  | 134.053 |  |  | 197.0781 |  |  | 352.1066
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5805 | 0.84897 |  | 6.7638 | 27.4337 |  | 10.9829 | 67.8468 |  | 15.6611 | 132.1483 |  | 19.8336 | 221.7037 |  | 23.6066 | 326.8185 |  | 25.7331 | 436.1405 |  | 30.947 | 532.1743 |  | 48.9219 | 617.8378 |  | 67.8934 | 703.1571
Globe, cage | 0.82654 | 0.83675 | 0.8475 | 0.84959 | 0.83855 | 0.83124 | 0.82242 | 0.812 | 0.812 | 0.812
Globe Parabolic | 0.93201 | 0.91576 | 0.89442 | 0.87869 | 0.86249 | 0.84852 | 0.83169 | 0.8091 | 0.77 | 0.77 |  |  | Next iteration flow rate |  |  | 0.86595 | Abs Value of | Flow this | 27.708 | Abs Value of | Flow this | 68.5253 | Abs Value of | Flow this | 133.4698 | Abs Value of | Flow this | 223.9208 | Abs Value of | Flow this | 330.0866 | Abs Value of | Flow this | 440.5019 | Abs Value of | Flow this | 537.496 | Abs Value of | Flow this | 624.0162 | Abs Value of | Flow this | 710.1887 | Abs Value of | Flow this
Rotary plug | 0.91 | 0.90719 | 0.88261 | 0.85303 | 0.82276 | 0.79493 | 0.7697 | 0.76 | 0.76 | 0.76 | [6 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
Segment ball | 0.94 | 0.92621 | 0.91266 | 0.89316 | 0.86748 | 0.83514 | 0.79614 | 0.74383 | 0.64753 | 0.44067 |  |  | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8902 |  |  | 56.7576 |  |  | 56.3145 |  |  | 55.2228 |  |  | 53.2364 |  |  | 50.3629 |  |  | 47.1592 |  |  | 43.7653 |  |  | 39.8824
Butterfly | 0.87 | 0.85948 | 0.84623 | 0.82722 | 0.80229 | 0.77106 | 0.73364 | 0.68386 | 0.59347 | 0.40478 |  |  | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.662 |  |  | 24.6885 |  |  | 24.7771 |  |  | 24.9954 |  |  | 25.3927 |  |  | 25.9674 |  |  | 26.6082 |  |  | 27.2869 |  |  | 28.0635
Full ball (Full and reduced port | 0.91 | 0.90099 | 0.89077 | 0.87629 | 0.85756 | 0.83455 | 0.80762 | 0.77286 | 0.71272 | 0.5989 |  |  | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2283 |  |  | 32.0691 |  |  | 31.5374 |  |  | 30.2273 |  |  | 27.8437 |  |  | 24.3955 |  |  | 20.5511 |  |  | 16.4784 |  |  | 11.8189
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4083 |  |  | 46.8505 |  |  | 44.452 |  |  | 41.0759 |  |  | 36.8004 |  |  | 32.0392 |  |  | 27.1674 |  |  | 21.717 |  |  | 14.8644
| 0.52556 | 1.2889 | 2.5556 | 4.3778 | 6.7778 | 9.8 | 13.4444 | 18.3333 | 27.3333 | 46.6667 |  |  | C Non choked w/ reducers | 7 |  | 0.15248 |  |  | 4.8846 |  |  | 12.138 |  |  | 23.9817 |  |  | 41.6056 |  |  | 65.3412 |  |  | 96.5247 |  |  | 136.1513 |  |  | 200.9181 |  |  | 361.6363
[13 empty] | C Choked w/ reducers | 7 |  | 0.1226 |  |  | 3.9855 |  |  | 10.0423 |  |  | 20.1998 |  |  | 35.6909 |  |  | 56.836 |  |  | 84.2272 |  |  | 118.4172 |  |  | 175.0152 |  |  | 322.4688
[13 empty] | Selected C this iteration |  |  | 0.15248 |  |  | 4.8846 |  |  | 12.138 |  |  | 23.9817 |  |  | 41.6056 |  |  | 65.3412 |  |  | 96.5247 |  |  | 136.1513 |  |  | 200.9181 |  |  | 361.6363
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5775 | 0.86595 |  | 6.7154 | 27.708 |  | 10.862 | 68.5253 |  | 15.4183 | 133.4698 |  | 19.3944 | 223.9208 |  | 22.8588 | 330.0866 |  | 24.4753 | 440.5019 |  | 28.8487 | 537.496 |  | 45.0819 | 624.0162 |  | 58.3637 | 710.1887
[13 empty] | Next iteration flow rate |  |  | 0.88326 | Abs Value of | Flow this | 27.9851 | Abs Value of | Flow this | 69.2105 | Abs Value of | Flow this | 134.8045 | Abs Value of | Flow this | 226.16 | Abs Value of | Flow this | 333.3875 | Abs Value of | Flow this | 444.9069 | Abs Value of | Flow this | 542.871 | Abs Value of | Flow this | 630.2564 | Abs Value of | Flow this | 717.2906 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8897 |  |  | 56.7544 |  |  | 56.3024 |  |  | 55.1887 |  |  | 53.1624 |  |  | 50.2312 |  |  | 46.9631 |  |  | 43.501 |  |  | 39.5401
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6621 |  |  | 24.6891 |  |  | 24.7795 |  |  | 25.0023 |  |  | 25.4075 |  |  | 25.9938 |  |  | 26.6474 |  |  | 27.3398 |  |  | 28.132
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2276 |  |  | 32.0652 |  |  | 31.5229 |  |  | 30.1865 |  |  | 27.7549 |  |  | 24.2374 |  |  | 20.3157 |  |  | 16.1612 |  |  | 11.4081
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4078 |  |  | 46.8479 |  |  | 44.4424 |  |  | 41.0504 |  |  | 36.7489 |  |  | 31.9546 |  |  | 27.0534 |  |  | 21.5845 |  |  | 14.7354
[13 empty] | C Non choked w/ reducers | 7 |  | 0.15553 |  |  | 4.9335 |  |  | 12.2601 |  |  | 24.2271 |  |  | 42.05 |  |  | 66.1 |  |  | 97.8073 |  |  | 138.307 |  |  | 204.9091 |  |  | 371.7717
[13 empty] | C Choked w/ reducers | 7 |  | 0.12506 |  |  | 4.0254 |  |  | 10.143 |  |  | 20.404 |  |  | 36.059 |  |  | 57.4446 |  |  | 85.1819 |  |  | 119.8532 |  |  | 177.3071 |  |  | 327.1163
[13 empty] | Selected C this iteration |  |  | 0.15553 |  |  | 4.9335 |  |  | 12.2601 |  |  | 24.2271 |  |  | 42.05 |  |  | 66.1 |  |  | 97.8073 |  |  | 138.307 |  |  | 204.9091 |  |  | 371.7717
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5745 | 0.88326 |  | 6.6665 | 27.9851 |  | 10.7399 | 69.2105 |  | 15.1729 | 134.8045 |  | 18.95 | 226.16 |  | 22.1 | 333.3875 |  | 23.1927 | 444.9069 |  | 26.693 | 542.871 |  | 41.0909 | 630.2564 |  | 48.2283 | 717.2906
[13 empty] | Next iteration flow rate |  |  | 0.90093 | Abs Value of | Flow this | 28.265 | Abs Value of | Flow this | 69.9027 | Abs Value of | Flow this | 136.1525 | Abs Value of | Flow this | 228.4216 | Abs Value of | Flow this | 336.7214 | Abs Value of | Flow this | 449.356 | Abs Value of | Flow this | 548.2997 | Abs Value of | Flow this | 636.5589 | Abs Value of | Flow this | 724.4635 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8892 |  |  | 56.7511 |  |  | 56.2901 |  |  | 55.154 |  |  | 53.087 |  |  | 50.0968 |  |  | 46.7631 |  |  | 43.2313 |  |  | 39.1908
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6622 |  |  | 24.6898 |  |  | 24.782 |  |  | 25.0092 |  |  | 25.4226 |  |  | 26.0206 |  |  | 26.6874 |  |  | 27.3937 |  |  | 28.2018
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.227 |  |  | 32.0613 |  |  | 31.5081 |  |  | 30.1448 |  |  | 27.6644 |  |  | 24.0762 |  |  | 20.0757 |  |  | 15.8376 |  |  | 10.989
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4074 |  |  | 46.8452 |  |  | 44.4326 |  |  | 41.0243 |  |  | 36.6963 |  |  | 31.8684 |  |  | 26.9371 |  |  | 21.4494 |  |  | 14.6037
[13 empty] | C Non choked w/ reducers | 7 |  | 0.15864 |  |  | 4.9829 |  |  | 12.3835 |  |  | 24.4751 |  |  | 42.4999 |  |  | 66.8702 |  |  | 99.1156 |  |  | 140.5228 |  |  | 209.0616 |  |  | 382.5828
[13 empty] | C Choked w/ reducers | 7 |  | 0.12756 |  |  | 4.0657 |  |  | 10.2448 |  |  | 20.6103 |  |  | 36.4312 |  |  | 58.0606 |  |  | 86.15 |  |  | 121.3129 |  |  | 179.6435 |  |  | 331.8731
[13 empty] | Selected C this iteration |  |  | 0.15864 |  |  | 4.9829 |  |  | 12.3835 |  |  | 24.4751 |  |  | 42.4999 |  |  | 66.8702 |  |  | 99.1156 |  |  | 140.5228 |  |  | 209.0616 |  |  | 382.5828
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5714 | 0.90093 |  | 6.6171 | 28.265 |  | 10.6165 | 69.9027 |  | 14.9249 | 136.1525 |  | 18.5001 | 228.4216 |  | 21.3298 | 336.7214 |  | 21.8844 | 449.356 |  | 24.4772 | 548.2997 |  | 36.9384 | 636.5589 |  | 37.4172 | 724.4635
[13 empty] | Next iteration flow rate |  |  | 0.91895 | Abs Value of | Flow this | 28.5476 | Abs Value of | Flow this | 70.6017 | Abs Value of | Flow this | 137.514 | Abs Value of | Flow this | 230.7058 | Abs Value of | Flow this | 340.0886 | Abs Value of | Flow this | 453.8496 | Abs Value of | Flow this | 553.7827 | Abs Value of | Flow this | 642.9245 | Abs Value of | Flow this | 731.7081 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8886 |  |  | 56.7478 |  |  | 56.2775 |  |  | 55.1186 |  |  | 53.01 |  |  | 49.9597 |  |  | 46.559 |  |  | 42.9563 |  |  | 38.8345
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6623 |  |  | 24.6904 |  |  | 24.7845 |  |  | 25.0163 |  |  | 25.438 |  |  | 26.0481 |  |  | 26.7282 |  |  | 27.4487 |  |  | 28.2731
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2263 |  |  | 32.0574 |  |  | 31.493 |  |  | 30.1023 |  |  | 27.572 |  |  | 23.9117 |  |  | 19.8308 |  |  | 15.5075 |  |  | 10.5614
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4069 |  |  | 46.8424 |  |  | 44.4225 |  |  | 40.9978 |  |  | 36.6426 |  |  | 31.7804 |  |  | 26.8184 |  |  | 21.3115 |  |  | 14.4695
[13 empty] | C Non choked w/ reducers | 7 |  | 0.16182 |  |  | 5.0328 |  |  | 12.5081 |  |  | 24.7258 |  |  | 42.9552 |  |  | 67.6519 |  |  | 100.4505 |  |  | 142.8017 |  |  | 213.3876 |  |  | 394.1521
[13 empty] | C Choked w/ reducers | 7 |  | 0.13011 |  |  | 4.1064 |  |  | 10.3475 |  |  | 20.8188 |  |  | 36.8074 |  |  | 58.6842 |  |  | 87.1319 |  |  | 122.7968 |  |  | 182.0259 |  |  | 336.7434
[13 empty] | Selected C this iteration |  |  | 0.16182 |  |  | 5.0328 |  |  | 12.5081 |  |  | 24.7258 |  |  | 42.9552 |  |  | 67.6519 |  |  | 100.4505 |  |  | 142.8017 |  |  | 213.3876 |  |  | 394.1521
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5682 | 0.91895 |  | 6.5672 | 28.5476 |  | 10.4919 | 70.6017 |  | 14.6742 | 137.514 |  | 18.0448 | 230.7058 |  | 20.5481 | 340.0886 |  | 20.5495 | 453.8496 |  | 22.1983 | 553.7827 |  | 32.6124 | 642.9245 |  | 25.8479 | 731.7081
[13 empty] | Next iteration flow rate |  |  | 0.93733 | Abs Value of | Flow this | 28.8331 | Abs Value of | Flow this | 71.3077 | Abs Value of | Flow this | 138.8892 | Abs Value of | Flow this | 233.0129 | Abs Value of | Flow this | 343.4895 | Abs Value of | Flow this | 458.3881 | Abs Value of | Flow this | 559.3205 | Abs Value of | Flow this | 649.3538 | Abs Value of | Flow this | 739.0252 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8881 |  |  | 56.7444 |  |  | 56.2647 |  |  | 55.0825 |  |  | 52.9315 |  |  | 49.8199 |  |  | 46.3508 |  |  | 42.6757 |  |  | 38.4711
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6624 |  |  | 24.6911 |  |  | 24.7871 |  |  | 25.0235 |  |  | 25.4537 |  |  | 26.076 |  |  | 26.7698 |  |  | 27.5049 |  |  | 28.3458
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2257 |  |  | 32.0533 |  |  | 31.4776 |  |  | 30.059 |  |  | 27.4778 |  |  | 23.7439 |  |  | 19.581 |  |  | 15.1708 |  |  | 10.1253
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4065 |  |  | 46.8396 |  |  | 44.4123 |  |  | 40.9707 |  |  | 36.5879 |  |  | 31.6907 |  |  | 26.6973 |  |  | 21.1709 |  |  | 14.3325
[13 empty] | C Non choked w/ reducers | 7 |  | 0.16505 |  |  | 5.0831 |  |  | 12.634 |  |  | 24.9791 |  |  | 43.416 |  |  | 68.4454 |  |  | 101.8128 |  |  | 145.1468 |  |  | 217.9001 |  |  | 406.5768
[13 empty] | C Choked w/ reducers | 7 |  | 0.13271 |  |  | 4.1475 |  |  | 10.4513 |  |  | 21.0294 |  |  | 37.1878 |  |  | 59.3153 |  |  | 88.1277 |  |  | 124.3056 |  |  | 184.4559 |  |  | 341.7321
[13 empty] | Selected C this iteration |  |  | 0.16505 |  |  | 5.0831 |  |  | 12.634 |  |  | 24.9791 |  |  | 43.416 |  |  | 68.4454 |  |  | 101.8128 |  |  | 145.1468 |  |  | 217.9001 |  |  | 406.5768
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5649 | 0.93733 |  | 6.5169 | 28.8331 |  | 10.366 | 71.3077 |  | 14.4209 | 138.8892 |  | 17.584 | 233.0129 |  | 19.7546 | 343.4895 |  | 19.1872 | 458.3881 |  | 19.8532 | 559.3205 |  | 28.0999 | 649.3538 |  | 13.4232 | 739.0252
[13 empty] | Next iteration flow rate |  |  | 0.95607 | Abs Value of | Flow this | 29.1214 | Abs Value of | Flow this | 72.0208 | Abs Value of | Flow this | 140.2781 | Abs Value of | Flow this | 235.343 | Abs Value of | Flow this | 346.9244 | Abs Value of | Flow this | 462.9719 | Abs Value of | Flow this | 564.9137 | Abs Value of | Flow this | 655.8473 | Abs Value of | Flow this | 746.4154 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8875 |  |  | 56.741 |  |  | 56.2516 |  |  | 55.0456 |  |  | 52.8514 |  |  | 49.6773 |  |  | 46.1384 |  |  | 42.3894 |  |  | 38.1003
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6625 |  |  | 24.6918 |  |  | 24.7897 |  |  | 25.0309 |  |  | 25.4697 |  |  | 26.1045 |  |  | 26.8123 |  |  | 27.5621 |  |  | 28.4199
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.225 |  |  | 32.0492 |  |  | 31.4619 |  |  | 30.0147 |  |  | 27.3817 |  |  | 23.5727 |  |  | 19.3261 |  |  | 14.8273 |  |  | 9.6804
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.406 |  |  | 46.8367 |  |  | 44.4019 |  |  | 40.943 |  |  | 36.5321 |  |  | 31.5992 |  |  | 26.5738 |  |  | 21.0274 |  |  | 14.1928
[13 empty] | C Non choked w/ reducers | 7 |  | 0.16835 |  |  | 5.134 |  |  | 12.7611 |  |  | 25.2352 |  |  | 43.8824 |  |  | 69.2511 |  |  | 103.2036 |  |  | 147.5616 |  |  | 222.6136 |  |  | 419.9728
[13 empty] | C Choked w/ reducers | 7 |  | 0.13536 |  |  | 4.1889 |  |  | 10.5561 |  |  | 21.2422 |  |  | 37.5723 |  |  | 59.9542 |  |  | 89.1378 |  |  | 125.84 |  |  | 186.9349 |  |  | 346.8441
[13 empty] | Selected C this iteration |  |  | 0.16835 |  |  | 5.134 |  |  | 12.7611 |  |  | 25.2352 |  |  | 43.8824 |  |  | 69.2511 |  |  | 103.2036 |  |  | 147.5616 |  |  | 222.6136 |  |  | 419.9728
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5616 | 0.95607 |  | 6.466 | 29.1214 |  | 10.2389 | 72.0208 |  | 14.1648 | 140.2781 |  | 17.1176 | 235.343 |  | 18.9489 | 346.9244 |  | 17.7964 | 462.9719 |  | 17.4384 | 564.9137 |  | 23.3864 | 655.8473 |  | 0.027164 | 746.4154
[13 empty] | Next iteration flow rate |  |  | 0.9752 | Abs Value of | Flow this | 29.4126 | Abs Value of | Flow this | 72.741 | Abs Value of | Flow this | 141.6809 | Abs Value of | Flow this | 237.6964 | Abs Value of | Flow this | 350.3936 | Abs Value of | Flow this | 467.6017 | Abs Value of | Flow this | 570.5629 | Abs Value of | Flow this | 662.4058 | Abs Value of | Flow this | 753.8796 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8869 |  |  | 56.7374 |  |  | 56.2382 |  |  | 55.008 |  |  | 52.7697 |  |  | 49.5318 |  |  | 45.9218 |  |  | 42.0975 |  |  | 37.7221
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6626 |  |  | 24.6925 |  |  | 24.7924 |  |  | 25.0384 |  |  | 25.4861 |  |  | 26.1336 |  |  | 26.8556 |  |  | 27.6205 |  |  | 28.4956
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2243 |  |  | 32.0449 |  |  | 31.4459 |  |  | 29.9696 |  |  | 27.2837 |  |  | 23.3981 |  |  | 19.0662 |  |  | 14.4769 |  |  | 9.2266
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4055 |  |  | 46.8338 |  |  | 44.3913 |  |  | 40.9149 |  |  | 36.4751 |  |  | 31.5058 |  |  | 26.4479 |  |  | 20.881 |  |  | 14.0502
[13 empty] | C Non choked w/ reducers | 7 |  | 0.17172 |  |  | 5.1854 |  |  | 12.8896 |  |  | 25.4941 |  |  | 44.3546 |  |  | 70.0692 |  |  | 104.6239 |  |  | 150.0498 |  |  | 227.5443 |  |  | 434.4795
[13 empty] | C Choked w/ reducers | 7 |  | 0.13807 |  |  | 4.2309 |  |  | 10.662 |  |  | 21.4572 |  |  | 37.9611 |  |  | 60.601 |  |  | 90.1625 |  |  | 127.4008 |  |  | 189.4648 |  |  | 352.0849
[13 empty] | Selected C this iteration |  |  | 0.17172 |  |  | 5.1854 |  |  | 12.8896 |  |  | 25.4941 |  |  | 44.3546 |  |  | 70.0692 |  |  | 104.6239 |  |  | 150.0498 |  |  | 227.5443 |  |  | 434.4795
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5583 | 0.9752 |  | 6.4146 | 29.4126 |  | 10.1104 | 72.741 |  | 13.9059 | 141.6809 |  | 16.6454 | 237.6964 |  | 18.1308 | 350.3936 |  | 16.3761 | 467.6017 |  | 14.9502 | 570.5629 |  | 18.4557 | 662.4058 |  | 14.4795 | 753.8796
[13 empty] | Next iteration flow rate |  |  | 0.9947 | Abs Value of | Flow this | 29.7068 | Abs Value of | Flow this | 73.4684 | Abs Value of | Flow this | 143.0977 | Abs Value of | Flow this | 240.0734 | Abs Value of | Flow this | 353.8976 | Abs Value of | Flow this | 472.2777 | Abs Value of | Flow this | 576.2685 | Abs Value of | Flow this | 669.0298 | Abs Value of | Flow this | 761.4184 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8863 |  |  | 56.7339 |  |  | 56.2246 |  |  | 54.9697 |  |  | 52.6864 |  |  | 49.3833 |  |  | 45.7008 |  |  | 41.7996 |  |  | 37.3363
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6627 |  |  | 24.6932 |  |  | 24.7951 |  |  | 25.0461 |  |  | 25.5027 |  |  | 26.1633 |  |  | 26.8998 |  |  | 27.6801 |  |  | 28.5727
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2236 |  |  | 32.0406 |  |  | 31.4295 |  |  | 29.9236 |  |  | 27.1836 |  |  | 23.22 |  |  | 18.801 |  |  | 14.1195 |  |  | 8.7636
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.405 |  |  | 46.8308 |  |  | 44.3804 |  |  | 40.8861 |  |  | 36.417 |  |  | 31.4105 |  |  | 26.3194 |  |  | 20.7317 |  |  | 13.9048
[13 empty] | C Non choked w/ reducers | 7 |  | 0.17515 |  |  | 5.2373 |  |  | 13.0194 |  |  | 25.7557 |  |  | 44.8326 |  |  | 70.8999 |  |  | 106.0746 |  |  | 152.6154 |  |  | 232.7105 |  |  | 450.2661
[13 empty] | C Choked w/ reducers | 7 |  | 0.14083 |  |  | 4.2732 |  |  | 10.769 |  |  | 21.6744 |  |  | 38.3542 |  |  | 61.2558 |  |  | 91.2021 |  |  | 128.9885 |  |  | 192.0473 |  |  | 357.4601
[13 empty] | Selected C this iteration |  |  | 0.17515 |  |  | 5.2373 |  |  | 13.0194 |  |  | 25.7557 |  |  | 44.8326 |  |  | 70.8999 |  |  | 106.0746 |  |  | 152.6154 |  |  | 232.7105 |  |  | 450.2661
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5548 | 0.9947 |  | 6.3627 | 29.7068 |  | 9.9806 | 73.4684 |  | 13.6443 | 143.0977 |  | 16.1674 | 240.0734 |  | 17.3001 | 353.8976 |  | 14.9254 | 472.2777 |  | 12.3846 | 576.2685 |  | 13.2895 | 669.0298 |  | 30.2661 | 761.4184
[13 empty] | Next iteration flow rate |  |  | 1.0146 | Abs Value of | Flow this | 30.0038 | Abs Value of | Flow this | 74.2031 | Abs Value of | Flow this | 144.5286 | Abs Value of | Flow this | 242.4741 | Abs Value of | Flow this | 357.4365 | Abs Value of | Flow this | 477.0004 | Abs Value of | Flow this | 582.0312 | Abs Value of | Flow this | 675.7201 | Abs Value of | Flow this | 769.0326 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8857 |  |  | 56.7302 |  |  | 56.2107 |  |  | 54.9305 |  |  | 52.6014 |  |  | 49.2319 |  |  | 45.4754 |  |  | 41.4958 |  |  | 36.9428
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6629 |  |  | 24.694 |  |  | 24.7979 |  |  | 25.0539 |  |  | 25.5197 |  |  | 26.1936 |  |  | 26.9449 |  |  | 27.7408 |  |  | 28.6514
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2229 |  |  | 32.0362 |  |  | 31.4128 |  |  | 29.8766 |  |  | 27.0816 |  |  | 23.0383 |  |  | 18.5305 |  |  | 13.7549 |  |  | 8.2913
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4045 |  |  | 46.8278 |  |  | 44.3694 |  |  | 40.8568 |  |  | 36.3578 |  |  | 31.3134 |  |  | 26.1883 |  |  | 20.5794 |  |  | 13.7565
[13 empty] | C Non choked w/ reducers | 7 |  | 0.17866 |  |  | 5.2898 |  |  | 13.1505 |  |  | 26.0202 |  |  | 45.3165 |  |  | 71.7437 |  |  | 107.557 |  |  | 155.2626 |  |  | 238.1324 |  |  | 467.5409
[13 empty] | C Choked w/ reducers | 7 |  | 0.14365 |  |  | 4.3159 |  |  | 10.877 |  |  | 21.8939 |  |  | 38.7517 |  |  | 61.9188 |  |  | 92.257 |  |  | 130.6041 |  |  | 194.6842 |  |  | 362.9757
[13 empty] | Selected C this iteration |  |  | 0.17866 |  |  | 5.2898 |  |  | 13.1505 |  |  | 26.0202 |  |  | 45.3165 |  |  | 71.7437 |  |  | 107.557 |  |  | 155.2626 |  |  | 238.1324 |  |  | 467.5409
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5513 | 1.0146 |  | 6.3102 | 30.0038 |  | 9.8495 | 74.2031 |  | 13.3798 | 144.5286 |  | 15.6835 | 242.4741 |  | 16.4563 | 357.4365 |  | 13.443 | 477.0004 |  | 9.7374 | 582.0312 |  | 7.8676 | 675.7201 |  | 47.5409 | 769.0326
[13 empty] | Next iteration flow rate |  |  | 1.0349 | Abs Value of | Flow this | 30.3039 | Abs Value of | Flow this | 74.9451 | Abs Value of | Flow this | 145.9739 | Abs Value of | Flow this | 244.8988 | Abs Value of | Flow this | 361.0109 | Abs Value of | Flow this | 481.7705 | Abs Value of | Flow this | 587.8515 | Abs Value of | Flow this | 682.4773 | Abs Value of | Flow this | 776.7229 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8851 |  |  | 56.7265 |  |  | 56.1965 |  |  | 54.8906 |  |  | 52.5146 |  |  | 49.0775 |  |  | 45.2454 |  |  | 41.1858 |  |  | 36.5413
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.663 |  |  | 24.6947 |  |  | 24.8007 |  |  | 25.0619 |  |  | 25.5371 |  |  | 26.2245 |  |  | 26.9909 |  |  | 27.8028 |  |  | 28.7317
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2222 |  |  | 32.0317 |  |  | 31.3958 |  |  | 29.8288 |  |  | 26.9776 |  |  | 22.853 |  |  | 18.2545 |  |  | 13.383 |  |  | 7.8096
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4039 |  |  | 46.8247 |  |  | 44.3581 |  |  | 40.8268 |  |  | 36.2973 |  |  | 31.2142 |  |  | 26.0546 |  |  | 20.4241 |  |  | 13.6052
[13 empty] | C Non choked w/ reducers | 7 |  | 0.18223 |  |  | 5.3427 |  |  | 13.2829 |  |  | 26.2875 |  |  | 45.8064 |  |  | 72.6008 |  |  | 109.0722 |  |  | 157.996 |  |  | 243.833 |  |  | 486.5634
[13 empty] | C Choked w/ reducers | 7 |  | 0.14652 |  |  | 4.3591 |  |  | 10.9862 |  |  | 22.1156 |  |  | 39.1535 |  |  | 62.59 |  |  | 93.3274 |  |  | 132.2482 |  |  | 197.3775 |  |  | 368.6383
[13 empty] | Selected C this iteration |  |  | 0.18223 |  |  | 5.3427 |  |  | 13.2829 |  |  | 26.2875 |  |  | 45.8064 |  |  | 72.6008 |  |  | 109.0722 |  |  | 157.996 |  |  | 243.833 |  |  | 486.5634
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5478 | 1.0349 |  | 6.2573 | 30.3039 |  | 9.7171 | 74.9451 |  | 13.1125 | 145.9739 |  | 15.1936 | 244.8988 |  | 15.5992 | 361.0109 |  | 11.9278 | 481.7705 |  | 7.004 | 587.8515 |  | 2.167 | 682.4773 |  | 66.5634 | 776.7229
[13 empty] | Next iteration flow rate |  |  | 1.0556 | Abs Value of | Flow this | 30.6069 | Abs Value of | Flow this | 75.6946 | Abs Value of | Flow this | 147.4337 | Abs Value of | Flow this | 247.3478 | Abs Value of | Flow this | 364.621 | Abs Value of | Flow this | 486.5882 | Abs Value of | Flow this | 593.73 | Abs Value of | Flow this | 689.3021 | Abs Value of | Flow this | 784.4901 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8845 |  |  | 56.7226 |  |  | 56.182 |  |  | 54.8499 |  |  | 52.4262 |  |  | 48.9199 |  |  | 45.0109 |  |  | 40.8696 |  |  | 36.1318
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6631 |  |  | 24.6955 |  |  | 24.8036 |  |  | 25.07 |  |  | 25.5548 |  |  | 26.256 |  |  | 27.0378 |  |  | 27.8661 |  |  | 28.8136
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2214 |  |  | 32.0272 |  |  | 31.3785 |  |  | 29.7799 |  |  | 26.8714 |  |  | 22.6639 |  |  | 17.973 |  |  | 13.0035 |  |  | 7.3181
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4034 |  |  | 46.8215 |  |  | 44.3466 |  |  | 40.7963 |  |  | 36.2357 |  |  | 31.1131 |  |  | 25.9181 |  |  | 20.2656 |  |  | 13.4509
[13 empty] | C Non choked w/ reducers | 7 |  | 0.18588 |  |  | 5.3962 |  |  | 13.4167 |  |  | 26.5577 |  |  | 46.3024 |  |  | 73.4715 |  |  | 110.6214 |  |  | 160.8208 |  |  | 249.8383 |  |  | 507.6616
[13 empty] | C Choked w/ reducers | 7 |  | 0.14945 |  |  | 4.4027 |  |  | 11.0964 |  |  | 22.3397 |  |  | 39.5598 |  |  | 63.2697 |  |  | 94.4137 |  |  | 133.9217 |  |  | 200.1293 |  |  | 374.4546
[13 empty] | Selected C this iteration |  |  | 0.18588 |  |  | 5.3962 |  |  | 13.4167 |  |  | 26.5577 |  |  | 46.3024 |  |  | 73.4715 |  |  | 110.6214 |  |  | 160.8208 |  |  | 249.8383 |  |  | 507.6616
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5441 | 1.0556 |  | 6.2038 | 30.6069 |  | 9.5833 | 75.6946 |  | 12.8423 | 147.4337 |  | 14.6976 | 247.3478 |  | 14.7285 | 364.621 |  | 10.3786 | 486.5882 |  | 4.1792 | 593.73 |  | 3.8383 | 689.3021 |  | 87.6616 | 784.4901
[13 empty] | Next iteration flow rate |  |  | 1.0767 | Abs Value of | Flow this | 30.913 | Abs Value of | Flow this | 76.4515 | Abs Value of | Flow this | 148.908 | Abs Value of | Flow this | 249.8213 | Abs Value of | Flow this | 368.2672 | Abs Value of | Flow this | 491.454 | Abs Value of | Flow this | 599.6673 | Abs Value of | Flow this | 696.1951 | Abs Value of | Flow this | 792.335 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8839 |  |  | 56.7187 |  |  | 56.1673 |  |  | 54.8084 |  |  | 52.3359 |  |  | 48.7592 |  |  | 44.7716 |  |  | 40.5471 |  |  | 35.714
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6632 |  |  | 24.6963 |  |  | 24.8065 |  |  | 25.0783 |  |  | 25.5728 |  |  | 26.2882 |  |  | 27.0857 |  |  | 27.9306 |  |  | 28.8972
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2206 |  |  | 32.0225 |  |  | 31.3607 |  |  | 29.7301 |  |  | 26.7631 |  |  | 22.471 |  |  | 17.6859 |  |  | 12.6165 |  |  | 6.8168
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4029 |  |  | 46.8183 |  |  | 44.3349 |  |  | 40.7652 |  |  | 36.1728 |  |  | 31.01 |  |  | 25.779 |  |  | 20.1039 |  |  | 13.2935
[13 empty] | C Non choked w/ reducers | 7 |  | 0.18959 |  |  | 5.4502 |  |  | 13.5519 |  |  | 26.8309 |  |  | 46.8046 |  |  | 74.3562 |  |  | 112.2061 |  |  | 163.7423 |  |  | 256.178 |  |  | 531.2575
[13 empty] | C Choked w/ reducers | 7 |  | 0.15244 |  |  | 4.4468 |  |  | 11.2078 |  |  | 22.566 |  |  | 39.9707 |  |  | 63.9579 |  |  | 95.5163 |  |  | 135.6255 |  |  | 202.9417 |  |  | 380.4322
[13 empty] | Selected C this iteration |  |  | 0.18959 |  |  | 5.4502 |  |  | 13.5519 |  |  | 26.8309 |  |  | 46.8046 |  |  | 74.3562 |  |  | 112.2061 |  |  | 163.7423 |  |  | 256.178 |  |  | 531.2575
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5404 | 1.0767 |  | 6.1498 | 30.913 |  | 9.4481 | 76.4515 |  | 12.5691 | 148.908 |  | 14.1954 | 249.8213 |  | 13.8438 | 368.2672 |  | 8.7939 | 491.454 |  | 1.2577 | 599.6673 |  | 10.178 | 696.1951 |  | 111.2575 | 792.335
[13 empty] | Next iteration flow rate |  |  | 1.0982 | Abs Value of | Flow this | 31.2221 | Abs Value of | Flow this | 77.216 | Abs Value of | Flow this | 150.3971 | Abs Value of | Flow this | 252.3195 | Abs Value of | Flow this | 371.9499 | Abs Value of | Flow this | 496.3686 | Abs Value of | Flow this | 605.664 | Abs Value of | Flow this | 703.1571 | Abs Value of | Flow this | 800.2584 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8832 |  |  | 56.7148 |  |  | 56.1522 |  |  | 54.766 |  |  | 52.2438 |  |  | 48.5952 |  |  | 44.5275 |  |  | 40.2181 |  |  | 35.2879
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6634 |  |  | 24.697 |  |  | 24.8096 |  |  | 25.0868 |  |  | 25.5912 |  |  | 26.321 |  |  | 27.1345 |  |  | 27.9964 |  |  | 28.9824
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2199 |  |  | 32.0177 |  |  | 31.3427 |  |  | 29.6792 |  |  | 26.6526 |  |  | 22.2743 |  |  | 17.393 |  |  | 12.2217 |  |  | 6.3054
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4023 |  |  | 46.815 |  |  | 44.3229 |  |  | 40.7334 |  |  | 36.1086 |  |  | 30.9048 |  |  | 25.637 |  |  | 19.939 |  |  | 13.1329
[13 empty] | C Non choked w/ reducers | 7 |  | 0.19338 |  |  | 5.5048 |  |  | 13.6884 |  |  | 27.107 |  |  | 47.3131 |  |  | 75.2552 |  |  | 113.8276 |  |  | 166.7666 |  |  | 262.8858 |  |  | 557.9049
[13 empty] | C Choked w/ reducers | 7 |  | 0.15549 |  |  | 4.4913 |  |  | 11.3202 |  |  | 22.7948 |  |  | 40.3861 |  |  | 64.6549 |  |  | 96.6355 |  |  | 137.3604 |  |  | 205.817 |  |  | 386.5788
[13 empty] | Selected C this iteration |  |  | 0.19338 |  |  | 5.5048 |  |  | 13.6884 |  |  | 27.107 |  |  | 47.3131 |  |  | 75.2552 |  |  | 113.8276 |  |  | 166.7666 |  |  | 262.8858 |  |  | 557.9049
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5366 | 1.0982 |  | 6.0952 | 31.2221 |  | 9.3116 | 77.216 |  | 12.293 | 150.3971 |  | 13.6869 | 252.3195 |  | 12.9448 | 371.9499 |  | 7.1724 | 496.3686 |  | 1.7666 | 605.664 |  | 16.8858 | 703.1571 |  | 137.9049 | 800.2584
[13 empty] | Next iteration flow rate |  |  | 1.1202 | Abs Value of | Flow this | 31.5343 | Abs Value of | Flow this | 77.9882 | Abs Value of | Flow this | 151.9011 | Abs Value of | Flow this | 254.8427 | Abs Value of | Flow this | 375.6694 | Abs Value of | Flow this | 501.3323 | Abs Value of | Flow this | 611.7206 | Abs Value of | Flow this | 710.1887 | Abs Value of | Flow this | 808.2609 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8826 |  |  | 56.7107 |  |  | 56.1369 |  |  | 54.7228 |  |  | 52.1499 |  |  | 48.428 |  |  | 44.2784 |  |  | 39.8824 |  |  | 34.8531
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6635 |  |  | 24.6979 |  |  | 24.8126 |  |  | 25.0954 |  |  | 25.61 |  |  | 26.3544 |  |  | 27.1843 |  |  | 28.0635 |  |  | 29.0694
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2191 |  |  | 32.0129 |  |  | 31.3243 |  |  | 29.6274 |  |  | 26.5399 |  |  | 22.0736 |  |  | 17.0941 |  |  | 11.8189 |  |  | 5.7838
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4017 |  |  | 46.8116 |  |  | 44.3107 |  |  | 40.701 |  |  | 36.0431 |  |  | 30.7974 |  |  | 25.4922 |  |  | 19.7707 |  |  | 12.969
[13 empty] | C Non choked w/ reducers | 7 |  | 0.19725 |  |  | 5.5599 |  |  | 13.8263 |  |  | 27.3861 |  |  | 47.828 |  |  | 76.169 |  |  | 115.4873 |  |  | 169.9 |  |  | 270.0008 |  |  | 588.3475
[13 empty] | C Choked w/ reducers | 7 |  | 0.1586 |  |  | 4.5362 |  |  | 11.4338 |  |  | 23.0259 |  |  | 40.8062 |  |  | 65.3607 |  |  | 97.7718 |  |  | 139.1275 |  |  | 208.7578 |  |  | 392.903
[13 empty] | Selected C this iteration |  |  | 0.19725 |  |  | 5.5599 |  |  | 13.8263 |  |  | 27.3861 |  |  | 47.828 |  |  | 76.169 |  |  | 115.4873 |  |  | 169.9 |  |  | 270.0008 |  |  | 588.3475
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5327 | 1.1202 |  | 6.0401 | 31.5343 |  | 9.1737 | 77.9882 |  | 12.0139 | 151.9011 |  | 13.172 | 254.8427 |  | 12.031 | 375.6694 |  | 5.5127 | 501.3323 |  | 4.9 | 611.7206 |  | 24.0008 | 710.1887 |  | 168.3475 | 808.2609
[13 empty] | Next iteration flow rate |  |  | 1.1426 | Abs Value of | Flow this | 31.8497 | Abs Value of | Flow this | 78.7681 | Abs Value of | Flow this | 153.4201 | Abs Value of | Flow this | 257.3912 | Abs Value of | Flow this | 379.4261 | Abs Value of | Flow this | 506.3456 | Abs Value of | Flow this | 617.8378 | Abs Value of | Flow this | 717.2906 | Abs Value of | Flow this | 816.3436 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8819 |  |  | 56.7066 |  |  | 56.1212 |  |  | 54.6787 |  |  | 52.0541 |  |  | 48.2574 |  |  | 44.0244 |  |  | 39.5401 |  |  | 34.4097
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6636 |  |  | 24.6987 |  |  | 24.8158 |  |  | 25.1043 |  |  | 25.6292 |  |  | 26.3885 |  |  | 27.2351 |  |  | 28.132 |  |  | 29.1581
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2183 |  |  | 32.0079 |  |  | 31.3055 |  |  | 29.5745 |  |  | 26.425 |  |  | 21.8689 |  |  | 16.7893 |  |  | 11.4081 |  |  | 5.2516
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4011 |  |  | 46.8082 |  |  | 44.2982 |  |  | 40.6679 |  |  | 35.9764 |  |  | 30.6879 |  |  | 25.3445 |  |  | 19.5991 |  |  | 12.8019
[13 empty] | C Non choked w/ reducers | 7 |  | 0.2012 |  |  | 5.6156 |  |  | 13.9657 |  |  | 27.6683 |  |  | 48.3495 |  |  | 77.0978 |  |  | 117.1869 |  |  | 173.1498 |  |  | 277.5679 |  |  | 623.6122
[13 empty] | C Choked w/ reducers | 7 |  | 0.16177 |  |  | 4.5816 |  |  | 11.5486 |  |  | 23.2594 |  |  | 41.231 |  |  | 66.0755 |  |  | 98.9255 |  |  | 140.9277 |  |  | 211.7665 |  |  | 399.414
[13 empty] | Selected C this iteration |  |  | 0.2012 |  |  | 5.6156 |  |  | 13.9657 |  |  | 27.6683 |  |  | 48.3495 |  |  | 77.0978 |  |  | 117.1869 |  |  | 173.1498 |  |  | 277.5679 |  |  | 623.6122
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5288 | 1.1426 |  | 5.9844 | 31.8497 |  | 9.0343 | 78.7681 |  | 11.7317 | 153.4201 |  | 12.6505 | 257.3912 |  | 11.1022 | 379.4261 |  | 3.8131 | 506.3456 |  | 8.1498 | 617.8378 |  | 31.5679 | 717.2906 |  | 203.6122 | 816.3436
[13 empty] | Next iteration flow rate |  |  | 1.1654 | Abs Value of | Flow this | 32.1682 | Abs Value of | Flow this | 79.5557 | Abs Value of | Flow this | 154.9543 | Abs Value of | Flow this | 259.9651 | Abs Value of | Flow this | 383.2203 | Abs Value of | Flow this | 511.409 | Abs Value of | Flow this | 624.0162 | Abs Value of | Flow this | 724.4635 | Abs Value of | Flow this | 824.507 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8812 |  |  | 56.7024 |  |  | 56.1052 |  |  | 54.6337 |  |  | 51.9564 |  |  | 48.0833 |  |  | 43.7653 |  |  | 39.1908 |  |  | 33.9573
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6638 |  |  | 24.6995 |  |  | 24.819 |  |  | 25.1133 |  |  | 25.6487 |  |  | 26.4233 |  |  | 27.2869 |  |  | 28.2018 |  |  | 29.2485
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2174 |  |  | 32.0029 |  |  | 31.2863 |  |  | 29.5205 |  |  | 26.3077 |  |  | 21.66 |  |  | 16.4784 |  |  | 10.989 |  |  | 4.7087
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4006 |  |  | 46.8047 |  |  | 44.2855 |  |  | 40.6342 |  |  | 35.9082 |  |  | 30.5762 |  |  | 25.1938 |  |  | 19.424 |  |  | 12.6314
[13 empty] | C Non choked w/ reducers | 7 |  | 0.20522 |  |  | 5.6718 |  |  | 14.1064 |  |  | 27.9535 |  |  | 48.8776 |  |  | 78.0422 |  |  | 118.928 |  |  | 176.5236 |  |  | 285.6396 |  |  | 665.1648
[13 empty] | C Choked w/ reducers | 7 |  | 0.16501 |  |  | 4.6275 |  |  | 11.6645 |  |  | 23.4954 |  |  | 41.6606 |  |  | 66.7996 |  |  | 100.0971 |  |  | 142.762 |  |  | 214.8458 |  |  | 406.1214
[13 empty] | Selected C this iteration |  |  | 0.20522 |  |  | 5.6718 |  |  | 14.1064 |  |  | 27.9535 |  |  | 48.8776 |  |  | 78.0422 |  |  | 118.928 |  |  | 176.5236 |  |  | 285.6396 |  |  | 665.1648
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5248 | 1.1654 |  | 5.9282 | 32.1682 |  | 8.8936 | 79.5557 |  | 11.4465 | 154.9543 |  | 12.1224 | 259.9651 |  | 10.1578 | 383.2203 |  | 2.072 | 511.409 |  | 11.5236 | 624.0162 |  | 39.6396 | 724.4635 |  | 245.1648 | 824.507
[13 empty] | Next iteration flow rate |  |  | 1.1888 | Abs Value of | Flow this | 32.4899 | Abs Value of | Flow this | 80.3513 | Abs Value of | Flow this | 156.5038 | Abs Value of | Flow this | 262.5647 | Abs Value of | Flow this | 387.0526 | Abs Value of | Flow this | 516.5231 | Abs Value of | Flow this | 630.2564 | Abs Value of | Flow this | 731.7081 | Abs Value of | Flow this | 832.7521 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8805 |  |  | 56.6981 |  |  | 56.0889 |  |  | 54.5879 |  |  | 51.8567 |  |  | 47.9058 |  |  | 43.501 |  |  | 38.8345 |  |  | 33.4958
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6639 |  |  | 24.7004 |  |  | 24.8222 |  |  | 25.1224 |  |  | 25.6687 |  |  | 26.4588 |  |  | 27.3398 |  |  | 28.2731 |  |  | 29.3408
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2166 |  |  | 31.9977 |  |  | 31.2667 |  |  | 29.4654 |  |  | 26.1881 |  |  | 21.447 |  |  | 16.1612 |  |  | 10.5614 |  |  | 4.155
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.4 |  |  | 46.8011 |  |  | 44.2725 |  |  | 40.5998 |  |  | 35.8387 |  |  | 30.4623 |  |  | 25.0401 |  |  | 19.2455 |  |  | 12.4575
[13 empty] | C Non choked w/ reducers | 7 |  | 0.20933 |  |  | 5.7286 |  |  | 14.2486 |  |  | 28.2419 |  |  | 49.4125 |  |  | 79.0024 |  |  | 120.7124 |  |  | 180.0299 |  |  | 294.2774 |  |  | 715.1858
[13 empty] | C Choked w/ reducers | 7 |  | 0.16831 |  |  | 4.6738 |  |  | 11.7816 |  |  | 23.7338 |  |  | 42.0951 |  |  | 67.5329 |  |  | 101.287 |  |  | 144.6315 |  |  | 217.9988 |  |  | 413.0358
[13 empty] | Selected C this iteration |  |  | 0.20933 |  |  | 5.7286 |  |  | 14.2486 |  |  | 28.2419 |  |  | 49.4125 |  |  | 79.0024 |  |  | 120.7124 |  |  | 180.0299 |  |  | 294.2774 |  |  | 715.1858
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5207 | 1.1888 |  | 5.8714 | 32.4899 |  | 8.7514 | 80.3513 |  | 11.1581 | 156.5038 |  | 11.5875 | 262.5647 |  | 9.1976 | 387.0526 |  | 0.28755 | 516.5231 |  | 15.0299 | 630.2564 |  | 48.2774 | 731.7081 |  | 295.1858 | 832.7521
[13 empty] | Next iteration flow rate |  |  | 1.2125 | Abs Value of | Flow this | 32.8148 | Abs Value of | Flow this | 81.1548 | Abs Value of | Flow this | 158.0689 | Abs Value of | Flow this | 265.1904 | Abs Value of | Flow this | 390.9231 | Abs Value of | Flow this | 521.6884 | Abs Value of | Flow this | 636.5589 | Abs Value of | Flow this | 739.0252 | Abs Value of | Flow this | 841.0796 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8798 |  |  | 56.6937 |  |  | 56.0723 |  |  | 54.5411 |  |  | 51.755 |  |  | 47.7247 |  |  | 43.2313 |  |  | 38.4711 |  |  | 33.0251
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.664 |  |  | 24.7013 |  |  | 24.8255 |  |  | 25.1318 |  |  | 25.689 |  |  | 26.4951 |  |  | 27.3937 |  |  | 28.3458 |  |  | 29.435
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2157 |  |  | 31.9925 |  |  | 31.2468 |  |  | 29.4093 |  |  | 26.066 |  |  | 21.2296 |  |  | 15.8376 |  |  | 10.1253 |  |  | 3.5901
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3993 |  |  | 46.7974 |  |  | 44.2593 |  |  | 40.5647 |  |  | 35.7679 |  |  | 30.3461 |  |  | 24.8833 |  |  | 19.0633 |  |  | 12.2801
[13 empty] | C Non choked w/ reducers | 7 |  | 0.21351 |  |  | 5.786 |  |  | 14.3923 |  |  | 28.5334 |  |  | 49.9542 |  |  | 79.979 |  |  | 122.542 |  |  | 183.6783 |  |  | 303.5538 |  |  | 777.0923
[13 empty] | C Choked w/ reducers | 7 |  | 0.17167 |  |  | 4.7205 |  |  | 11.8999 |  |  | 23.9747 |  |  | 42.5344 |  |  | 68.2758 |  |  | 102.4956 |  |  | 146.5373 |  |  | 221.2283 |  |  | 420.1687
[13 empty] | Selected C this iteration |  |  | 0.21351 |  |  | 5.786 |  |  | 14.3923 |  |  | 28.5334 |  |  | 49.9542 |  |  | 79.979 |  |  | 122.542 |  |  | 183.6783 |  |  | 303.5538 |  |  | 777.0923
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5165 | 1.2125 |  | 5.814 | 32.8148 |  | 8.6077 | 81.1548 |  | 10.8666 | 158.0689 |  | 11.0458 | 265.1904 |  | 8.221 | 390.9231 |  | 1.542 | 521.6884 |  | 18.6783 | 636.5589 |  | 57.5538 | 739.0252 |  | 357.0923 | 841.0796
[13 empty] | Next iteration flow rate |  |  | 1.2368 | Abs Value of | Flow this | 33.1429 | Abs Value of | Flow this | 81.9664 | Abs Value of | Flow this | 159.6495 | Abs Value of | Flow this | 267.8423 | Abs Value of | Flow this | 394.8323 | Abs Value of | Flow this | 526.9052 | Abs Value of | Flow this | 642.9245 | Abs Value of | Flow this | 746.4154 | Abs Value of | Flow this | 849.4904 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.879 |  |  | 56.6892 |  |  | 56.0554 |  |  | 54.4933 |  |  | 51.6513 |  |  | 47.5399 |  |  | 42.9563 |  |  | 38.1003 |  |  | 32.5449
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6642 |  |  | 24.7022 |  |  | 24.8289 |  |  | 25.1413 |  |  | 25.7097 |  |  | 26.532 |  |  | 27.4487 |  |  | 28.4199 |  |  | 29.531
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2149 |  |  | 31.9871 |  |  | 31.2264 |  |  | 29.352 |  |  | 25.9415 |  |  | 21.0079 |  |  | 15.5075 |  |  | 9.6804 |  |  | 3.0138
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3987 |  |  | 46.7937 |  |  | 44.2458 |  |  | 40.5289 |  |  | 35.6956 |  |  | 30.2275 |  |  | 24.7234 |  |  | 18.8774 |  |  | 12.0991
[13 empty] | C Non choked w/ reducers | 7 |  | 0.21778 |  |  | 5.8439 |  |  | 14.5375 |  |  | 28.8281 |  |  | 50.503 |  |  | 80.9724 |  |  | 124.4188 |  |  | 187.479 |  |  | 313.5553 |  |  | 856.6175
[13 empty] | C Choked w/ reducers | 7 |  | 0.17511 |  |  | 4.7678 |  |  | 12.0194 |  |  | 24.2182 |  |  | 42.9787 |  |  | 69.0284 |  |  | 103.7234 |  |  | 148.4807 |  |  | 224.5377 |  |  | 427.5324
[13 empty] | Selected C this iteration |  |  | 0.21778 |  |  | 5.8439 |  |  | 14.5375 |  |  | 28.8281 |  |  | 50.503 |  |  | 80.9724 |  |  | 124.4188 |  |  | 187.479 |  |  | 313.5553 |  |  | 856.6175
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5122 | 1.2368 |  | 5.7561 | 33.1429 |  | 8.4625 | 81.9664 |  | 10.5719 | 159.6495 |  | 10.497 | 267.8423 |  | 7.2276 | 394.8323 |  | 3.4188 | 526.9052 |  | 22.479 | 642.9245 |  | 67.5553 | 746.4154 |  | 436.6175 | 849.4904
[13 empty] | Next iteration flow rate |  |  | 1.2615 | Abs Value of | Flow this | 33.4743 | Abs Value of | Flow this | 82.786 | Abs Value of | Flow this | 161.246 | Abs Value of | Flow this | 270.5207 | Abs Value of | Flow this | 398.7806 | Abs Value of | Flow this | 532.1743 | Abs Value of | Flow this | 649.3538 | Abs Value of | Flow this | 753.8796 | Abs Value of | Flow this | 857.9853 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8783 |  |  | 56.6847 |  |  | 56.0381 |  |  | 54.4446 |  |  | 51.5455 |  |  | 47.3515 |  |  | 42.6757 |  |  | 37.7221 |  |  | 32.055
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6643 |  |  | 24.7031 |  |  | 24.8324 |  |  | 25.1511 |  |  | 25.7309 |  |  | 26.5697 |  |  | 27.5049 |  |  | 28.4956 |  |  | 29.629
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.214 |  |  | 31.9816 |  |  | 31.2057 |  |  | 29.2936 |  |  | 25.8145 |  |  | 20.7818 |  |  | 15.1708 |  |  | 9.2266 |  |  | 2.426
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3981 |  |  | 46.7899 |  |  | 44.232 |  |  | 40.4924 |  |  | 35.6218 |  |  | 30.1065 |  |  | 24.5602 |  |  | 18.6879 |  |  | 11.9145
[13 empty] | C Non choked w/ reducers | 7 |  | 0.22214 |  |  | 5.9024 |  |  | 14.6841 |  |  | 29.1261 |  |  | 51.0589 |  |  | 81.983 |  |  | 126.3449 |  |  | 191.4436 |  |  | 324.3861 |  |  | 964.3238
[13 empty] | C Choked w/ reducers | 7 |  | 0.17861 |  |  | 4.8155 |  |  | 12.1401 |  |  | 24.4642 |  |  | 43.4281 |  |  | 69.7908 |  |  | 104.9708 |  |  | 150.4628 |  |  | 227.9305 |  |  | 435.1402
[13 empty] | Selected C this iteration |  |  | 0.22214 |  |  | 5.9024 |  |  | 14.6841 |  |  | 29.1261 |  |  | 51.0589 |  |  | 81.983 |  |  | 126.3449 |  |  | 191.4436 |  |  | 324.3861 |  |  | 964.3238
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5079 | 1.2615 |  | 5.6976 | 33.4743 |  | 8.3159 | 82.786 |  | 10.2739 | 161.246 |  | 9.9411 | 270.5207 |  | 6.217 | 398.7806 |  | 5.3449 | 532.1743 |  | 26.4436 | 649.3538 |  | 78.3861 | 753.8796 |  | 544.3238 | 857.9853
[13 empty] | Next iteration flow rate |  |  | 1.2867 | Abs Value of | Flow this | 33.8091 | Abs Value of | Flow this | 83.6139 | Abs Value of | Flow this | 162.8585 | Abs Value of | Flow this | 273.2259 | Abs Value of | Flow this | 402.7684 | Abs Value of | Flow this | 537.496 | Abs Value of | Flow this | 655.8473 | Abs Value of | Flow this | 761.4184 | Abs Value of | Flow this | 866.5651 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8775 |  |  | 56.68 |  |  | 56.0204 |  |  | 54.395 |  |  | 51.4375 |  |  | 47.1592 |  |  | 42.3894 |  |  | 37.3363 |  |  | 31.5553
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6645 |  |  | 24.704 |  |  | 24.8359 |  |  | 25.161 |  |  | 25.7525 |  |  | 26.6082 |  |  | 27.5621 |  |  | 28.5727 |  |  | 29.7289
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.213 |  |  | 31.976 |  |  | 31.1845 |  |  | 29.2339 |  |  | 25.685 |  |  | 20.5511 |  |  | 14.8273 |  |  | 8.7636 |  |  | 1.8263
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3974 |  |  | 46.7861 |  |  | 44.218 |  |  | 40.4552 |  |  | 35.5465 |  |  | 29.9832 |  |  | 24.3938 |  |  | 18.4945 |  |  | 11.7262
[13 empty] | C Non choked w/ reducers | 7 |  | 0.22658 |  |  | 5.9615 |  |  | 14.8322 |  |  | 29.4273 |  |  | 51.622 |  |  | 83.0114 |  |  | 128.3226 |  |  | 195.5848 |  |  | 336.1725 |  |  | 1122.5305
[13 empty] | C Choked w/ reducers | 7 |  | 0.18218 |  |  | 4.8637 |  |  | 12.262 |  |  | 24.7127 |  |  | 43.8825 |  |  | 70.5633 |  |  | 106.2385 |  |  | 152.485 |  |  | 231.4102 |  |  | 443.0067
[13 empty] | Selected C this iteration |  |  | 0.22658 |  |  | 5.9615 |  |  | 14.8322 |  |  | 29.4273 |  |  | 51.622 |  |  | 83.0114 |  |  | 128.3226 |  |  | 195.5848 |  |  | 336.1725 |  |  | 1122.5305
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5034 | 1.2867 |  | 5.6385 | 33.8091 |  | 8.1678 | 83.6139 |  | 9.9727 | 162.8585 |  | 9.378 | 273.2259 |  | 5.1886 | 402.7684 |  | 7.3226 | 537.496 |  | 30.5848 | 655.8473 |  | 90.1725 | 761.4184 |  | 702.5305 | 866.5651
[13 empty] | Next iteration flow rate |  |  | 1.3125 | Abs Value of | Flow this | 34.1472 | Abs Value of | Flow this | 84.45 | Abs Value of | Flow this | 164.4871 | Abs Value of | Flow this | 275.9582 | Abs Value of | Flow this | 406.7961 | Abs Value of | Flow this | 542.871 | Abs Value of | Flow this | 662.4058 | Abs Value of | Flow this | 769.0326 | Abs Value of | Flow this | 875.2308 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8768 |  |  | 56.6753 |  |  | 56.0024 |  |  | 54.3443 |  |  | 51.3274 |  |  | 46.9631 |  |  | 42.0975 |  |  | 36.9428 |  |  | 31.0455
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6646 |  |  | 24.7049 |  |  | 24.8395 |  |  | 25.1711 |  |  | 25.7745 |  |  | 26.6474 |  |  | 27.6205 |  |  | 28.6514 |  |  | 29.8309
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2121 |  |  | 31.9703 |  |  | 31.1629 |  |  | 29.1731 |  |  | 25.5529 |  |  | 20.3157 |  |  | 14.4769 |  |  | 8.2913 |  |  | 1.2146
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3968 |  |  | 46.7821 |  |  | 44.2037 |  |  | 40.4172 |  |  | 35.4698 |  |  | 29.8573 |  |  | 24.224 |  |  | 18.2972 |  |  | 11.5341
[13 empty] | C Non choked w/ reducers | 7 |  | 0.23111 |  |  | 6.0213 |  |  | 14.9819 |  |  | 29.7319 |  |  | 52.1926 |  |  | 84.058 |  |  | 130.3543 |  |  | 199.9169 |  |  | 349.0701 |  |  | 1390.2325
[13 empty] | C Choked w/ reducers | 7 |  | 0.18583 |  |  | 4.9123 |  |  | 12.3851 |  |  | 24.9639 |  |  | 44.3422 |  |  | 71.346 |  |  | 107.5268 |  |  | 154.5487 |  |  | 234.9809 |  |  | 451.1475
[13 empty] | Selected C this iteration |  |  | 0.23111 |  |  | 6.0213 |  |  | 14.9819 |  |  | 29.7319 |  |  | 52.1926 |  |  | 84.058 |  |  | 130.3543 |  |  | 199.9169 |  |  | 349.0701 |  |  | 1390.2325
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4989 | 1.3125 |  | 5.5787 | 34.1472 |  | 8.0181 | 84.45 |  | 9.6681 | 164.4871 |  | 8.8074 | 275.9582 |  | 4.142 | 406.7961 |  | 9.3543 | 542.871 |  | 34.9169 | 662.4058 |  | 103.0701 | 769.0326 |  | 970.2325 | 875.2308
[13 empty] | Next iteration flow rate |  |  | 1.3387 | Abs Value of | Flow this | 34.4886 | Abs Value of | Flow this | 85.2945 | Abs Value of | Flow this | 166.132 | Abs Value of | Flow this | 278.7177 | Abs Value of | Flow this | 410.8641 | Abs Value of | Flow this | 548.2997 | Abs Value of | Flow this | 669.0298 | Abs Value of | Flow this | 776.7229 | Abs Value of | Flow this | 883.9831 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.876 |  |  | 56.6704 |  |  | 55.984 |  |  | 54.2926 |  |  | 51.2151 |  |  | 46.7631 |  |  | 41.7996 |  |  | 36.5413 |  |  | 30.5255
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6648 |  |  | 24.7059 |  |  | 24.8432 |  |  | 25.1815 |  |  | 25.797 |  |  | 26.6874 |  |  | 27.6801 |  |  | 28.7317 |  |  | 29.9349
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2112 |  |  | 31.9645 |  |  | 31.1408 |  |  | 29.1111 |  |  | 25.4181 |  |  | 20.0757 |  |  | 14.1195 |  |  | 7.8096 |  |  | 0.59063
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3961 |  |  | 46.7781 |  |  | 44.1891 |  |  | 40.3784 |  |  | 35.3915 |  |  | 29.7289 |  |  | 24.0508 |  |  | 18.096 |  |  | 11.3381
[13 empty] | C Non choked w/ reducers | 7 |  | 0.23573 |  |  | 6.0816 |  |  | 15.1331 |  |  | 30.0399 |  |  | 52.7706 |  |  | 85.1234 |  |  | 132.4427 |  |  | 204.4558 |  |  | 363.2724 |  |  | 2013.5955
[13 empty] | C Choked w/ reducers | 7 |  | 0.18954 |  |  | 4.9615 |  |  | 12.5095 |  |  | 25.2177 |  |  | 44.8071 |  |  | 72.1391 |  |  | 108.8363 |  |  | 156.6552 |  |  | 238.6467 |  |  | 459.58
[13 empty] | Selected C this iteration |  |  | 0.23573 |  |  | 6.0816 |  |  | 15.1331 |  |  | 30.0399 |  |  | 52.7706 |  |  | 85.1234 |  |  | 132.4427 |  |  | 204.4558 |  |  | 363.2724 |  |  | 2013.5955
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4943 | 1.3387 |  | 5.5184 | 34.4886 |  | 7.8669 | 85.2945 |  | 9.3601 | 166.132 |  | 8.2294 | 278.7177 |  | 3.0766 | 410.8641 |  | 11.4427 | 548.2997 |  | 39.4558 | 669.0298 |  | 117.2724 | 776.7229 |  | 1593.5955 | 883.9831
[13 empty] | Next iteration flow rate |  |  | 1.3655 | Abs Value of | Flow this | 34.8335 | Abs Value of | Flow this | 86.1475 | Abs Value of | Flow this | 167.7933 | Abs Value of | Flow this | 281.5049 | Abs Value of | Flow this | 414.9727 | Abs Value of | Flow this | 553.7827 | Abs Value of | Flow this | 675.7201 | Abs Value of | Flow this | 784.4901 | Abs Value of | Flow this | 892.8229 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8752 |  |  | 56.6655 |  |  | 55.9653 |  |  | 54.2399 |  |  | 51.1005 |  |  | 46.559 |  |  | 41.4958 |  |  | 36.1318 |  |  | 29.9951
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.665 |  |  | 24.7069 |  |  | 24.8469 |  |  | 25.192 |  |  | 25.8199 |  |  | 26.7282 |  |  | 27.7408 |  |  | 28.8136 |  |  | 30.041
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2102 |  |  | 31.9586 |  |  | 31.1184 |  |  | 29.0478 |  |  | 25.2806 |  |  | 19.8308 |  |  | 13.7549 |  |  | 7.3181 |  |  | -0.045908
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3954 |  |  | 46.774 |  |  | 44.1742 |  |  | 40.3389 |  |  | 35.3116 |  |  | 29.5979 |  |  | 23.8741 |  |  | 17.8907 |  |  | 11.1382
[13 empty] | C Non choked w/ reducers | 7 |  | 0.24045 |  |  | 6.1425 |  |  | 15.2858 |  |  | 30.3512 |  |  | 53.3563 |  |  | 86.2082 |  |  | 134.5906 |  |  | 209.2194 |  |  | 379.0245 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.19333 |  |  | 5.0111 |  |  | 12.6352 |  |  | 25.4742 |  |  | 45.2773 |  |  | 72.9429 |  |  | 110.1676 |  |  | 158.8062 |  |  | 242.412 |  |  | 468.3227
[13 empty] | Selected C this iteration |  |  | 0.24045 |  |  | 6.1425 |  |  | 15.2858 |  |  | 30.3512 |  |  | 53.3563 |  |  | 86.2082 |  |  | 134.5906 |  |  | 209.2194 |  |  | 379.0245 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4896 | 1.3655 |  | 5.4575 | 34.8335 |  | 7.7142 | 86.1475 |  | 9.0488 | 167.7933 |  | 7.6437 | 281.5049 |  | 1.9918 | 414.9727 |  | 13.5906 | 553.7827 |  | 44.2194 | 675.7201 |  | 133.0245 | 784.4901 |  | 5500 | 892.8229
[13 empty] | Next iteration flow rate |  |  | 1.3928 | Abs Value of | Flow this | 35.1819 | Abs Value of | Flow this | 87.0089 | Abs Value of | Flow this | 169.4712 | Abs Value of | Flow this | 284.32 | Abs Value of | Flow this | 419.1225 | Abs Value of | Flow this | 559.3205 | Abs Value of | Flow this | 682.4773 | Abs Value of | Flow this | 792.335 | Abs Value of | Flow this | 901.7512 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8743 |  |  | 56.6605 |  |  | 55.9462 |  |  | 54.1861 |  |  | 50.9836 |  |  | 46.3508 |  |  | 41.1858 |  |  | 35.714 |  |  | 29.454
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6651 |  |  | 24.7079 |  |  | 24.8508 |  |  | 25.2028 |  |  | 25.8433 |  |  | 26.7698 |  |  | 27.8028 |  |  | 28.8972 |  |  | 30.1492
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2092 |  |  | 31.9526 |  |  | 31.0954 |  |  | 28.9833 |  |  | 25.1403 |  |  | 19.581 |  |  | 13.383 |  |  | 6.8168 |  |  | -0.69524
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3947 |  |  | 46.7698 |  |  | 44.159 |  |  | 40.2985 |  |  | 35.2301 |  |  | 29.4643 |  |  | 23.6939 |  |  | 17.6813 |  |  | 10.9343
[13 empty] | C Non choked w/ reducers | 7 |  | 0.24526 |  |  | 6.204 |  |  | 15.4401 |  |  | 30.666 |  |  | 53.9499 |  |  | 87.3128 |  |  | 136.8009 |  |  | 214.2279 |  |  | 396.6414 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.1972 |  |  | 5.0613 |  |  | 12.7621 |  |  | 25.7334 |  |  | 45.753 |  |  | 73.7575 |  |  | 111.5213 |  |  | 161.0031 |  |  | 246.2817 |  |  | 477.3964
[13 empty] | Selected C this iteration |  |  | 0.24526 |  |  | 6.204 |  |  | 15.4401 |  |  | 30.666 |  |  | 53.9499 |  |  | 87.3128 |  |  | 136.8009 |  |  | 214.2279 |  |  | 396.6414 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4847 | 1.3928 |  | 5.396 | 35.1819 |  | 7.5599 | 87.0089 |  | 8.734 | 169.4712 |  | 7.0501 | 284.32 |  | 0.88717 | 419.1225 |  | 15.8009 | 559.3205 |  | 49.2279 | 682.4773 |  | 150.6414 | 792.335 |  | 5500 | 901.7512
[13 empty] | Next iteration flow rate |  |  | 1.4207 | Abs Value of | Flow this | 35.5337 | Abs Value of | Flow this | 87.879 | Abs Value of | Flow this | 171.1659 | Abs Value of | Flow this | 287.1632 | Abs Value of | Flow this | 423.3137 | Abs Value of | Flow this | 564.9137 | Abs Value of | Flow this | 689.3021 | Abs Value of | Flow this | 800.2584 | Abs Value of | Flow this | 910.7687 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8735 |  |  | 56.6553 |  |  | 55.9267 |  |  | 54.1312 |  |  | 50.8643 |  |  | 46.1384 |  |  | 40.8696 |  |  | 35.2879 |  |  | 28.902
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6653 |  |  | 24.7089 |  |  | 24.8547 |  |  | 25.2138 |  |  | 25.8671 |  |  | 26.8123 |  |  | 27.8661 |  |  | 28.9824 |  |  | 30.2596
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2082 |  |  | 31.9464 |  |  | 31.072 |  |  | 28.9174 |  |  | 24.9972 |  |  | 19.3261 |  |  | 13.0035 |  |  | 6.3054 |  |  | -1.3576
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.394 |  |  | 46.7655 |  |  | 44.1434 |  |  | 40.2574 |  |  | 35.147 |  |  | 29.328 |  |  | 23.51 |  |  | 17.4677 |  |  | 10.7262
[13 empty] | C Non choked w/ reducers | 7 |  | 0.25016 |  |  | 6.2661 |  |  | 15.5961 |  |  | 30.9844 |  |  | 54.5514 |  |  | 88.438 |  |  | 139.0768 |  |  | 219.5041 |  |  | 416.5366 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.20114 |  |  | 5.1119 |  |  | 12.8903 |  |  | 25.9953 |  |  | 46.2341 |  |  | 74.5831 |  |  | 112.8979 |  |  | 163.2478 |  |  | 250.2609 |  |  | 486.8235
[13 empty] | Selected C this iteration |  |  | 0.25016 |  |  | 6.2661 |  |  | 15.5961 |  |  | 30.9844 |  |  | 54.5514 |  |  | 88.438 |  |  | 139.0768 |  |  | 219.5041 |  |  | 416.5366 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4798 | 1.4207 |  | 5.3339 | 35.5337 |  | 7.4039 | 87.879 |  | 8.4156 | 171.1659 |  | 6.4486 | 287.1632 |  | 0.238 | 423.3137 |  | 18.0768 | 564.9137 |  | 54.5041 | 689.3021 |  | 170.5366 | 800.2584 |  | 5500 | 910.7687
[13 empty] | Next iteration flow rate |  |  | 1.4491 | Abs Value of | Flow this | 35.889 | Abs Value of | Flow this | 88.7578 | Abs Value of | Flow this | 172.8776 | Abs Value of | Flow this | 290.0348 | Abs Value of | Flow this | 427.5468 | Abs Value of | Flow this | 570.5629 | Abs Value of | Flow this | 696.1951 | Abs Value of | Flow this | 808.2609 | Abs Value of | Flow this | 919.8764 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8726 |  |  | 56.6501 |  |  | 55.9068 |  |  | 54.0752 |  |  | 50.7427 |  |  | 45.9218 |  |  | 40.5471 |  |  | 34.8531 |  |  | 28.3389
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6655 |  |  | 24.71 |  |  | 24.8586 |  |  | 25.225 |  |  | 25.8915 |  |  | 26.8556 |  |  | 27.9306 |  |  | 29.0694 |  |  | 30.3722
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2072 |  |  | 31.9401 |  |  | 31.0482 |  |  | 28.8502 |  |  | 24.8512 |  |  | 19.0662 |  |  | 12.6165 |  |  | 5.7838 |  |  | -2.0333
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3932 |  |  | 46.7611 |  |  | 44.1276 |  |  | 40.2154 |  |  | 35.0622 |  |  | 29.189 |  |  | 23.3224 |  |  | 17.2498 |  |  | 10.514
[13 empty] | C Non choked w/ reducers | 7 |  | 0.25517 |  |  | 6.3289 |  |  | 15.7536 |  |  | 31.3062 |  |  | 55.161 |  |  | 89.5843 |  |  | 141.422 |  |  | 225.074 |  |  | 439.2653 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.20517 |  |  | 5.1631 |  |  | 13.0198 |  |  | 26.2599 |  |  | 46.7208 |  |  | 75.4199 |  |  | 114.2981 |  |  | 165.5419 |  |  | 254.355 |  |  | 496.6289
[13 empty] | Selected C this iteration |  |  | 0.25517 |  |  | 6.3289 |  |  | 15.7536 |  |  | 31.3062 |  |  | 55.161 |  |  | 89.5843 |  |  | 141.422 |  |  | 225.074 |  |  | 439.2653 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4748 | 1.4491 |  | 5.2711 | 35.889 |  | 7.2464 | 88.7578 |  | 8.0938 | 172.8776 |  | 5.839 | 290.0348 |  | 1.3843 | 427.5468 |  | 20.422 | 570.5629 |  | 60.074 | 696.1951 |  | 193.2653 | 808.2609 |  | 5500 | 919.8764
[13 empty] | Next iteration flow rate |  |  | 1.4781 | Abs Value of | Flow this | 36.2479 | Abs Value of | Flow this | 89.6454 | Abs Value of | Flow this | 174.6063 | Abs Value of | Flow this | 292.9351 | Abs Value of | Flow this | 431.8223 | Abs Value of | Flow this | 576.2685 | Abs Value of | Flow this | 703.1571 | Abs Value of | Flow this | 816.3436 | Abs Value of | Flow this | 929.0751 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8718 |  |  | 56.6447 |  |  | 55.8865 |  |  | 54.0181 |  |  | 50.6186 |  |  | 45.7008 |  |  | 40.2181 |  |  | 34.4097 |  |  | 27.7645
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6656 |  |  | 24.7111 |  |  | 24.8627 |  |  | 25.2364 |  |  | 25.9163 |  |  | 26.8998 |  |  | 27.9964 |  |  | 29.1581 |  |  | 30.4871
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2061 |  |  | 31.9337 |  |  | 31.0238 |  |  | 28.7817 |  |  | 24.7023 |  |  | 18.801 |  |  | 12.2217 |  |  | 5.2516 |  |  | -2.7226
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3925 |  |  | 46.7567 |  |  | 44.1115 |  |  | 40.1726 |  |  | 34.9757 |  |  | 29.0472 |  |  | 23.1311 |  |  | 17.0275 |  |  | 10.2976
[13 empty] | C Non choked w/ reducers | 7 |  | 0.26027 |  |  | 6.3923 |  |  | 15.9127 |  |  | 31.6317 |  |  | 55.7789 |  |  | 90.7525 |  |  | 143.84 |  |  | 230.9674 |  |  | 465.5942 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.20927 |  |  | 5.2148 |  |  | 13.1506 |  |  | 26.5274 |  |  | 47.2132 |  |  | 76.2682 |  |  | 115.7225 |  |  | 167.8874 |  |  | 258.57 |  |  | 506.8399
[13 empty] | Selected C this iteration |  |  | 0.26027 |  |  | 6.3923 |  |  | 15.9127 |  |  | 31.6317 |  |  | 55.7789 |  |  | 90.7525 |  |  | 143.84 |  |  | 230.9674 |  |  | 465.5942 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4697 | 1.4781 |  | 5.2077 | 36.2479 |  | 7.0873 | 89.6454 |  | 7.7683 | 174.6063 |  | 5.2211 | 292.9351 |  | 2.5525 | 431.8223 |  | 22.84 | 576.2685 |  | 65.9674 | 703.1571 |  | 219.5942 | 816.3436 |  | 5500 | 929.0751
[13 empty] | Next iteration flow rate |  |  | 1.5076 | Abs Value of | Flow this | 36.6104 | Abs Value of | Flow this | 90.5419 | Abs Value of | Flow this | 176.3524 | Abs Value of | Flow this | 295.8645 | Abs Value of | Flow this | 436.1405 | Abs Value of | Flow this | 582.0312 | Abs Value of | Flow this | 710.1887 | Abs Value of | Flow this | 824.507 | Abs Value of | Flow this | 938.3659 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8709 |  |  | 56.6393 |  |  | 55.8658 |  |  | 53.9599 |  |  | 50.492 |  |  | 45.4754 |  |  | 39.8824 |  |  | 33.9573 |  |  | 27.1785
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6658 |  |  | 24.7121 |  |  | 24.8668 |  |  | 25.248 |  |  | 25.9416 |  |  | 26.9449 |  |  | 28.0635 |  |  | 29.2485 |  |  | 30.6043
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2051 |  |  | 31.9271 |  |  | 30.999 |  |  | 28.7118 |  |  | 24.5504 |  |  | 18.5305 |  |  | 11.8189 |  |  | 4.7087 |  |  | -3.4258
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3917 |  |  | 46.7522 |  |  | 44.095 |  |  | 40.1289 |  |  | 34.8875 |  |  | 28.9025 |  |  | 22.9359 |  |  | 16.8007 |  |  | 10.0767
[13 empty] | C Non choked w/ reducers | 7 |  | 0.26548 |  |  | 6.4563 |  |  | 16.0735 |  |  | 31.9608 |  |  | 56.4052 |  |  | 91.9431 |  |  | 146.335 |  |  | 237.2185 |  |  | 496.6177 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.21346 |  |  | 5.267 |  |  | 13.2828 |  |  | 26.7976 |  |  | 47.7113 |  |  | 77.1283 |  |  | 117.1719 |  |  | 170.2862 |  |  | 262.9122 |  |  | 517.4869
[13 empty] | Selected C this iteration |  |  | 0.26548 |  |  | 6.4563 |  |  | 16.0735 |  |  | 31.9608 |  |  | 56.4052 |  |  | 91.9431 |  |  | 146.335 |  |  | 237.2185 |  |  | 496.6177 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4645 | 1.5076 |  | 5.1437 | 36.6104 |  | 6.9265 | 90.5419 |  | 7.4392 | 176.3524 |  | 4.5948 | 295.8645 |  | 3.7431 | 436.1405 |  | 25.335 | 582.0312 |  | 72.2185 | 710.1887 |  | 250.6177 | 824.507 |  | 5500 | 938.3659
[13 empty] | Next iteration flow rate |  |  | 1.5378 | Abs Value of | Flow this | 36.9765 | Abs Value of | Flow this | 91.4473 | Abs Value of | Flow this | 178.1159 | Abs Value of | Flow this | 298.8231 | Abs Value of | Flow this | 440.5019 | Abs Value of | Flow this | 587.8515 | Abs Value of | Flow this | 717.2906 | Abs Value of | Flow this | 832.7521 | Abs Value of | Flow this | 947.7495 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.87 |  |  | 56.6337 |  |  | 55.8447 |  |  | 53.9004 |  |  | 50.3629 |  |  | 45.2454 |  |  | 39.5401 |  |  | 33.4958 |  |  | 26.5808
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.666 |  |  | 24.7133 |  |  | 24.8711 |  |  | 25.2599 |  |  | 25.9674 |  |  | 26.9909 |  |  | 28.132 |  |  | 29.3408 |  |  | 30.7238
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.204 |  |  | 31.9205 |  |  | 30.9736 |  |  | 28.6405 |  |  | 24.3955 |  |  | 18.2545 |  |  | 11.4081 |  |  | 4.155 |  |  | -4.143
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3909 |  |  | 46.7475 |  |  | 44.0782 |  |  | 40.0844 |  |  | 34.7975 |  |  | 28.7549 |  |  | 22.7368 |  |  | 16.5694 |  |  | 9.8515
[13 empty] | C Non choked w/ reducers | 7 |  | 0.27079 |  |  | 6.521 |  |  | 16.2359 |  |  | 32.2936 |  |  | 57.0401 |  |  | 93.157 |  |  | 148.9112 |  |  | 243.8669 |  |  | 533.9639 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.21773 |  |  | 5.3197 |  |  | 13.4163 |  |  | 27.0708 |  |  | 48.2151 |  |  | 78.0002 |  |  | 118.647 |  |  | 172.7404 |  |  | 267.3885 |  |  | 528.6035
[13 empty] | Selected C this iteration |  |  | 0.27079 |  |  | 6.521 |  |  | 16.2359 |  |  | 32.2936 |  |  | 57.0401 |  |  | 93.157 |  |  | 148.9112 |  |  | 243.8669 |  |  | 533.9639 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4592 | 1.5378 |  | 5.079 | 36.9765 |  | 6.7641 | 91.4473 |  | 7.1064 | 178.1159 |  | 3.9599 | 298.8231 |  | 4.957 | 440.5019 |  | 27.9112 | 587.8515 |  | 78.8669 | 717.2906 |  | 287.9639 | 832.7521 |  | 5500 | 947.7495
[13 empty] | Next iteration flow rate |  |  | 1.5685 | Abs Value of | Flow this | 37.3463 | Abs Value of | Flow this | 92.3617 | Abs Value of | Flow this | 179.8971 | Abs Value of | Flow this | 301.8114 | Abs Value of | Flow this | 444.9069 | Abs Value of | Flow this | 593.73 | Abs Value of | Flow this | 724.4635 | Abs Value of | Flow this | 841.0796 | Abs Value of | Flow this | 957.227 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.869 |  |  | 56.628 |  |  | 55.8232 |  |  | 53.8398 |  |  | 50.2312 |  |  | 45.0109 |  |  | 39.1908 |  |  | 33.0251 |  |  | 25.9711
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6662 |  |  | 24.7144 |  |  | 24.8754 |  |  | 25.272 |  |  | 25.9938 |  |  | 27.0378 |  |  | 28.2018 |  |  | 29.435 |  |  | 30.8458
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2028 |  |  | 31.9136 |  |  | 30.9478 |  |  | 28.5678 |  |  | 24.2374 |  |  | 17.973 |  |  | 10.989 |  |  | 3.5901 |  |  | -4.8747
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3901 |  |  | 46.7428 |  |  | 44.0611 |  |  | 40.0389 |  |  | 34.7057 |  |  | 28.6044 |  |  | 22.5337 |  |  | 16.3334 |  |  | 9.6217
[13 empty] | C Non choked w/ reducers | 7 |  | 0.2762 |  |  | 6.5863 |  |  | 16.4 |  |  | 32.6302 |  |  | 57.6838 |  |  | 94.3949 |  |  | 151.5736 |  |  | 250.9585 |  |  | 580.1838 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.22208 |  |  | 5.3729 |  |  | 13.5511 |  |  | 27.3468 |  |  | 48.7249 |  |  | 78.8844 |  |  | 120.1484 |  |  | 175.2523 |  |  | 272.0061 |  |  | 540.2272
[13 empty] | Selected C this iteration |  |  | 0.2762 |  |  | 6.5863 |  |  | 16.4 |  |  | 32.6302 |  |  | 57.6838 |  |  | 94.3949 |  |  | 151.5736 |  |  | 250.9585 |  |  | 580.1838 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4538 | 1.5685 |  | 5.0137 | 37.3463 |  | 6.6 | 92.3617 |  | 6.7698 | 179.8971 |  | 3.3162 | 301.8114 |  | 6.1949 | 444.9069 |  | 30.5736 | 593.73 |  | 85.9585 | 724.4635 |  | 334.1838 | 841.0796 |  | 5500 | 957.227
[13 empty] | Next iteration flow rate |  |  | 1.5999 | Abs Value of | Flow this | 37.7197 | Abs Value of | Flow this | 93.2854 | Abs Value of | Flow this | 181.6961 | Abs Value of | Flow this | 304.8295 | Abs Value of | Flow this | 449.356 | Abs Value of | Flow this | 599.6673 | Abs Value of | Flow this | 731.7081 | Abs Value of | Flow this | 849.4904 | Abs Value of | Flow this | 966.7993 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8681 |  |  | 56.6223 |  |  | 55.8012 |  |  | 53.778 |  |  | 50.0968 |  |  | 44.7716 |  |  | 38.8345 |  |  | 32.5449 |  |  | 25.3491
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6664 |  |  | 24.7155 |  |  | 24.8798 |  |  | 25.2844 |  |  | 26.0206 |  |  | 27.0857 |  |  | 28.2731 |  |  | 29.531 |  |  | 30.9702
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2017 |  |  | 31.9067 |  |  | 30.9214 |  |  | 28.4936 |  |  | 24.0762 |  |  | 17.6859 |  |  | 10.5614 |  |  | 3.0138 |  |  | -5.6211
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3893 |  |  | 46.738 |  |  | 44.0436 |  |  | 39.9926 |  |  | 34.612 |  |  | 28.4508 |  |  | 22.3266 |  |  | 16.0927 |  |  | 9.3873
[13 empty] | C Non choked w/ reducers | 7 |  | 0.28173 |  |  | 6.6523 |  |  | 16.5658 |  |  | 32.9705 |  |  | 58.3365 |  |  | 95.6575 |  |  | 154.3271 |  |  | 258.5475 |  |  | 639.558 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.22652 |  |  | 5.4267 |  |  | 13.6873 |  |  | 27.6257 |  |  | 49.2407 |  |  | 79.7809 |  |  | 121.6769 |  |  | 177.8241 |  |  | 276.7732 |  |  | 552.3999
[13 empty] | Selected C this iteration |  |  | 0.28173 |  |  | 6.6523 |  |  | 16.5658 |  |  | 32.9705 |  |  | 58.3365 |  |  | 95.6575 |  |  | 154.3271 |  |  | 258.5475 |  |  | 639.558 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4483 | 1.5999 |  | 4.9477 | 37.7197 |  | 6.4342 | 93.2854 |  | 6.4295 | 181.6961 |  | 2.6635 | 304.8295 |  | 7.4575 | 449.356 |  | 33.3271 | 599.6673 |  | 93.5475 | 731.7081 |  | 393.558 | 849.4904 |  | 5500 | 966.7993
[13 empty] | Next iteration flow rate |  |  | 1.6319 | Abs Value of | Flow this | 38.0969 | Abs Value of | Flow this | 94.2182 | Abs Value of | Flow this | 183.513 | Abs Value of | Flow this | 307.8778 | Abs Value of | Flow this | 453.8496 | Abs Value of | Flow this | 605.664 | Abs Value of | Flow this | 739.0252 | Abs Value of | Flow this | 857.9853 | Abs Value of | Flow this | 976.4673 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8671 |  |  | 56.6163 |  |  | 55.7788 |  |  | 53.7149 |  |  | 49.9597 |  |  | 44.5275 |  |  | 38.4711 |  |  | 32.055 |  |  | 24.7146
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6666 |  |  | 24.7167 |  |  | 24.8842 |  |  | 25.297 |  |  | 26.0481 |  |  | 27.1345 |  |  | 28.3458 |  |  | 29.629 |  |  | 31.0971
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2006 |  |  | 31.8996 |  |  | 30.8945 |  |  | 28.4179 |  |  | 23.9117 |  |  | 17.393 |  |  | 10.1253 |  |  | 2.426 |  |  | -6.3825
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3885 |  |  | 46.7331 |  |  | 44.0258 |  |  | 39.9453 |  |  | 34.5165 |  |  | 28.2942 |  |  | 22.1152 |  |  | 15.8472 |  |  | 9.1482
[13 empty] | C Non choked w/ reducers | 7 |  | 0.28736 |  |  | 6.7189 |  |  | 16.7333 |  |  | 33.3147 |  |  | 58.9983 |  |  | 96.9458 |  |  | 157.1775 |  |  | 266.6976 |  |  | 719.9724 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.23105 |  |  | 5.481 |  |  | 13.8249 |  |  | 27.9077 |  |  | 49.7625 |  |  | 80.6902 |  |  | 123.2334 |  |  | 180.4585 |  |  | 281.6983 |  |  | 565.1685
[13 empty] | Selected C this iteration |  |  | 0.28736 |  |  | 6.7189 |  |  | 16.7333 |  |  | 33.3147 |  |  | 58.9983 |  |  | 96.9458 |  |  | 157.1775 |  |  | 266.6976 |  |  | 719.9724 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4426 | 1.6319 |  | 4.8811 | 38.0969 |  | 6.2667 | 94.2182 |  | 6.0853 | 183.513 |  | 2.0017 | 307.8778 |  | 8.7458 | 453.8496 |  | 36.1775 | 605.664 |  | 101.6976 | 739.0252 |  | 473.9724 | 857.9853 |  | 5500 | 976.4673
[13 empty] | Next iteration flow rate |  |  | 1.6645 | Abs Value of | Flow this | 38.4779 | Abs Value of | Flow this | 95.1604 | Abs Value of | Flow this | 185.3482 | Abs Value of | Flow this | 310.9566 | Abs Value of | Flow this | 458.3881 | Abs Value of | Flow this | 611.7206 | Abs Value of | Flow this | 746.4154 | Abs Value of | Flow this | 866.5651 | Abs Value of | Flow this | 986.232 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8661 |  |  | 56.6103 |  |  | 55.7559 |  |  | 53.6506 |  |  | 49.8199 |  |  | 44.2784 |  |  | 38.1003 |  |  | 31.5553 |  |  | 24.0673
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6668 |  |  | 24.7179 |  |  | 24.8888 |  |  | 25.3099 |  |  | 26.076 |  |  | 27.1843 |  |  | 28.4199 |  |  | 29.7289 |  |  | 31.2265
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.1994 |  |  | 31.8924 |  |  | 30.8671 |  |  | 28.3407 |  |  | 23.7439 |  |  | 17.0941 |  |  | 9.6804 |  |  | 1.8263 |  |  | -7.1592
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3876 |  |  | 46.7281 |  |  | 44.0076 |  |  | 39.897 |  |  | 34.419 |  |  | 28.1343 |  |  | 21.8996 |  |  | 15.5967 |  |  | 8.9042
[13 empty] | C Non choked w/ reducers | 7 |  | 0.29311 |  |  | 6.7862 |  |  | 16.9026 |  |  | 33.6628 |  |  | 59.6694 |  |  | 98.2606 |  |  | 160.1307 |  |  | 275.4848 |  |  | 838.0909 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.23567 |  |  | 5.5359 |  |  | 13.9639 |  |  | 28.1926 |  |  | 50.2905 |  |  | 81.6124 |  |  | 124.8188 |  |  | 183.1581 |  |  | 286.7908 |  |  | 578.5859
[13 empty] | Selected C this iteration |  |  | 0.29311 |  |  | 6.7862 |  |  | 16.9026 |  |  | 33.6628 |  |  | 59.6694 |  |  | 98.2606 |  |  | 160.1307 |  |  | 275.4848 |  |  | 838.0909 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4369 | 1.6645 |  | 4.8138 | 38.4779 |  | 6.0974 | 95.1604 |  | 5.7372 | 185.3482 |  | 1.3306 | 310.9566 |  | 10.0606 | 458.3881 |  | 39.1307 | 611.7206 |  | 110.4848 | 746.4154 |  | 592.0909 | 866.5651 |  | 5500 | 986.232
[13 empty] | Next iteration flow rate |  |  | 1.6978 | Abs Value of | Flow this | 38.8627 | Abs Value of | Flow this | 96.112 | Abs Value of | Flow this | 187.2016 | Abs Value of | Flow this | 314.0661 | Abs Value of | Flow this | 462.9719 | Abs Value of | Flow this | 617.8378 | Abs Value of | Flow this | 753.8796 | Abs Value of | Flow this | 875.2308 | Abs Value of | Flow this | 996.0943 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8651 |  |  | 56.6042 |  |  | 55.7326 |  |  | 53.5849 |  |  | 49.6773 |  |  | 44.0244 |  |  | 37.7221 |  |  | 31.0455 |  |  | 23.4071
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.667 |  |  | 24.7192 |  |  | 24.8935 |  |  | 25.323 |  |  | 26.1045 |  |  | 27.2351 |  |  | 28.4956 |  |  | 29.8309 |  |  | 31.3586
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.1982 |  |  | 31.885 |  |  | 30.8391 |  |  | 28.2619 |  |  | 23.5727 |  |  | 16.7893 |  |  | 9.2266 |  |  | 1.2146 |  |  | -7.9515
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3868 |  |  | 46.7229 |  |  | 43.989 |  |  | 39.8478 |  |  | 34.3196 |  |  | 27.9713 |  |  | 21.6797 |  |  | 15.3412 |  |  | 8.6554
[13 empty] | C Non choked w/ reducers | 7 |  | 0.29897 |  |  | 6.8542 |  |  | 17.0736 |  |  | 34.0148 |  |  | 60.35 |  |  | 99.6029 |  |  | 163.1936 |  |  | 285.0006 |  |  | 1037.9595 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.24039 |  |  | 5.5913 |  |  | 14.1043 |  |  | 28.4805 |  |  | 50.8248 |  |  | 82.5478 |  |  | 126.4338 |  |  | 185.9256 |  |  | 292.061 |  |  | 592.7121
[13 empty] | Selected C this iteration |  |  | 0.29897 |  |  | 6.8542 |  |  | 17.0736 |  |  | 34.0148 |  |  | 60.35 |  |  | 99.6029 |  |  | 163.1936 |  |  | 285.0006 |  |  | 1037.9595 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.431 | 1.6978 |  | 4.7458 | 38.8627 |  | 5.9264 | 96.112 |  | 5.3852 | 187.2016 |  | 0.65001 | 314.0661 |  | 11.4029 | 462.9719 |  | 42.1936 | 617.8378 |  | 120.0006 | 753.8796 |  | 791.9595 | 875.2308 |  | 5500 | 996.0943
[13 empty] | Next iteration flow rate |  |  | 1.7318 | Abs Value of | Flow this | 39.2513 | Abs Value of | Flow this | 97.0731 | Abs Value of | Flow this | 189.0737 | Abs Value of | Flow this | 317.2068 | Abs Value of | Flow this | 467.6017 | Abs Value of | Flow this | 624.0162 | Abs Value of | Flow this | 761.4184 | Abs Value of | Flow this | 883.9831 | Abs Value of | Flow this | 1006.0552 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8641 |  |  | 56.5979 |  |  | 55.7088 |  |  | 53.518 |  |  | 49.5318 |  |  | 43.7653 |  |  | 37.3363 |  |  | 30.5255 |  |  | 22.7335
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6672 |  |  | 24.7204 |  |  | 24.8982 |  |  | 25.3364 |  |  | 26.1336 |  |  | 27.2869 |  |  | 28.5727 |  |  | 29.9349 |  |  | 31.4933
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.1969 |  |  | 31.8775 |  |  | 30.8106 |  |  | 28.1816 |  |  | 23.3981 |  |  | 16.4784 |  |  | 8.7636 |  |  | 0.59063 |  |  | -8.7598
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3859 |  |  | 46.7177 |  |  | 43.9701 |  |  | 39.7976 |  |  | 34.2182 |  |  | 27.805 |  |  | 21.4554 |  |  | 15.0805 |  |  | 8.4016
[13 empty] | C Non choked w/ reducers | 7 |  | 0.30495 |  |  | 6.9229 |  |  | 17.2464 |  |  | 34.3709 |  |  | 61.0403 |  |  | 100.9736 |  |  | 166.3734 |  |  | 295.356 |  |  | 1503.3677 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.24519 |  |  | 5.6472 |  |  | 14.2462 |  |  | 28.7715 |  |  | 51.3654 |  |  | 83.4968 |  |  | 128.0794 |  |  | 188.764 |  |  | 297.5199 |  |  | 607.615
[13 empty] | Selected C this iteration |  |  | 0.30495 |  |  | 6.9229 |  |  | 17.2464 |  |  | 34.3709 |  |  | 61.0403 |  |  | 100.9736 |  |  | 166.3734 |  |  | 295.356 |  |  | 1503.3677 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4251 | 1.7318 |  | 4.6771 | 39.2513 |  | 5.7536 | 97.0731 |  | 5.0291 | 189.0737 |  | 0.040324 | 317.2068 |  | 12.7736 | 467.6017 |  | 45.3734 | 624.0162 |  | 130.356 | 761.4184 |  | 1257.3677 | 883.9831 |  | 5500 | 1006.0552
[13 empty] | Next iteration flow rate |  |  | 1.7664 | Abs Value of | Flow this | 39.6438 | Abs Value of | Flow this | 98.0438 | Abs Value of | Flow this | 190.9644 | Abs Value of | Flow this | 320.3788 | Abs Value of | Flow this | 472.2777 | Abs Value of | Flow this | 630.2564 | Abs Value of | Flow this | 769.0326 | Abs Value of | Flow this | 892.8229 | Abs Value of | Flow this | 1016.1158 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8631 |  |  | 56.5915 |  |  | 55.6846 |  |  | 53.4497 |  |  | 49.3833 |  |  | 43.501 |  |  | 36.9428 |  |  | 29.9951 |  |  | 22.0465
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6674 |  |  | 24.7217 |  |  | 24.9031 |  |  | 25.3501 |  |  | 26.1633 |  |  | 27.3398 |  |  | 28.6514 |  |  | 30.041 |  |  | 31.6307
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1957 |  |  | 31.8698 |  |  | 30.7815 |  |  | 28.0996 |  |  | 23.22 |  |  | 16.1612 |  |  | 8.2913 |  |  | -0.045908 |  |  | -9.5842
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.385 |  |  | 46.7124 |  |  | 43.9508 |  |  | 39.7464 |  |  | 34.1147 |  |  | 27.6354 |  |  | 21.2265 |  |  | 14.8146 |  |  | 8.1427
[13 empty] | C Non choked w/ reducers | 7 |  | 0.31105 |  |  | 6.9923 |  |  | 17.4209 |  |  | 34.731 |  |  | 61.7406 |  |  | 102.3737 |  |  | 169.6782 |  |  | 306.6875 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.2501 |  |  | 5.7038 |  |  | 14.3895 |  |  | 29.0656 |  |  | 51.9125 |  |  | 84.4595 |  |  | 129.7567 |  |  | 191.6767 |  |  | 303.1798 |  |  | 623.3723
[13 empty] | Selected C this iteration |  |  | 0.31105 |  |  | 6.9923 |  |  | 17.4209 |  |  | 34.731 |  |  | 61.7406 |  |  | 102.3737 |  |  | 169.6782 |  |  | 306.6875 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.419 | 1.7664 |  | 4.6077 | 39.6438 |  | 5.5791 | 98.0438 |  | 4.669 | 190.9644 |  | 0.74058 | 320.3788 |  | 14.1737 | 472.2777 |  | 48.6782 | 630.2564 |  | 141.6875 | 769.0326 |  | 5500 | 892.8229 |  | 5500 | 1016.1158
[13 empty] | Next iteration flow rate |  |  | 1.8018 | Abs Value of | Flow this | 40.0402 | Abs Value of | Flow this | 99.0243 | Abs Value of | Flow this | 192.874 | Abs Value of | Flow this | 323.5826 | Abs Value of | Flow this | 477.0004 | Abs Value of | Flow this | 636.5589 | Abs Value of | Flow this | 776.7229 | Abs Value of | Flow this | 901.7512 | Abs Value of | Flow this | 1026.2769 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.862 |  |  | 56.585 |  |  | 55.6598 |  |  | 53.38 |  |  | 49.2319 |  |  | 43.2313 |  |  | 36.5413 |  |  | 29.454 |  |  | 21.3456
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6676 |  |  | 24.723 |  |  | 24.908 |  |  | 25.364 |  |  | 26.1936 |  |  | 27.3937 |  |  | 28.7317 |  |  | 30.1492 |  |  | 31.7709
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1944 |  |  | 31.862 |  |  | 30.7518 |  |  | 28.016 |  |  | 23.0383 |  |  | 15.8376 |  |  | 7.8096 |  |  | -0.69524 |  |  | -10.4253
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3841 |  |  | 46.707 |  |  | 43.9311 |  |  | 39.6942 |  |  | 34.0092 |  |  | 27.4623 |  |  | 20.9931 |  |  | 14.5434 |  |  | 7.8785
[13 empty] | C Non choked w/ reducers | 7 |  | 0.31727 |  |  | 7.0623 |  |  | 17.5973 |  |  | 35.0953 |  |  | 62.451 |  |  | 103.8043 |  |  | 173.1168 |  |  | 319.1655 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.2551 |  |  | 5.7609 |  |  | 14.5342 |  |  | 29.3628 |  |  | 52.4661 |  |  | 85.4364 |  |  | 131.4665 |  |  | 194.6669 |  |  | 309.0538 |  |  | 640.0731
[13 empty] | Selected C this iteration |  |  | 0.31727 |  |  | 7.0623 |  |  | 17.5973 |  |  | 35.0953 |  |  | 62.451 |  |  | 103.8043 |  |  | 173.1168 |  |  | 319.1655 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4127 | 1.8018 |  | 4.5377 | 40.0402 |  | 5.4027 | 99.0243 |  | 4.3047 | 192.874 |  | 1.451 | 323.5826 |  | 15.6043 | 477.0004 |  | 52.1168 | 636.5589 |  | 154.1655 | 776.7229 |  | 5500 | 901.7512 |  | 5500 | 1026.2769
[13 empty] | Next iteration flow rate |  |  | 1.8378 | Abs Value of | Flow this | 40.4406 | Abs Value of | Flow this | 100.0145 | Abs Value of | Flow this | 194.8028 | Abs Value of | Flow this | 326.8185 | Abs Value of | Flow this | 481.7705 | Abs Value of | Flow this | 642.9245 | Abs Value of | Flow this | 784.4901 | Abs Value of | Flow this | 910.7687 | Abs Value of | Flow this | 1036.5397 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8609 |  |  | 56.5783 |  |  | 55.6345 |  |  | 53.3089 |  |  | 49.0775 |  |  | 42.9563 |  |  | 36.1318 |  |  | 28.902 |  |  | 20.6306
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6678 |  |  | 24.7243 |  |  | 24.9131 |  |  | 25.3782 |  |  | 26.2245 |  |  | 27.4487 |  |  | 28.8136 |  |  | 30.2596 |  |  | 31.9139
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1931 |  |  | 31.854 |  |  | 30.7215 |  |  | 27.9307 |  |  | 22.853 |  |  | 15.5075 |  |  | 7.3181 |  |  | -1.3576 |  |  | -11.2833
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3832 |  |  | 46.7014 |  |  | 43.911 |  |  | 39.6409 |  |  | 33.9016 |  |  | 27.2858 |  |  | 20.7549 |  |  | 14.2667 |  |  | 7.6091
[13 empty] | C Non choked w/ reducers | 7 |  | 0.32361 |  |  | 7.1331 |  |  | 17.7755 |  |  | 35.4637 |  |  | 63.1717 |  |  | 105.2667 |  |  | 176.699 |  |  | 333.0051 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.2602 |  |  | 5.8185 |  |  | 14.6804 |  |  | 29.6632 |  |  | 53.0264 |  |  | 86.4276 |  |  | 133.21 |  |  | 197.7383 |  |  | 315.1567 |  |  | 657.8204
[13 empty] | Selected C this iteration |  |  | 0.32361 |  |  | 7.1331 |  |  | 17.7755 |  |  | 35.4637 |  |  | 63.1717 |  |  | 105.2667 |  |  | 176.699 |  |  | 333.0051 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4064 | 1.8378 |  | 4.4669 | 40.4406 |  | 5.2245 | 100.0145 |  | 3.9363 | 194.8028 |  | 2.1717 | 326.8185 |  | 17.0667 | 481.7705 |  | 55.699 | 642.9245 |  | 168.0051 | 784.4901 |  | 5500 | 910.7687 |  | 5500 | 1036.5397
[13 empty] | Next iteration flow rate |  |  | 1.8746 | Abs Value of | Flow this | 40.8451 | Abs Value of | Flow this | 101.0147 | Abs Value of | Flow this | 196.7508 | Abs Value of | Flow this | 330.0866 | Abs Value of | Flow this | 486.5882 | Abs Value of | Flow this | 649.3538 | Abs Value of | Flow this | 792.335 | Abs Value of | Flow this | 919.8764 | Abs Value of | Flow this | 1046.9051 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8598 |  |  | 56.5715 |  |  | 55.6088 |  |  | 53.2364 |  |  | 48.9199 |  |  | 42.6757 |  |  | 35.714 |  |  | 28.3389 |  |  | 19.9013
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.668 |  |  | 24.7257 |  |  | 24.9182 |  |  | 25.3927 |  |  | 26.256 |  |  | 27.5049 |  |  | 28.8972 |  |  | 30.3722 |  |  | 32.0597
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1918 |  |  | 31.8458 |  |  | 30.6905 |  |  | 27.8437 |  |  | 22.6639 |  |  | 15.1708 |  |  | 6.8168 |  |  | -2.0333 |  |  | -12.1585
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3822 |  |  | 46.6958 |  |  | 43.8905 |  |  | 39.5865 |  |  | 33.7917 |  |  | 27.1057 |  |  | 20.512 |  |  | 13.9845 |  |  | 7.3342
[13 empty] | C Non choked w/ reducers | 7 |  | 0.33009 |  |  | 7.2046 |  |  | 17.9555 |  |  | 35.8364 |  |  | 63.903 |  |  | 106.7619 |  |  | 180.4356 |  |  | 348.483 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.26541 |  |  | 5.8768 |  |  | 14.8281 |  |  | 29.9668 |  |  | 53.5934 |  |  | 87.4336 |  |  | 134.9883 |  |  | 200.8949 |  |  | 321.5044 |  |  | 676.7338
[13 empty] | Selected C this iteration |  |  | 0.33009 |  |  | 7.2046 |  |  | 17.9555 |  |  | 35.8364 |  |  | 63.903 |  |  | 106.7619 |  |  | 180.4356 |  |  | 348.483 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3999 | 1.8746 |  | 4.3954 | 40.8451 |  | 5.0445 | 101.0147 |  | 3.5636 | 196.7508 |  | 2.903 | 330.0866 |  | 18.5619 | 486.5882 |  | 59.4356 | 649.3538 |  | 183.483 | 792.335 |  | 5500 | 919.8764 |  | 5500 | 1046.9051
[13 empty] | Next iteration flow rate |  |  | 1.912 | Abs Value of | Flow this | 41.2535 | Abs Value of | Flow this | 102.0248 | Abs Value of | Flow this | 198.7183 | Abs Value of | Flow this | 333.3875 | Abs Value of | Flow this | 491.454 | Abs Value of | Flow this | 655.8473 | Abs Value of | Flow this | 800.2584 | Abs Value of | Flow this | 929.0751 | Abs Value of | Flow this | 1057.3741 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8587 |  |  | 56.5646 |  |  | 55.5825 |  |  | 53.1624 |  |  | 48.7592 |  |  | 42.3894 |  |  | 35.2879 |  |  | 27.7645 |  |  | 19.1573
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6683 |  |  | 24.7271 |  |  | 24.9235 |  |  | 25.4075 |  |  | 26.2882 |  |  | 27.5621 |  |  | 28.9824 |  |  | 30.4871 |  |  | 32.2085
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1904 |  |  | 31.8375 |  |  | 30.659 |  |  | 27.7549 |  |  | 22.471 |  |  | 14.8273 |  |  | 6.3054 |  |  | -2.7226 |  |  | -13.0513
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8986 |  |  | 48.3812 |  |  | 46.69 |  |  | 43.8696 |  |  | 39.531 |  |  | 33.6797 |  |  | 26.922 |  |  | 20.2642 |  |  | 13.6965 |  |  | 7.0538
[13 empty] | C Non choked w/ reducers | 7 |  | 0.33669 |  |  | 7.2768 |  |  | 18.1375 |  |  | 36.2134 |  |  | 64.6452 |  |  | 108.2913 |  |  | 184.3387 |  |  | 365.9626 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.27071 |  |  | 5.9356 |  |  | 14.9773 |  |  | 30.2737 |  |  | 54.1673 |  |  | 88.4547 |  |  | 136.8025 |  |  | 204.1408 |  |  | 328.1148 |  |  | 696.9531
[13 empty] | Selected C this iteration |  |  | 0.33669 |  |  | 7.2768 |  |  | 18.1375 |  |  | 36.2134 |  |  | 64.6452 |  |  | 108.2913 |  |  | 184.3387 |  |  | 365.9626 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3933 | 1.912 |  | 4.3232 | 41.2535 |  | 4.8625 | 102.0248 |  | 3.1866 | 198.7183 |  | 3.6452 | 333.3875 |  | 20.0913 | 491.454 |  | 63.3387 | 655.8473 |  | 200.9626 | 800.2584 |  | 5500 | 929.0751 |  | 5500 | 1057.3741
[13 empty] | Next iteration flow rate |  |  | 1.9503 | Abs Value of | Flow this | 41.666 | Abs Value of | Flow this | 103.0451 | Abs Value of | Flow this | 200.7055 | Abs Value of | Flow this | 336.7214 | Abs Value of | Flow this | 496.3686 | Abs Value of | Flow this | 662.4058 | Abs Value of | Flow this | 808.2609 | Abs Value of | Flow this | 938.3659 | Abs Value of | Flow this | 1067.9479 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8575 |  |  | 56.5575 |  |  | 55.5557 |  |  | 53.087 |  |  | 48.5952 |  |  | 42.0975 |  |  | 34.8531 |  |  | 27.1785 |  |  | 18.3983
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6685 |  |  | 24.7285 |  |  | 24.9289 |  |  | 25.4226 |  |  | 26.321 |  |  | 27.6205 |  |  | 29.0694 |  |  | 30.6043 |  |  | 32.3603
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.189 |  |  | 31.829 |  |  | 30.6268 |  |  | 27.6644 |  |  | 22.2743 |  |  | 14.4769 |  |  | 5.7838 |  |  | -3.4258 |  |  | -13.962
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3802 |  |  | 46.6841 |  |  | 43.8483 |  |  | 39.4745 |  |  | 33.5654 |  |  | 26.7346 |  |  | 20.0114 |  |  | 13.4028 |  |  | 6.7678
[13 empty] | C Non choked w/ reducers | 7 |  | 0.34342 |  |  | 7.3497 |  |  | 18.3213 |  |  | 36.5947 |  |  | 65.3984 |  |  | 109.8562 |  |  | 188.4217 |  |  | 385.9317 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.27613 |  |  | 5.995 |  |  | 15.128 |  |  | 30.5839 |  |  | 54.7481 |  |  | 89.4912 |  |  | 138.6539 |  |  | 207.4804 |  |  | 335.0074 |  |  | 718.6434
[13 empty] | Selected C this iteration |  |  | 0.34342 |  |  | 7.3497 |  |  | 18.3213 |  |  | 36.5947 |  |  | 65.3984 |  |  | 109.8562 |  |  | 188.4217 |  |  | 385.9317 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3866 | 1.9503 |  | 4.2503 | 41.666 |  | 4.6787 | 103.0451 |  | 2.8053 | 200.7055 |  | 4.3984 | 336.7214 |  | 21.6562 | 496.3686 |  | 67.4217 | 662.4058 |  | 220.9317 | 808.2609 |  | 5500 | 938.3659 |  | 5500 | 1067.9479
[13 empty] | Next iteration flow rate |  |  | 1.9893 | Abs Value of | Flow this | 42.0827 | Abs Value of | Flow this | 104.0755 | Abs Value of | Flow this | 202.7126 | Abs Value of | Flow this | 340.0886 | Abs Value of | Flow this | 501.3323 | Abs Value of | Flow this | 669.0298 | Abs Value of | Flow this | 816.3436 | Abs Value of | Flow this | 947.7495 | Abs Value of | Flow this | 1078.6274 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8563 |  |  | 56.5503 |  |  | 55.5284 |  |  | 53.01 |  |  | 48.428 |  |  | 41.7996 |  |  | 34.4097 |  |  | 26.5808 |  |  | 17.6241
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6687 |  |  | 24.7299 |  |  | 24.9343 |  |  | 25.438 |  |  | 26.3544 |  |  | 27.6801 |  |  | 29.1581 |  |  | 30.7238 |  |  | 32.5152
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1876 |  |  | 31.8204 |  |  | 30.594 |  |  | 27.572 |  |  | 22.0736 |  |  | 14.1195 |  |  | 5.2516 |  |  | -4.143 |  |  | -14.8911
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3792 |  |  | 46.6782 |  |  | 43.8265 |  |  | 39.4168 |  |  | 33.4488 |  |  | 26.5435 |  |  | 19.7535 |  |  | 13.1032 |  |  | 6.476
[13 empty] | C Non choked w/ reducers | 7 |  | 0.35029 |  |  | 7.4234 |  |  | 18.507 |  |  | 36.9805 |  |  | 66.1629 |  |  | 111.458 |  |  | 192.6996 |  |  | 409.0638 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.28165 |  |  | 6.055 |  |  | 15.2803 |  |  | 30.8974 |  |  | 55.3361 |  |  | 90.5435 |  |  | 140.5438 |  |  | 210.9186 |  |  | 342.204 |  |  | 742.0004
[13 empty] | Selected C this iteration |  |  | 0.35029 |  |  | 7.4234 |  |  | 18.507 |  |  | 36.9805 |  |  | 66.1629 |  |  | 111.458 |  |  | 192.6996 |  |  | 409.0638 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3797 | 1.9893 |  | 4.1766 | 42.0827 |  | 4.493 | 104.0755 |  | 2.4195 | 202.7126 |  | 5.1629 | 340.0886 |  | 23.258 | 501.3323 |  | 71.6996 | 669.0298 |  | 244.0638 | 816.3436 |  | 5500 | 947.7495 |  | 5500 | 1078.6274
[13 empty] | Next iteration flow rate |  |  | 2.0291 | Abs Value of | Flow this | 42.5035 | Abs Value of | Flow this | 105.1163 | Abs Value of | Flow this | 204.7397 | Abs Value of | Flow this | 343.4895 | Abs Value of | Flow this | 506.3456 | Abs Value of | Flow this | 675.7201 | Abs Value of | Flow this | 824.507 | Abs Value of | Flow this | 957.227 | Abs Value of | Flow this | 1089.4136 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8551 |  |  | 56.543 |  |  | 55.5005 |  |  | 52.9315 |  |  | 48.2574 |  |  | 41.4958 |  |  | 33.9573 |  |  | 25.9711 |  |  | 16.8343
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.669 |  |  | 24.7314 |  |  | 24.9399 |  |  | 25.4537 |  |  | 26.3885 |  |  | 27.7408 |  |  | 29.2485 |  |  | 30.8458 |  |  | 32.6731
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1862 |  |  | 31.8116 |  |  | 30.5606 |  |  | 27.4778 |  |  | 21.8689 |  |  | 13.7549 |  |  | 4.7087 |  |  | -4.8747 |  |  | -15.8388
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3782 |  |  | 46.672 |  |  | 43.8043 |  |  | 39.3579 |  |  | 33.3299 |  |  | 26.3485 |  |  | 19.4904 |  |  | 12.7976 |  |  | 6.1784
[13 empty] | C Non choked w/ reducers | 7 |  | 0.3573 |  |  | 7.4978 |  |  | 18.6947 |  |  | 37.3707 |  |  | 66.939 |  |  | 113.0983 |  |  | 197.1893 |  |  | 436.3207 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.28728 |  |  | 6.1156 |  |  | 15.4341 |  |  | 31.2143 |  |  | 55.9312 |  |  | 91.6119 |  |  | 142.4735 |  |  | 214.4606 |  |  | 349.7288 |  |  | 767.2592
[13 empty] | Selected C this iteration |  |  | 0.3573 |  |  | 7.4978 |  |  | 18.6947 |  |  | 37.3707 |  |  | 66.939 |  |  | 113.0983 |  |  | 197.1893 |  |  | 436.3207 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3727 | 2.0291 |  | 4.1022 | 42.5035 |  | 4.3053 | 105.1163 |  | 2.0293 | 204.7397 |  | 5.939 | 343.4895 |  | 24.8983 | 506.3456 |  | 76.1893 | 675.7201 |  | 271.3207 | 824.507 |  | 5500 | 957.227 |  | 5500 | 1089.4136
[13 empty] | Next iteration flow rate |  |  | 2.0697 | Abs Value of | Flow this | 42.9286 | Abs Value of | Flow this | 106.1674 | Abs Value of | Flow this | 206.7871 | Abs Value of | Flow this | 346.9244 | Abs Value of | Flow this | 511.409 | Abs Value of | Flow this | 682.4773 | Abs Value of | Flow this | 832.7521 | Abs Value of | Flow this | 966.7993 | Abs Value of | Flow this | 1100.3078 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8539 |  |  | 56.5355 |  |  | 55.472 |  |  | 52.8514 |  |  | 48.0833 |  |  | 41.1858 |  |  | 33.4958 |  |  | 25.3491 |  |  | 16.0287
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6692 |  |  | 24.7329 |  |  | 24.9456 |  |  | 25.4697 |  |  | 26.4233 |  |  | 27.8028 |  |  | 29.3408 |  |  | 30.9702 |  |  | 32.8343
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1847 |  |  | 31.8026 |  |  | 30.5264 |  |  | 27.3817 |  |  | 21.66 |  |  | 13.383 |  |  | 4.155 |  |  | -5.6211 |  |  | -16.8056
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3772 |  |  | 46.6658 |  |  | 43.7817 |  |  | 39.2978 |  |  | 33.2086 |  |  | 26.1496 |  |  | 19.2221 |  |  | 12.4858 |  |  | 5.8748
[13 empty] | C Non choked w/ reducers | 7 |  | 0.36444 |  |  | 7.5729 |  |  | 18.8843 |  |  | 37.7655 |  |  | 67.7269 |  |  | 114.7787 |  |  | 201.9097 |  |  | 469.1324 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.29303 |  |  | 6.1769 |  |  | 15.5895 |  |  | 31.5346 |  |  | 56.5337 |  |  | 92.6969 |  |  | 144.4446 |  |  | 218.1119 |  |  | 357.6091 |  |  | 794.7043
[13 empty] | Selected C this iteration |  |  | 0.36444 |  |  | 7.5729 |  |  | 18.8843 |  |  | 37.7655 |  |  | 67.7269 |  |  | 114.7787 |  |  | 201.9097 |  |  | 469.1324 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3656 | 2.0697 |  | 4.0271 | 42.9286 |  | 4.1157 | 106.1674 |  | 1.6345 | 206.7871 |  | 6.7269 | 346.9244 |  | 26.5787 | 511.409 |  | 80.9097 | 682.4773 |  | 304.1324 | 832.7521 |  | 5500 | 966.7993 |  | 5500 | 1100.3078
[13 empty] | Next iteration flow rate |  |  | 2.111 | Abs Value of | Flow this | 43.3578 | Abs Value of | Flow this | 107.2291 | Abs Value of | Flow this | 208.8549 | Abs Value of | Flow this | 350.3936 | Abs Value of | Flow this | 516.5231 | Abs Value of | Flow this | 689.3021 | Abs Value of | Flow this | 841.0796 | Abs Value of | Flow this | 976.4673 | Abs Value of | Flow this | 1111.3109 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8527 |  |  | 56.5278 |  |  | 55.443 |  |  | 52.7697 |  |  | 47.9058 |  |  | 40.8696 |  |  | 33.0251 |  |  | 24.7146 |  |  | 15.2069
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6695 |  |  | 24.7344 |  |  | 24.9514 |  |  | 25.4861 |  |  | 26.4588 |  |  | 27.8661 |  |  | 29.435 |  |  | 31.0971 |  |  | 32.9986
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1832 |  |  | 31.7934 |  |  | 30.4916 |  |  | 27.2837 |  |  | 21.447 |  |  | 13.0035 |  |  | 3.5901 |  |  | -6.3825 |  |  | -17.7918
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3761 |  |  | 46.6594 |  |  | 43.7586 |  |  | 39.2366 |  |  | 33.0849 |  |  | 25.9467 |  |  | 18.9483 |  |  | 12.1678 |  |  | 5.5651
[13 empty] | C Non choked w/ reducers | 7 |  | 0.37173 |  |  | 7.6488 |  |  | 19.0759 |  |  | 38.165 |  |  | 68.527 |  |  | 116.5008 |  |  | 206.8825 |  |  | 509.7405 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.29889 |  |  | 6.2387 |  |  | 15.7465 |  |  | 31.8583 |  |  | 57.1436 |  |  | 93.7988 |  |  | 146.4584 |  |  | 221.8786 |  |  | 365.8751 |  |  | 824.6845
[13 empty] | Selected C this iteration |  |  | 0.37173 |  |  | 7.6488 |  |  | 19.0759 |  |  | 38.165 |  |  | 68.527 |  |  | 116.5008 |  |  | 206.8825 |  |  | 509.7405 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3583 | 2.111 |  | 3.9512 | 43.3578 |  | 3.9241 | 107.2291 |  | 1.235 | 208.8549 |  | 7.527 | 350.3936 |  | 28.3008 | 516.5231 |  | 85.8825 | 689.3021 |  | 344.7405 | 841.0796 |  | 5500 | 976.4673 |  | 5500 | 1111.3109
[13 empty] | Next iteration flow rate |  |  | 2.1533 | Abs Value of | Flow this | 43.7914 | Abs Value of | Flow this | 108.3014 | Abs Value of | Flow this | 210.9435 | Abs Value of | Flow this | 353.8976 | Abs Value of | Flow this | 521.6884 | Abs Value of | Flow this | 696.1951 | Abs Value of | Flow this | 849.4904 | Abs Value of | Flow this | 986.232 | Abs Value of | Flow this | 1122.424 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8514 |  |  | 56.52 |  |  | 55.4134 |  |  | 52.6864 |  |  | 47.7247 |  |  | 40.5471 |  |  | 32.5449 |  |  | 24.0673 |  |  | 14.3685
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6697 |  |  | 24.736 |  |  | 24.9573 |  |  | 25.5027 |  |  | 26.4951 |  |  | 27.9306 |  |  | 29.531 |  |  | 31.2265 |  |  | 33.1663
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1817 |  |  | 31.784 |  |  | 30.456 |  |  | 27.1836 |  |  | 21.2296 |  |  | 12.6165 |  |  | 3.0138 |  |  | -7.1592 |  |  | -18.7978
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.375 |  |  | 46.6529 |  |  | 43.7351 |  |  | 39.1741 |  |  | 32.9586 |  |  | 25.7397 |  |  | 18.6691 |  |  | 11.8433 |  |  | 5.2491
[13 empty] | C Non choked w/ reducers | 7 |  | 0.37917 |  |  | 7.7255 |  |  | 19.2695 |  |  | 38.5691 |  |  | 69.3395 |  |  | 118.2666 |  |  | 212.1322 |  |  | 561.9057 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.30487 |  |  | 6.3012 |  |  | 15.905 |  |  | 32.1856 |  |  | 57.761 |  |  | 94.918 |  |  | 148.5165 |  |  | 225.7671 |  |  | 374.5612 |  |  | 857.6323
[13 empty] | Selected C this iteration |  |  | 0.37917 |  |  | 7.7255 |  |  | 19.2695 |  |  | 38.5691 |  |  | 69.3395 |  |  | 118.2666 |  |  | 212.1322 |  |  | 561.9057 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3508 | 2.1533 |  | 3.8745 | 43.7914 |  | 3.7305 | 108.3014 |  | 0.83091 | 210.9435 |  | 8.3395 | 353.8976 |  | 30.0666 | 521.6884 |  | 91.1322 | 696.1951 |  | 396.9057 | 849.4904 |  | 5500 | 986.232 |  | 5500 | 1122.424
[13 empty] | Next iteration flow rate |  |  | 2.1963 | Abs Value of | Flow this | 44.2293 | Abs Value of | Flow this | 109.3844 | Abs Value of | Flow this | 213.0529 | Abs Value of | Flow this | 357.4365 | Abs Value of | Flow this | 526.9052 | Abs Value of | Flow this | 703.1571 | Abs Value of | Flow this | 857.9853 | Abs Value of | Flow this | 996.0943 | Abs Value of | Flow this | 1133.6482 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8501 |  |  | 56.5121 |  |  | 55.3832 |  |  | 52.6014 |  |  | 47.5399 |  |  | 40.2181 |  |  | 32.055 |  |  | 23.4071 |  |  | 13.5133
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.67 |  |  | 24.7376 |  |  | 24.9634 |  |  | 25.5197 |  |  | 26.532 |  |  | 27.9964 |  |  | 29.629 |  |  | 31.3586 |  |  | 33.3373
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1801 |  |  | 31.7745 |  |  | 30.4198 |  |  | 27.0816 |  |  | 21.0079 |  |  | 12.2217 |  |  | 2.426 |  |  | -7.9515 |  |  | -19.824
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3739 |  |  | 46.6463 |  |  | 43.711 |  |  | 39.1103 |  |  | 32.8298 |  |  | 25.5285 |  |  | 18.3842 |  |  | 11.5124 |  |  | 4.9268
[13 empty] | C Non choked w/ reducers | 7 |  | 0.38675 |  |  | 7.8029 |  |  | 19.4651 |  |  | 38.978 |  |  | 70.1647 |  |  | 120.0779 |  |  | 217.6868 |  |  | 632.5566 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.31097 |  |  | 6.3642 |  |  | 16.0652 |  |  | 32.5164 |  |  | 58.3862 |  |  | 96.0551 |  |  | 150.6208 |  |  | 229.7846 |  |  | 383.7061 |  |  | 894.092
[13 empty] | Selected C this iteration |  |  | 0.38675 |  |  | 7.8029 |  |  | 19.4651 |  |  | 38.978 |  |  | 70.1647 |  |  | 120.0779 |  |  | 217.6868 |  |  | 632.5566 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3433 | 2.1963 |  | 3.7971 | 44.2293 |  | 3.5349 | 109.3844 |  | 0.42202 | 213.0529 |  | 9.1647 | 357.4365 |  | 31.8779 | 526.9052 |  | 96.6868 | 703.1571 |  | 467.5566 | 857.9853 |  | 5500 | 996.0943 |  | 5500 | 1133.6482
[13 empty] | Next iteration flow rate |  |  | 2.2403 | Abs Value of | Flow this | 44.6716 | Abs Value of | Flow this | 110.4783 | Abs Value of | Flow this | 215.1835 | Abs Value of | Flow this | 361.0109 | Abs Value of | Flow this | 532.1743 | Abs Value of | Flow this | 710.1887 | Abs Value of | Flow this | 866.5651 | Abs Value of | Flow this | 1006.0552 | Abs Value of | Flow this | 1144.9847 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8487 |  |  | 56.5039 |  |  | 55.3523 |  |  | 52.5146 |  |  | 47.3515 |  |  | 39.8824 |  |  | 31.5553 |  |  | 22.7335 |  |  | 12.6409
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6703 |  |  | 24.7392 |  |  | 24.9695 |  |  | 25.5371 |  |  | 26.5697 |  |  | 28.0635 |  |  | 29.7289 |  |  | 31.4933 |  |  | 33.5118
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1785 |  |  | 31.7647 |  |  | 30.3828 |  |  | 26.9776 |  |  | 20.7818 |  |  | 11.8189 |  |  | 1.8263 |  |  | -8.7598 |  |  | -20.8709
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3727 |  |  | 46.6396 |  |  | 43.6865 |  |  | 39.0453 |  |  | 32.6985 |  |  | 25.3131 |  |  | 18.0937 |  |  | 11.1747 |  |  | 4.598
[13 empty] | C Non choked w/ reducers | 7 |  | 0.39448 |  |  | 7.8812 |  |  | 19.6628 |  |  | 39.3917 |  |  | 71.0029 |  |  | 121.9368 |  |  | 223.5784 |  |  | 736.3337 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.31718 |  |  | 6.428 |  |  | 16.2271 |  |  | 32.8507 |  |  | 59.0191 |  |  | 97.2103 |  |  | 152.7729 |  |  | 233.9386 |  |  | 393.3539 |  |  | 934.7604
[13 empty] | Selected C this iteration |  |  | 0.39448 |  |  | 7.8812 |  |  | 19.6628 |  |  | 39.3917 |  |  | 71.0029 |  |  | 121.9368 |  |  | 223.5784 |  |  | 736.3337 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3355 | 2.2403 |  | 3.7188 | 44.6716 |  | 3.3372 | 110.4783 |  | 0.0082948 | 215.1835 |  | 10.0029 | 361.0109 |  | 33.7368 | 532.1743 |  | 102.5784 | 710.1887 |  | 571.3337 | 866.5651 |  | 5500 | 1006.0552 |  | 5500 | 1144.9847
[13 empty] | Next iteration flow rate |  |  | 2.2851 | Abs Value of | Flow this | 45.1183 | Abs Value of | Flow this | 111.583 | Abs Value of | Flow this | 217.3353 | Abs Value of | Flow this | 364.621 | Abs Value of | Flow this | 537.496 | Abs Value of | Flow this | 717.2906 | Abs Value of | Flow this | 875.2308 | Abs Value of | Flow this | 1016.1158 | Abs Value of | Flow this | 1156.4345 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8474 |  |  | 56.4957 |  |  | 55.3209 |  |  | 52.4262 |  |  | 47.1592 |  |  | 39.5401 |  |  | 31.0455 |  |  | 22.0465 |  |  | 11.751
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6705 |  |  | 24.7409 |  |  | 24.9758 |  |  | 25.5548 |  |  | 26.6082 |  |  | 28.132 |  |  | 29.8309 |  |  | 31.6307 |  |  | 33.6898
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1769 |  |  | 31.7548 |  |  | 30.3451 |  |  | 26.8714 |  |  | 20.5511 |  |  | 11.4081 |  |  | 1.2146 |  |  | -9.5842 |  |  | -21.9388
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3716 |  |  | 46.6327 |  |  | 43.6615 |  |  | 38.979 |  |  | 32.5645 |  |  | 25.0934 |  |  | 17.7972 |  |  | 10.8303 |  |  | 4.2627
[13 empty] | C Non choked w/ reducers | 7 |  | 0.40237 |  |  | 7.9602 |  |  | 19.8625 |  |  | 39.8103 |  |  | 71.8544 |  |  | 123.8455 |  |  | 229.8445 |  |  | 911.9351 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.32353 |  |  | 6.4923 |  |  | 16.3905 |  |  | 33.1887 |  |  | 59.66 |  |  | 98.3842 |  |  | 154.9747 |  |  | 238.2376 |  |  | 403.5547 |  |  | 980.5456
[13 empty] | Selected C this iteration |  |  | 0.40237 |  |  | 7.9602 |  |  | 19.8625 |  |  | 39.8103 |  |  | 71.8544 |  |  | 123.8455 |  |  | 229.8445 |  |  | 911.9351 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3276 | 2.2851 |  | 3.6398 | 45.1183 |  | 3.1375 | 111.583 |  | 0.41034 | 217.3353 |  | 10.8544 | 364.621 |  | 35.6455 | 537.496 |  | 108.8445 | 717.2906 |  | 746.9351 | 875.2308 |  | 5500 | 1016.1158 |  | 5500 | 1156.4345
[13 empty] | Next iteration flow rate |  |  | 2.3308 | Abs Value of | Flow this | 45.5695 | Abs Value of | Flow this | 112.6989 | Abs Value of | Flow this | 219.5086 | Abs Value of | Flow this | 368.2672 | Abs Value of | Flow this | 542.871 | Abs Value of | Flow this | 724.4635 | Abs Value of | Flow this | 883.9831 | Abs Value of | Flow this | 1026.2769 | Abs Value of | Flow this | 1167.9989 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.846 |  |  | 56.4872 |  |  | 55.2889 |  |  | 52.3359 |  |  | 46.9631 |  |  | 39.1908 |  |  | 30.5255 |  |  | 21.3456 |  |  | 10.8431
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6708 |  |  | 24.7426 |  |  | 24.9822 |  |  | 25.5728 |  |  | 26.6474 |  |  | 28.2018 |  |  | 29.9349 |  |  | 31.7709 |  |  | 33.8714
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1752 |  |  | 31.7446 |  |  | 30.3066 |  |  | 26.7631 |  |  | 20.3157 |  |  | 10.989 |  |  | 0.59063 |  |  | -10.4253 |  |  | -23.0282
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3704 |  |  | 46.6256 |  |  | 43.636 |  |  | 38.9113 |  |  | 32.4278 |  |  | 24.8692 |  |  | 17.4948 |  |  | 10.479 |  |  | 3.9205
[13 empty] | C Non choked w/ reducers | 7 |  | 0.41042 |  |  | 8.04 |  |  | 20.0643 |  |  | 40.234 |  |  | 72.7197 |  |  | 125.8063 |  |  | 236.5284 |  |  | 1320.8356 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.33 |  |  | 6.5573 |  |  | 16.5557 |  |  | 33.5304 |  |  | 60.309 |  |  | 99.5773 |  |  | 157.2282 |  |  | 242.6905 |  |  | 414.3664 |  |  | 1032.6586
[13 empty] | Selected C this iteration |  |  | 0.41042 |  |  | 8.04 |  |  | 20.0643 |  |  | 40.234 |  |  | 72.7197 |  |  | 125.8063 |  |  | 236.5284 |  |  | 1320.8356 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3196 | 2.3308 |  | 3.56 | 45.5695 |  | 2.9357 | 112.6989 |  | 0.83396 | 219.5086 |  | 11.7197 | 368.2672 |  | 37.6063 | 542.871 |  | 115.5284 | 724.4635 |  | 1155.8356 | 883.9831 |  | 5500 | 1026.2769 |  | 5500 | 1167.9989
[13 empty] | Next iteration flow rate |  |  | 2.3774 | Abs Value of | Flow this | 46.0252 | Abs Value of | Flow this | 113.8259 | Abs Value of | Flow this | 221.7037 | Abs Value of | Flow this | 371.9499 | Abs Value of | Flow this | 548.2997 | Abs Value of | Flow this | 731.7081 | Abs Value of | Flow this | 892.8229 | Abs Value of | Flow this | 1036.5397 | Abs Value of | Flow this | 1179.6789 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8446 |  |  | 56.4786 |  |  | 55.2561 |  |  | 52.2438 |  |  | 46.7631 |  |  | 38.8345 |  |  | 29.9951 |  |  | 20.6306 |  |  | 9.9171
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6711 |  |  | 24.7443 |  |  | 24.9888 |  |  | 25.5912 |  |  | 26.6874 |  |  | 28.2731 |  |  | 30.041 |  |  | 31.9139 |  |  | 34.0566
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1735 |  |  | 31.7343 |  |  | 30.2674 |  |  | 26.6526 |  |  | 20.0757 |  |  | 10.5614 |  |  | -0.045908 |  |  | -11.2833 |  |  | -24.1395
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3692 |  |  | 46.6185 |  |  | 43.61 |  |  | 38.8423 |  |  | 32.2883 |  |  | 24.6406 |  |  | 17.1864 |  |  | 10.1206 |  |  | 3.5715
[13 empty] | C Non choked w/ reducers | 7 |  | 0.41863 |  |  | 8.1206 |  |  | 20.2683 |  |  | 40.6626 |  |  | 73.5989 |  |  | 127.8218 |  |  | 243.681 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.3366 |  |  | 6.623 |  |  | 16.7225 |  |  | 33.8758 |  |  | 60.9662 |  |  | 100.79 |  |  | 159.5356 |  |  | 247.3073 |  |  | 425.8555 |  |  | 1092.7564
[13 empty] | Selected C this iteration |  |  | 0.41863 |  |  | 8.1206 |  |  | 20.2683 |  |  | 40.6626 |  |  | 73.5989 |  |  | 127.8218 |  |  | 243.681 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3114 | 2.3774 |  | 3.4794 | 46.0252 |  | 2.7317 | 113.8259 |  | 1.2626 | 221.7037 |  | 12.5989 | 371.9499 |  | 39.6218 | 548.2997 |  | 122.681 | 731.7081 |  | 5500 | 892.8229 |  | 5500 | 1036.5397 |  | 5500 | 1179.6789
[13 empty] | Next iteration flow rate |  |  | 2.4249 | Abs Value of | Flow this | 46.4855 | Abs Value of | Flow this | 114.9641 | Abs Value of | Flow this | 223.9208 | Abs Value of | Flow this | 375.6694 | Abs Value of | Flow this | 553.7827 | Abs Value of | Flow this | 739.0252 | Abs Value of | Flow this | 901.7512 | Abs Value of | Flow this | 1046.9051 | Abs Value of | Flow this | 1191.4757 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8432 |  |  | 56.4698 |  |  | 55.2228 |  |  | 52.1499 |  |  | 46.559 |  |  | 38.4711 |  |  | 29.454 |  |  | 19.9013 |  |  | 8.9724
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6714 |  |  | 24.746 |  |  | 24.9954 |  |  | 25.61 |  |  | 26.7282 |  |  | 28.3458 |  |  | 30.1492 |  |  | 32.0597 |  |  | 34.2455
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1718 |  |  | 31.7237 |  |  | 30.2273 |  |  | 26.5399 |  |  | 19.8308 |  |  | 10.1253 |  |  | -0.69524 |  |  | -12.1585 |  |  | -25.2731
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3679 |  |  | 46.6111 |  |  | 43.5834 |  |  | 38.7719 |  |  | 32.1461 |  |  | 24.4073 |  |  | 16.8717 |  |  | 9.7551 |  |  | 3.2155
[13 empty] | C Non choked w/ reducers | 7 |  | 0.427 |  |  | 8.202 |  |  | 20.4744 |  |  | 41.0965 |  |  | 74.4926 |  |  | 129.8947 |  |  | 251.3625 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.34333 |  |  | 6.6893 |  |  | 16.8911 |  |  | 34.225 |  |  | 61.6317 |  |  | 102.0228 |  |  | 161.899 |  |  | 252.0988 |  |  | 438.0996 |  |  | 1163.1791
[13 empty] | Selected C this iteration |  |  | 0.427 |  |  | 8.202 |  |  | 20.4744 |  |  | 41.0965 |  |  | 74.4926 |  |  | 129.8947 |  |  | 251.3625 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.303 | 2.4249 |  | 3.398 | 46.4855 |  | 2.5256 | 114.9641 |  | 1.6965 | 223.9208 |  | 13.4926 | 375.6694 |  | 41.6947 | 553.7827 |  | 130.3625 | 739.0252 |  | 5500 | 901.7512 |  | 5500 | 1046.9051 |  | 5500 | 1191.4757
[13 empty] | Next iteration flow rate |  |  | 2.4734 | Abs Value of | Flow this | 46.9503 | Abs Value of | Flow this | 116.1138 | Abs Value of | Flow this | 226.16 | Abs Value of | Flow this | 379.4261 | Abs Value of | Flow this | 559.3205 | Abs Value of | Flow this | 746.4154 | Abs Value of | Flow this | 910.7687 | Abs Value of | Flow this | 1057.3741 | Abs Value of | Flow this | 1203.3904 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8417 |  |  | 56.4608 |  |  | 55.1887 |  |  | 52.0541 |  |  | 46.3508 |  |  | 38.1003 |  |  | 28.902 |  |  | 19.1573 |  |  | 8.0087
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6717 |  |  | 24.7478 |  |  | 25.0023 |  |  | 25.6292 |  |  | 26.7698 |  |  | 28.4199 |  |  | 30.2596 |  |  | 32.2085 |  |  | 34.4383
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.17 |  |  | 31.713 |  |  | 30.1865 |  |  | 26.425 |  |  | 19.581 |  |  | 9.6804 |  |  | -1.3576 |  |  | -13.0513 |  |  | -26.4295
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3667 |  |  | 46.6037 |  |  | 43.5564 |  |  | 38.7 |  |  | 32.001 |  |  | 24.1694 |  |  | 16.5507 |  |  | 9.3821 |  |  | 2.8524
[13 empty] | C Non choked w/ reducers | 7 |  | 0.43554 |  |  | 8.2843 |  |  | 20.6826 |  |  | 41.5355 |  |  | 75.401 |  |  | 132.0279 |  |  | 259.6444 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.3502 |  |  | 6.7563 |  |  | 17.0614 |  |  | 34.578 |  |  | 62.3058 |  |  | 103.2764 |  |  | 164.3209 |  |  | 257.077 |  |  | 451.189 |  |  | 1247.3612
[13 empty] | Selected C this iteration |  |  | 0.43554 |  |  | 8.2843 |  |  | 20.6826 |  |  | 41.5355 |  |  | 75.401 |  |  | 132.0279 |  |  | 259.6444 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2945 | 2.4734 |  | 3.3157 | 46.9503 |  | 2.3174 | 116.1138 |  | 2.1355 | 226.16 |  | 14.401 | 379.4261 |  | 43.8279 | 559.3205 |  | 138.6444 | 746.4154 |  | 5500 | 910.7687 |  | 5500 | 1057.3741 |  | 5500 | 1203.3904
[13 empty] | Next iteration flow rate |  |  | 2.5229 | Abs Value of | Flow this | 47.4198 | Abs Value of | Flow this | 117.2749 | Abs Value of | Flow this | 228.4216 | Abs Value of | Flow this | 383.2203 | Abs Value of | Flow this | 564.9137 | Abs Value of | Flow this | 753.8796 | Abs Value of | Flow this | 919.8764 | Abs Value of | Flow this | 1067.9479 | Abs Value of | Flow this | 1215.4243 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8402 |  |  | 56.4517 |  |  | 55.154 |  |  | 51.9564 |  |  | 46.1384 |  |  | 37.7221 |  |  | 28.3389 |  |  | 18.3983 |  |  | 7.0257
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.672 |  |  | 24.7497 |  |  | 25.0092 |  |  | 25.6487 |  |  | 26.8123 |  |  | 28.4956 |  |  | 30.3722 |  |  | 32.3603 |  |  | 34.6349
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1682 |  |  | 31.702 |  |  | 30.1448 |  |  | 26.3077 |  |  | 19.3261 |  |  | 9.2266 |  |  | -2.0333 |  |  | -13.962 |  |  | -27.6092
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3654 |  |  | 46.5961 |  |  | 43.5287 |  |  | 38.6268 |  |  | 31.853 |  |  | 23.9267 |  |  | 16.2233 |  |  | 9.0017 |  |  | 2.4819
[13 empty] | C Non choked w/ reducers | 7 |  | 0.44425 |  |  | 8.3674 |  |  | 20.8931 |  |  | 41.9798 |  |  | 76.3245 |  |  | 134.2245 |  |  | 268.613 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.3572 |  |  | 6.8239 |  |  | 17.2334 |  |  | 34.9349 |  |  | 62.9885 |  |  | 104.5513 |  |  | 166.8038 |  |  | 262.2549 |  |  | 465.2307 |  |  | 1350.5935
[13 empty] | Selected C this iteration |  |  | 0.44425 |  |  | 8.3674 |  |  | 20.8931 |  |  | 41.9798 |  |  | 76.3245 |  |  | 134.2245 |  |  | 268.613 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2857 | 2.5229 |  | 3.2326 | 47.4198 |  | 2.1069 | 117.2749 |  | 2.5798 | 228.4216 |  | 15.3245 | 383.2203 |  | 46.0245 | 564.9137 |  | 147.613 | 753.8796 |  | 5500 | 919.8764 |  | 5500 | 1067.9479 |  | 5500 | 1215.4243
[13 empty] | Next iteration flow rate |  |  | 2.5734 | Abs Value of | Flow this | 47.894 | Abs Value of | Flow this | 118.4477 | Abs Value of | Flow this | 230.7058 | Abs Value of | Flow this | 387.0526 | Abs Value of | Flow this | 570.5629 | Abs Value of | Flow this | 761.4184 | Abs Value of | Flow this | 929.0751 | Abs Value of | Flow this | 1078.6274 | Abs Value of | Flow this | 1227.5786 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8387 |  |  | 56.4423 |  |  | 55.1186 |  |  | 51.8567 |  |  | 45.9218 |  |  | 37.3363 |  |  | 27.7645 |  |  | 17.6241 |  |  | 6.0229
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6723 |  |  | 24.7515 |  |  | 25.0163 |  |  | 25.6687 |  |  | 26.8556 |  |  | 28.5727 |  |  | 30.4871 |  |  | 32.5152 |  |  | 34.8354
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1664 |  |  | 31.6908 |  |  | 30.1023 |  |  | 26.1881 |  |  | 19.0662 |  |  | 8.7636 |  |  | -2.7226 |  |  | -14.8911 |  |  | -28.8125
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3641 |  |  | 46.5883 |  |  | 43.5006 |  |  | 38.552 |  |  | 31.702 |  |  | 23.6791 |  |  | 15.8893 |  |  | 8.6136 |  |  | 2.104
[13 empty] | C Non choked w/ reducers | 7 |  | 0.45314 |  |  | 8.4513 |  |  | 21.1057 |  |  | 42.4295 |  |  | 77.2636 |  |  | 136.4878 |  |  | 278.373 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.36435 |  |  | 6.8923 |  |  | 17.4072 |  |  | 35.2956 |  |  | 63.68 |  |  | 105.848 |  |  | 169.3504 |  |  | 267.6471 |  |  | 480.3514 |  |  | 1481.5537
[13 empty] | Selected C this iteration |  |  | 0.45314 |  |  | 8.4513 |  |  | 21.1057 |  |  | 42.4295 |  |  | 77.2636 |  |  | 136.4878 |  |  | 278.373 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2769 | 2.5734 |  | 3.1487 | 47.894 |  | 1.8943 | 118.4477 |  | 3.0295 | 230.7058 |  | 16.2636 | 387.0526 |  | 48.2878 | 570.5629 |  | 157.373 | 761.4184 |  | 5500 | 929.0751 |  | 5500 | 1078.6274 |  | 5500 | 1227.5786
[13 empty] | Next iteration flow rate |  |  | 2.6248 | Abs Value of | Flow this | 48.373 | Abs Value of | Flow this | 119.6321 | Abs Value of | Flow this | 233.0129 | Abs Value of | Flow this | 390.9231 | Abs Value of | Flow this | 576.2685 | Abs Value of | Flow this | 769.0326 | Abs Value of | Flow this | 938.3659 | Abs Value of | Flow this | 1089.4136 | Abs Value of | Flow this | 1239.8543 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8371 |  |  | 56.4328 |  |  | 55.0825 |  |  | 51.755 |  |  | 45.7008 |  |  | 36.9428 |  |  | 27.1785 |  |  | 16.8343 |  |  | 4.9999
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6726 |  |  | 24.7534 |  |  | 25.0235 |  |  | 25.689 |  |  | 26.8998 |  |  | 28.6514 |  |  | 30.6043 |  |  | 32.6731 |  |  | 35.04
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1645 |  |  | 31.6794 |  |  | 30.059 |  |  | 26.066 |  |  | 18.801 |  |  | 8.2913 |  |  | -3.4258 |  |  | -15.8388 |  |  | -30.0401
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8985 |  |  | 48.3628 |  |  | 46.5804 |  |  | 43.4718 |  |  | 38.4758 |  |  | 31.5479 |  |  | 23.4265 |  |  | 15.5486 |  |  | 8.2177 |  |  | 1.7185
[13 empty] | C Non choked w/ reducers | 7 |  | 0.4622 |  |  | 8.536 |  |  | 21.3206 |  |  | 42.8847 |  |  | 78.2187 |  |  | 138.8215 |  |  | 289.053 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.37163 |  |  | 6.9613 |  |  | 17.5827 |  |  | 35.6604 |  |  | 64.3805 |  |  | 107.1671 |  |  | 171.9634 |  |  | 273.2694 |  |  | 496.7033 |  |  | 1655.7297
[13 empty] | Selected C this iteration |  |  | 0.4622 |  |  | 8.536 |  |  | 21.3206 |  |  | 42.8847 |  |  | 78.2187 |  |  | 138.8215 |  |  | 289.053 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2678 | 2.6248 |  | 3.064 | 48.373 |  | 1.6794 | 119.6321 |  | 3.4847 | 233.0129 |  | 17.2187 | 390.9231 |  | 50.6215 | 576.2685 |  | 168.053 | 769.0326 |  | 5500 | 938.3659 |  | 5500 | 1089.4136 |  | 5500 | 1239.8543
[13 empty] | Next iteration flow rate |  |  | 2.6773 | Abs Value of | Flow this | 48.8567 | Abs Value of | Flow this | 120.8284 | Abs Value of | Flow this | 235.343 | Abs Value of | Flow this | 394.8323 | Abs Value of | Flow this | 582.0312 | Abs Value of | Flow this | 776.7229 | Abs Value of | Flow this | 947.7495 | Abs Value of | Flow this | 1100.3078 | Abs Value of | Flow this | 1252.2529 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8355 |  |  | 56.4231 |  |  | 55.0456 |  |  | 51.6513 |  |  | 45.4754 |  |  | 36.5413 |  |  | 26.5808 |  |  | 16.0287 |  |  | 3.9564
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6729 |  |  | 24.7554 |  |  | 25.0309 |  |  | 25.7097 |  |  | 26.9449 |  |  | 28.7317 |  |  | 30.7238 |  |  | 32.8343 |  |  | 35.2487
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1626 |  |  | 31.6677 |  |  | 30.0147 |  |  | 25.9415 |  |  | 18.5305 |  |  | 7.8096 |  |  | -4.143 |  |  | -16.8056 |  |  | -31.2923
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8984 |  |  | 48.3614 |  |  | 46.5723 |  |  | 43.4425 |  |  | 38.398 |  |  | 31.3908 |  |  | 23.1689 |  |  | 15.201 |  |  | 7.8139 |  |  | 1.3252
[13 empty] | C Non choked w/ reducers | 7 |  | 0.47145 |  |  | 8.6216 |  |  | 21.5378 |  |  | 43.3455 |  |  | 79.1902 |  |  | 141.2294 |  |  | 300.8135 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.37907 |  |  | 7.031 |  |  | 17.7601 |  |  | 36.0291 |  |  | 65.0902 |  |  | 108.5094 |  |  | 174.6461 |  |  | 279.1398 |  |  | 514.4706 |  |  | 1904.3228
[13 empty] | Selected C this iteration |  |  | 0.47145 |  |  | 8.6216 |  |  | 21.5378 |  |  | 43.3455 |  |  | 79.1902 |  |  | 141.2294 |  |  | 300.8135 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2586 | 2.6773 |  | 2.9784 | 48.8567 |  | 1.4622 | 120.8284 |  | 3.9455 | 235.343 |  | 18.1902 | 394.8323 |  | 53.0294 | 582.0312 |  | 179.8135 | 776.7229 |  | 5500 | 947.7495 |  | 5500 | 1100.3078 |  | 5500 | 1252.2529
[13 empty] | Next iteration flow rate |  |  | 2.7309 | Abs Value of | Flow this | 49.3453 | Abs Value of | Flow this | 122.0367 | Abs Value of | Flow this | 237.6964 | Abs Value of | Flow this | 398.7806 | Abs Value of | Flow this | 587.8515 | Abs Value of | Flow this | 784.4901 | Abs Value of | Flow this | 957.227 | Abs Value of | Flow this | 1111.3109 | Abs Value of | Flow this | 1264.7754 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8339 |  |  | 56.4132 |  |  | 55.008 |  |  | 51.5455 |  |  | 45.2454 |  |  | 36.1318 |  |  | 25.9711 |  |  | 15.2069 |  |  | 2.8919
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6732 |  |  | 24.7574 |  |  | 25.0384 |  |  | 25.7309 |  |  | 26.9909 |  |  | 28.8136 |  |  | 30.8458 |  |  | 32.9986 |  |  | 35.4616
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1607 |  |  | 31.6558 |  |  | 29.9696 |  |  | 25.8145 |  |  | 18.2545 |  |  | 7.3181 |  |  | -4.8747 |  |  | -17.7918 |  |  | -32.5697
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8984 |  |  | 48.36 |  |  | 46.5641 |  |  | 43.4126 |  |  | 38.3186 |  |  | 31.2305 |  |  | 22.906 |  |  | 14.8464 |  |  | 7.402 |  |  | 0.92402
[13 empty] | C Non choked w/ reducers | 7 |  | 0.48087 |  |  | 8.7081 |  |  | 21.7573 |  |  | 43.8119 |  |  | 80.1786 |  |  | 143.7158 |  |  | 313.8572 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.38665 |  |  | 7.1014 |  |  | 17.9393 |  |  | 36.402 |  |  | 65.8091 |  |  | 109.8753 |  |  | 177.4017 |  |  | 285.2779 |  |  | 533.879 |  |  | 2303.349
[13 empty] | Selected C this iteration |  |  | 0.48087 |  |  | 8.7081 |  |  | 21.7573 |  |  | 43.8119 |  |  | 80.1786 |  |  | 143.7158 |  |  | 313.8572 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2491 | 2.7309 |  | 2.8919 | 49.3453 |  | 1.2427 | 122.0367 |  | 4.4119 | 237.6964 |  | 19.1786 | 398.7806 |  | 55.5158 | 587.8515 |  | 192.8572 | 784.4901 |  | 5500 | 957.227 |  | 5500 | 1111.3109 |  | 5500 | 1264.7754
[13 empty] | Next iteration flow rate |  |  | 2.7855 | Abs Value of | Flow this | 49.8387 | Abs Value of | Flow this | 123.2571 | Abs Value of | Flow this | 240.0734 | Abs Value of | Flow this | 402.7684 | Abs Value of | Flow this | 593.73 | Abs Value of | Flow this | 792.335 | Abs Value of | Flow this | 966.7993 | Abs Value of | Flow this | 1122.424 | Abs Value of | Flow this | 1277.4232 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8323 |  |  | 56.4031 |  |  | 54.9697 |  |  | 51.4375 |  |  | 45.0109 |  |  | 35.714 |  |  | 25.3491 |  |  | 14.3685 |  |  | 1.806
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6735 |  |  | 24.7594 |  |  | 25.0461 |  |  | 25.7525 |  |  | 27.0378 |  |  | 28.8972 |  |  | 30.9702 |  |  | 33.1663 |  |  | 35.6788
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1587 |  |  | 31.6437 |  |  | 29.9236 |  |  | 25.685 |  |  | 17.973 |  |  | 6.8168 |  |  | -5.6211 |  |  | -18.7978 |  |  | -33.8727
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8984 |  |  | 48.3586 |  |  | 46.5556 |  |  | 43.3821 |  |  | 38.2377 |  |  | 31.067 |  |  | 22.6379 |  |  | 14.4847 |  |  | 6.9817 |  |  | 0.51479
[13 empty] | C Non choked w/ reducers | 7 |  | 0.49049 |  |  | 8.7955 |  |  | 21.979 |  |  | 44.284 |  |  | 81.1844 |  |  | 146.2852 |  |  | 328.4452 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.39438 |  |  | 7.1725 |  |  | 18.1203 |  |  | 36.7789 |  |  | 66.5375 |  |  | 111.2657 |  |  | 180.2336 |  |  | 291.7059 |  |  | 555.2085 |  |  | 3116.7844
[13 empty] | Selected C this iteration |  |  | 0.49049 |  |  | 8.7955 |  |  | 21.979 |  |  | 44.284 |  |  | 81.1844 |  |  | 146.2852 |  |  | 328.4452 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2395 | 2.7855 |  | 2.8045 | 49.8387 |  | 1.021 | 123.2571 |  | 4.884 | 240.0734 |  | 20.1844 | 402.7684 |  | 58.0852 | 593.73 |  | 207.4452 | 792.335 |  | 5500 | 966.7993 |  | 5500 | 1122.424 |  | 5500 | 1277.4232
[13 empty] | Next iteration flow rate |  |  | 2.8412 | Abs Value of | Flow this | 50.3371 | Abs Value of | Flow this | 124.4897 | Abs Value of | Flow this | 242.4741 | Abs Value of | Flow this | 406.7961 | Abs Value of | Flow this | 599.6673 | Abs Value of | Flow this | 800.2584 | Abs Value of | Flow this | 976.4673 | Abs Value of | Flow this | 1133.6482 | Abs Value of | Flow this | 1290.1974 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8306 |  |  | 56.3927 |  |  | 54.9305 |  |  | 51.3274 |  |  | 44.7716 |  |  | 35.2879 |  |  | 24.7146 |  |  | 13.5133 |  |  | 0.69833
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6739 |  |  | 24.7615 |  |  | 25.0539 |  |  | 25.7745 |  |  | 27.0857 |  |  | 28.9824 |  |  | 31.0971 |  |  | 33.3373 |  |  | 35.9003
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.1567 |  |  | 31.6313 |  |  | 29.8766 |  |  | 25.5529 |  |  | 17.6859 |  |  | 6.3054 |  |  | -6.3825 |  |  | -19.824 |  |  | -35.202
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8984 |  |  | 48.3571 |  |  | 46.5471 |  |  | 43.3509 |  |  | 38.1551 |  |  | 30.9002 |  |  | 22.3644 |  |  | 14.1158 |  |  | 6.553 |  |  | 0.097335
[13 empty] | C Non choked w/ reducers | 7 |  | 0.5003 |  |  | 8.8837 |  |  | 22.2032 |  |  | 44.762 |  |  | 82.208 |  |  | 148.9427 |  |  | 344.9197 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.40227 |  |  | 7.2444 |  |  | 18.3032 |  |  | 37.16 |  |  | 67.2755 |  |  | 112.6813 |  |  | 183.1456 |  |  | 298.4486 |  |  | 578.8115 |  |  | 7239.5203
[13 empty] | Selected C this iteration |  |  | 0.5003 |  |  | 8.8837 |  |  | 22.2032 |  |  | 44.762 |  |  | 82.208 |  |  | 148.9427 |  |  | 344.9197 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2297 | 2.8412 |  | 2.7163 | 50.3371 |  | 0.79682 | 124.4897 |  | 5.362 | 242.4741 |  | 21.208 | 406.7961 |  | 60.7427 | 599.6673 |  | 223.9197 | 800.2584 |  | 5500 | 976.4673 |  | 5500 | 1133.6482 |  | 5500 | 1290.1974
[13 empty] | Next iteration flow rate |  |  | 2.898 | Abs Value of | Flow this | 50.8405 | Abs Value of | Flow this | 125.7346 | Abs Value of | Flow this | 244.8988 | Abs Value of | Flow this | 410.8641 | Abs Value of | Flow this | 605.664 | Abs Value of | Flow this | 808.2609 | Abs Value of | Flow this | 986.232 | Abs Value of | Flow this | 1144.9847 | Abs Value of | Flow this | 1303.0994 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8288 |  |  | 56.3822 |  |  | 54.8906 |  |  | 51.2151 |  |  | 44.5275 |  |  | 34.8531 |  |  | 24.0673 |  |  | 12.6409 |  |  | -0.43164
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6742 |  |  | 24.7636 |  |  | 25.0619 |  |  | 25.797 |  |  | 27.1345 |  |  | 29.0694 |  |  | 31.2265 |  |  | 33.5118 |  |  | 36.1263
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.1546 |  |  | 31.6187 |  |  | 29.8288 |  |  | 25.4181 |  |  | 17.393 |  |  | 5.7838 |  |  | -7.1592 |  |  | -20.8709 |  |  | -36.558
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8984 |  |  | 48.3557 |  |  | 46.5383 |  |  | 43.3192 |  |  | 38.0709 |  |  | 30.7301 |  |  | 22.0854 |  |  | 13.7394 |  |  | 6.1157 |  |  | -0.32851
[13 empty] | C Non choked w/ reducers | 7 |  | 0.51031 |  |  | 8.9728 |  |  | 22.4297 |  |  | 45.2459 |  |  | 83.2499 |  |  | 151.6936 |  |  | 363.7406 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.41031 |  |  | 7.3169 |  |  | 18.488 |  |  | 37.5454 |  |  | 68.0234 |  |  | 114.1227 |  |  | 186.1418 |  |  | 305.534 |  |  | 605.1392 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.51031 |  |  | 8.9728 |  |  | 22.4297 |  |  | 45.2459 |  |  | 83.2499 |  |  | 151.6936 |  |  | 363.7406 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2197 | 2.898 |  | 2.6272 | 50.8405 |  | 0.57031 | 125.7346 |  | 5.8459 | 244.8988 |  | 22.2499 | 410.8641 |  | 63.4936 | 605.664 |  | 242.7406 | 808.2609 |  | 5500 | 986.232 |  | 5500 | 1144.9847 |  | 5500 | 1303.0994
[13 empty] | Next iteration flow rate |  |  | 2.956 | Abs Value of | Flow this | 51.3489 | Abs Value of | Flow this | 126.9919 | Abs Value of | Flow this | 247.3478 | Abs Value of | Flow this | 414.9727 | Abs Value of | Flow this | 611.7206 | Abs Value of | Flow this | 816.3436 | Abs Value of | Flow this | 996.0943 | Abs Value of | Flow this | 1156.4345 | Abs Value of | Flow this | 1316.1304 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8271 |  |  | 56.3715 |  |  | 54.8499 |  |  | 51.1005 |  |  | 44.2784 |  |  | 34.4097 |  |  | 23.4071 |  |  | 11.751 |  |  | -1.5843
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6746 |  |  | 24.7657 |  |  | 25.07 |  |  | 25.8199 |  |  | 27.1843 |  |  | 29.1581 |  |  | 31.3586 |  |  | 33.6898 |  |  | 36.3569
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.1525 |  |  | 31.6058 |  |  | 29.7799 |  |  | 25.2806 |  |  | 17.0941 |  |  | 5.2516 |  |  | -7.9515 |  |  | -21.9388 |  |  | -37.9412
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8984 |  |  | 48.3542 |  |  | 46.5294 |  |  | 43.2868 |  |  | 37.985 |  |  | 30.5565 |  |  | 21.8008 |  |  | 13.3554 |  |  | 5.6697 |  |  | -0.76292
[13 empty] | C Non choked w/ reducers | 7 |  | 0.52051 |  |  | 9.0629 |  |  | 22.6586 |  |  | 45.7358 |  |  | 84.3108 |  |  | 154.5438 |  |  | 385.5426 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.41852 |  |  | 7.3902 |  |  | 18.6747 |  |  | 37.935 |  |  | 68.7813 |  |  | 115.5909 |  |  | 189.2264 |  |  | 312.9936 |  |  | 634.7793 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.52051 |  |  | 9.0629 |  |  | 22.6586 |  |  | 45.7358 |  |  | 84.3108 |  |  | 154.5438 |  |  | 385.5426 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2095 | 2.956 |  | 2.5371 | 51.3489 |  | 0.3414 | 126.9919 |  | 6.3358 | 247.3478 |  | 23.3108 | 414.9727 |  | 66.3438 | 611.7206 |  | 264.5426 | 816.3436 |  | 5500 | 996.0943 |  | 5500 | 1156.4345 |  | 5500 | 1316.1304
[13 empty] | Next iteration flow rate |  |  | 3.0151 | Abs Value of | Flow this | 51.8624 | Abs Value of | Flow this | 128.2618 | Abs Value of | Flow this | 249.8213 | Abs Value of | Flow this | 419.1225 | Abs Value of | Flow this | 617.8378 | Abs Value of | Flow this | 824.507 | Abs Value of | Flow this | 1006.0552 | Abs Value of | Flow this | 1167.9989 | Abs Value of | Flow this | 1329.2917 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8253 |  |  | 56.3606 |  |  | 54.8084 |  |  | 50.9836 |  |  | 44.0244 |  |  | 33.9573 |  |  | 22.7335 |  |  | 10.8431 |  |  | -2.7602
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6749 |  |  | 24.7679 |  |  | 25.0783 |  |  | 25.8433 |  |  | 27.2351 |  |  | 29.2485 |  |  | 31.4933 |  |  | 33.8714 |  |  | 36.592
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.1504 |  |  | 31.5927 |  |  | 29.7301 |  |  | 25.1403 |  |  | 16.7893 |  |  | 4.7087 |  |  | -8.7598 |  |  | -23.0282 |  |  | -39.3522
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8984 |  |  | 48.3526 |  |  | 46.5203 |  |  | 43.2538 |  |  | 37.8973 |  |  | 30.3794 |  |  | 21.5105 |  |  | 12.9638 |  |  | 5.2146 |  |  | -1.2061
[13 empty] | C Non choked w/ reducers | 7 |  | 0.53092 |  |  | 9.1538 |  |  | 22.8899 |  |  | 46.2319 |  |  | 85.3911 |  |  | 157.4999 |  |  | 411.2322 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.42689 |  |  | 7.4642 |  |  | 18.8633 |  |  | 38.329 |  |  | 69.5494 |  |  | 117.0865 |  |  | 192.4041 |  |  | 320.8634 |  |  | 668.5159 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.53092 |  |  | 9.1538 |  |  | 22.8899 |  |  | 46.2319 |  |  | 85.3911 |  |  | 157.4999 |  |  | 411.2322 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1991 | 3.0151 |  | 2.4462 | 51.8624 |  | 0.11006 | 128.2618 |  | 6.8319 | 249.8213 |  | 24.3911 | 419.1225 |  | 69.2999 | 617.8378 |  | 290.2322 | 824.507 |  | 5500 | 1006.0552 |  | 5500 | 1167.9989 |  | 5500 | 1329.2917
[13 empty] | Next iteration flow rate |  |  | 3.0754 | Abs Value of | Flow this | 52.381 | Abs Value of | Flow this | 129.5445 | Abs Value of | Flow this | 252.3195 | Abs Value of | Flow this | 423.3137 | Abs Value of | Flow this | 624.0162 | Abs Value of | Flow this | 832.7521 | Abs Value of | Flow this | 1016.1158 | Abs Value of | Flow this | 1179.6789 | Abs Value of | Flow this | 1342.5846 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8235 |  |  | 56.3494 |  |  | 54.766 |  |  | 50.8643 |  |  | 43.7653 |  |  | 33.4958 |  |  | 22.0465 |  |  | 9.9171 |  |  | -3.9597
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6753 |  |  | 24.7701 |  |  | 25.0868 |  |  | 25.8671 |  |  | 27.2869 |  |  | 29.3408 |  |  | 31.6307 |  |  | 34.0566 |  |  | 36.8319
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.1482 |  |  | 31.5793 |  |  | 29.6792 |  |  | 24.9972 |  |  | 16.4784 |  |  | 4.155 |  |  | -9.5842 |  |  | -24.1395 |  |  | -40.7916
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8984 |  |  | 48.3511 |  |  | 46.511 |  |  | 43.22 |  |  | 37.8079 |  |  | 30.1988 |  |  | 21.2143 |  |  | 12.5642 |  |  | 4.7504 |  |  | -1.6581
[13 empty] | C Non choked w/ reducers | 7 |  | 0.54154 |  |  | 9.2456 |  |  | 23.1237 |  |  | 46.7342 |  |  | 86.4915 |  |  | 160.5687 |  |  | 442.1572 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.43543 |  |  | 7.539 |  |  | 19.0538 |  |  | 38.7274 |  |  | 70.3279 |  |  | 118.6105 |  |  | 195.6799 |  |  | 329.1843 |  |  | 707.4216 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.54154 |  |  | 9.2456 |  |  | 23.1237 |  |  | 46.7342 |  |  | 86.4915 |  |  | 160.5687 |  |  | 442.1572 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1885 | 3.0754 |  | 2.3544 | 52.381 |  | 0.12374 | 129.5445 |  | 7.3342 | 252.3195 |  | 25.4915 | 423.3137 |  | 72.3687 | 624.0162 |  | 321.1572 | 832.7521 |  | 5500 | 1016.1158 |  | 5500 | 1179.6789 |  | 5500 | 1342.5846
[13 empty] | Next iteration flow rate |  |  | 3.1369 | Abs Value of | Flow this | 52.9048 | Abs Value of | Flow this | 130.8399 | Abs Value of | Flow this | 254.8427 | Abs Value of | Flow this | 427.5468 | Abs Value of | Flow this | 630.2564 | Abs Value of | Flow this | 841.0796 | Abs Value of | Flow this | 1026.2769 | Abs Value of | Flow this | 1191.4757 | Abs Value of | Flow this | 1356.0104 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8216 |  |  | 56.338 |  |  | 54.7228 |  |  | 50.7427 |  |  | 43.501 |  |  | 33.0251 |  |  | 21.3456 |  |  | 8.9724 |  |  | -5.1833
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6757 |  |  | 24.7724 |  |  | 25.0954 |  |  | 25.8915 |  |  | 27.3398 |  |  | 29.435 |  |  | 31.7709 |  |  | 34.2455 |  |  | 37.0767
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.1459 |  |  | 31.5656 |  |  | 29.6274 |  |  | 24.8512 |  |  | 16.1612 |  |  | 3.5901 |  |  | -10.4253 |  |  | -25.2731 |  |  | -42.26
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8984 |  |  | 48.3495 |  |  | 46.5015 |  |  | 43.1857 |  |  | 37.7167 |  |  | 30.0146 |  |  | 20.9122 |  |  | 12.1567 |  |  | 4.2769 |  |  | -2.1192
[13 empty] | C Non choked w/ reducers | 7 |  | 0.55237 |  |  | 9.3384 |  |  | 23.36 |  |  | 47.2428 |  |  | 87.6126 |  |  | 163.7582 |  |  | 480.4304 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.44414 |  |  | 7.6145 |  |  | 19.2463 |  |  | 39.1302 |  |  | 71.117 |  |  | 120.1637 |  |  | 199.0592 |  |  | 338.0035 |  |  | 753.0114 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.55237 |  |  | 9.3384 |  |  | 23.36 |  |  | 47.2428 |  |  | 87.6126 |  |  | 163.7582 |  |  | 480.4304 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1776 | 3.1369 |  | 2.2616 | 52.9048 |  | 0.36004 | 130.8399 |  | 7.8428 | 254.8427 |  | 26.6126 | 427.5468 |  | 75.5582 | 630.2564 |  | 359.4304 | 841.0796 |  | 5500 | 1026.2769 |  | 5500 | 1191.4757 |  | 5500 | 1356.0104
[13 empty] | Next iteration flow rate |  |  | 3.1996 | Abs Value of | Flow this | 53.4339 | Abs Value of | Flow this | 132.1483 | Abs Value of | Flow this | 257.3912 | Abs Value of | Flow this | 431.8223 | Abs Value of | Flow this | 636.5589 | Abs Value of | Flow this | 849.4904 | Abs Value of | Flow this | 1036.5397 | Abs Value of | Flow this | 1203.3904 | Abs Value of | Flow this | 1369.5705 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8197 |  |  | 56.3264 |  |  | 54.6787 |  |  | 50.6186 |  |  | 43.2313 |  |  | 32.5449 |  |  | 20.6306 |  |  | 8.0087 |  |  | -6.4315
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6761 |  |  | 24.7747 |  |  | 25.1043 |  |  | 25.9163 |  |  | 27.3937 |  |  | 29.531 |  |  | 31.9139 |  |  | 34.4383 |  |  | 37.3263
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.1437 |  |  | 31.5516 |  |  | 29.5745 |  |  | 24.7023 |  |  | 15.8376 |  |  | 3.0138 |  |  | -11.2833 |  |  | -26.4295 |  |  | -43.7578
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8984 |  |  | 48.3478 |  |  | 46.4918 |  |  | 43.1506 |  |  | 37.6237 |  |  | 29.8266 |  |  | 20.604 |  |  | 11.7409 |  |  | 3.7938 |  |  | -2.5896
[13 empty] | C Non choked w/ reducers | 7 |  | 0.56342 |  |  | 9.4321 |  |  | 23.5989 |  |  | 47.7579 |  |  | 88.7551 |  |  | 167.0768 |  |  | 529.5961 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.45302 |  |  | 7.6908 |  |  | 19.4408 |  |  | 39.5376 |  |  | 71.917 |  |  | 121.7471 |  |  | 202.5478 |  |  | 347.3754 |  |  | 807.5086 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.56342 |  |  | 9.4321 |  |  | 23.5989 |  |  | 47.7579 |  |  | 88.7551 |  |  | 167.0768 |  |  | 529.5961 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1666 | 3.1996 |  | 2.1679 | 53.4339 |  | 0.59885 | 132.1483 |  | 8.3579 | 257.3912 |  | 27.7551 | 431.8223 |  | 78.8768 | 636.5589 |  | 408.5961 | 849.4904 |  | 5500 | 1036.5397 |  | 5500 | 1203.3904 |  | 5500 | 1369.5705
[13 empty] | Next iteration flow rate |  |  | 3.2636 | Abs Value of | Flow this | 53.9682 | Abs Value of | Flow this | 133.4698 | Abs Value of | Flow this | 259.9651 | Abs Value of | Flow this | 436.1405 | Abs Value of | Flow this | 642.9245 | Abs Value of | Flow this | 857.9853 | Abs Value of | Flow this | 1046.9051 | Abs Value of | Flow this | 1215.4243 | Abs Value of | Flow this | 1383.2662 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8178 |  |  | 56.3145 |  |  | 54.6337 |  |  | 50.492 |  |  | 42.9563 |  |  | 32.055 |  |  | 19.9013 |  |  | 7.0257 |  |  | -7.7048
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6764 |  |  | 24.7771 |  |  | 25.1133 |  |  | 25.9416 |  |  | 27.4487 |  |  | 29.629 |  |  | 32.0597 |  |  | 34.6349 |  |  | 37.581
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2589 |  |  | 32.1413 |  |  | 31.5374 |  |  | 29.5205 |  |  | 24.5504 |  |  | 15.5075 |  |  | 2.426 |  |  | -12.1585 |  |  | -27.6092 |  |  | -45.2857
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8983 |  |  | 48.3462 |  |  | 46.482 |  |  | 43.1148 |  |  | 37.5288 |  |  | 29.6349 |  |  | 20.2896 |  |  | 11.3168 |  |  | 3.3011 |  |  | -3.0695
[13 empty] | C Non choked w/ reducers | 7 |  | 0.57469 |  |  | 9.5268 |  |  | 23.8402 |  |  | 48.2795 |  |  | 89.9195 |  |  | 170.534 |  |  | 596.1846 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.46208 |  |  | 7.7678 |  |  | 19.6373 |  |  | 39.9495 |  |  | 72.7279 |  |  | 123.3617 |  |  | 206.1521 |  |  | 357.3629 |  |  | 874.3386 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.57469 |  |  | 9.5268 |  |  | 23.8402 |  |  | 48.2795 |  |  | 89.9195 |  |  | 170.534 |  |  | 596.1846 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1553 | 3.2636 |  | 2.0732 | 53.9682 |  | 0.84022 | 133.4698 |  | 8.8795 | 259.9651 |  | 28.9195 | 436.1405 |  | 82.334 | 642.9245 |  | 475.1846 | 857.9853 |  | 5500 | 1046.9051 |  | 5500 | 1215.4243 |  | 5500 | 1383.2662
[13 empty] | Next iteration flow rate |  |  | 3.3289 | Abs Value of | Flow this | 54.5079 | Abs Value of | Flow this | 134.8045 | Abs Value of | Flow this | 262.5647 | Abs Value of | Flow this | 440.5019 | Abs Value of | Flow this | 649.3538 | Abs Value of | Flow this | 866.5651 | Abs Value of | Flow this | 1057.3741 | Abs Value of | Flow this | 1227.5786 | Abs Value of | Flow this | 1397.0989 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8158 |  |  | 56.3024 |  |  | 54.5879 |  |  | 50.3629 |  |  | 42.6757 |  |  | 31.5553 |  |  | 19.1573 |  |  | 6.0229 |  |  | -9.0037
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6768 |  |  | 24.7795 |  |  | 25.1224 |  |  | 25.9674 |  |  | 27.5049 |  |  | 29.7289 |  |  | 32.2085 |  |  | 34.8354 |  |  | 37.8407
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2589 |  |  | 32.139 |  |  | 31.5229 |  |  | 29.4654 |  |  | 24.3955 |  |  | 15.1708 |  |  | 1.8263 |  |  | -13.0513 |  |  | -28.8125 |  |  | -46.8444
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8983 |  |  | 48.3445 |  |  | 46.4719 |  |  | 43.0783 |  |  | 37.432 |  |  | 29.4393 |  |  | 19.9689 |  |  | 10.8842 |  |  | 2.7984 |  |  | -3.559
[13 empty] | C Non choked w/ reducers | 7 |  | 0.58618 |  |  | 9.6224 |  |  | 24.0842 |  |  | 48.8079 |  |  | 91.1067 |  |  | 174.1403 |  |  | 693.9944 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.47132 |  |  | 7.8456 |  |  | 19.8358 |  |  | 40.3661 |  |  | 73.5501 |  |  | 125.0085 |  |  | 209.8789 |  |  | 368.0402 |  |  | 959.1187 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.58618 |  |  | 9.6224 |  |  | 24.0842 |  |  | 48.8079 |  |  | 91.1067 |  |  | 174.1403 |  |  | 693.9944 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1438 | 3.3289 |  | 1.9776 | 54.5079 |  | 1.0842 | 134.8045 |  | 9.4079 | 262.5647 |  | 30.1067 | 440.5019 |  | 85.9403 | 649.3538 |  | 572.9944 | 866.5651 |  | 5500 | 1057.3741 |  | 5500 | 1227.5786 |  | 5500 | 1397.0989
[13 empty] | Next iteration flow rate |  |  | 3.3955 | Abs Value of | Flow this | 55.053 | Abs Value of | Flow this | 136.1525 | Abs Value of | Flow this | 265.1904 | Abs Value of | Flow this | 444.9069 | Abs Value of | Flow this | 655.8473 | Abs Value of | Flow this | 875.2308 | Abs Value of | Flow this | 1067.9479 | Abs Value of | Flow this | 1239.8543 | Abs Value of | Flow this | 1411.0699 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8138 |  |  | 56.2901 |  |  | 54.5411 |  |  | 50.2312 |  |  | 42.3894 |  |  | 31.0455 |  |  | 18.3983 |  |  | 4.9999 |  |  | -10.3286
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6772 |  |  | 24.782 |  |  | 25.1318 |  |  | 25.9938 |  |  | 27.5621 |  |  | 29.8309 |  |  | 32.3603 |  |  | 35.04 |  |  | 38.1057
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2589 |  |  | 32.1365 |  |  | 31.5081 |  |  | 29.4093 |  |  | 24.2374 |  |  | 14.8273 |  |  | 1.2146 |  |  | -13.962 |  |  | -30.0401 |  |  | -48.4344
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8983 |  |  | 48.3428 |  |  | 46.4617 |  |  | 43.0411 |  |  | 37.3332 |  |  | 29.2398 |  |  | 19.6418 |  |  | 10.4428 |  |  | 2.2857 |  |  | -4.0583
[13 empty] | C Non choked w/ reducers | 7 |  | 0.59791 |  |  | 9.719 |  |  | 24.3307 |  |  | 49.343 |  |  | 92.3173 |  |  | 177.9072 |  |  | 859.4988 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.48075 |  |  | 7.9242 |  |  | 20.0364 |  |  | 40.7874 |  |  | 74.3838 |  |  | 126.6886 |  |  | 213.7357 |  |  | 379.4941 |  |  | 1071.8756 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.59791 |  |  | 9.719 |  |  | 24.3307 |  |  | 49.343 |  |  | 92.3173 |  |  | 177.9072 |  |  | 859.4988 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1321 | 3.3955 |  | 1.881 | 55.053 |  | 1.3307 | 136.1525 |  | 9.943 | 265.1904 |  | 31.3173 | 444.9069 |  | 89.7072 | 655.8473 |  | 738.4988 | 875.2308 |  | 5500 | 1067.9479 |  | 5500 | 1239.8543 |  | 5500 | 1411.0699
[13 empty] | Next iteration flow rate |  |  | 3.4634 | Abs Value of | Flow this | 55.6035 | Abs Value of | Flow this | 137.514 | Abs Value of | Flow this | 267.8423 | Abs Value of | Flow this | 449.356 | Abs Value of | Flow this | 662.4058 | Abs Value of | Flow this | 883.9831 | Abs Value of | Flow this | 1078.6274 | Abs Value of | Flow this | 1252.2529 | Abs Value of | Flow this | 1425.1806 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9157 |  |  | 56.8117 |  |  | 56.2775 |  |  | 54.4933 |  |  | 50.0968 |  |  | 42.0975 |  |  | 30.5255 |  |  | 17.6241 |  |  | 3.9564 |  |  | -11.6803
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6777 |  |  | 24.7845 |  |  | 25.1413 |  |  | 26.0206 |  |  | 27.6205 |  |  | 29.9349 |  |  | 32.5152 |  |  | 35.2487 |  |  | 38.3761
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2589 |  |  | 32.1341 |  |  | 31.493 |  |  | 29.352 |  |  | 24.0762 |  |  | 14.4769 |  |  | 0.59063 |  |  | -14.8911 |  |  | -31.2923 |  |  | -50.0563
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8983 |  |  | 48.341 |  |  | 46.4512 |  |  | 43.0031 |  |  | 37.2324 |  |  | 29.0363 |  |  | 19.3081 |  |  | 9.9926 |  |  | 1.7626 |  |  | -4.5677
[13 empty] | C Non choked w/ reducers | 7 |  | 0.60987 |  |  | 9.8166 |  |  | 24.5799 |  |  | 49.885 |  |  | 93.5522 |  |  | 181.8477 |  |  | 1244.8874 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.49036 |  |  | 8.0036 |  |  | 20.239 |  |  | 41.2135 |  |  | 75.2292 |  |  | 128.4032 |  |  | 217.7307 |  |  | 391.8283 |  |  | 1232.8082 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.60987 |  |  | 9.8166 |  |  | 24.5799 |  |  | 49.885 |  |  | 93.5522 |  |  | 181.8477 |  |  | 1244.8874 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1201 | 3.4634 |  | 1.7834 | 55.6035 |  | 1.5799 | 137.514 |  | 10.485 | 267.8423 |  | 32.5522 | 449.356 |  | 93.6477 | 662.4058 |  | 1123.8874 | 883.9831 |  | 5500 | 1078.6274 |  | 5500 | 1252.2529 |  | 5500 | 1425.1806
[13 empty] | Next iteration flow rate |  |  | 3.5327 | Abs Value of | Flow this | 56.1595 | Abs Value of | Flow this | 138.8892 | Abs Value of | Flow this | 270.5207 | Abs Value of | Flow this | 453.8496 | Abs Value of | Flow this | 669.0298 | Abs Value of | Flow this | 892.8229 | Abs Value of | Flow this | 1089.4136 | Abs Value of | Flow this | 1264.7754 | Abs Value of | Flow this | 1439.4324 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9157 |  |  | 56.8096 |  |  | 56.2647 |  |  | 54.4446 |  |  | 49.9597 |  |  | 41.7996 |  |  | 29.9951 |  |  | 16.8343 |  |  | 2.8919 |  |  | -13.0591
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6781 |  |  | 24.7871 |  |  | 25.1511 |  |  | 26.0481 |  |  | 27.6801 |  |  | 30.041 |  |  | 32.6731 |  |  | 35.4616 |  |  | 38.6518
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2589 |  |  | 32.1316 |  |  | 31.4776 |  |  | 29.2936 |  |  | 23.9117 |  |  | 14.1195 |  |  | -0.045908 |  |  | -15.8388 |  |  | -32.5697 |  |  | -51.7109
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8983 |  |  | 48.3392 |  |  | 46.4405 |  |  | 42.9644 |  |  | 37.1297 |  |  | 28.8287 |  |  | 18.9676 |  |  | 9.5334 |  |  | 1.229 |  |  | -5.0873
[13 empty] | C Non choked w/ reducers | 7 |  | 0.62206 |  |  | 9.9151 |  |  | 24.8318 |  |  | 50.4341 |  |  | 94.8121 |  |  | 185.9764 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.50017 |  |  | 8.0838 |  |  | 20.4437 |  |  | 41.6444 |  |  | 76.0866 |  |  | 130.1533 |  |  | 221.8727 |  |  | 405.1667 |  |  | 1491.1273 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.62206 |  |  | 9.9151 |  |  | 24.8318 |  |  | 50.4341 |  |  | 94.8121 |  |  | 185.9764 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1079 | 3.5327 |  | 1.6849 | 56.1595 |  | 1.8318 | 138.8892 |  | 11.0341 | 270.5207 |  | 33.8121 | 453.8496 |  | 97.7764 | 669.0298 |  | 5500 | 892.8229 |  | 5500 | 1089.4136 |  | 5500 | 1264.7754 |  | 5500 | 1439.4324
[13 empty] | Next iteration flow rate |  |  | 3.6033 | Abs Value of | Flow this | 56.7211 | Abs Value of | Flow this | 140.2781 | Abs Value of | Flow this | 273.2259 | Abs Value of | Flow this | 458.3881 | Abs Value of | Flow this | 675.7201 | Abs Value of | Flow this | 901.7512 | Abs Value of | Flow this | 1100.3078 | Abs Value of | Flow this | 1277.4232 | Abs Value of | Flow this | 1453.8267 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9157 |  |  | 56.8075 |  |  | 56.2516 |  |  | 54.395 |  |  | 49.8199 |  |  | 41.4958 |  |  | 29.454 |  |  | 16.0287 |  |  | 1.806 |  |  | -14.4656
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6785 |  |  | 24.7897 |  |  | 25.161 |  |  | 26.076 |  |  | 27.7408 |  |  | 30.1492 |  |  | 32.8343 |  |  | 35.6788 |  |  | 38.9331
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2588 |  |  | 32.129 |  |  | 31.4619 |  |  | 29.2339 |  |  | 23.7439 |  |  | 13.7549 |  |  | -0.69524 |  |  | -16.8056 |  |  | -33.8727 |  |  | -53.3987
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8983 |  |  | 48.3374 |  |  | 46.4296 |  |  | 42.9248 |  |  | 37.0248 |  |  | 28.6169 |  |  | 18.6204 |  |  | 9.0649 |  |  | 0.68471 |  |  | -5.6174
[13 empty] | C Non choked w/ reducers | 7 |  | 0.63451 |  |  | 10.0147 |  |  | 25.0864 |  |  | 50.9904 |  |  | 96.098 |  |  | 190.3094 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.51017 |  |  | 8.1648 |  |  | 20.6506 |  |  | 42.0802 |  |  | 76.9562 |  |  | 131.9404 |  |  | 226.1714 |  |  | 419.6597 |  |  | 2017.7238 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.63451 |  |  | 10.0147 |  |  | 25.0864 |  |  | 50.9904 |  |  | 96.098 |  |  | 190.3094 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.0955 | 3.6033 |  | 1.5853 | 56.7211 |  | 2.0864 | 140.2781 |  | 11.5904 | 273.2259 |  | 35.098 | 458.3881 |  | 102.1094 | 675.7201 |  | 5500 | 901.7512 |  | 5500 | 1100.3078 |  | 5500 | 1277.4232 |  | 5500 | 1453.8267
[13 empty] | Next iteration flow rate |  |  | 3.6754 | Abs Value of | Flow this | 57.2883 | Abs Value of | Flow this | 141.6809 | Abs Value of | Flow this | 275.9582 | Abs Value of | Flow this | 462.9719 | Abs Value of | Flow this | 682.4773 | Abs Value of | Flow this | 910.7687 | Abs Value of | Flow this | 1111.3109 | Abs Value of | Flow this | 1290.1974 | Abs Value of | Flow this | 1468.365 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9157 |  |  | 56.8053 |  |  | 56.2382 |  |  | 54.3443 |  |  | 49.6773 |  |  | 41.1858 |  |  | 28.902 |  |  | 15.2069 |  |  | 0.69833 |  |  | -15.9003
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6789 |  |  | 24.7924 |  |  | 25.1711 |  |  | 26.1045 |  |  | 27.8028 |  |  | 30.2596 |  |  | 32.9986 |  |  | 35.9003 |  |  | 39.2201
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2588 |  |  | 32.1264 |  |  | 31.4459 |  |  | 29.1731 |  |  | 23.5727 |  |  | 13.383 |  |  | -1.3576 |  |  | -17.7918 |  |  | -35.202 |  |  | -55.1204
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8983 |  |  | 48.3355 |  |  | 46.4185 |  |  | 42.8845 |  |  | 36.9179 |  |  | 28.4008 |  |  | 18.2661 |  |  | 8.587 |  |  | 0.12946 |  |  | -6.1581
[13 empty] | C Non choked w/ reducers | 7 |  | 0.6472 |  |  | 10.1153 |  |  | 25.3437 |  |  | 51.5539 |  |  | 97.4107 |  |  | 194.8652 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.52038 |  |  | 8.2466 |  |  | 20.8596 |  |  | 42.5209 |  |  | 77.8383 |  |  | 133.7657 |  |  | 230.6376 |  |  | 435.4913 |  |  | 4686.6741 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.6472 |  |  | 10.1153 |  |  | 25.3437 |  |  | 51.5539 |  |  | 97.4107 |  |  | 194.8652 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.0828 | 3.6754 |  | 1.4847 | 57.2883 |  | 2.3437 | 141.6809 |  | 12.1539 | 275.9582 |  | 36.4107 | 462.9719 |  | 106.6652 | 682.4773 |  | 5500 | 910.7687 |  | 5500 | 1111.3109 |  | 5500 | 1290.1974 |  | 5500 | 1468.365
[13 empty] | Next iteration flow rate |  |  | 3.7489 | Abs Value of | Flow this | 57.8612 | Abs Value of | Flow this | 143.0977 | Abs Value of | Flow this | 278.7177 | Abs Value of | Flow this | 467.6017 | Abs Value of | Flow this | 689.3021 | Abs Value of | Flow this | 919.8764 | Abs Value of | Flow this | 1122.424 | Abs Value of | Flow this | 1303.0994 | Abs Value of | Flow this | 1483.0486 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9157 |  |  | 56.8031 |  |  | 56.2246 |  |  | 54.2926 |  |  | 49.5318 |  |  | 40.8696 |  |  | 28.3389 |  |  | 14.3685 |  |  | -0.43164 |  |  | -17.3639
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6794 |  |  | 24.7951 |  |  | 25.1815 |  |  | 26.1336 |  |  | 27.8661 |  |  | 30.3722 |  |  | 33.1663 |  |  | 36.1263 |  |  | 39.5128
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2588 |  |  | 32.1237 |  |  | 31.4295 |  |  | 29.1111 |  |  | 23.3981 |  |  | 13.0035 |  |  | -2.0333 |  |  | -18.7978 |  |  | -36.558 |  |  | -56.8767
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8982 |  |  | 48.3336 |  |  | 46.4072 |  |  | 42.8434 |  |  | 36.8088 |  |  | 28.1805 |  |  | 17.9047 |  |  | 8.0995 |  |  | -0.43695 |  |  | -6.7097
[13 empty] | C Non choked w/ reducers | 7 |  | 0.66014 |  |  | 10.2168 |  |  | 25.6038 |  |  | 52.1249 |  |  | 98.7512 |  |  | 199.6645 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.53078 |  |  | 8.3292 |  |  | 21.0708 |  |  | 42.9668 |  |  | 78.7331 |  |  | 135.6306 |  |  | 235.283 |  |  | 452.89 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.66014 |  |  | 10.2168 |  |  | 25.6038 |  |  | 52.1249 |  |  | 98.7512 |  |  | 199.6645 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.0699 | 3.7489 |  | 1.3832 | 57.8612 |  | 2.6038 | 143.0977 |  | 12.7249 | 278.7177 |  | 37.7512 | 467.6017 |  | 111.4645 | 689.3021 |  | 5500 | 919.8764 |  | 5500 | 1122.424 |  | 5500 | 1303.0994 |  | 5500 | 1483.0486
[13 empty] | Next iteration flow rate |  |  | 3.8239 | Abs Value of | Flow this | 58.4398 | Abs Value of | Flow this | 144.5286 | Abs Value of | Flow this | 281.5049 | Abs Value of | Flow this | 472.2777 | Abs Value of | Flow this | 696.1951 | Abs Value of | Flow this | 929.0751 | Abs Value of | Flow this | 1133.6482 | Abs Value of | Flow this | 1316.1304 | Abs Value of | Flow this | 1497.8791 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9156 |  |  | 56.8008 |  |  | 56.2107 |  |  | 54.2399 |  |  | 49.3833 |  |  | 40.5471 |  |  | 27.7645 |  |  | 13.5133 |  |  | -1.5843 |  |  | -18.857
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6798 |  |  | 24.7979 |  |  | 25.192 |  |  | 26.1633 |  |  | 27.9306 |  |  | 30.4871 |  |  | 33.3373 |  |  | 36.3569 |  |  | 39.8114
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2588 |  |  | 32.121 |  |  | 31.4128 |  |  | 29.0478 |  |  | 23.22 |  |  | 12.6165 |  |  | -2.7226 |  |  | -19.824 |  |  | -37.9412 |  |  | -58.6684
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8982 |  |  | 48.3316 |  |  | 46.3956 |  |  | 42.8014 |  |  | 36.6975 |  |  | 27.9556 |  |  | 17.5361 |  |  | 7.6022 |  |  | -1.0147 |  |  | -7.2723
[13 empty] | C Non choked w/ reducers | 7 |  | 0.67334 |  |  | 10.3194 |  |  | 25.8667 |  |  | 52.7035 |  |  | 100.1205 |  |  | 204.731 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.5414 |  |  | 8.4127 |  |  | 21.2841 |  |  | 43.4177 |  |  | 79.6409 |  |  | 137.5366 |  |  | 240.1206 |  |  | 472.1433 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.67334 |  |  | 10.3194 |  |  | 25.8667 |  |  | 52.7035 |  |  | 100.1205 |  |  | 204.731 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.0567 | 3.8239 |  | 1.2806 | 58.4398 |  | 2.8667 | 144.5286 |  | 13.3035 | 281.5049 |  | 39.1205 | 472.2777 |  | 116.531 | 696.1951 |  | 5500 | 929.0751 |  | 5500 | 1133.6482 |  | 5500 | 1316.1304 |  | 5500 | 1497.8791
[13 empty] | Next iteration flow rate |  |  | 3.9004 | Abs Value of | Flow this | 59.0242 | Abs Value of | Flow this | 145.9739 | Abs Value of | Flow this | 284.32 | Abs Value of | Flow this | 477.0004 | Abs Value of | Flow this | 703.1571 | Abs Value of | Flow this | 938.3659 | Abs Value of | Flow this | 1144.9847 | Abs Value of | Flow this | 1329.2917 | Abs Value of | Flow this | 1512.8579 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9156 |  |  | 56.7985 |  |  | 56.1965 |  |  | 54.1861 |  |  | 49.2319 |  |  | 40.2181 |  |  | 27.1785 |  |  | 12.6409 |  |  | -2.7602 |  |  | -20.38
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6803 |  |  | 24.8007 |  |  | 25.2028 |  |  | 26.1936 |  |  | 27.9964 |  |  | 30.6043 |  |  | 33.5118 |  |  | 36.592 |  |  | 40.116
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2588 |  |  | 32.1182 |  |  | 31.3958 |  |  | 28.9833 |  |  | 23.0383 |  |  | 12.2217 |  |  | -3.4258 |  |  | -20.8709 |  |  | -39.3522 |  |  | -60.496
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8982 |  |  | 48.3296 |  |  | 46.3838 |  |  | 42.7586 |  |  | 36.584 |  |  | 27.7263 |  |  | 17.1601 |  |  | 7.0949 |  |  | -1.6041 |  |  | -7.8463
[13 empty] | C Non choked w/ reducers | 7 |  | 0.68681 |  |  | 10.4231 |  |  | 26.1324 |  |  | 53.2897 |  |  | 101.5197 |  |  | 210.0917 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.55223 |  |  | 8.497 |  |  | 21.4997 |  |  | 43.8738 |  |  | 80.562 |  |  | 139.4853 |  |  | 245.1647 |  |  | 493.6191 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.68681 |  |  | 10.4231 |  |  | 26.1324 |  |  | 53.2897 |  |  | 101.5197 |  |  | 210.0917 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.0432 | 3.9004 |  | 1.1769 | 59.0242 |  | 3.1324 | 145.9739 |  | 13.8897 | 284.32 |  | 40.5197 | 477.0004 |  | 121.8917 | 703.1571 |  | 5500 | 938.3659 |  | 5500 | 1144.9847 |  | 5500 | 1329.2917 |  | 5500 | 1512.8579
[13 empty] | Next iteration flow rate |  |  | 3.9784 | Abs Value of | Flow this | 59.6145 | Abs Value of | Flow this | 147.4337 | Abs Value of | Flow this | 287.1632 | Abs Value of | Flow this | 481.7705 | Abs Value of | Flow this | 710.1887 | Abs Value of | Flow this | 947.7495 | Abs Value of | Flow this | 1156.4345 | Abs Value of | Flow this | 1342.5846 | Abs Value of | Flow this | 1527.9865 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9156 |  |  | 56.7961 |  |  | 56.182 |  |  | 54.1312 |  |  | 49.0775 |  |  | 39.8824 |  |  | 26.5808 |  |  | 11.751 |  |  | -3.9597 |  |  | -21.9337
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6808 |  |  | 24.8036 |  |  | 25.2138 |  |  | 26.2245 |  |  | 28.0635 |  |  | 30.7238 |  |  | 33.6898 |  |  | 36.8319 |  |  | 40.4267
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2587 |  |  | 32.1153 |  |  | 31.3785 |  |  | 28.9174 |  |  | 22.853 |  |  | 11.8189 |  |  | -4.143 |  |  | -21.9388 |  |  | -40.7916 |  |  | -62.3604
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8982 |  |  | 48.3276 |  |  | 46.3718 |  |  | 42.715 |  |  | 36.4682 |  |  | 27.4924 |  |  | 16.7765 |  |  | 6.5774 |  |  | -2.2054 |  |  | -8.4318
[13 empty] | C Non choked w/ reducers | 7 |  | 0.70055 |  |  | 10.5278 |  |  | 26.4011 |  |  | 53.8839 |  |  | 102.9498 |  |  | 215.7778 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.56327 |  |  | 8.5821 |  |  | 21.7175 |  |  | 44.3352 |  |  | 81.4967 |  |  | 141.4783 |  |  | 250.4313 |  |  | 517.7969 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.70055 |  |  | 10.5278 |  |  | 26.4011 |  |  | 53.8839 |  |  | 102.9498 |  |  | 215.7778 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.0295 | 3.9784 |  | 1.0722 | 59.6145 |  | 3.4011 | 147.4337 |  | 14.4839 | 287.1632 |  | 41.9498 | 481.7705 |  | 127.5778 | 710.1887 |  | 5500 | 947.7495 |  | 5500 | 1156.4345 |  | 5500 | 1342.5846 |  | 5500 | 1527.9865
[13 empty] | Next iteration flow rate |  |  | 4.0579 | Abs Value of | Flow this | 60.2106 | Abs Value of | Flow this | 148.908 | Abs Value of | Flow this | 290.0348 | Abs Value of | Flow this | 486.5882 | Abs Value of | Flow this | 717.2906 | Abs Value of | Flow this | 957.227 | Abs Value of | Flow this | 1167.9989 | Abs Value of | Flow this | 1356.0104 | Abs Value of | Flow this | 1543.2664 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9156 |  |  | 56.7937 |  |  | 56.1673 |  |  | 54.0752 |  |  | 48.9199 |  |  | 39.5401 |  |  | 25.9711 |  |  | 10.8431 |  |  | -5.1833 |  |  | -23.5185
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6813 |  |  | 24.8065 |  |  | 25.225 |  |  | 26.256 |  |  | 28.132 |  |  | 30.8458 |  |  | 33.8714 |  |  | 37.0767 |  |  | 40.7437
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2587 |  |  | 32.1124 |  |  | 31.3607 |  |  | 28.8502 |  |  | 22.6639 |  |  | 11.4081 |  |  | -4.8747 |  |  | -23.0282 |  |  | -42.26 |  |  | -64.2623
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8982 |  |  | 48.3255 |  |  | 46.3595 |  |  | 42.6705 |  |  | 36.35 |  |  | 27.2537 |  |  | 16.3851 |  |  | 6.0494 |  |  | -2.8187 |  |  | -9.0291
[13 empty] | C Non choked w/ reducers | 7 |  | 0.71456 |  |  | 10.6335 |  |  | 26.6726 |  |  | 54.486 |  |  | 104.4121 |  |  | 221.8253 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.57454 |  |  | 8.6682 |  |  | 21.9376 |  |  | 44.8019 |  |  | 82.4453 |  |  | 143.5173 |  |  | 255.9381 |  |  | 545.3162 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.71456 |  |  | 10.6335 |  |  | 26.6726 |  |  | 54.486 |  |  | 104.4121 |  |  | 221.8253 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.0154 | 4.0579 |  | 0.96646 | 60.2106 |  | 3.6726 | 148.908 |  | 15.086 | 290.0348 |  | 43.4121 | 486.5882 |  | 133.6253 | 717.2906 |  | 5500 | 957.227 |  | 5500 | 1167.9989 |  | 5500 | 1356.0104 |  | 5500 | 1543.2664
[13 empty] | Next iteration flow rate |  |  | 4.1391 | Abs Value of | Flow this | 60.8127 | Abs Value of | Flow this | 150.3971 | Abs Value of | Flow this | 292.9351 | Abs Value of | Flow this | 491.454 | Abs Value of | Flow this | 724.4635 | Abs Value of | Flow this | 966.7993 | Abs Value of | Flow this | 1179.6789 | Abs Value of | Flow this | 1369.5705 | Abs Value of | Flow this | 1558.699 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9156 |  |  | 56.7912 |  |  | 56.1522 |  |  | 54.0181 |  |  | 48.7592 |  |  | 39.1908 |  |  | 25.3491 |  |  | 9.9171 |  |  | -6.4315 |  |  | -25.1353
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6818 |  |  | 24.8096 |  |  | 25.2364 |  |  | 26.2882 |  |  | 28.2018 |  |  | 30.9702 |  |  | 34.0566 |  |  | 37.3263 |  |  | 41.0671
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2587 |  |  | 32.1095 |  |  | 31.3427 |  |  | 28.7817 |  |  | 22.471 |  |  | 10.989 |  |  | -5.6211 |  |  | -24.1395 |  |  | -43.7578 |  |  | -66.2023
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8981 |  |  | 48.3234 |  |  | 46.347 |  |  | 42.625 |  |  | 36.2295 |  |  | 27.0103 |  |  | 15.986 |  |  | 5.5109 |  |  | -3.4444 |  |  | -9.6384
[13 empty] | C Non choked w/ reducers | 7 |  | 0.72885 |  |  | 10.7404 |  |  | 26.9471 |  |  | 55.0964 |  |  | 105.9079 |  |  | 228.276 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.58603 |  |  | 8.755 |  |  | 22.16 |  |  | 45.274 |  |  | 83.4082 |  |  | 145.6043 |  |  | 261.7051 |  |  | 577.0521 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.72885 |  |  | 10.7404 |  |  | 26.9471 |  |  | 55.0964 |  |  | 105.9079 |  |  | 228.276 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.0012 | 4.1391 |  | 0.85963 | 60.8127 |  | 3.9471 | 150.3971 |  | 15.6964 | 292.9351 |  | 44.9079 | 491.454 |  | 140.076 | 724.4635 |  | 5500 | 966.7993 |  | 5500 | 1179.6789 |  | 5500 | 1369.5705 |  | 5500 | 1558.699
[13 empty] | Next iteration flow rate |  |  | 4.2219 | Abs Value of | Flow this | 61.4208 | Abs Value of | Flow this | 151.9011 | Abs Value of | Flow this | 295.8645 | Abs Value of | Flow this | 496.3686 | Abs Value of | Flow this | 731.7081 | Abs Value of | Flow this | 976.4673 | Abs Value of | Flow this | 1191.4757 | Abs Value of | Flow this | 1383.2662 | Abs Value of | Flow this | 1574.286 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9155 |  |  | 56.7887 |  |  | 56.1369 |  |  | 53.9599 |  |  | 48.5952 |  |  | 38.8345 |  |  | 24.7146 |  |  | 8.9724 |  |  | -7.7048 |  |  | -26.7845
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6823 |  |  | 24.8126 |  |  | 25.248 |  |  | 26.321 |  |  | 28.2731 |  |  | 31.0971 |  |  | 34.2455 |  |  | 37.581 |  |  | 41.3969
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2586 |  |  | 32.1065 |  |  | 31.3243 |  |  | 28.7118 |  |  | 22.2743 |  |  | 10.5614 |  |  | -6.3825 |  |  | -25.2731 |  |  | -45.2857 |  |  | -68.1814
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8981 |  |  | 48.3213 |  |  | 46.3342 |  |  | 42.5787 |  |  | 36.1066 |  |  | 26.7619 |  |  | 15.5788 |  |  | 4.9616 |  |  | -4.0826 |  |  | -10.2599
[13 empty] | C Non choked w/ reducers | 7 |  | 0.74343 |  |  | 10.8483 |  |  | 27.2246 |  |  | 55.715 |  |  | 107.4383 |  |  | 235.1791 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.59775 |  |  | 8.8428 |  |  | 22.3846 |  |  | 45.7516 |  |  | 84.3855 |  |  | 147.7411 |  |  | 267.7543 |  |  | 614.2402 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.74343 |  |  | 10.8483 |  |  | 27.2246 |  |  | 55.715 |  |  | 107.4383 |  |  | 235.1791 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.9866 | 4.2219 |  | 0.75171 | 61.4208 |  | 4.2246 | 151.9011 |  | 16.315 | 295.8645 |  | 46.4383 | 496.3686 |  | 146.9791 | 731.7081 |  | 5500 | 976.4673 |  | 5500 | 1191.4757 |  | 5500 | 1383.2662 |  | 5500 | 1574.286
[13 empty] | Next iteration flow rate |  |  | 4.3063 | Abs Value of | Flow this | 62.0351 | Abs Value of | Flow this | 153.4201 | Abs Value of | Flow this | 298.8231 | Abs Value of | Flow this | 501.3323 | Abs Value of | Flow this | 739.0252 | Abs Value of | Flow this | 986.232 | Abs Value of | Flow this | 1203.3904 | Abs Value of | Flow this | 1397.0989 | Abs Value of | Flow this | 1590.0289 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9155 |  |  | 56.7862 |  |  | 56.1212 |  |  | 53.9004 |  |  | 48.428 |  |  | 38.4711 |  |  | 24.0673 |  |  | 8.0087 |  |  | -9.0037 |  |  | -28.4669
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6828 |  |  | 24.8158 |  |  | 25.2599 |  |  | 26.3544 |  |  | 28.3458 |  |  | 31.2265 |  |  | 34.4383 |  |  | 37.8407 |  |  | 41.7334
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2586 |  |  | 32.1034 |  |  | 31.3055 |  |  | 28.6405 |  |  | 22.0736 |  |  | 10.1253 |  |  | -7.1592 |  |  | -26.4295 |  |  | -46.8444 |  |  | -70.2003
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8981 |  |  | 48.3191 |  |  | 46.3212 |  |  | 42.5314 |  |  | 35.9812 |  |  | 26.5086 |  |  | 15.1634 |  |  | 4.4012 |  |  | -4.7337 |  |  | -10.894
[13 empty] | C Non choked w/ reducers | 7 |  | 0.7583 |  |  | 10.9573 |  |  | 27.505 |  |  | 56.3422 |  |  | 109.0049 |  |  | 242.5925 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.6097 |  |  | 8.9314 |  |  | 22.6117 |  |  | 46.2348 |  |  | 85.3778 |  |  | 149.9298 |  |  | 274.111 |  |  | 658.6942 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.7583 |  |  | 10.9573 |  |  | 27.505 |  |  | 56.3422 |  |  | 109.0049 |  |  | 242.5925 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.9717 | 4.3063 |  | 0.64271 | 62.0351 |  | 4.505 | 153.4201 |  | 16.9422 | 298.8231 |  | 48.0049 | 501.3323 |  | 154.3925 | 739.0252 |  | 5500 | 986.232 |  | 5500 | 1203.3904 |  | 5500 | 1397.0989 |  | 5500 | 1590.0289
[13 empty] | Next iteration flow rate |  |  | 4.3924 | Abs Value of | Flow this | 62.6554 | Abs Value of | Flow this | 154.9543 | Abs Value of | Flow this | 301.8114 | Abs Value of | Flow this | 506.3456 | Abs Value of | Flow this | 746.4154 | Abs Value of | Flow this | 996.0943 | Abs Value of | Flow this | 1215.4243 | Abs Value of | Flow this | 1411.0699 | Abs Value of | Flow this | 1605.9292 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9155 |  |  | 56.7836 |  |  | 56.1052 |  |  | 53.8398 |  |  | 48.2574 |  |  | 38.1003 |  |  | 23.4071 |  |  | 7.0257 |  |  | -10.3286 |  |  | -30.1831
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6833 |  |  | 24.819 |  |  | 25.272 |  |  | 26.3885 |  |  | 28.4199 |  |  | 31.3586 |  |  | 34.6349 |  |  | 38.1057 |  |  | 42.0766
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2586 |  |  | 32.1003 |  |  | 31.2863 |  |  | 28.5678 |  |  | 21.8689 |  |  | 9.6804 |  |  | -7.9515 |  |  | -27.6092 |  |  | -48.4344 |  |  | -72.2597
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8981 |  |  | 48.3168 |  |  | 46.3079 |  |  | 42.4832 |  |  | 35.8533 |  |  | 26.2502 |  |  | 14.7396 |  |  | 3.8296 |  |  | -5.3979 |  |  | -11.5407
[13 empty] | C Non choked w/ reducers | 7 |  | 0.77346 |  |  | 11.0674 |  |  | 27.7886 |  |  | 56.978 |  |  | 110.6091 |  |  | 250.5855 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.6219 |  |  | 9.0209 |  |  | 22.8411 |  |  | 46.7237 |  |  | 86.3852 |  |  | 152.1726 |  |  | 280.8034 |  |  | 713.2082 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.77346 |  |  | 11.0674 |  |  | 27.7886 |  |  | 56.978 |  |  | 110.6091 |  |  | 250.5855 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.9565 | 4.3924 |  | 0.53259 | 62.6554 |  | 4.7886 | 154.9543 |  | 17.578 | 301.8114 |  | 49.6091 | 506.3456 |  | 162.3855 | 746.4154 |  | 5500 | 996.0943 |  | 5500 | 1215.4243 |  | 5500 | 1411.0699 |  | 5500 | 1605.9292
[13 empty] | Next iteration flow rate |  |  | 4.4803 | Abs Value of | Flow this | 63.282 | Abs Value of | Flow this | 156.5038 | Abs Value of | Flow this | 304.8295 | Abs Value of | Flow this | 511.409 | Abs Value of | Flow this | 753.8796 | Abs Value of | Flow this | 1006.0552 | Abs Value of | Flow this | 1227.5786 | Abs Value of | Flow this | 1425.1806 | Abs Value of | Flow this | 1621.9885 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9155 |  |  | 56.7809 |  |  | 56.0889 |  |  | 53.778 |  |  | 48.0833 |  |  | 37.7221 |  |  | 22.7335 |  |  | 6.0229 |  |  | -11.6803 |  |  | -31.9338
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6838 |  |  | 24.8222 |  |  | 25.2844 |  |  | 26.4233 |  |  | 28.4956 |  |  | 31.4933 |  |  | 34.8354 |  |  | 38.3761 |  |  | 42.4268
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2586 |  |  | 32.0971 |  |  | 31.2667 |  |  | 28.4936 |  |  | 21.66 |  |  | 9.2266 |  |  | -8.7598 |  |  | -28.8125 |  |  | -50.0563 |  |  | -74.3606
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8981 |  |  | 48.3145 |  |  | 46.2943 |  |  | 42.434 |  |  | 35.7228 |  |  | 25.9866 |  |  | 14.3074 |  |  | 3.2464 |  |  | -6.0754 |  |  | -12.2005
[13 empty] | C Non choked w/ reducers | 7 |  | 0.78893 |  |  | 11.1786 |  |  | 28.0753 |  |  | 57.6227 |  |  | 112.2525 |  |  | 259.2412 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.63434 |  |  | 9.1113 |  |  | 23.0729 |  |  | 47.2183 |  |  | 87.4083 |  |  | 154.4719 |  |  | 287.8638 |  |  | 782.3644 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.78893 |  |  | 11.1786 |  |  | 28.0753 |  |  | 57.6227 |  |  | 112.2525 |  |  | 259.2412 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.9411 | 4.4803 |  | 0.42136 | 63.282 |  | 5.0753 | 156.5038 |  | 18.2227 | 304.8295 |  | 51.2525 | 511.409 |  | 171.0412 | 753.8796 |  | 5500 | 1006.0552 |  | 5500 | 1227.5786 |  | 5500 | 1425.1806 |  | 5500 | 1621.9885
[13 empty] | Next iteration flow rate |  |  | 4.5699 | Abs Value of | Flow this | 63.9148 | Abs Value of | Flow this | 158.0689 | Abs Value of | Flow this | 307.8778 | Abs Value of | Flow this | 516.5231 | Abs Value of | Flow this | 761.4184 | Abs Value of | Flow this | 1016.1158 | Abs Value of | Flow this | 1239.8543 | Abs Value of | Flow this | 1439.4324 | Abs Value of | Flow this | 1638.2083 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9154 |  |  | 56.7782 |  |  | 56.0723 |  |  | 53.7149 |  |  | 47.9058 |  |  | 37.3363 |  |  | 22.0465 |  |  | 4.9999 |  |  | -13.0591 |  |  | -33.7197
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6844 |  |  | 24.8255 |  |  | 25.297 |  |  | 26.4588 |  |  | 28.5727 |  |  | 31.6307 |  |  | 35.04 |  |  | 38.6518 |  |  | 42.7839
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2585 |  |  | 32.0938 |  |  | 31.2468 |  |  | 28.4179 |  |  | 21.447 |  |  | 8.7636 |  |  | -9.5842 |  |  | -30.0401 |  |  | -51.7109 |  |  | -76.5036
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.898 |  |  | 48.3122 |  |  | 46.2805 |  |  | 42.3838 |  |  | 35.5896 |  |  | 25.7177 |  |  | 13.8664 |  |  | 2.6516 |  |  | -6.7665 |  |  | -12.8735
[13 empty] | C Non choked w/ reducers | 7 |  | 0.80471 |  |  | 11.291 |  |  | 28.3651 |  |  | 58.2764 |  |  | 113.9367 |  |  | 268.6606 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.64702 |  |  | 9.2027 |  |  | 23.3071 |  |  | 47.7187 |  |  | 88.4474 |  |  | 156.8302 |  |  | 295.329 |  |  | 874.3415 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.80471 |  |  | 11.291 |  |  | 28.3651 |  |  | 58.2764 |  |  | 113.9367 |  |  | 268.6606 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.9253 | 4.5699 |  | 0.309 | 63.9148 |  | 5.3651 | 158.0689 |  | 18.8764 | 307.8778 |  | 52.9367 | 516.5231 |  | 180.4606 | 761.4184 |  | 5500 | 1016.1158 |  | 5500 | 1239.8543 |  | 5500 | 1439.4324 |  | 5500 | 1638.2083
[13 empty] | Next iteration flow rate |  |  | 4.6613 | Abs Value of | Flow this | 64.5539 | Abs Value of | Flow this | 159.6495 | Abs Value of | Flow this | 310.9566 | Abs Value of | Flow this | 521.6884 | Abs Value of | Flow this | 769.0326 | Abs Value of | Flow this | 1026.2769 | Abs Value of | Flow this | 1252.2529 | Abs Value of | Flow this | 1453.8267 | Abs Value of | Flow this | 1654.5904 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9154 |  |  | 56.7754 |  |  | 56.0554 |  |  | 53.6506 |  |  | 47.7247 |  |  | 36.9428 |  |  | 21.3456 |  |  | 3.9564 |  |  | -14.4656 |  |  | -35.5415
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6849 |  |  | 24.8289 |  |  | 25.3099 |  |  | 26.4951 |  |  | 28.6514 |  |  | 31.7709 |  |  | 35.2487 |  |  | 38.9331 |  |  | 43.1483
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2585 |  |  | 32.0905 |  |  | 31.2264 |  |  | 28.3407 |  |  | 21.2296 |  |  | 8.2913 |  |  | -10.4253 |  |  | -31.2923 |  |  | -53.3987 |  |  | -78.6897
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.898 |  |  | 48.3098 |  |  | 46.2664 |  |  | 42.3326 |  |  | 35.4538 |  |  | 25.4434 |  |  | 13.4166 |  |  | 2.0448 |  |  | -7.4715 |  |  | -13.5601
[13 empty] | C Non choked w/ reducers | 7 |  | 0.82081 |  |  | 11.4045 |  |  | 28.6581 |  |  | 58.9392 |  |  | 115.6636 |  |  | 278.968 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.65996 |  |  | 9.2949 |  |  | 23.5437 |  |  | 48.225 |  |  | 89.5027 |  |  | 159.2501 |  |  | 303.2411 |  |  | 1005.6161 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.82081 |  |  | 11.4045 |  |  | 28.6581 |  |  | 58.9392 |  |  | 115.6636 |  |  | 278.968 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.9092 | 4.6613 |  | 0.1955 | 64.5539 |  | 5.6581 | 159.6495 |  | 19.5392 | 310.9566 |  | 54.6636 | 521.6884 |  | 190.768 | 769.0326 |  | 5500 | 1026.2769 |  | 5500 | 1252.2529 |  | 5500 | 1453.8267 |  | 5500 | 1654.5904
[13 empty] | Next iteration flow rate |  |  | 4.7545 | Abs Value of | Flow this | 65.1995 | Abs Value of | Flow this | 161.246 | Abs Value of | Flow this | 314.0661 | Abs Value of | Flow this | 526.9052 | Abs Value of | Flow this | 776.7229 | Abs Value of | Flow this | 1036.5397 | Abs Value of | Flow this | 1264.7754 | Abs Value of | Flow this | 1468.365 | Abs Value of | Flow this | 1671.1363 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9154 |  |  | 56.7726 |  |  | 56.0381 |  |  | 53.5849 |  |  | 47.5399 |  |  | 36.5413 |  |  | 20.6306 |  |  | 2.8919 |  |  | -15.9003 |  |  | -37.3999
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6855 |  |  | 24.8324 |  |  | 25.323 |  |  | 26.532 |  |  | 28.7317 |  |  | 31.9139 |  |  | 35.4616 |  |  | 39.2201 |  |  | 43.52
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2585 |  |  | 32.0871 |  |  | 31.2057 |  |  | 28.2619 |  |  | 21.0079 |  |  | 7.8096 |  |  | -11.2833 |  |  | -32.5697 |  |  | -55.1204 |  |  | -80.9198
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.898 |  |  | 48.3074 |  |  | 46.252 |  |  | 42.2804 |  |  | 35.3153 |  |  | 25.1635 |  |  | 12.9578 |  |  | 1.4258 |  |  | -8.1907 |  |  | -14.2605
[13 empty] | C Non choked w/ reducers | 7 |  | 0.83722 |  |  | 11.5192 |  |  | 28.9543 |  |  | 59.6115 |  |  | 117.435 |  |  | 290.3182 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.67316 |  |  | 9.3881 |  |  | 23.7829 |  |  | 48.7373 |  |  | 90.5749 |  |  | 161.7345 |  |  | 311.6491 |  |  | 1216.33 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.83722 |  |  | 11.5192 |  |  | 28.9543 |  |  | 59.6115 |  |  | 117.435 |  |  | 290.3182 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.8928 | 4.7545 |  | 0.080847 | 65.1995 |  | 5.9543 | 161.246 |  | 20.2115 | 314.0661 |  | 56.435 | 526.9052 |  | 202.1182 | 776.7229 |  | 5500 | 1036.5397 |  | 5500 | 1264.7754 |  | 5500 | 1468.365 |  | 5500 | 1671.1363
[13 empty] | Next iteration flow rate |  |  | 4.8496 | Abs Value of | Flow this | 65.8515 | Abs Value of | Flow this | 162.8585 | Abs Value of | Flow this | 317.2068 | Abs Value of | Flow this | 532.1743 | Abs Value of | Flow this | 784.4901 | Abs Value of | Flow this | 1046.9051 | Abs Value of | Flow this | 1277.4232 | Abs Value of | Flow this | 1483.0486 | Abs Value of | Flow this | 1687.8477 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9153 |  |  | 56.7697 |  |  | 56.0204 |  |  | 53.518 |  |  | 47.3515 |  |  | 36.1318 |  |  | 19.9013 |  |  | 1.806 |  |  | -17.3639 |  |  | -39.2956
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6861 |  |  | 24.8359 |  |  | 25.3364 |  |  | 26.5697 |  |  | 28.8136 |  |  | 32.0597 |  |  | 35.6788 |  |  | 39.5128 |  |  | 43.8991
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2584 |  |  | 32.0836 |  |  | 31.1845 |  |  | 28.1816 |  |  | 20.7818 |  |  | 7.3181 |  |  | -12.1585 |  |  | -33.8727 |  |  | -56.8767 |  |  | -83.1947
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.898 |  |  | 48.3049 |  |  | 46.2373 |  |  | 42.2271 |  |  | 35.174 |  |  | 24.8781 |  |  | 12.4897 |  |  | 0.79433 |  |  | -8.9244 |  |  | -14.9749
[13 empty] | C Non choked w/ reducers | 7 |  | 0.85397 |  |  | 11.635 |  |  | 29.2537 |  |  | 60.2934 |  |  | 119.253 |  |  | 302.9068 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.68663 |  |  | 9.4822 |  |  | 24.0245 |  |  | 49.2557 |  |  | 91.6642 |  |  | 164.2863 |  |  | 320.6095 |  |  | 1645.8809 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.85397 |  |  | 11.635 |  |  | 29.2537 |  |  | 60.2934 |  |  | 119.253 |  |  | 302.9068 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.876 | 4.8496 |  | 0.034973 | 65.8515 |  | 6.2537 | 162.8585 |  | 20.8934 | 317.2068 |  | 58.253 | 532.1743 |  | 214.7068 | 784.4901 |  | 5500 | 1046.9051 |  | 5500 | 1277.4232 |  | 5500 | 1483.0486 |  | 5500 | 1687.8477
[13 empty] | Next iteration flow rate |  |  | 4.9466 | Abs Value of | Flow this | 66.51 | Abs Value of | Flow this | 164.4871 | Abs Value of | Flow this | 320.3788 | Abs Value of | Flow this | 537.496 | Abs Value of | Flow this | 792.335 | Abs Value of | Flow this | 1057.3741 | Abs Value of | Flow this | 1290.1974 | Abs Value of | Flow this | 1497.8791 | Abs Value of | Flow this | 1704.7262 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9153 |  |  | 56.7667 |  |  | 56.0024 |  |  | 53.4497 |  |  | 47.1592 |  |  | 35.714 |  |  | 19.1573 |  |  | 0.69833 |  |  | -18.857 |  |  | -41.2295
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6867 |  |  | 24.8395 |  |  | 25.3501 |  |  | 26.6082 |  |  | 28.8972 |  |  | 32.2085 |  |  | 35.9003 |  |  | 39.8114 |  |  | 44.2859
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2584 |  |  | 32.0801 |  |  | 31.1629 |  |  | 28.0996 |  |  | 20.5511 |  |  | 6.8168 |  |  | -13.0513 |  |  | -35.202 |  |  | -58.6684 |  |  | -85.5154
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8979 |  |  | 48.3024 |  |  | 46.2223 |  |  | 42.1728 |  |  | 35.0299 |  |  | 24.5869 |  |  | 12.0122 |  |  | 0.15019 |  |  | -9.6728 |  |  | -15.7037
[13 empty] | C Non choked w/ reducers | 7 |  | 0.87105 |  |  | 11.752 |  |  | 29.5565 |  |  | 60.9851 |  |  | 121.1197 |  |  | 316.9858 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.70036 |  |  | 9.5773 |  |  | 24.2687 |  |  | 49.7803 |  |  | 92.7711 |  |  | 166.9089 |  |  | 330.1886 |  |  | 3822.9749 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.87105 |  |  | 11.752 |  |  | 29.5565 |  |  | 60.9851 |  |  | 121.1197 |  |  | 316.9858 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.859 | 4.9466 |  | 0.15197 | 66.51 |  | 6.5565 | 164.4871 |  | 21.5851 | 320.3788 |  | 60.1197 | 537.496 |  | 228.7858 | 792.335 |  | 5500 | 1057.3741 |  | 5500 | 1290.1974 |  | 5500 | 1497.8791 |  | 5500 | 1704.7262
[13 empty] | Next iteration flow rate |  |  | 5.0455 | Abs Value of | Flow this | 67.1751 | Abs Value of | Flow this | 166.132 | Abs Value of | Flow this | 323.5826 | Abs Value of | Flow this | 542.871 | Abs Value of | Flow this | 800.2584 | Abs Value of | Flow this | 1067.9479 | Abs Value of | Flow this | 1303.0994 | Abs Value of | Flow this | 1512.8579 | Abs Value of | Flow this | 1721.7734 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9153 |  |  | 56.7637 |  |  | 55.984 |  |  | 53.38 |  |  | 46.9631 |  |  | 35.2879 |  |  | 18.3983 |  |  | -0.43164 |  |  | -20.38 |  |  | -43.2022
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6873 |  |  | 24.8432 |  |  | 25.364 |  |  | 26.6474 |  |  | 28.9824 |  |  | 32.3603 |  |  | 36.1263 |  |  | 40.116 |  |  | 44.6804
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2583 |  |  | 32.0765 |  |  | 31.1408 |  |  | 28.016 |  |  | 20.3157 |  |  | 6.3054 |  |  | -13.962 |  |  | -36.558 |  |  | -60.496 |  |  | -87.8826
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8979 |  |  | 48.2998 |  |  | 46.207 |  |  | 42.1174 |  |  | 34.8828 |  |  | 24.2898 |  |  | 11.5251 |  |  | -0.5069 |  |  | -10.4362 |  |  | -16.4472
[13 empty] | C Non choked w/ reducers | 7 |  | 0.88847 |  |  | 11.8702 |  |  | 29.8626 |  |  | 61.6868 |  |  | 123.0374 |  |  | 332.8855 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.71437 |  |  | 9.6734 |  |  | 24.5154 |  |  | 50.3112 |  |  | 93.8961 |  |  | 169.6056 |  |  | 340.4646 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.88847 |  |  | 11.8702 |  |  | 29.8626 |  |  | 61.6868 |  |  | 123.0374 |  |  | 332.8855 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.8415 | 5.0455 |  | 0.27016 | 67.1751 |  | 6.8626 | 166.132 |  | 22.2868 | 323.5826 |  | 62.0374 | 542.871 |  | 244.6855 | 800.2584 |  | 5500 | 1067.9479 |  | 5500 | 1303.0994 |  | 5500 | 1512.8579 |  | 5500 | 1721.7734
[13 empty] | Next iteration flow rate |  |  | 5.1464 | Abs Value of | Flow this | 67.8468 | Abs Value of | Flow this | 167.7933 | Abs Value of | Flow this | 326.8185 | Abs Value of | Flow this | 548.2997 | Abs Value of | Flow this | 808.2609 | Abs Value of | Flow this | 1078.6274 | Abs Value of | Flow this | 1316.1304 | Abs Value of | Flow this | 1527.9865 | Abs Value of | Flow this | 1738.9912 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9152 |  |  | 56.7607 |  |  | 55.9653 |  |  | 53.3089 |  |  | 46.7631 |  |  | 34.8531 |  |  | 17.6241 |  |  | -1.5843 |  |  | -21.9337 |  |  | -45.2146
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6879 |  |  | 24.8469 |  |  | 25.3782 |  |  | 26.6874 |  |  | 29.0694 |  |  | 32.5152 |  |  | 36.3569 |  |  | 40.4267 |  |  | 45.0829
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2583 |  |  | 32.0728 |  |  | 31.1184 |  |  | 27.9307 |  |  | 20.0757 |  |  | 5.7838 |  |  | -14.8911 |  |  | -37.9412 |  |  | -62.3604 |  |  | -90.2975
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8979 |  |  | 48.2972 |  |  | 46.1915 |  |  | 42.0608 |  |  | 34.7328 |  |  | 23.9868 |  |  | 11.0283 |  |  | -1.1772 |  |  | -11.215 |  |  | -17.2055
[13 empty] | C Non choked w/ reducers | 7 |  | 0.90624 |  |  | 11.9895 |  |  | 30.1722 |  |  | 62.3987 |  |  | 125.0086 |  |  | 351.0498 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.72866 |  |  | 9.7704 |  |  | 24.7648 |  |  | 50.8484 |  |  | 95.0397 |  |  | 172.3803 |  |  | 351.5302 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.90624 |  |  | 11.9895 |  |  | 30.1722 |  |  | 62.3987 |  |  | 125.0086 |  |  | 351.0498 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.8238 | 5.1464 |  | 0.38954 | 67.8468 |  | 7.1722 | 167.7933 |  | 22.9987 | 326.8185 |  | 64.0086 | 548.2997 |  | 262.8498 | 808.2609 |  | 5500 | 1078.6274 |  | 5500 | 1316.1304 |  | 5500 | 1527.9865 |  | 5500 | 1738.9912
[13 empty] | Next iteration flow rate |  |  | 5.2494 | Abs Value of | Flow this | 68.5253 | Abs Value of | Flow this | 169.4712 | Abs Value of | Flow this | 330.0866 | Abs Value of | Flow this | 553.7827 | Abs Value of | Flow this | 816.3436 | Abs Value of | Flow this | 1089.4136 | Abs Value of | Flow this | 1329.2917 | Abs Value of | Flow this | 1543.2664 | Abs Value of | Flow this | 1756.3811 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9152 |  |  | 56.7576 |  |  | 55.9462 |  |  | 53.2364 |  |  | 46.559 |  |  | 34.4097 |  |  | 16.8343 |  |  | -2.7602 |  |  | -23.5185 |  |  | -47.2674
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6885 |  |  | 24.8508 |  |  | 25.3927 |  |  | 26.7282 |  |  | 29.1581 |  |  | 32.6731 |  |  | 36.592 |  |  | 40.7437 |  |  | 45.4935
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2583 |  |  | 32.0691 |  |  | 31.0954 |  |  | 27.8437 |  |  | 19.8308 |  |  | 5.2516 |  |  | -15.8388 |  |  | -39.3522 |  |  | -64.2623 |  |  | -92.7609
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8978 |  |  | 48.2945 |  |  | 46.1756 |  |  | 42.0031 |  |  | 34.5798 |  |  | 23.6777 |  |  | 10.5214 |  |  | -1.861 |  |  | -12.0094 |  |  | -17.9792
[13 empty] | C Non choked w/ reducers | 7 |  | 0.92436 |  |  | 12.1101 |  |  | 30.4851 |  |  | 63.1211 |  |  | 127.0358 |  |  | 372.0912 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.74323 |  |  | 9.8683 |  |  | 25.0167 |  |  | 51.3922 |  |  | 96.2022 |  |  | 175.2368 |  |  | 363.4968 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.92436 |  |  | 12.1101 |  |  | 30.4851 |  |  | 63.1211 |  |  | 127.0358 |  |  | 372.0912 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.8056 | 5.2494 |  | 0.51015 | 68.5253 |  | 7.4851 | 169.4712 |  | 23.7211 | 330.0866 |  | 66.0358 | 553.7827 |  | 283.8912 | 816.3436 |  | 5500 | 1089.4136 |  | 5500 | 1329.2917 |  | 5500 | 1543.2664 |  | 5500 | 1756.3811
[13 empty] | Next iteration flow rate |  |  | 5.3543 | Abs Value of | Flow this | 69.2105 | Abs Value of | Flow this | 171.1659 | Abs Value of | Flow this | 333.3875 | Abs Value of | Flow this | 559.3205 | Abs Value of | Flow this | 824.507 | Abs Value of | Flow this | 1100.3078 | Abs Value of | Flow this | 1342.5846 | Abs Value of | Flow this | 1558.699 | Abs Value of | Flow this | 1773.9449 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9152 |  |  | 56.7544 |  |  | 55.9267 |  |  | 53.1624 |  |  | 46.3508 |  |  | 33.9573 |  |  | 16.0287 |  |  | -3.9597 |  |  | -25.1353 |  |  | -49.3615
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6891 |  |  | 24.8547 |  |  | 25.4075 |  |  | 26.7698 |  |  | 29.2485 |  |  | 32.8343 |  |  | 36.8319 |  |  | 41.0671 |  |  | 45.9123
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2582 |  |  | 32.0652 |  |  | 31.072 |  |  | 27.7549 |  |  | 19.581 |  |  | 4.7087 |  |  | -16.8056 |  |  | -40.7916 |  |  | -66.2023 |  |  | -95.2738
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8978 |  |  | 48.2918 |  |  | 46.1593 |  |  | 41.9443 |  |  | 34.4237 |  |  | 23.3624 |  |  | 10.0044 |  |  | -2.5585 |  |  | -12.8198 |  |  | -18.7684
[13 empty] | C Non choked w/ reducers | 7 |  | 0.94285 |  |  | 12.232 |  |  | 30.8016 |  |  | 63.8542 |  |  | 129.1221 |  |  | 396.8844 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.75809 |  |  | 9.9673 |  |  | 25.2713 |  |  | 51.9425 |  |  | 97.3843 |  |  | 178.1796 |  |  | 376.4993 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.94285 |  |  | 12.232 |  |  | 30.8016 |  |  | 63.8542 |  |  | 129.1221 |  |  | 396.8844 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.7871 | 5.3543 |  | 0.63198 | 69.2105 |  | 7.8016 | 171.1659 |  | 24.4542 | 333.3875 |  | 68.1221 | 559.3205 |  | 308.6844 | 824.507 |  | 5500 | 1100.3078 |  | 5500 | 1342.5846 |  | 5500 | 1558.699 |  | 5500 | 1773.9449
[13 empty] | Next iteration flow rate |  |  | 5.4614 | Abs Value of | Flow this | 69.9027 | Abs Value of | Flow this | 172.8776 | Abs Value of | Flow this | 336.7214 | Abs Value of | Flow this | 564.9137 | Abs Value of | Flow this | 832.7521 | Abs Value of | Flow this | 1111.3109 | Abs Value of | Flow this | 1356.0104 | Abs Value of | Flow this | 1574.286 | Abs Value of | Flow this | 1791.6843 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9151 |  |  | 56.7511 |  |  | 55.9068 |  |  | 53.087 |  |  | 46.1384 |  |  | 33.4958 |  |  | 15.2069 |  |  | -5.1833 |  |  | -26.7845 |  |  | -51.4977
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6898 |  |  | 24.8586 |  |  | 25.4226 |  |  | 26.8123 |  |  | 29.3408 |  |  | 32.9986 |  |  | 37.0767 |  |  | 41.3969 |  |  | 46.3395
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2582 |  |  | 32.0613 |  |  | 31.0482 |  |  | 27.6644 |  |  | 19.3261 |  |  | 4.155 |  |  | -17.7918 |  |  | -42.26 |  |  | -68.1814 |  |  | -97.8372
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8978 |  |  | 48.289 |  |  | 46.1428 |  |  | 41.8843 |  |  | 34.2645 |  |  | 23.0407 |  |  | 9.477 |  |  | -3.27 |  |  | -13.6465 |  |  | -19.5734
[13 empty] | C Non choked w/ reducers | 7 |  | 0.96171 |  |  | 12.3551 |  |  | 31.1215 |  |  | 64.5982 |  |  | 131.2703 |  |  | 426.7305 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.77326 |  |  | 10.0673 |  |  | 25.5286 |  |  | 52.4995 |  |  | 98.5864 |  |  | 181.2132 |  |  | 390.7027 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.96171 |  |  | 12.3551 |  |  | 31.1215 |  |  | 64.5982 |  |  | 131.2703 |  |  | 426.7305 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.7683 | 5.4614 |  | 0.75505 | 69.9027 |  | 8.1215 | 172.8776 |  | 25.1982 | 336.7214 |  | 70.2703 | 564.9137 |  | 338.5305 | 832.7521 |  | 5500 | 1111.3109 |  | 5500 | 1356.0104 |  | 5500 | 1574.286 |  | 5500 | 1791.6843
[13 empty] | Next iteration flow rate |  |  | 5.5707 | Abs Value of | Flow this | 70.6017 | Abs Value of | Flow this | 174.6063 | Abs Value of | Flow this | 340.0886 | Abs Value of | Flow this | 570.5629 | Abs Value of | Flow this | 841.0796 | Abs Value of | Flow this | 1122.424 | Abs Value of | Flow this | 1369.5705 | Abs Value of | Flow this | 1590.0289 | Abs Value of | Flow this | 1809.6012 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9151 |  |  | 56.7478 |  |  | 55.8865 |  |  | 53.01 |  |  | 45.9218 |  |  | 33.0251 |  |  | 14.3685 |  |  | -6.4315 |  |  | -28.4669 |  |  | -53.6768
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6904 |  |  | 24.8627 |  |  | 25.438 |  |  | 26.8556 |  |  | 29.435 |  |  | 33.1663 |  |  | 37.3263 |  |  | 41.7334 |  |  | 46.7754
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2581 |  |  | 32.0574 |  |  | 31.0238 |  |  | 27.572 |  |  | 19.0662 |  |  | 3.5901 |  |  | -18.7978 |  |  | -43.7578 |  |  | -70.2003 |  |  | -100.4521
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8977 |  |  | 48.2862 |  |  | 46.1259 |  |  | 41.823 |  |  | 34.1021 |  |  | 22.7126 |  |  | 8.9389 |  |  | -3.9958 |  |  | -14.4898 |  |  | -20.3946
[13 empty] | C Non choked w/ reducers | 7 |  | 0.98094 |  |  | 12.4794 |  |  | 31.4451 |  |  | 65.3533 |  |  | 133.4838 |  |  | 463.6683 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.78872 |  |  | 10.1682 |  |  | 25.7886 |  |  | 53.0633 |  |  | 99.8091 |  |  | 184.3427 |  |  | 406.312 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.98094 |  |  | 12.4794 |  |  | 31.4451 |  |  | 65.3533 |  |  | 133.4838 |  |  | 463.6683 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.7491 | 5.5707 |  | 0.87938 | 70.6017 |  | 8.4451 | 174.6063 |  | 25.9533 | 340.0886 |  | 72.4838 | 570.5629 |  | 375.4683 | 841.0796 |  | 5500 | 1122.424 |  | 5500 | 1369.5705 |  | 5500 | 1590.0289 |  | 5500 | 1809.6012
[13 empty] | Next iteration flow rate |  |  | 5.6821 | Abs Value of | Flow this | 71.3077 | Abs Value of | Flow this | 176.3524 | Abs Value of | Flow this | 343.4895 | Abs Value of | Flow this | 576.2685 | Abs Value of | Flow this | 849.4904 | Abs Value of | Flow this | 1133.6482 | Abs Value of | Flow this | 1383.2662 | Abs Value of | Flow this | 1605.9292 | Abs Value of | Flow this | 1827.6972 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9151 |  |  | 56.7444 |  |  | 55.8658 |  |  | 52.9315 |  |  | 45.7008 |  |  | 32.5449 |  |  | 13.5133 |  |  | -7.7048 |  |  | -30.1831 |  |  | -55.8997
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6911 |  |  | 24.8668 |  |  | 25.4537 |  |  | 26.8998 |  |  | 29.531 |  |  | 33.3373 |  |  | 37.581 |  |  | 42.0766 |  |  | 47.2199
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2581 |  |  | 32.0533 |  |  | 30.999 |  |  | 27.4778 |  |  | 18.801 |  |  | 3.0138 |  |  | -19.824 |  |  | -45.2857 |  |  | -72.2597 |  |  | -103.1196
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8977 |  |  | 48.2833 |  |  | 46.1087 |  |  | 41.7606 |  |  | 33.9364 |  |  | 22.3779 |  |  | 8.3901 |  |  | -4.7363 |  |  | -15.35 |  |  | -21.2324
[13 empty] | C Non choked w/ reducers | 7 |  | 1.0006 |  |  | 12.605 |  |  | 31.7723 |  |  | 66.1199 |  |  | 135.7661 |  |  | 511.1186 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.8045 |  |  | 10.2702 |  |  | 26.0514 |  |  | 53.634 |  |  | 101.053 |  |  | 187.5734 |  |  | 423.5852 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.0006 |  |  | 12.605 |  |  | 31.7723 |  |  | 66.1199 |  |  | 135.7661 |  |  | 511.1186 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.7294 | 5.6821 |  | 1.005 | 71.3077 |  | 8.7723 | 176.3524 |  | 26.7199 | 343.4895 |  | 74.7661 | 576.2685 |  | 422.9186 | 849.4904 |  | 5500 | 1133.6482 |  | 5500 | 1383.2662 |  | 5500 | 1605.9292 |  | 5500 | 1827.6972
[13 empty] | Next iteration flow rate |  |  | 5.7957 | Abs Value of | Flow this | 72.0208 | Abs Value of | Flow this | 178.1159 | Abs Value of | Flow this | 346.9244 | Abs Value of | Flow this | 582.0312 | Abs Value of | Flow this | 857.9853 | Abs Value of | Flow this | 1144.9847 | Abs Value of | Flow this | 1397.0989 | Abs Value of | Flow this | 1621.9885 | Abs Value of | Flow this | 1845.9742 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.915 |  |  | 56.741 |  |  | 55.8447 |  |  | 52.8514 |  |  | 45.4754 |  |  | 32.055 |  |  | 12.6409 |  |  | -9.0037 |  |  | -31.9338 |  |  | -58.1673
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6918 |  |  | 24.8711 |  |  | 25.4697 |  |  | 26.9449 |  |  | 29.629 |  |  | 33.5118 |  |  | 37.8407 |  |  | 42.4268 |  |  | 47.6735
[13 empty] | Delta P at this iteration flow rate |  |  | 32.258 |  |  | 32.0492 |  |  | 30.9736 |  |  | 27.3817 |  |  | 18.5305 |  |  | 2.426 |  |  | -20.8709 |  |  | -46.8444 |  |  | -74.3606 |  |  | -105.8408
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8977 |  |  | 48.2803 |  |  | 46.0911 |  |  | 41.6969 |  |  | 33.7673 |  |  | 22.0364 |  |  | 7.8302 |  |  | -5.4916 |  |  | -16.2276 |  |  | -22.087
[13 empty] | C Non choked w/ reducers | 7 |  | 1.0206 |  |  | 12.7318 |  |  | 32.1031 |  |  | 66.8982 |  |  | 138.121 |  |  | 575.3839 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.82059 |  |  | 10.3732 |  |  | 26.3169 |  |  | 54.2117 |  |  | 102.3186 |  |  | 190.9112 |  |  | 442.8522 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.0206 |  |  | 12.7318 |  |  | 32.1031 |  |  | 66.8982 |  |  | 138.121 |  |  | 575.3839 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.7094 | 5.7957 |  | 1.1318 | 72.0208 |  | 9.1031 | 178.1159 |  | 27.4982 | 346.9244 |  | 77.121 | 582.0312 |  | 487.1839 | 857.9853 |  | 5500 | 1144.9847 |  | 5500 | 1397.0989 |  | 5500 | 1621.9885 |  | 5500 | 1845.9742
[13 empty] | Next iteration flow rate |  |  | 5.9116 | Abs Value of | Flow this | 72.741 | Abs Value of | Flow this | 179.8971 | Abs Value of | Flow this | 350.3936 | Abs Value of | Flow this | 587.8515 | Abs Value of | Flow this | 866.5651 | Abs Value of | Flow this | 1156.4345 | Abs Value of | Flow this | 1411.0699 | Abs Value of | Flow this | 1638.2083 | Abs Value of | Flow this | 1864.4339 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.915 |  |  | 56.7374 |  |  | 55.8232 |  |  | 52.7697 |  |  | 45.2454 |  |  | 31.5553 |  |  | 11.751 |  |  | -10.3286 |  |  | -33.7197 |  |  | -60.4805
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6925 |  |  | 24.8754 |  |  | 25.4861 |  |  | 26.9909 |  |  | 29.7289 |  |  | 33.6898 |  |  | 38.1057 |  |  | 42.7839 |  |  | 48.1361
[13 empty] | Delta P at this iteration flow rate |  |  | 32.258 |  |  | 32.0449 |  |  | 30.9478 |  |  | 27.2837 |  |  | 18.2545 |  |  | 1.8263 |  |  | -21.9388 |  |  | -48.4344 |  |  | -76.5036 |  |  | -108.6166
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8976 |  |  | 48.2773 |  |  | 46.0732 |  |  | 41.6319 |  |  | 33.5949 |  |  | 21.6881 |  |  | 7.2591 |  |  | -6.2621 |  |  | -17.1228 |  |  | -22.9587
[13 empty] | C Non choked w/ reducers | 7 |  | 1.041 |  |  | 12.86 |  |  | 32.4377 |  |  | 67.6885 |  |  | 140.5527 |  |  | 669.7812 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.837 |  |  | 10.4773 |  |  | 26.5852 |  |  | 54.7966 |  |  | 103.6067 |  |  | 194.3625 |  |  | 464.5435 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.041 |  |  | 12.86 |  |  | 32.4377 |  |  | 67.6885 |  |  | 140.5527 |  |  | 669.7812 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.689 | 5.9116 |  | 1.26 | 72.741 |  | 9.4377 | 179.8971 |  | 28.2885 | 350.3936 |  | 79.5527 | 587.8515 |  | 581.5812 | 866.5651 |  | 5500 | 1156.4345 |  | 5500 | 1411.0699 |  | 5500 | 1638.2083 |  | 5500 | 1864.4339
[13 empty] | Next iteration flow rate |  |  | 6.0299 | Abs Value of | Flow this | 73.4684 | Abs Value of | Flow this | 181.6961 | Abs Value of | Flow this | 353.8976 | Abs Value of | Flow this | 593.73 | Abs Value of | Flow this | 875.2308 | Abs Value of | Flow this | 1167.9989 | Abs Value of | Flow this | 1425.1806 | Abs Value of | Flow this | 1654.5904 | Abs Value of | Flow this | 1883.0783 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9149 |  |  | 56.7339 |  |  | 55.8012 |  |  | 52.6864 |  |  | 45.0109 |  |  | 31.0455 |  |  | 10.8431 |  |  | -11.6803 |  |  | -35.5415 |  |  | -62.8401
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6932 |  |  | 24.8798 |  |  | 25.5027 |  |  | 27.0378 |  |  | 29.8309 |  |  | 33.8714 |  |  | 38.3761 |  |  | 43.1483 |  |  | 48.608
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2579 |  |  | 32.0406 |  |  | 30.9214 |  |  | 27.1836 |  |  | 17.973 |  |  | 1.2146 |  |  | -23.0282 |  |  | -50.0563 |  |  | -78.6897 |  |  | -111.4482
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8976 |  |  | 48.2742 |  |  | 46.055 |  |  | 41.5655 |  |  | 33.419 |  |  | 21.3328 |  |  | 6.6764 |  |  | -7.048 |  |  | -18.036 |  |  | -23.848
[13 empty] | C Non choked w/ reducers | 7 |  | 1.0618 |  |  | 12.9895 |  |  | 32.776 |  |  | 68.491 |  |  | 143.0656 |  |  | 829.5111 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.85374 |  |  | 10.5824 |  |  | 26.8564 |  |  | 55.3886 |  |  | 104.9178 |  |  | 197.9341 |  |  | 489.2325 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.0618 |  |  | 12.9895 |  |  | 32.776 |  |  | 68.491 |  |  | 143.0656 |  |  | 829.5111 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.6682 | 6.0299 |  | 1.3895 | 73.4684 |  | 9.776 | 181.6961 |  | 29.091 | 353.8976 |  | 82.0656 | 593.73 |  | 741.3111 | 875.2308 |  | 5500 | 1167.9989 |  | 5500 | 1425.1806 |  | 5500 | 1654.5904 |  | 5500 | 1883.0783
[13 empty] | Next iteration flow rate |  |  | 6.1505 | Abs Value of | Flow this | 74.2031 | Abs Value of | Flow this | 183.513 | Abs Value of | Flow this | 357.4365 | Abs Value of | Flow this | 599.6673 | Abs Value of | Flow this | 883.9831 | Abs Value of | Flow this | 1179.6789 | Abs Value of | Flow this | 1439.4324 | Abs Value of | Flow this | 1671.1363 | Abs Value of | Flow this | 1901.909 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9149 |  |  | 56.7302 |  |  | 55.7788 |  |  | 52.6014 |  |  | 44.7716 |  |  | 30.5255 |  |  | 9.9171 |  |  | -13.0591 |  |  | -37.3999 |  |  | -65.2472
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.694 |  |  | 24.8842 |  |  | 25.5197 |  |  | 27.0857 |  |  | 29.9349 |  |  | 34.0566 |  |  | 38.6518 |  |  | 43.52 |  |  | 49.0894
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2578 |  |  | 32.0362 |  |  | 30.8945 |  |  | 27.0816 |  |  | 17.6859 |  |  | 0.59063 |  |  | -24.1395 |  |  | -51.7109 |  |  | -80.9198 |  |  | -114.3367
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8975 |  |  | 48.2711 |  |  | 46.0363 |  |  | 41.4979 |  |  | 33.2396 |  |  | 20.9704 |  |  | 6.0821 |  |  | -7.8498 |  |  | -18.9675 |  |  | -24.7551
[13 empty] | C Non choked w/ reducers | 7 |  | 1.083 |  |  | 13.1203 |  |  | 33.1182 |  |  | 69.3061 |  |  | 145.6646 |  |  | 1201.4536 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.87081 |  |  | 10.6886 |  |  | 27.1304 |  |  | 55.9881 |  |  | 106.2525 |  |  | 201.6337 |  |  | 517.7045 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.083 |  |  | 13.1203 |  |  | 33.1182 |  |  | 69.3061 |  |  | 145.6646 |  |  | 1201.4536 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.647 | 6.1505 |  | 1.5203 | 74.2031 |  | 10.1182 | 183.513 |  | 29.9061 | 357.4365 |  | 84.6646 | 599.6673 |  | 1113.2536 | 883.9831 |  | 5500 | 1179.6789 |  | 5500 | 1439.4324 |  | 5500 | 1671.1363 |  | 5500 | 1901.909
[13 empty] | Next iteration flow rate |  |  | 6.2735 | Abs Value of | Flow this | 74.9451 | Abs Value of | Flow this | 185.3482 | Abs Value of | Flow this | 361.0109 | Abs Value of | Flow this | 605.664 | Abs Value of | Flow this | 892.8229 | Abs Value of | Flow this | 1191.4757 | Abs Value of | Flow this | 1453.8267 | Abs Value of | Flow this | 1687.8477 | Abs Value of | Flow this | 1920.9281 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9148 |  |  | 56.7265 |  |  | 55.7559 |  |  | 52.5146 |  |  | 44.5275 |  |  | 29.9951 |  |  | 8.9724 |  |  | -14.4656 |  |  | -39.2956 |  |  | -67.7027
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6947 |  |  | 24.8888 |  |  | 25.5371 |  |  | 27.1345 |  |  | 30.041 |  |  | 34.2455 |  |  | 38.9331 |  |  | 43.8991 |  |  | 49.5805
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2578 |  |  | 32.0317 |  |  | 30.8671 |  |  | 26.9776 |  |  | 17.393 |  |  | -0.045908 |  |  | -25.2731 |  |  | -53.3987 |  |  | -83.1947 |  |  | -117.2833
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8975 |  |  | 48.2679 |  |  | 46.0173 |  |  | 41.4289 |  |  | 33.0566 |  |  | 20.6006 |  |  | 5.4758 |  |  | -8.6677 |  |  | -19.9177 |  |  | -25.6805
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1047 |  |  | 13.2524 |  |  | 33.4642 |  |  | 70.1341 |  |  | 148.3549 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.88823 |  |  | 10.7958 |  |  | 27.4074 |  |  | 56.5951 |  |  | 107.6118 |  |  | 205.4695 |  |  | 551.0679 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.1047 |  |  | 13.2524 |  |  | 33.4642 |  |  | 70.1341 |  |  | 148.3549 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.6253 | 6.2735 |  | 1.6524 | 74.9451 |  | 10.4642 | 185.3482 |  | 30.7341 | 361.0109 |  | 87.3549 | 605.664 |  | 5500 | 892.8229 |  | 5500 | 1191.4757 |  | 5500 | 1453.8267 |  | 5500 | 1687.8477 |  | 5500 | 1920.9281
[13 empty] | Next iteration flow rate |  |  | 6.3989 | Abs Value of | Flow this | 75.6946 | Abs Value of | Flow this | 187.2016 | Abs Value of | Flow this | 364.621 | Abs Value of | Flow this | 611.7206 | Abs Value of | Flow this | 901.7512 | Abs Value of | Flow this | 1203.3904 | Abs Value of | Flow this | 1468.365 | Abs Value of | Flow this | 1704.7262 | Abs Value of | Flow this | 1940.1374 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9148 |  |  | 56.7226 |  |  | 55.7326 |  |  | 52.4262 |  |  | 44.2784 |  |  | 29.454 |  |  | 8.0087 |  |  | -15.9003 |  |  | -41.2295 |  |  | -70.2076
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6955 |  |  | 24.8935 |  |  | 25.5548 |  |  | 27.1843 |  |  | 30.1492 |  |  | 34.4383 |  |  | 39.2201 |  |  | 44.2859 |  |  | 50.0815
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2577 |  |  | 32.0272 |  |  | 30.8391 |  |  | 26.8714 |  |  | 17.0941 |  |  | -0.69524 |  |  | -26.4295 |  |  | -55.1204 |  |  | -85.5154 |  |  | -120.2891
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8974 |  |  | 48.2646 |  |  | 45.9979 |  |  | 41.3585 |  |  | 32.8699 |  |  | 20.2234 |  |  | 4.8574 |  |  | -9.502 |  |  | -20.8871 |  |  | -26.6245
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1268 |  |  | 13.3859 |  |  | 33.8142 |  |  | 70.9752 |  |  | 151.1424 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.90599 |  |  | 10.9042 |  |  | 27.6873 |  |  | 57.2096 |  |  | 108.9961 |  |  | 209.4504 |  |  | 590.95 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.1268 |  |  | 13.3859 |  |  | 33.8142 |  |  | 70.9752 |  |  | 151.1424 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.6032 | 6.3989 |  | 1.7859 | 75.6946 |  | 10.8142 | 187.2016 |  | 31.5752 | 364.621 |  | 90.1424 | 611.7206 |  | 5500 | 901.7512 |  | 5500 | 1203.3904 |  | 5500 | 1468.365 |  | 5500 | 1704.7262 |  | 5500 | 1940.1374
[13 empty] | Next iteration flow rate |  |  | 6.5269 | Abs Value of | Flow this | 76.4515 | Abs Value of | Flow this | 189.0737 | Abs Value of | Flow this | 368.2672 | Abs Value of | Flow this | 617.8378 | Abs Value of | Flow this | 910.7687 | Abs Value of | Flow this | 1215.4243 | Abs Value of | Flow this | 1483.0486 | Abs Value of | Flow this | 1721.7734 | Abs Value of | Flow this | 1959.5388 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9147 |  |  | 56.7187 |  |  | 55.7088 |  |  | 52.3359 |  |  | 44.0244 |  |  | 28.902 |  |  | 7.0257 |  |  | -17.3639 |  |  | -43.2022 |  |  | -72.7628
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.6963 |  |  | 24.8982 |  |  | 25.5728 |  |  | 27.2351 |  |  | 30.2596 |  |  | 34.6349 |  |  | 39.5128 |  |  | 44.6804 |  |  | 50.5926
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2576 |  |  | 32.0225 |  |  | 30.8106 |  |  | 26.7631 |  |  | 16.7893 |  |  | -1.3576 |  |  | -27.6092 |  |  | -56.8767 |  |  | -87.8826 |  |  | -123.3553
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8974 |  |  | 48.2613 |  |  | 45.9781 |  |  | 41.2867 |  |  | 32.6794 |  |  | 19.8387 |  |  | 4.2265 |  |  | -10.3531 |  |  | -21.8759 |  |  | -27.5874
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1493 |  |  | 13.5207 |  |  | 34.1681 |  |  | 71.8298 |  |  | 154.0334 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.92412 |  |  | 11.0136 |  |  | 27.9702 |  |  | 57.8319 |  |  | 110.4064 |  |  | 213.5864 |  |  | 639.8574 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.1493 |  |  | 13.5207 |  |  | 34.1681 |  |  | 71.8298 |  |  | 154.0334 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.5807 | 6.5269 |  | 1.9207 | 76.4515 |  | 11.1681 | 189.0737 |  | 32.4298 | 368.2672 |  | 93.0334 | 617.8378 |  | 5500 | 910.7687 |  | 5500 | 1215.4243 |  | 5500 | 1483.0486 |  | 5500 | 1721.7734 |  | 5500 | 1959.5388
[13 empty] | Next iteration flow rate |  |  | 6.6575 | Abs Value of | Flow this | 77.216 | Abs Value of | Flow this | 190.9644 | Abs Value of | Flow this | 371.9499 | Abs Value of | Flow this | 624.0162 | Abs Value of | Flow this | 919.8764 | Abs Value of | Flow this | 1227.5786 | Abs Value of | Flow this | 1497.8791 | Abs Value of | Flow this | 1738.9912 | Abs Value of | Flow this | 1979.1342 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9146 |  |  | 56.7148 |  |  | 55.6846 |  |  | 52.2438 |  |  | 43.7653 |  |  | 28.3389 |  |  | 6.0229 |  |  | -18.857 |  |  | -45.2146 |  |  | -75.3693
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.697 |  |  | 24.9031 |  |  | 25.5912 |  |  | 27.2869 |  |  | 30.3722 |  |  | 34.8354 |  |  | 39.8114 |  |  | 45.0829 |  |  | 51.1139
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2576 |  |  | 32.0177 |  |  | 30.7815 |  |  | 26.6526 |  |  | 16.4784 |  |  | -2.0333 |  |  | -28.8125 |  |  | -58.6684 |  |  | -90.2975 |  |  | -126.4832
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8973 |  |  | 48.2579 |  |  | 45.9579 |  |  | 41.2135 |  |  | 32.4851 |  |  | 19.4462 |  |  | 3.5829 |  |  | -11.2213 |  |  | -22.8847 |  |  | -28.5698
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1723 |  |  | 13.657 |  |  | 34.5261 |  |  | 72.6983 |  |  | 157.0347 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.9426 |  |  | 11.1241 |  |  | 28.2561 |  |  | 58.4621 |  |  | 111.8434 |  |  | 217.8884 |  |  | 701.9011 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.1723 |  |  | 13.657 |  |  | 34.5261 |  |  | 72.6983 |  |  | 157.0347 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.5577 | 6.6575 |  | 2.057 | 77.216 |  | 11.5261 | 190.9644 |  | 33.2983 | 371.9499 |  | 96.0347 | 624.0162 |  | 5500 | 919.8764 |  | 5500 | 1227.5786 |  | 5500 | 1497.8791 |  | 5500 | 1738.9912 |  | 5500 | 1979.1342
[13 empty] | Next iteration flow rate |  |  | 6.7906 | Abs Value of | Flow this | 77.9882 | Abs Value of | Flow this | 192.874 | Abs Value of | Flow this | 375.6694 | Abs Value of | Flow this | 630.2564 | Abs Value of | Flow this | 929.0751 | Abs Value of | Flow this | 1239.8543 | Abs Value of | Flow this | 1512.8579 | Abs Value of | Flow this | 1756.3811 | Abs Value of | Flow this | 1998.9255 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9146 |  |  | 56.7107 |  |  | 55.6598 |  |  | 52.1499 |  |  | 43.501 |  |  | 27.7645 |  |  | 4.9999 |  |  | -20.38 |  |  | -47.2674 |  |  | -78.0282
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.6979 |  |  | 24.908 |  |  | 25.61 |  |  | 27.3398 |  |  | 30.4871 |  |  | 35.04 |  |  | 40.116 |  |  | 45.4935 |  |  | 51.6456
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2575 |  |  | 32.0129 |  |  | 30.7518 |  |  | 26.5399 |  |  | 16.1612 |  |  | -2.7226 |  |  | -30.0401 |  |  | -60.496 |  |  | -92.7609 |  |  | -129.6739
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8973 |  |  | 48.2544 |  |  | 45.9373 |  |  | 41.1388 |  |  | 32.2869 |  |  | 19.0458 |  |  | 2.9264 |  |  | -12.107 |  |  | -23.9137 |  |  | -29.5718
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1958 |  |  | 13.7946 |  |  | 34.8882 |  |  | 73.581 |  |  | 160.154 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.96145 |  |  | 11.2358 |  |  | 28.5451 |  |  | 59.1004 |  |  | 113.3081 |  |  | 222.3683 |  |  | 784.4188 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.1958 |  |  | 13.7946 |  |  | 34.8882 |  |  | 73.581 |  |  | 160.154 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.5342 | 6.7906 |  | 2.1946 | 77.9882 |  | 11.8882 | 192.874 |  | 34.181 | 375.6694 |  | 99.154 | 630.2564 |  | 5500 | 929.0751 |  | 5500 | 1239.8543 |  | 5500 | 1512.8579 |  | 5500 | 1756.3811 |  | 5500 | 1998.9255
[13 empty] | Next iteration flow rate |  |  | 6.9264 | Abs Value of | Flow this | 78.7681 | Abs Value of | Flow this | 194.8028 | Abs Value of | Flow this | 379.4261 | Abs Value of | Flow this | 636.5589 | Abs Value of | Flow this | 938.3659 | Abs Value of | Flow this | 1252.2529 | Abs Value of | Flow this | 1527.9865 | Abs Value of | Flow this | 1773.9449 | Abs Value of | Flow this | 2018.9148 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9145 |  |  | 56.7066 |  |  | 55.6345 |  |  | 52.0541 |  |  | 43.2313 |  |  | 27.1785 |  |  | 3.9564 |  |  | -21.9337 |  |  | -49.3615 |  |  | -80.7406
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.6987 |  |  | 24.9131 |  |  | 25.6292 |  |  | 27.3937 |  |  | 30.6043 |  |  | 35.2487 |  |  | 40.4267 |  |  | 45.9123 |  |  | 52.1881
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2574 |  |  | 32.0079 |  |  | 30.7215 |  |  | 26.425 |  |  | 15.8376 |  |  | -3.4258 |  |  | -31.2923 |  |  | -62.3604 |  |  | -95.2738 |  |  | -132.9287
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8972 |  |  | 48.2508 |  |  | 45.9163 |  |  | 41.0626 |  |  | 32.0847 |  |  | 18.6374 |  |  | 2.2567 |  |  | -13.0104 |  |  | -24.9633 |  |  | -30.594
[13 empty] | C Non choked w/ reducers | 7 |  | 1.2197 |  |  | 13.9336 |  |  | 35.2545 |  |  | 74.4783 |  |  | 163.3995 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.98068 |  |  | 11.3485 |  |  | 28.8371 |  |  | 59.7467 |  |  | 114.8011 |  |  | 227.0395 |  |  | 902.1923 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.2197 |  |  | 13.9336 |  |  | 35.2545 |  |  | 74.4783 |  |  | 163.3995 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.5103 | 6.9264 |  | 2.3336 | 78.7681 |  | 12.2545 | 194.8028 |  | 35.0783 | 379.4261 |  | 102.3995 | 636.5589 |  | 5500 | 938.3659 |  | 5500 | 1252.2529 |  | 5500 | 1527.9865 |  | 5500 | 1773.9449 |  | 5500 | 2018.9148
[13 empty] | Next iteration flow rate |  |  | 7.0649 | Abs Value of | Flow this | 79.5557 | Abs Value of | Flow this | 196.7508 | Abs Value of | Flow this | 383.2203 | Abs Value of | Flow this | 642.9245 | Abs Value of | Flow this | 947.7495 | Abs Value of | Flow this | 1264.7754 | Abs Value of | Flow this | 1543.2664 | Abs Value of | Flow this | 1791.6843 | Abs Value of | Flow this | 2039.1039 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9145 |  |  | 56.7024 |  |  | 55.6088 |  |  | 51.9564 |  |  | 42.9563 |  |  | 26.5808 |  |  | 2.8919 |  |  | -23.5185 |  |  | -51.4977 |  |  | -83.5075
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.6995 |  |  | 24.9182 |  |  | 25.6487 |  |  | 27.4487 |  |  | 30.7238 |  |  | 35.4616 |  |  | 40.7437 |  |  | 46.3395 |  |  | 52.7415
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2573 |  |  | 32.0029 |  |  | 30.6905 |  |  | 26.3077 |  |  | 15.5075 |  |  | -4.143 |  |  | -32.5697 |  |  | -64.2623 |  |  | -97.8372 |  |  | -136.249
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8972 |  |  | 48.2472 |  |  | 45.8949 |  |  | 40.9848 |  |  | 31.8785 |  |  | 18.2208 |  |  | 1.5736 |  |  | -13.932 |  |  | -26.0341 |  |  | -31.6368
[13 empty] | C Non choked w/ reducers | 7 |  | 1.2441 |  |  | 14.074 |  |  | 35.625 |  |  | 75.3906 |  |  | 166.7807 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.0003 |  |  | 11.4624 |  |  | 29.1323 |  |  | 60.4014 |  |  | 116.3236 |  |  | 231.9168 |  |  | 1091.235 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.2441 |  |  | 14.074 |  |  | 35.625 |  |  | 75.3906 |  |  | 166.7807 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.4859 | 7.0649 |  | 2.474 | 79.5557 |  | 12.625 | 196.7508 |  | 35.9906 | 383.2203 |  | 105.7807 | 642.9245 |  | 5500 | 947.7495 |  | 5500 | 1264.7754 |  | 5500 | 1543.2664 |  | 5500 | 1791.6843 |  | 5500 | 2039.1039
[13 empty] | Next iteration flow rate |  |  | 7.2062 | Abs Value of | Flow this | 80.3513 | Abs Value of | Flow this | 198.7183 | Abs Value of | Flow this | 387.0526 | Abs Value of | Flow this | 649.3538 | Abs Value of | Flow this | 957.227 | Abs Value of | Flow this | 1277.4232 | Abs Value of | Flow this | 1558.699 | Abs Value of | Flow this | 1809.6012 | Abs Value of | Flow this | 2059.495 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9144 |  |  | 56.6981 |  |  | 55.5825 |  |  | 51.8567 |  |  | 42.6757 |  |  | 25.9711 |  |  | 1.806 |  |  | -25.1353 |  |  | -53.6768 |  |  | -86.33
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.7004 |  |  | 24.9235 |  |  | 25.6687 |  |  | 27.5049 |  |  | 30.8458 |  |  | 35.6788 |  |  | 41.0671 |  |  | 46.7754 |  |  | 53.306
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2573 |  |  | 31.9977 |  |  | 30.659 |  |  | 26.1881 |  |  | 15.1708 |  |  | -4.8747 |  |  | -33.8727 |  |  | -66.2023 |  |  | -100.4521 |  |  | -139.636
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8971 |  |  | 48.2435 |  |  | 45.873 |  |  | 40.9055 |  |  | 31.6681 |  |  | 17.7958 |  |  | 0.87666 |  |  | -14.8722 |  |  | -27.1264 |  |  | -32.7005
[13 empty] | C Non choked w/ reducers | 7 |  | 1.269 |  |  | 14.2159 |  |  | 35.9997 |  |  | 76.3182 |  |  | 170.3075 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.0203 |  |  | 11.5775 |  |  | 29.4306 |  |  | 61.0645 |  |  | 117.8765 |  |  | 237.0165 |  |  | 1476.6083 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.269 |  |  | 14.2159 |  |  | 35.9997 |  |  | 76.3182 |  |  | 170.3075 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.461 | 7.2062 |  | 2.6159 | 80.3513 |  | 12.9997 | 198.7183 |  | 36.9182 | 387.0526 |  | 109.3075 | 649.3538 |  | 5500 | 957.227 |  | 5500 | 1277.4232 |  | 5500 | 1558.699 |  | 5500 | 1809.6012 |  | 5500 | 2059.495
[13 empty] | Next iteration flow rate |  |  | 7.3504 | Abs Value of | Flow this | 81.1548 | Abs Value of | Flow this | 200.7055 | Abs Value of | Flow this | 390.9231 | Abs Value of | Flow this | 655.8473 | Abs Value of | Flow this | 966.7993 | Abs Value of | Flow this | 1290.1974 | Abs Value of | Flow this | 1574.286 | Abs Value of | Flow this | 1827.6972 | Abs Value of | Flow this | 2080.0899 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9143 |  |  | 56.6937 |  |  | 55.5557 |  |  | 51.755 |  |  | 42.3894 |  |  | 25.3491 |  |  | 0.69833 |  |  | -26.7845 |  |  | -55.8997 |  |  | -89.2093
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.7013 |  |  | 24.9289 |  |  | 25.689 |  |  | 27.5621 |  |  | 30.9702 |  |  | 35.9003 |  |  | 41.3969 |  |  | 47.2199 |  |  | 53.8819
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2572 |  |  | 31.9925 |  |  | 30.6268 |  |  | 26.066 |  |  | 14.8273 |  |  | -5.6211 |  |  | -35.202 |  |  | -68.1814 |  |  | -103.1196 |  |  | -143.0911
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.897 |  |  | 48.2398 |  |  | 45.8507 |  |  | 40.8246 |  |  | 31.4535 |  |  | 17.3622 |  |  | 0.16575 |  |  | -15.8312 |  |  | -28.2406 |  |  | -33.7855
[13 empty] | C Non choked w/ reducers | 7 |  | 1.2944 |  |  | 14.3593 |  |  | 36.3788 |  |  | 77.2616 |  |  | 173.9916 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.0407 |  |  | 11.6937 |  |  | 29.7322 |  |  | 61.7363 |  |  | 119.4607 |  |  | 242.3571 |  |  | 3429.7964 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.2944 |  |  | 14.3593 |  |  | 36.3788 |  |  | 77.2616 |  |  | 173.9916 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.4356 | 7.3504 |  | 2.7593 | 81.1548 |  | 13.3788 | 200.7055 |  | 37.8616 | 390.9231 |  | 112.9916 | 655.8473 |  | 5500 | 966.7993 |  | 5500 | 1290.1974 |  | 5500 | 1574.286 |  | 5500 | 1827.6972 |  | 5500 | 2080.0899
[13 empty] | Next iteration flow rate |  |  | 7.4974 | Abs Value of | Flow this | 81.9664 | Abs Value of | Flow this | 202.7126 | Abs Value of | Flow this | 394.8323 | Abs Value of | Flow this | 662.4058 | Abs Value of | Flow this | 976.4673 | Abs Value of | Flow this | 1303.0994 | Abs Value of | Flow this | 1590.0289 | Abs Value of | Flow this | 1845.9742 | Abs Value of | Flow this | 2100.8908 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9142 |  |  | 56.6892 |  |  | 55.5284 |  |  | 51.6513 |  |  | 42.0975 |  |  | 24.7146 |  |  | -0.43164 |  |  | -28.4669 |  |  | -58.1673 |  |  | -92.1464
[13 empty] | P2 at this iteration flow rate |  |  | 24.6572 |  |  | 24.7022 |  |  | 24.9343 |  |  | 25.7097 |  |  | 27.6205 |  |  | 31.0971 |  |  | 36.1263 |  |  | 41.7334 |  |  | 47.6735 |  |  | 54.4693
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2571 |  |  | 31.9871 |  |  | 30.594 |  |  | 25.9415 |  |  | 14.4769 |  |  | -6.3825 |  |  | -36.558 |  |  | -70.2003 |  |  | -105.8408 |  |  | -146.6157
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.897 |  |  | 48.236 |  |  | 45.828 |  |  | 40.7421 |  |  | 31.2346 |  |  | 16.92 |  |  | -0.55944 |  |  | -16.8095 |  |  | -29.3773 |  |  | -34.8924
[13 empty] | C Non choked w/ reducers | 7 |  | 1.3202 |  |  | 14.5041 |  |  | 36.7623 |  |  | 78.2213 |  |  | 177.8454 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.0615 |  |  | 11.8111 |  |  | 30.0369 |  |  | 62.4167 |  |  | 121.0775 |  |  | 247.9591 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.3202 |  |  | 14.5041 |  |  | 36.7623 |  |  | 78.2213 |  |  | 177.8454 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.4098 | 7.4974 |  | 2.9041 | 81.9664 |  | 13.7623 | 202.7126 |  | 38.8213 | 394.8323 |  | 116.8454 | 662.4058 |  | 5500 | 976.4673 |  | 5500 | 1303.0994 |  | 5500 | 1590.0289 |  | 5500 | 1845.9742 |  | 5500 | 2100.8908
[13 empty] | Next iteration flow rate |  |  | 7.6473 | Abs Value of | Flow this | 82.786 | Abs Value of | Flow this | 204.7397 | Abs Value of | Flow this | 398.7806 | Abs Value of | Flow this | 669.0298 | Abs Value of | Flow this | 986.232 | Abs Value of | Flow this | 1316.1304 | Abs Value of | Flow this | 1605.9292 | Abs Value of | Flow this | 1864.4339 | Abs Value of | Flow this | 2121.8997 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9142 |  |  | 56.6847 |  |  | 55.5005 |  |  | 51.5455 |  |  | 41.7996 |  |  | 24.0673 |  |  | -1.5843 |  |  | -30.1831 |  |  | -60.4805 |  |  | -95.1426
[13 empty] | P2 at this iteration flow rate |  |  | 24.6572 |  |  | 24.7031 |  |  | 24.9399 |  |  | 25.7309 |  |  | 27.6801 |  |  | 31.2265 |  |  | 36.3569 |  |  | 42.0766 |  |  | 48.1361 |  |  | 55.0685
[13 empty] | Delta P at this iteration flow rate |  |  | 32.257 |  |  | 31.9816 |  |  | 30.5606 |  |  | 25.8145 |  |  | 14.1195 |  |  | -7.1592 |  |  | -37.9412 |  |  | -72.2597 |  |  | -108.6166 |  |  | -150.2111
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8969 |  |  | 48.232 |  |  | 45.8048 |  |  | 40.6579 |  |  | 31.0112 |  |  | 16.4688 |  |  | -1.2992 |  |  | -17.8075 |  |  | -30.5368 |  |  | -36.0216
[13 empty] | C Non choked w/ reducers | 7 |  | 1.3466 |  |  | 14.6504 |  |  | 37.1502 |  |  | 79.1975 |  |  | 181.8831 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.0828 |  |  | 11.9297 |  |  | 30.345 |  |  | 63.1061 |  |  | 122.7278 |  |  | 253.8458 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.3466 |  |  | 14.6504 |  |  | 37.1502 |  |  | 79.1975 |  |  | 181.8831 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.3834 | 7.6473 |  | 3.0504 | 82.786 |  | 14.1502 | 204.7397 |  | 39.7975 | 398.7806 |  | 120.8831 | 669.0298 |  | 5500 | 986.232 |  | 5500 | 1316.1304 |  | 5500 | 1605.9292 |  | 5500 | 1864.4339 |  | 5500 | 2121.8997
[13 empty] | Next iteration flow rate |  |  | 7.8003 | Abs Value of | Flow this | 83.6139 | Abs Value of | Flow this | 206.7871 | Abs Value of | Flow this | 402.7684 | Abs Value of | Flow this | 675.7201 | Abs Value of | Flow this | 996.0943 | Abs Value of | Flow this | 1329.2917 | Abs Value of | Flow this | 1621.9885 | Abs Value of | Flow this | 1883.0783 | Abs Value of | Flow this | 2143.1187 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9141 |  |  | 56.68 |  |  | 55.472 |  |  | 51.4375 |  |  | 41.4958 |  |  | 23.4071 |  |  | -2.7602 |  |  | -31.9338 |  |  | -62.8401 |  |  | -98.1989
[13 empty] | P2 at this iteration flow rate |  |  | 24.6572 |  |  | 24.704 |  |  | 24.9456 |  |  | 25.7525 |  |  | 27.7408 |  |  | 31.3586 |  |  | 36.592 |  |  | 42.4268 |  |  | 48.608 |  |  | 55.6798
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2569 |  |  | 31.976 |  |  | 30.5264 |  |  | 25.685 |  |  | 13.7549 |  |  | -7.9515 |  |  | -39.3522 |  |  | -74.3606 |  |  | -111.4482 |  |  | -153.8787
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8968 |  |  | 48.2281 |  |  | 45.7811 |  |  | 40.572 |  |  | 30.7834 |  |  | 16.0086 |  |  | -2.0538 |  |  | -18.8256 |  |  | -31.7196 |  |  | -37.1734
[13 empty] | C Non choked w/ reducers | 7 |  | 1.3736 |  |  | 14.7982 |  |  | 37.5427 |  |  | 80.191 |  |  | 186.1208 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.1044 |  |  | 12.0495 |  |  | 30.6564 |  |  | 63.8046 |  |  | 124.4129 |  |  | 260.0434 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.3736 |  |  | 14.7982 |  |  | 37.5427 |  |  | 80.191 |  |  | 186.1208 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.3564 | 7.8003 |  | 3.1982 | 83.6139 |  | 14.5427 | 206.7871 |  | 40.791 | 402.7684 |  | 125.1208 | 675.7201 |  | 5500 | 996.0943 |  | 5500 | 1329.2917 |  | 5500 | 1621.9885 |  | 5500 | 1883.0783 |  | 5500 | 2143.1187
[13 empty] | Next iteration flow rate |  |  | 7.9563 | Abs Value of | Flow this | 84.45 | Abs Value of | Flow this | 208.8549 | Abs Value of | Flow this | 406.7961 | Abs Value of | Flow this | 682.4773 | Abs Value of | Flow this | 1006.0552 | Abs Value of | Flow this | 1342.5846 | Abs Value of | Flow this | 1638.2083 | Abs Value of | Flow this | 1901.909 | Abs Value of | Flow this | 2164.5499 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.914 |  |  | 56.6753 |  |  | 55.443 |  |  | 51.3274 |  |  | 41.1858 |  |  | 22.7335 |  |  | -3.9597 |  |  | -33.7197 |  |  | -65.2472 |  |  | -101.3168
[13 empty] | P2 at this iteration flow rate |  |  | 24.6572 |  |  | 24.7049 |  |  | 24.9514 |  |  | 25.7745 |  |  | 27.8028 |  |  | 31.4933 |  |  | 36.8319 |  |  | 42.7839 |  |  | 49.0894 |  |  | 56.3034
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2568 |  |  | 31.9703 |  |  | 30.4916 |  |  | 25.5529 |  |  | 13.383 |  |  | -8.7598 |  |  | -40.7916 |  |  | -76.5036 |  |  | -114.3367 |  |  | -157.6201
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8968 |  |  | 48.224 |  |  | 45.7569 |  |  | 40.4844 |  |  | 30.551 |  |  | 15.5391 |  |  | -2.8236 |  |  | -19.8641 |  |  | -32.9262 |  |  | -38.3484
[13 empty] | C Non choked w/ reducers | 7 |  | 1.4011 |  |  | 14.9475 |  |  | 37.9398 |  |  | 81.202 |  |  | 190.5763 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.1265 |  |  | 12.1705 |  |  | 30.9711 |  |  | 64.5124 |  |  | 126.134 |  |  | 266.5819 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.4011 |  |  | 14.9475 |  |  | 37.9398 |  |  | 81.202 |  |  | 190.5763 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.3289 | 7.9563 |  | 3.3475 | 84.45 |  | 14.9398 | 208.8549 |  | 41.802 | 406.7961 |  | 129.5763 | 682.4773 |  | 5500 | 1006.0552 |  | 5500 | 1342.5846 |  | 5500 | 1638.2083 |  | 5500 | 1901.909 |  | 5500 | 2164.5499
[13 empty] | Next iteration flow rate |  |  | 8.1154 | Abs Value of | Flow this | 85.2945 | Abs Value of | Flow this | 210.9435 | Abs Value of | Flow this | 410.8641 | Abs Value of | Flow this | 689.3021 | Abs Value of | Flow this | 1016.1158 | Abs Value of | Flow this | 1356.0104 | Abs Value of | Flow this | 1654.5904 | Abs Value of | Flow this | 1920.9281 | Abs Value of | Flow this | 2186.1954 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9139 |  |  | 56.6704 |  |  | 55.4134 |  |  | 51.2151 |  |  | 40.8696 |  |  | 22.0465 |  |  | -5.1833 |  |  | -35.5415 |  |  | -67.7027 |  |  | -104.4972
[13 empty] | P2 at this iteration flow rate |  |  | 24.6572 |  |  | 24.7059 |  |  | 24.9573 |  |  | 25.797 |  |  | 27.8661 |  |  | 31.6307 |  |  | 37.0767 |  |  | 43.1483 |  |  | 49.5805 |  |  | 56.9394
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2567 |  |  | 31.9645 |  |  | 30.456 |  |  | 25.4181 |  |  | 13.0035 |  |  | -9.5842 |  |  | -42.26 |  |  | -78.6897 |  |  | -117.2833 |  |  | -161.4367
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8967 |  |  | 48.2198 |  |  | 45.7323 |  |  | 40.395 |  |  | 30.3139 |  |  | 15.0602 |  |  | -3.6089 |  |  | -20.9234 |  |  | -34.157 |  |  | -39.547
[13 empty] | C Non choked w/ reducers | 7 |  | 1.4291 |  |  | 15.0983 |  |  | 38.3416 |  |  | 82.2312 |  |  | 195.27 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.149 |  |  | 12.2928 |  |  | 31.2892 |  |  | 65.2295 |  |  | 127.8926 |  |  | 273.4951 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.4291 |  |  | 15.0983 |  |  | 38.3416 |  |  | 82.2312 |  |  | 195.27 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.3009 | 8.1154 |  | 3.4983 | 85.2945 |  | 15.3416 | 210.9435 |  | 42.8312 | 410.8641 |  | 134.27 | 689.3021 |  | 5500 | 1016.1158 |  | 5500 | 1356.0104 |  | 5500 | 1654.5904 |  | 5500 | 1920.9281 |  | 5500 | 2186.1954
[13 empty] | Next iteration flow rate |  |  | 8.2777 | Abs Value of | Flow this | 86.1475 | Abs Value of | Flow this | 213.0529 | Abs Value of | Flow this | 414.9727 | Abs Value of | Flow this | 696.1951 | Abs Value of | Flow this | 1026.2769 | Abs Value of | Flow this | 1369.5705 | Abs Value of | Flow this | 1671.1363 | Abs Value of | Flow this | 1940.1374 | Abs Value of | Flow this | 2208.0573 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9138 |  |  | 56.6655 |  |  | 55.3832 |  |  | 51.1005 |  |  | 40.5471 |  |  | 21.3456 |  |  | -6.4315 |  |  | -37.3999 |  |  | -70.2076 |  |  | -107.7416
[13 empty] | P2 at this iteration flow rate |  |  | 24.6572 |  |  | 24.7069 |  |  | 24.9634 |  |  | 25.8199 |  |  | 27.9306 |  |  | 31.7709 |  |  | 37.3263 |  |  | 43.52 |  |  | 50.0815 |  |  | 57.5883
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2566 |  |  | 31.9586 |  |  | 30.4198 |  |  | 25.2806 |  |  | 12.6165 |  |  | -10.4253 |  |  | -43.7578 |  |  | -80.9198 |  |  | -120.2891 |  |  | -165.33
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8966 |  |  | 48.2156 |  |  | 45.7072 |  |  | 40.3038 |  |  | 30.0721 |  |  | 14.5717 |  |  | -4.41 |  |  | -22.0041 |  |  | -35.4126 |  |  | -40.7697
[13 empty] | C Non choked w/ reducers | 7 |  | 1.4577 |  |  | 15.2507 |  |  | 38.748 |  |  | 83.2791 |  |  | 200.225 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.172 |  |  | 12.4162 |  |  | 31.6108 |  |  | 65.9563 |  |  | 129.6898 |  |  | 280.8224 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.4577 |  |  | 15.2507 |  |  | 38.748 |  |  | 83.2791 |  |  | 200.225 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.2723 | 8.2777 |  | 3.6507 | 86.1475 |  | 15.748 | 213.0529 |  | 43.8791 | 414.9727 |  | 139.225 | 696.1951 |  | 5500 | 1026.2769 |  | 5500 | 1369.5705 |  | 5500 | 1671.1363 |  | 5500 | 1940.1374 |  | 5500 | 2208.0573
[13 empty] | Next iteration flow rate |  |  | 8.4433 | Abs Value of | Flow this | 87.0089 | Abs Value of | Flow this | 215.1835 | Abs Value of | Flow this | 419.1225 | Abs Value of | Flow this | 703.1571 | Abs Value of | Flow this | 1036.5397 | Abs Value of | Flow this | 1383.2662 | Abs Value of | Flow this | 1687.8477 | Abs Value of | Flow this | 1959.5388 | Abs Value of | Flow this | 2230.1379 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9137 |  |  | 56.6605 |  |  | 55.3523 |  |  | 50.9836 |  |  | 40.2181 |  |  | 20.6306 |  |  | -7.7048 |  |  | -39.2956 |  |  | -72.7628 |  |  | -111.0513
[13 empty] | P2 at this iteration flow rate |  |  | 24.6573 |  |  | 24.7079 |  |  | 24.9695 |  |  | 25.8433 |  |  | 27.9964 |  |  | 31.9139 |  |  | 37.581 |  |  | 43.8991 |  |  | 50.5926 |  |  | 58.2503
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2565 |  |  | 31.9526 |  |  | 30.3828 |  |  | 25.1403 |  |  | 12.2217 |  |  | -11.2833 |  |  | -45.2857 |  |  | -83.1947 |  |  | -123.3553 |  |  | -169.3015
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8965 |  |  | 48.2113 |  |  | 45.6816 |  |  | 40.2108 |  |  | 29.8254 |  |  | 14.0733 |  |  | -5.2271 |  |  | -23.1065 |  |  | -36.6934 |  |  | -42.017
[13 empty] | C Non choked w/ reducers | 7 |  | 1.4868 |  |  | 15.4047 |  |  | 39.1593 |  |  | 84.3463 |  |  | 205.4677 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.1955 |  |  | 12.541 |  |  | 31.9359 |  |  | 66.6928 |  |  | 131.5273 |  |  | 288.6087 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.4868 |  |  | 15.4047 |  |  | 39.1593 |  |  | 84.3463 |  |  | 205.4677 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.2432 | 8.4433 |  | 3.8047 | 87.0089 |  | 16.1593 | 215.1835 |  | 44.9463 | 419.1225 |  | 144.4677 | 703.1571 |  | 5500 | 1036.5397 |  | 5500 | 1383.2662 |  | 5500 | 1687.8477 |  | 5500 | 1959.5388 |  | 5500 | 2230.1379
[13 empty] | Next iteration flow rate |  |  | 8.6121 | Abs Value of | Flow this | 87.879 | Abs Value of | Flow this | 217.3353 | Abs Value of | Flow this | 423.3137 | Abs Value of | Flow this | 710.1887 | Abs Value of | Flow this | 1046.9051 | Abs Value of | Flow this | 1397.0989 | Abs Value of | Flow this | 1704.7262 | Abs Value of | Flow this | 1979.1342 | Abs Value of | Flow this | 2252.4393 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9136 |  |  | 56.6553 |  |  | 55.3209 |  |  | 50.8643 |  |  | 39.8824 |  |  | 19.9013 |  |  | -9.0037 |  |  | -41.2295 |  |  | -75.3693 |  |  | -114.4274
[13 empty] | P2 at this iteration flow rate |  |  | 24.6573 |  |  | 24.7089 |  |  | 24.9758 |  |  | 25.8671 |  |  | 28.0635 |  |  | 32.0597 |  |  | 37.8407 |  |  | 44.2859 |  |  | 51.1139 |  |  | 58.9255
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2564 |  |  | 31.9464 |  |  | 30.3451 |  |  | 24.9972 |  |  | 11.8189 |  |  | -12.1585 |  |  | -46.8444 |  |  | -85.5154 |  |  | -126.4832 |  |  | -173.3529
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8964 |  |  | 48.2069 |  |  | 45.6554 |  |  | 40.116 |  |  | 29.5738 |  |  | 13.565 |  |  | -6.0607 |  |  | -24.231 |  |  | -37.9999 |  |  | -43.2893
[13 empty] | C Non choked w/ reducers | 7 |  | 1.5166 |  |  | 15.5602 |  |  | 39.5755 |  |  | 85.4332 |  |  | 211.0287 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.2194 |  |  | 12.667 |  |  | 32.2645 |  |  | 67.4394 |  |  | 133.4066 |  |  | 296.9067 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.5166 |  |  | 15.5602 |  |  | 39.5755 |  |  | 85.4332 |  |  | 211.0287 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.2134 | 8.6121 |  | 3.9602 | 87.879 |  | 16.5755 | 217.3353 |  | 46.0332 | 423.3137 |  | 150.0287 | 710.1887 |  | 5500 | 1046.9051 |  | 5500 | 1397.0989 |  | 5500 | 1704.7262 |  | 5500 | 1979.1342 |  | 5500 | 2252.4393
[13 empty] | Next iteration flow rate |  |  | 8.7844 | Abs Value of | Flow this | 88.7578 | Abs Value of | Flow this | 219.5086 | Abs Value of | Flow this | 427.5468 | Abs Value of | Flow this | 717.2906 | Abs Value of | Flow this | 1057.3741 | Abs Value of | Flow this | 1411.0699 | Abs Value of | Flow this | 1721.7734 | Abs Value of | Flow this | 1998.9255 | Abs Value of | Flow this | 2274.9637 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9135 |  |  | 56.6501 |  |  | 55.2889 |  |  | 50.7427 |  |  | 39.5401 |  |  | 19.1573 |  |  | -10.3286 |  |  | -43.2022 |  |  | -78.0282 |  |  | -117.8714
[13 empty] | P2 at this iteration flow rate |  |  | 24.6573 |  |  | 24.71 |  |  | 24.9822 |  |  | 25.8915 |  |  | 28.132 |  |  | 32.2085 |  |  | 38.1057 |  |  | 44.6804 |  |  | 51.6456 |  |  | 59.6143
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2562 |  |  | 31.9401 |  |  | 30.3066 |  |  | 24.8512 |  |  | 11.4081 |  |  | -13.0513 |  |  | -48.4344 |  |  | -87.8826 |  |  | -129.6739 |  |  | -177.4857
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8964 |  |  | 48.2024 |  |  | 45.6287 |  |  | 40.0192 |  |  | 29.317 |  |  | 13.0464 |  |  | -6.9111 |  |  | -25.3782 |  |  | -39.3327 |  |  | -44.5872
[13 empty] | C Non choked w/ reducers | 7 |  | 1.5469 |  |  | 15.7174 |  |  | 39.9966 |  |  | 86.5406 |  |  | 216.9431 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.2438 |  |  | 12.7942 |  |  | 32.5966 |  |  | 68.1961 |  |  | 135.3293 |  |  | 305.7776 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.5469 |  |  | 15.7174 |  |  | 39.9966 |  |  | 86.5406 |  |  | 216.9431 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.1831 | 8.7844 |  | 4.1174 | 88.7578 |  | 16.9966 | 219.5086 |  | 47.1406 | 427.5468 |  | 155.9431 | 717.2906 |  | 5500 | 1057.3741 |  | 5500 | 1411.0699 |  | 5500 | 1721.7734 |  | 5500 | 1998.9255 |  | 5500 | 2274.9637
[13 empty] | Next iteration flow rate |  |  | 8.9601 | Abs Value of | Flow this | 89.6454 | Abs Value of | Flow this | 221.7037 | Abs Value of | Flow this | 431.8223 | Abs Value of | Flow this | 724.4635 | Abs Value of | Flow this | 1067.9479 | Abs Value of | Flow this | 1425.1806 | Abs Value of | Flow this | 1738.9912 | Abs Value of | Flow this | 2018.9148 | Abs Value of | Flow this | 2297.7133 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9134 |  |  | 56.6447 |  |  | 55.2561 |  |  | 50.6186 |  |  | 39.1908 |  |  | 18.3983 |  |  | -11.6803 |  |  | -45.2146 |  |  | -80.7406 |  |  | -121.3847
[13 empty] | P2 at this iteration flow rate |  |  | 24.6573 |  |  | 24.7111 |  |  | 24.9888 |  |  | 25.9163 |  |  | 28.2018 |  |  | 32.3603 |  |  | 38.3761 |  |  | 45.0829 |  |  | 52.1881 |  |  | 60.3169
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2561 |  |  | 31.9337 |  |  | 30.2674 |  |  | 24.7023 |  |  | 10.989 |  |  | -13.962 |  |  | -50.0563 |  |  | -90.2975 |  |  | -132.9287 |  |  | -181.7016
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8963 |  |  | 48.1978 |  |  | 45.6015 |  |  | 39.9205 |  |  | 29.0552 |  |  | 12.5174 |  |  | -7.7785 |  |  | -26.5484 |  |  | -40.6923 |  |  | -45.9112
[13 empty] | C Non choked w/ reducers | 7 |  | 1.5778 |  |  | 15.8761 |  |  | 40.4228 |  |  | 87.669 |  |  | 223.2518 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.2686 |  |  | 12.9228 |  |  | 32.9324 |  |  | 68.9631 |  |  | 137.2972 |  |  | 315.2939 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.5778 |  |  | 15.8761 |  |  | 40.4228 |  |  | 87.669 |  |  | 223.2518 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.1522 | 8.9601 |  | 4.2761 | 89.6454 |  | 17.4228 | 221.7037 |  | 48.269 | 431.8223 |  | 162.2518 | 724.4635 |  | 5500 | 1067.9479 |  | 5500 | 1425.1806 |  | 5500 | 1738.9912 |  | 5500 | 2018.9148 |  | 5500 | 2297.7133
[13 empty] | Next iteration flow rate |  |  | 9.1393 | Abs Value of | Flow this | 90.5419 | Abs Value of | Flow this | 223.9208 | Abs Value of | Flow this | 436.1405 | Abs Value of | Flow this | 731.7081 | Abs Value of | Flow this | 1078.6274 | Abs Value of | Flow this | 1439.4324 | Abs Value of | Flow this | 1756.3811 | Abs Value of | Flow this | 2039.1039 | Abs Value of | Flow this | 2320.6905 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9133 |  |  | 56.6393 |  |  | 55.2228 |  |  | 50.492 |  |  | 38.8345 |  |  | 17.6241 |  |  | -13.0591 |  |  | -47.2674 |  |  | -83.5075 |  |  | -124.9685
[13 empty] | P2 at this iteration flow rate |  |  | 24.6573 |  |  | 24.7121 |  |  | 24.9954 |  |  | 25.9416 |  |  | 28.2731 |  |  | 32.5152 |  |  | 38.6518 |  |  | 45.4935 |  |  | 52.7415 |  |  | 61.0337
[13 empty] | Delta P at this iteration flow rate |  |  | 32.256 |  |  | 31.9271 |  |  | 30.2273 |  |  | 24.5504 |  |  | 10.5614 |  |  | -14.8911 |  |  | -51.7109 |  |  | -92.7609 |  |  | -136.249 |  |  | -186.0022
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8962 |  |  | 48.1931 |  |  | 45.5738 |  |  | 39.8198 |  |  | 28.788 |  |  | 11.9777 |  |  | -8.6634 |  |  | -27.7421 |  |  | -42.0792 |  |  | -47.2619
[13 empty] | C Non choked w/ reducers | 7 |  | 1.6094 |  |  | 16.0366 |  |  | 40.854 |  |  | 88.8192 |  |  | 230.0029 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.294 |  |  | 13.0526 |  |  | 33.2719 |  |  | 69.7408 |  |  | 139.3121 |  |  | 325.5414 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.6094 |  |  | 16.0366 |  |  | 40.854 |  |  | 88.8192 |  |  | 230.0029 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.1206 | 9.1393 |  | 4.4366 | 90.5419 |  | 17.854 | 223.9208 |  | 49.4192 | 436.1405 |  | 169.0029 | 731.7081 |  | 5500 | 1078.6274 |  | 5500 | 1439.4324 |  | 5500 | 1756.3811 |  | 5500 | 2039.1039 |  | 5500 | 2320.6905
[13 empty] | Next iteration flow rate |  |  | 9.322 | Abs Value of | Flow this | 91.4473 | Abs Value of | Flow this | 226.16 | Abs Value of | Flow this | 440.5019 | Abs Value of | Flow this | 739.0252 | Abs Value of | Flow this | 1089.4136 | Abs Value of | Flow this | 1453.8267 | Abs Value of | Flow this | 1773.9449 | Abs Value of | Flow this | 2059.495 | Abs Value of | Flow this | 2343.8974 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9132 |  |  | 56.6337 |  |  | 55.1887 |  |  | 50.3629 |  |  | 38.4711 |  |  | 16.8343 |  |  | -14.4656 |  |  | -49.3615 |  |  | -86.33 |  |  | -128.6244
[13 empty] | P2 at this iteration flow rate |  |  | 24.6574 |  |  | 24.7133 |  |  | 25.0023 |  |  | 25.9674 |  |  | 28.3458 |  |  | 32.6731 |  |  | 38.9331 |  |  | 45.9123 |  |  | 53.306 |  |  | 61.7649
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2559 |  |  | 31.9205 |  |  | 30.1865 |  |  | 24.3955 |  |  | 10.1253 |  |  | -15.8388 |  |  | -53.3987 |  |  | -95.2738 |  |  | -139.636 |  |  | -190.3893
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8961 |  |  | 48.1883 |  |  | 45.5454 |  |  | 39.7171 |  |  | 28.5155 |  |  | 11.4272 |  |  | -9.566 |  |  | -28.9598 |  |  | -43.494 |  |  | -48.6396
[13 empty] | C Non choked w/ reducers | 7 |  | 1.6416 |  |  | 16.1986 |  |  | 41.2905 |  |  | 89.9919 |  |  | 237.2532 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.3199 |  |  | 13.1838 |  |  | 33.615 |  |  | 70.5292 |  |  | 141.3759 |  |  | 336.6233 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.6416 |  |  | 16.1986 |  |  | 41.2905 |  |  | 89.9919 |  |  | 237.2532 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.0884 | 9.322 |  | 4.5986 | 91.4473 |  | 18.2905 | 226.16 |  | 50.5919 | 440.5019 |  | 176.2532 | 739.0252 |  | 5500 | 1089.4136 |  | 5500 | 1453.8267 |  | 5500 | 1773.9449 |  | 5500 | 2059.495 |  | 5500 | 2343.8974
[13 empty] | Next iteration flow rate |  |  | 9.5085 | Abs Value of | Flow this | 92.3617 | Abs Value of | Flow this | 228.4216 | Abs Value of | Flow this | 444.9069 | Abs Value of | Flow this | 746.4154 | Abs Value of | Flow this | 1100.3078 | Abs Value of | Flow this | 1468.365 | Abs Value of | Flow this | 1791.6843 | Abs Value of | Flow this | 2080.0899 | Abs Value of | Flow this | 2367.3363 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9131 |  |  | 56.628 |  |  | 55.154 |  |  | 50.2312 |  |  | 38.1003 |  |  | 16.0287 |  |  | -15.9003 |  |  | -51.4977 |  |  | -89.2093 |  |  | -132.3537
[13 empty] | P2 at this iteration flow rate |  |  | 24.6574 |  |  | 24.7144 |  |  | 25.0092 |  |  | 25.9938 |  |  | 28.4199 |  |  | 32.8343 |  |  | 39.2201 |  |  | 46.3395 |  |  | 53.8819 |  |  | 62.5107
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2557 |  |  | 31.9136 |  |  | 30.1448 |  |  | 24.2374 |  |  | 9.6804 |  |  | -16.8056 |  |  | -55.1204 |  |  | -97.8372 |  |  | -143.0911 |  |  | -194.8645
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.896 |  |  | 48.1835 |  |  | 45.5166 |  |  | 39.6123 |  |  | 28.2375 |  |  | 10.8657 |  |  | -10.4868 |  |  | -30.202 |  |  | -44.9373 |  |  | -50.0451
[13 empty] | C Non choked w/ reducers | 7 |  | 1.6744 |  |  | 16.3623 |  |  | 41.7322 |  |  | 91.1877 |  |  | 245.0703 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.3463 |  |  | 13.3163 |  |  | 33.962 |  |  | 71.3287 |  |  | 143.4908 |  |  | 348.6645 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.6744 |  |  | 16.3623 |  |  | 41.7322 |  |  | 91.1877 |  |  | 245.0703 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.0556 | 9.5085 |  | 4.7623 | 92.3617 |  | 18.7322 | 228.4216 |  | 51.7877 | 444.9069 |  | 184.0703 | 746.4154 |  | 5500 | 1100.3078 |  | 5500 | 1468.365 |  | 5500 | 1791.6843 |  | 5500 | 2080.0899 |  | 5500 | 2367.3363
[13 empty] | Next iteration flow rate |  |  | 9.6987 | Abs Value of | Flow this | 93.2854 | Abs Value of | Flow this | 230.7058 | Abs Value of | Flow this | 449.356 | Abs Value of | Flow this | 753.8796 | Abs Value of | Flow this | 1111.3109 | Abs Value of | Flow this | 1483.0486 | Abs Value of | Flow this | 1809.6012 | Abs Value of | Flow this | 2100.8908 | Abs Value of | Flow this | 2391.0097 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.913 |  |  | 56.6223 |  |  | 55.1186 |  |  | 50.0968 |  |  | 37.7221 |  |  | 15.2069 |  |  | -17.3639 |  |  | -53.6768 |  |  | -92.1464 |  |  | -136.1581
[13 empty] | P2 at this iteration flow rate |  |  | 24.6574 |  |  | 24.7155 |  |  | 25.0163 |  |  | 26.0206 |  |  | 28.4956 |  |  | 32.9986 |  |  | 39.5128 |  |  | 46.7754 |  |  | 54.4693 |  |  | 63.2716
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2556 |  |  | 31.9067 |  |  | 30.1023 |  |  | 24.0762 |  |  | 9.2266 |  |  | -17.7918 |  |  | -56.8767 |  |  | -100.4521 |  |  | -146.6157 |  |  | -199.4297
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8959 |  |  | 48.1785 |  |  | 45.4871 |  |  | 39.5054 |  |  | 27.954 |  |  | 10.2928 |  |  | -11.4261 |  |  | -31.4692 |  |  | -46.4095 |  |  | -51.4788
[13 empty] | C Non choked w/ reducers | 7 |  | 1.7079 |  |  | 16.5278 |  |  | 42.1792 |  |  | 92.4074 |  |  | 253.5355 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.3732 |  |  | 13.4502 |  |  | 34.3127 |  |  | 72.1394 |  |  | 145.6589 |  |  | 361.8178 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.7079 |  |  | 16.5278 |  |  | 42.1792 |  |  | 92.4074 |  |  | 253.5355 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.0221 | 9.6987 |  | 4.9278 | 93.2854 |  | 19.1792 | 230.7058 |  | 53.0074 | 449.356 |  | 192.5355 | 753.8796 |  | 5500 | 1111.3109 |  | 5500 | 1483.0486 |  | 5500 | 1809.6012 |  | 5500 | 2100.8908 |  | 5500 | 2391.0097
[13 empty] | Next iteration flow rate |  |  | 9.8926 | Abs Value of | Flow this | 94.2182 | Abs Value of | Flow this | 233.0129 | Abs Value of | Flow this | 453.8496 | Abs Value of | Flow this | 761.4184 | Abs Value of | Flow this | 1122.424 | Abs Value of | Flow this | 1497.8791 | Abs Value of | Flow this | 1827.6972 | Abs Value of | Flow this | 2121.8997 | Abs Value of | Flow this | 2414.9198 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9128 |  |  | 56.6163 |  |  | 55.0825 |  |  | 49.9597 |  |  | 37.3363 |  |  | 14.3685 |  |  | -18.857 |  |  | -55.8997 |  |  | -95.1426 |  |  | -140.0389
[13 empty] | P2 at this iteration flow rate |  |  | 24.6574 |  |  | 24.7167 |  |  | 25.0235 |  |  | 26.0481 |  |  | 28.5727 |  |  | 33.1663 |  |  | 39.8114 |  |  | 47.2199 |  |  | 55.0685 |  |  | 64.0478
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2554 |  |  | 31.8996 |  |  | 30.059 |  |  | 23.9117 |  |  | 8.7636 |  |  | -18.7978 |  |  | -58.6684 |  |  | -103.1196 |  |  | -150.2111 |  |  | -204.0866
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8957 |  |  | 48.1734 |  |  | 45.457 |  |  | 39.3963 |  |  | 27.6647 |  |  | 9.7085 |  |  | -12.3843 |  |  | -32.7618 |  |  | -47.9114 |  |  | -52.9413
[13 empty] | C Non choked w/ reducers | 7 |  | 1.7421 |  |  | 16.6949 |  |  | 42.6318 |  |  | 93.652 |  |  | 262.7476 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.4007 |  |  | 13.5854 |  |  | 34.6673 |  |  | 72.9616 |  |  | 147.8827 |  |  | 376.2732 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.7421 |  |  | 16.6949 |  |  | 42.6318 |  |  | 93.652 |  |  | 262.7476 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.9879 | 9.8926 |  | 5.0949 | 94.2182 |  | 19.6318 | 233.0129 |  | 54.252 | 453.8496 |  | 201.7476 | 761.4184 |  | 5500 | 1122.424 |  | 5500 | 1497.8791 |  | 5500 | 1827.6972 |  | 5500 | 2121.8997 |  | 5500 | 2414.9198
[13 empty] | Next iteration flow rate |  |  | 10.0905 | Abs Value of | Flow this | 95.1604 | Abs Value of | Flow this | 235.343 | Abs Value of | Flow this | 458.3881 | Abs Value of | Flow this | 769.0326 | Abs Value of | Flow this | 1133.6482 | Abs Value of | Flow this | 1512.8579 | Abs Value of | Flow this | 1845.9742 | Abs Value of | Flow this | 2143.1187 | Abs Value of | Flow this | 2439.069 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9127 |  |  | 56.6103 |  |  | 55.0456 |  |  | 49.8199 |  |  | 36.9428 |  |  | 13.5133 |  |  | -20.38 |  |  | -58.1673 |  |  | -98.1989 |  |  | -143.9977
[13 empty] | P2 at this iteration flow rate |  |  | 24.6575 |  |  | 24.7179 |  |  | 25.0309 |  |  | 26.076 |  |  | 28.6514 |  |  | 33.3373 |  |  | 40.116 |  |  | 47.6735 |  |  | 55.6798 |  |  | 64.8395
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2552 |  |  | 31.8924 |  |  | 30.0147 |  |  | 23.7439 |  |  | 8.2913 |  |  | -19.824 |  |  | -60.496 |  |  | -105.8408 |  |  | -153.8787 |  |  | -208.8372
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8956 |  |  | 48.1683 |  |  | 45.4264 |  |  | 39.2851 |  |  | 27.3696 |  |  | 9.1124 |  |  | -13.3618 |  |  | -34.0805 |  |  | -49.4434 |  |  | -54.4333
[13 empty] | C Non choked w/ reducers | 7 |  | 1.7769 |  |  | 16.8638 |  |  | 43.0898 |  |  | 94.9221 |  |  | 272.8281 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.4287 |  |  | 13.722 |  |  | 35.0258 |  |  | 73.7954 |  |  | 150.1645 |  |  | 392.2693 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.7769 |  |  | 16.8638 |  |  | 43.0898 |  |  | 94.9221 |  |  | 272.8281 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.9531 | 10.0905 |  | 5.2638 | 95.1604 |  | 20.0898 | 235.343 |  | 55.5221 | 458.3881 |  | 211.8281 | 769.0326 |  | 5500 | 1133.6482 |  | 5500 | 1512.8579 |  | 5500 | 1845.9742 |  | 5500 | 2143.1187 |  | 5500 | 2439.069
[13 empty] | Next iteration flow rate |  |  | 10.2923 | Abs Value of | Flow this | 96.112 | Abs Value of | Flow this | 237.6964 | Abs Value of | Flow this | 462.9719 | Abs Value of | Flow this | 776.7229 | Abs Value of | Flow this | 1144.9847 | Abs Value of | Flow this | 1527.9865 | Abs Value of | Flow this | 1864.4339 | Abs Value of | Flow this | 2164.5499 | Abs Value of | Flow this | 2463.4597 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9126 |  |  | 56.6042 |  |  | 55.008 |  |  | 49.6773 |  |  | 36.5413 |  |  | 12.6409 |  |  | -21.9337 |  |  | -60.4805 |  |  | -101.3168 |  |  | -148.036
[13 empty] | P2 at this iteration flow rate |  |  | 24.6575 |  |  | 24.7192 |  |  | 25.0384 |  |  | 26.1045 |  |  | 28.7317 |  |  | 33.5118 |  |  | 40.4267 |  |  | 48.1361 |  |  | 56.3034 |  |  | 65.6472
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2551 |  |  | 31.885 |  |  | 29.9696 |  |  | 23.5727 |  |  | 7.8096 |  |  | -20.8709 |  |  | -62.3604 |  |  | -108.6166 |  |  | -157.6201 |  |  | -213.6832
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8955 |  |  | 48.163 |  |  | 45.3951 |  |  | 39.1716 |  |  | 27.0686 |  |  | 8.5043 |  |  | -14.3589 |  |  | -35.4256 |  |  | -51.0062 |  |  | -55.9552
[13 empty] | C Non choked w/ reducers | 7 |  | 1.8125 |  |  | 17.0344 |  |  | 43.5534 |  |  | 96.2187 |  |  | 283.9285 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.4573 |  |  | 13.86 |  |  | 35.3882 |  |  | 74.6413 |  |  | 152.5071 |  |  | 410.112 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.8125 |  |  | 17.0344 |  |  | 43.5534 |  |  | 96.2187 |  |  | 283.9285 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.9175 | 10.2923 |  | 5.4344 | 96.112 |  | 20.5534 | 237.6964 |  | 56.8187 | 462.9719 |  | 222.9285 | 776.7229 |  | 5500 | 1144.9847 |  | 5500 | 1527.9865 |  | 5500 | 1864.4339 |  | 5500 | 2164.5499 |  | 5500 | 2463.4597
[13 empty] | Next iteration flow rate |  |  | 10.4981 | Abs Value of | Flow this | 97.0731 | Abs Value of | Flow this | 240.0734 | Abs Value of | Flow this | 467.6017 | Abs Value of | Flow this | 784.4901 | Abs Value of | Flow this | 1156.4345 | Abs Value of | Flow this | 1543.2664 | Abs Value of | Flow this | 1883.0783 | Abs Value of | Flow this | 2186.1954 | Abs Value of | Flow this | 2488.0943 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9124 |  |  | 56.5979 |  |  | 54.9697 |  |  | 49.5318 |  |  | 36.1318 |  |  | 11.751 |  |  | -23.5185 |  |  | -62.8401 |  |  | -104.4972 |  |  | -152.1556
[13 empty] | P2 at this iteration flow rate |  |  | 24.6575 |  |  | 24.7204 |  |  | 25.0461 |  |  | 26.1336 |  |  | 28.8136 |  |  | 33.6898 |  |  | 40.7437 |  |  | 48.608 |  |  | 56.9394 |  |  | 66.4711
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2549 |  |  | 31.8775 |  |  | 29.9236 |  |  | 23.3981 |  |  | 7.3181 |  |  | -21.9388 |  |  | -64.2623 |  |  | -111.4482 |  |  | -161.4367 |  |  | -218.6267
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8954 |  |  | 48.1576 |  |  | 45.3632 |  |  | 39.0558 |  |  | 26.7615 |  |  | 7.884 |  |  | -15.376 |  |  | -36.7978 |  |  | -52.6005 |  |  | -57.5077
[13 empty] | C Non choked w/ reducers | 7 |  | 1.8487 |  |  | 17.2067 |  |  | 44.0228 |  |  | 97.5429 |  |  | 296.2401 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.4864 |  |  | 13.9994 |  |  | 35.7546 |  |  | 75.4993 |  |  | 154.9134 |  |  | 430.1995 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.8487 |  |  | 17.2067 |  |  | 44.0228 |  |  | 97.5429 |  |  | 296.2401 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.8813 | 10.4981 |  | 5.6067 | 97.0731 |  | 21.0228 | 240.0734 |  | 58.1429 | 467.6017 |  | 235.2401 | 784.4901 |  | 5500 | 1156.4345 |  | 5500 | 1543.2664 |  | 5500 | 1883.0783 |  | 5500 | 2186.1954 |  | 5500 | 2488.0943
[13 empty] | Next iteration flow rate |  |  | 10.7081 | Abs Value of | Flow this | 98.0438 | Abs Value of | Flow this | 242.4741 | Abs Value of | Flow this | 472.2777 | Abs Value of | Flow this | 792.335 | Abs Value of | Flow this | 1167.9989 | Abs Value of | Flow this | 1558.699 | Abs Value of | Flow this | 1901.909 | Abs Value of | Flow this | 2208.0573 | Abs Value of | Flow this | 2512.9752 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9123 |  |  | 56.5915 |  |  | 54.9305 |  |  | 49.3833 |  |  | 35.714 |  |  | 10.8431 |  |  | -25.1353 |  |  | -65.2472 |  |  | -107.7416 |  |  | -156.3579
[13 empty] | P2 at this iteration flow rate |  |  | 24.6575 |  |  | 24.7217 |  |  | 25.0539 |  |  | 26.1633 |  |  | 28.8972 |  |  | 33.8714 |  |  | 41.0671 |  |  | 49.0894 |  |  | 57.5883 |  |  | 67.3116
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2547 |  |  | 31.8698 |  |  | 29.8766 |  |  | 23.22 |  |  | 6.8168 |  |  | -23.0282 |  |  | -66.2023 |  |  | -114.3367 |  |  | -165.33 |  |  | -223.6695
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8952 |  |  | 48.1521 |  |  | 45.3306 |  |  | 38.9378 |  |  | 26.4483 |  |  | 7.2512 |  |  | -16.4136 |  |  | -38.1975 |  |  | -54.2267 |  |  | -59.0914
[13 empty] | C Non choked w/ reducers | 7 |  | 1.8857 |  |  | 17.3809 |  |  | 44.4979 |  |  | 98.8954 |  |  | 310.0092 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.5161 |  |  | 14.1402 |  |  | 36.1252 |  |  | 76.3698 |  |  | 157.3863 |  |  | 453.0633 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.8857 |  |  | 17.3809 |  |  | 44.4979 |  |  | 98.8954 |  |  | 310.0092 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.8443 | 10.7081 |  | 5.7809 | 98.0438 |  | 21.4979 | 242.4741 |  | 59.4954 | 472.2777 |  | 249.0092 | 792.335 |  | 5500 | 1167.9989 |  | 5500 | 1558.699 |  | 5500 | 1901.909 |  | 5500 | 2208.0573 |  | 5500 | 2512.9752
[13 empty] | Next iteration flow rate |  |  | 10.9223 | Abs Value of | Flow this | 99.0243 | Abs Value of | Flow this | 244.8988 | Abs Value of | Flow this | 477.0004 | Abs Value of | Flow this | 800.2584 | Abs Value of | Flow this | 1179.6789 | Abs Value of | Flow this | 1574.286 | Abs Value of | Flow this | 1920.9281 | Abs Value of | Flow this | 2230.1379 | Abs Value of | Flow this | 2538.105 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9121 |  |  | 56.585 |  |  | 54.8906 |  |  | 49.2319 |  |  | 35.2879 |  |  | 9.9171 |  |  | -26.7845 |  |  | -67.7027 |  |  | -111.0513 |  |  | -160.6447
[13 empty] | P2 at this iteration flow rate |  |  | 24.6576 |  |  | 24.723 |  |  | 25.0619 |  |  | 26.1936 |  |  | 28.9824 |  |  | 34.0566 |  |  | 41.3969 |  |  | 49.5805 |  |  | 58.2503 |  |  | 68.1689
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2545 |  |  | 31.862 |  |  | 29.8288 |  |  | 23.0383 |  |  | 6.3054 |  |  | -24.1395 |  |  | -68.1814 |  |  | -117.2833 |  |  | -169.3015 |  |  | -228.8137
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8951 |  |  | 48.1465 |  |  | 45.2974 |  |  | 38.8173 |  |  | 26.1288 |  |  | 6.6057 |  |  | -17.472 |  |  | -39.6254 |  |  | -55.8857 |  |  | -60.7069
[13 empty] | C Non choked w/ reducers | 7 |  | 1.9234 |  |  | 17.5569 |  |  | 44.979 |  |  | 100.2775 |  |  | 325.5589 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.5465 |  |  | 14.2824 |  |  | 36.4998 |  |  | 77.2531 |  |  | 159.9292 |  |  | 479.4303 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.9234 |  |  | 17.5569 |  |  | 44.979 |  |  | 100.2775 |  |  | 325.5589 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.8066 | 10.9223 |  | 5.9569 | 99.0243 |  | 21.979 | 244.8988 |  | 60.8775 | 477.0004 |  | 264.5589 | 800.2584 |  | 5500 | 1179.6789 |  | 5500 | 1574.286 |  | 5500 | 1920.9281 |  | 5500 | 2230.1379 |  | 5500 | 2538.105
[13 empty] | Next iteration flow rate |  |  | 11.1407 | Abs Value of | Flow this | 100.0145 | Abs Value of | Flow this | 247.3478 | Abs Value of | Flow this | 481.7705 | Abs Value of | Flow this | 808.2609 | Abs Value of | Flow this | 1191.4757 | Abs Value of | Flow this | 1590.0289 | Abs Value of | Flow this | 1940.1374 | Abs Value of | Flow this | 2252.4393 | Abs Value of | Flow this | 2563.486 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.912 |  |  | 56.5783 |  |  | 54.8499 |  |  | 49.0775 |  |  | 34.8531 |  |  | 8.9724 |  |  | -28.4669 |  |  | -70.2076 |  |  | -114.4274 |  |  | -165.0177
[13 empty] | P2 at this iteration flow rate |  |  | 24.6576 |  |  | 24.7243 |  |  | 25.07 |  |  | 26.2245 |  |  | 29.0694 |  |  | 34.2455 |  |  | 41.7334 |  |  | 50.0815 |  |  | 58.9255 |  |  | 69.0435
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2543 |  |  | 31.854 |  |  | 29.7799 |  |  | 22.853 |  |  | 5.7838 |  |  | -25.2731 |  |  | -70.2003 |  |  | -120.2891 |  |  | -173.3529 |  |  | -234.0612
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.895 |  |  | 48.1408 |  |  | 45.2636 |  |  | 38.6944 |  |  | 25.8028 |  |  | 5.9473 |  |  | -18.5517 |  |  | -41.0819 |  |  | -57.578 |  |  | -62.3549
[13 empty] | C Non choked w/ reducers | 7 |  | 1.9619 |  |  | 17.7347 |  |  | 45.466 |  |  | 101.6901 |  |  | 343.3234 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.5774 |  |  | 14.4261 |  |  | 36.8786 |  |  | 78.1494 |  |  | 162.5455 |  |  | 510.3272 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.9619 |  |  | 17.7347 |  |  | 45.466 |  |  | 101.6901 |  |  | 343.3234 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.7681 | 11.1407 |  | 6.1347 | 100.0145 |  | 22.466 | 247.3478 |  | 62.2901 | 481.7705 |  | 282.3234 | 808.2609 |  | 5500 | 1191.4757 |  | 5500 | 1590.0289 |  | 5500 | 1940.1374 |  | 5500 | 2252.4393 |  | 5500 | 2563.486
[13 empty] | Next iteration flow rate |  |  | 11.3635 | Abs Value of | Flow this | 101.0147 | Abs Value of | Flow this | 249.8213 | Abs Value of | Flow this | 486.5882 | Abs Value of | Flow this | 816.3436 | Abs Value of | Flow this | 1203.3904 | Abs Value of | Flow this | 1605.9292 | Abs Value of | Flow this | 1959.5388 | Abs Value of | Flow this | 2274.9637 | Abs Value of | Flow this | 2589.1209 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9118 |  |  | 56.5715 |  |  | 54.8084 |  |  | 48.9199 |  |  | 34.4097 |  |  | 8.0087 |  |  | -30.1831 |  |  | -72.7628 |  |  | -117.8714 |  |  | -169.4786
[13 empty] | P2 at this iteration flow rate |  |  | 24.6576 |  |  | 24.7257 |  |  | 25.0783 |  |  | 26.256 |  |  | 29.1581 |  |  | 34.4383 |  |  | 42.0766 |  |  | 50.5926 |  |  | 59.6143 |  |  | 69.9357
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2541 |  |  | 31.8458 |  |  | 29.7301 |  |  | 22.6639 |  |  | 5.2516 |  |  | -26.4295 |  |  | -72.2597 |  |  | -123.3553 |  |  | -177.4857 |  |  | -239.4143
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8948 |  |  | 48.135 |  |  | 45.229 |  |  | 38.5691 |  |  | 25.4703 |  |  | 5.2756 |  |  | -19.6531 |  |  | -42.5678 |  |  | -59.3044 |  |  | -64.0361
[13 empty] | C Non choked w/ reducers | 7 |  | 2.0011 |  |  | 17.9143 |  |  | 45.9591 |  |  | 103.1345 |  |  | 363.9017 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.6089 |  |  | 14.5712 |  |  | 37.2616 |  |  | 79.0591 |  |  | 165.2391 |  |  | 547.2608 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.0011 |  |  | 17.9143 |  |  | 45.9591 |  |  | 103.1345 |  |  | 363.9017 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.7289 | 11.3635 |  | 6.3143 | 101.0147 |  | 22.9591 | 249.8213 |  | 63.7345 | 486.5882 |  | 302.9017 | 816.3436 |  | 5500 | 1203.3904 |  | 5500 | 1605.9292 |  | 5500 | 1959.5388 |  | 5500 | 2274.9637 |  | 5500 | 2589.1209
[13 empty] | Next iteration flow rate |  |  | 11.5908 | Abs Value of | Flow this | 102.0248 | Abs Value of | Flow this | 252.3195 | Abs Value of | Flow this | 491.454 | Abs Value of | Flow this | 824.507 | Abs Value of | Flow this | 1215.4243 | Abs Value of | Flow this | 1621.9885 | Abs Value of | Flow this | 1979.1342 | Abs Value of | Flow this | 2297.7133 | Abs Value of | Flow this | 2615.0121 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9116 |  |  | 56.5646 |  |  | 54.766 |  |  | 48.7592 |  |  | 33.9573 |  |  | 7.0257 |  |  | -31.9338 |  |  | -75.3693 |  |  | -121.3847 |  |  | -174.0291
[13 empty] | P2 at this iteration flow rate |  |  | 24.6577 |  |  | 24.7271 |  |  | 25.0868 |  |  | 26.2882 |  |  | 29.2485 |  |  | 34.6349 |  |  | 42.4268 |  |  | 51.1139 |  |  | 60.3169 |  |  | 70.8458
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2539 |  |  | 31.8375 |  |  | 29.6792 |  |  | 22.471 |  |  | 4.7087 |  |  | -27.6092 |  |  | -74.3606 |  |  | -126.4832 |  |  | -181.7016 |  |  | -244.8749
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8947 |  |  | 48.1291 |  |  | 45.1938 |  |  | 38.4412 |  |  | 25.1311 |  |  | 4.5904 |  |  | -20.7767 |  |  | -44.0835 |  |  | -61.0654 |  |  | -65.751
[13 empty] | C Non choked w/ reducers | 7 |  | 2.0412 |  |  | 18.0958 |  |  | 46.4585 |  |  | 104.6119 |  |  | 388.1492 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.6411 |  |  | 14.7178 |  |  | 37.6489 |  |  | 79.9824 |  |  | 168.014 |  |  | 592.5524 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.0412 |  |  | 18.0958 |  |  | 46.4585 |  |  | 104.6119 |  |  | 388.1492 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.6888 | 11.5908 |  | 6.4958 | 102.0248 |  | 23.4585 | 252.3195 |  | 65.2119 | 491.454 |  | 327.1492 | 824.507 |  | 5500 | 1215.4243 |  | 5500 | 1621.9885 |  | 5500 | 1979.1342 |  | 5500 | 2297.7133 |  | 5500 | 2615.0121
[13 empty] | Next iteration flow rate |  |  | 11.8226 | Abs Value of | Flow this | 103.0451 | Abs Value of | Flow this | 254.8427 | Abs Value of | Flow this | 496.3686 | Abs Value of | Flow this | 832.7521 | Abs Value of | Flow this | 1227.5786 | Abs Value of | Flow this | 1638.2083 | Abs Value of | Flow this | 1998.9255 | Abs Value of | Flow this | 2320.6905 | Abs Value of | Flow this | 2641.1622 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9114 |  |  | 56.5575 |  |  | 54.7228 |  |  | 48.5952 |  |  | 33.4958 |  |  | 6.0229 |  |  | -33.7197 |  |  | -78.0282 |  |  | -124.9685 |  |  | -178.6711
[13 empty] | P2 at this iteration flow rate |  |  | 24.6577 |  |  | 24.7285 |  |  | 25.0954 |  |  | 26.321 |  |  | 29.3408 |  |  | 34.8354 |  |  | 42.7839 |  |  | 51.6456 |  |  | 61.0337 |  |  | 71.7742
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2537 |  |  | 31.829 |  |  | 29.6274 |  |  | 22.2743 |  |  | 4.155 |  |  | -28.8125 |  |  | -76.5036 |  |  | -129.6739 |  |  | -186.0022 |  |  | -250.4453
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8945 |  |  | 48.123 |  |  | 45.1578 |  |  | 38.3108 |  |  | 24.7851 |  |  | 3.8914 |  |  | -21.9228 |  |  | -45.6297 |  |  | -62.8618 |  |  | -67.5004
[13 empty] | C Non choked w/ reducers | 7 |  | 2.082 |  |  | 18.2792 |  |  | 46.9641 |  |  | 106.1237 |  |  | 417.3384 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.674 |  |  | 14.8659 |  |  | 38.0405 |  |  | 80.9196 |  |  | 170.8746 |  |  | 650.0092 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.082 |  |  | 18.2792 |  |  | 46.9641 |  |  | 106.1237 |  |  | 417.3384 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.648 | 11.8226 |  | 6.6792 | 103.0451 |  | 23.9641 | 254.8427 |  | 66.7237 | 496.3686 |  | 356.3384 | 832.7521 |  | 5500 | 1227.5786 |  | 5500 | 1638.2083 |  | 5500 | 1998.9255 |  | 5500 | 2320.6905 |  | 5500 | 2641.1622
[13 empty] | Next iteration flow rate |  |  | 12.0591 | Abs Value of | Flow this | 104.0755 | Abs Value of | Flow this | 257.3912 | Abs Value of | Flow this | 501.3323 | Abs Value of | Flow this | 841.0796 | Abs Value of | Flow this | 1239.8543 | Abs Value of | Flow this | 1654.5904 | Abs Value of | Flow this | 2018.9148 | Abs Value of | Flow this | 2343.8974 | Abs Value of | Flow this | 2667.5738 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9112 |  |  | 56.5503 |  |  | 54.6787 |  |  | 48.428 |  |  | 33.0251 |  |  | 4.9999 |  |  | -35.5415 |  |  | -80.7406 |  |  | -128.6244 |  |  | -183.4064
[13 empty] | P2 at this iteration flow rate |  |  | 24.6578 |  |  | 24.7299 |  |  | 25.1043 |  |  | 26.3544 |  |  | 29.435 |  |  | 35.04 |  |  | 43.1483 |  |  | 52.1881 |  |  | 61.7649 |  |  | 72.7213
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2535 |  |  | 31.8204 |  |  | 29.5745 |  |  | 22.0736 |  |  | 3.5901 |  |  | -30.0401 |  |  | -78.6897 |  |  | -132.9287 |  |  | -190.3893 |  |  | -256.1277
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8943 |  |  | 48.1168 |  |  | 45.1212 |  |  | 38.1777 |  |  | 24.4321 |  |  | 3.1784 |  |  | -23.092 |  |  | -47.207 |  |  | -64.6943 |  |  | -69.285
[13 empty] | C Non choked w/ reducers | 7 |  | 2.1236 |  |  | 18.4645 |  |  | 47.4762 |  |  | 107.6711 |  |  | 453.4633 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.7074 |  |  | 15.0156 |  |  | 38.4365 |  |  | 81.8711 |  |  | 173.8255 |  |  | 726.4263 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.1236 |  |  | 18.4645 |  |  | 47.4762 |  |  | 107.6711 |  |  | 453.4633 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.6064 | 12.0591 |  | 6.8645 | 104.0755 |  | 24.4762 | 257.3912 |  | 68.2711 | 501.3323 |  | 392.4633 | 841.0796 |  | 5500 | 1239.8543 |  | 5500 | 1654.5904 |  | 5500 | 2018.9148 |  | 5500 | 2343.8974 |  | 5500 | 2667.5738
[13 empty] | Next iteration flow rate |  |  | 12.3002 | Abs Value of | Flow this | 105.1163 | Abs Value of | Flow this | 259.9651 | Abs Value of | Flow this | 506.3456 | Abs Value of | Flow this | 849.4904 | Abs Value of | Flow this | 1252.2529 | Abs Value of | Flow this | 1671.1363 | Abs Value of | Flow this | 2039.1039 | Abs Value of | Flow this | 2367.3363 | Abs Value of | Flow this | 2694.2496 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.911 |  |  | 56.543 |  |  | 54.6337 |  |  | 48.2574 |  |  | 32.5449 |  |  | 3.9564 |  |  | -37.3999 |  |  | -83.5075 |  |  | -132.3537 |  |  | -188.2369
[13 empty] | P2 at this iteration flow rate |  |  | 24.6578 |  |  | 24.7314 |  |  | 25.1133 |  |  | 26.3885 |  |  | 29.531 |  |  | 35.2487 |  |  | 43.52 |  |  | 52.7415 |  |  | 62.5107 |  |  | 73.6874
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2532 |  |  | 31.8116 |  |  | 29.5205 |  |  | 21.8689 |  |  | 3.0138 |  |  | -31.2923 |  |  | -80.9198 |  |  | -136.249 |  |  | -194.8645 |  |  | -261.9242
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8941 |  |  | 48.1105 |  |  | 45.0837 |  |  | 38.042 |  |  | 24.0721 |  |  | 2.451 |  |  | -24.2847 |  |  | -48.8159 |  |  | -66.5637 |  |  | -71.1054
[13 empty] | C Non choked w/ reducers | 7 |  | 2.1661 |  |  | 18.6517 |  |  | 47.9947 |  |  | 109.2556 |  |  | 499.8692 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.7416 |  |  | 15.1667 |  |  | 38.837 |  |  | 82.8372 |  |  | 176.8719 |  |  | 835.4927 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.1661 |  |  | 18.6517 |  |  | 47.9947 |  |  | 109.2556 |  |  | 499.8692 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.5639 | 12.3002 |  | 7.0517 | 105.1163 |  | 24.9947 | 259.9651 |  | 69.8556 | 506.3456 |  | 438.8692 | 849.4904 |  | 5500 | 1252.2529 |  | 5500 | 1671.1363 |  | 5500 | 2039.1039 |  | 5500 | 2367.3363 |  | 5500 | 2694.2496
[13 empty] | Next iteration flow rate |  |  | 12.5462 | Abs Value of | Flow this | 106.1674 | Abs Value of | Flow this | 262.5647 | Abs Value of | Flow this | 511.409 | Abs Value of | Flow this | 857.9853 | Abs Value of | Flow this | 1264.7754 | Abs Value of | Flow this | 1687.8477 | Abs Value of | Flow this | 2059.495 | Abs Value of | Flow this | 2391.0097 | Abs Value of | Flow this | 2721.1921 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9108 |  |  | 56.5355 |  |  | 54.5879 |  |  | 48.0833 |  |  | 32.055 |  |  | 2.8919 |  |  | -39.2956 |  |  | -86.33 |  |  | -136.1581 |  |  | -193.1644
[13 empty] | P2 at this iteration flow rate |  |  | 24.6578 |  |  | 24.7329 |  |  | 25.1224 |  |  | 26.4233 |  |  | 29.629 |  |  | 35.4616 |  |  | 43.8991 |  |  | 53.306 |  |  | 63.2716 |  |  | 74.6729
[13 empty] | Delta P at this iteration flow rate |  |  | 32.253 |  |  | 31.8026 |  |  | 29.4654 |  |  | 21.66 |  |  | 2.426 |  |  | -32.5697 |  |  | -83.1947 |  |  | -139.636 |  |  | -199.4297 |  |  | -267.8373
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.894 |  |  | 48.1041 |  |  | 45.0456 |  |  | 37.9035 |  |  | 23.7048 |  |  | 1.709 |  |  | -25.5013 |  |  | -50.4572 |  |  | -68.4707 |  |  | -72.9624
[13 empty] | C Non choked w/ reducers | 7 |  | 2.2095 |  |  | 18.8409 |  |  | 48.5199 |  |  | 110.8789 |  |  | 562.72 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.7764 |  |  | 15.3194 |  |  | 39.242 |  |  | 83.8182 |  |  | 180.0192 |  |  | 1010.5595 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.2095 |  |  | 18.8409 |  |  | 48.5199 |  |  | 110.8789 |  |  | 562.72 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.5205 | 12.5462 |  | 7.2409 | 106.1674 |  | 25.5199 | 262.5647 |  | 71.4789 | 511.409 |  | 501.72 | 857.9853 |  | 5500 | 1264.7754 |  | 5500 | 1687.8477 |  | 5500 | 2059.495 |  | 5500 | 2391.0097 |  | 5500 | 2721.1921
[13 empty] | Next iteration flow rate |  |  | 12.7972 | Abs Value of | Flow this | 107.2291 | Abs Value of | Flow this | 265.1904 | Abs Value of | Flow this | 516.5231 | Abs Value of | Flow this | 866.5651 | Abs Value of | Flow this | 1277.4232 | Abs Value of | Flow this | 1704.7262 | Abs Value of | Flow this | 2080.0899 | Abs Value of | Flow this | 2414.9198 | Abs Value of | Flow this | 2748.404 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9106 |  |  | 56.5278 |  |  | 54.5411 |  |  | 47.9058 |  |  | 31.5553 |  |  | 1.806 |  |  | -41.2295 |  |  | -89.2093 |  |  | -140.0389 |  |  | -198.1911
[13 empty] | P2 at this iteration flow rate |  |  | 24.6579 |  |  | 24.7344 |  |  | 25.1318 |  |  | 26.4588 |  |  | 29.7289 |  |  | 35.6788 |  |  | 44.2859 |  |  | 53.8819 |  |  | 64.0478 |  |  | 75.6782
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2527 |  |  | 31.7934 |  |  | 29.4093 |  |  | 21.447 |  |  | 1.8263 |  |  | -33.8727 |  |  | -85.5154 |  |  | -143.0911 |  |  | -204.0866 |  |  | -273.8693
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8938 |  |  | 48.0975 |  |  | 45.0066 |  |  | 37.7623 |  |  | 23.3301 |  |  | 0.95213 |  |  | -26.7424 |  |  | -52.1315 |  |  | -70.4159 |  |  | -74.8568
[13 empty] | C Non choked w/ reducers | 7 |  | 2.2537 |  |  | 19.0321 |  |  | 49.0519 |  |  | 112.5426 |  |  | 655.0397 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.812 |  |  | 15.4737 |  |  | 39.6515 |  |  | 84.8146 |  |  | 183.2736 |  |  | 1367.4419 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.2537 |  |  | 19.0321 |  |  | 49.0519 |  |  | 112.5426 |  |  | 655.0397 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.4763 | 12.7972 |  | 7.4321 | 107.2291 |  | 26.0519 | 265.1904 |  | 73.1426 | 516.5231 |  | 594.0397 | 866.5651 |  | 5500 | 1277.4232 |  | 5500 | 1704.7262 |  | 5500 | 2080.0899 |  | 5500 | 2414.9198 |  | 5500 | 2748.404
[13 empty] | Next iteration flow rate |  |  | 13.0531 | Abs Value of | Flow this | 108.3014 | Abs Value of | Flow this | 267.8423 | Abs Value of | Flow this | 521.6884 | Abs Value of | Flow this | 875.2308 | Abs Value of | Flow this | 1290.1974 | Abs Value of | Flow this | 1721.7734 | Abs Value of | Flow this | 2100.8908 | Abs Value of | Flow this | 2439.069 | Abs Value of | Flow this | 2775.888 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9104 |  |  | 56.52 |  |  | 54.4933 |  |  | 47.7247 |  |  | 31.0455 |  |  | 0.69833 |  |  | -43.2022 |  |  | -92.1464 |  |  | -143.9977 |  |  | -203.3187
[13 empty] | P2 at this iteration flow rate |  |  | 24.6579 |  |  | 24.736 |  |  | 25.1413 |  |  | 26.4951 |  |  | 29.8309 |  |  | 35.9003 |  |  | 44.6804 |  |  | 54.4693 |  |  | 64.8395 |  |  | 76.7037
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2525 |  |  | 31.784 |  |  | 29.352 |  |  | 21.2296 |  |  | 1.2146 |  |  | -35.202 |  |  | -87.8826 |  |  | -146.6157 |  |  | -208.8372 |  |  | -280.0225
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8936 |  |  | 48.0908 |  |  | 44.9669 |  |  | 37.6182 |  |  | 22.9479 |  |  | 0.18002 |  |  | -28.0085 |  |  | -53.8395 |  |  | -72.4003 |  |  | -76.7892
[13 empty] | C Non choked w/ reducers | 7 |  | 2.2987 |  |  | 19.2252 |  |  | 49.5907 |  |  | 114.2483 |  |  | 811.2541 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.8482 |  |  | 15.6295 |  |  | 40.0657 |  |  | 85.8266 |  |  | 186.6415 |  |  | 3176.2298 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.2987 |  |  | 19.2252 |  |  | 49.5907 |  |  | 114.2483 |  |  | 811.2541 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.4313 | 13.0531 |  | 7.6252 | 108.3014 |  | 26.5907 | 267.8423 |  | 74.8483 | 521.6884 |  | 750.2541 | 875.2308 |  | 5500 | 1290.1974 |  | 5500 | 1721.7734 |  | 5500 | 2100.8908 |  | 5500 | 2439.069 |  | 5500 | 2775.888
[13 empty] | Next iteration flow rate |  |  | 13.3142 | Abs Value of | Flow this | 109.3844 | Abs Value of | Flow this | 270.5207 | Abs Value of | Flow this | 526.9052 | Abs Value of | Flow this | 883.9831 | Abs Value of | Flow this | 1303.0994 | Abs Value of | Flow this | 1738.9912 | Abs Value of | Flow this | 2121.8997 | Abs Value of | Flow this | 2463.4597 | Abs Value of | Flow this | 2803.6469 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9102 |  |  | 56.5121 |  |  | 54.4446 |  |  | 47.5399 |  |  | 30.5255 |  |  | -0.43164 |  |  | -45.2146 |  |  | -95.1426 |  |  | -148.036 |  |  | -208.5494
[13 empty] | P2 at this iteration flow rate |  |  | 24.658 |  |  | 24.7376 |  |  | 25.1511 |  |  | 26.532 |  |  | 29.9349 |  |  | 36.1263 |  |  | 45.0829 |  |  | 55.0685 |  |  | 65.6472 |  |  | 77.7499
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2522 |  |  | 31.7745 |  |  | 29.2936 |  |  | 21.0079 |  |  | 0.59063 |  |  | -36.558 |  |  | -90.2975 |  |  | -150.2111 |  |  | -213.6832 |  |  | -286.2993
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8934 |  |  | 48.084 |  |  | 44.9264 |  |  | 37.4712 |  |  | 22.558 |  |  | -0.6076 |  |  | -29.3 |  |  | -55.5818 |  |  | -74.4245 |  |  | -78.7604
[13 empty] | C Non choked w/ reducers | 7 |  | 2.3447 |  |  | 19.4204 |  |  | 50.1366 |  |  | 115.9981 |  |  | 1175.0104 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.8852 |  |  | 15.7869 |  |  | 40.4846 |  |  | 86.8548 |  |  | 190.1301 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.3447 |  |  | 19.4204 |  |  | 50.1366 |  |  | 115.9981 |  |  | 1175.0104 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.3853 | 13.3142 |  | 7.8204 | 109.3844 |  | 27.1366 | 270.5207 |  | 76.5981 | 526.9052 |  | 1114.0104 | 883.9831 |  | 5500 | 1303.0994 |  | 5500 | 1738.9912 |  | 5500 | 2121.8997 |  | 5500 | 2463.4597 |  | 5500 | 2803.6469
[13 empty] | Next iteration flow rate |  |  | 13.5805 | Abs Value of | Flow this | 110.4783 | Abs Value of | Flow this | 273.2259 | Abs Value of | Flow this | 532.1743 | Abs Value of | Flow this | 892.8229 | Abs Value of | Flow this | 1316.1304 | Abs Value of | Flow this | 1756.3811 | Abs Value of | Flow this | 2143.1187 | Abs Value of | Flow this | 2488.0943 | Abs Value of | Flow this | 2831.6834 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9099 |  |  | 56.5039 |  |  | 54.395 |  |  | 47.3515 |  |  | 29.9951 |  |  | -1.5843 |  |  | -47.2674 |  |  | -98.1989 |  |  | -152.1556 |  |  | -213.8853
[13 empty] | P2 at this iteration flow rate |  |  | 24.658 |  |  | 24.7392 |  |  | 25.161 |  |  | 26.5697 |  |  | 30.041 |  |  | 36.3569 |  |  | 45.4935 |  |  | 55.6798 |  |  | 66.4711 |  |  | 78.8171
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2519 |  |  | 31.7647 |  |  | 29.2339 |  |  | 20.7818 |  |  | -0.045908 |  |  | -37.9412 |  |  | -92.7609 |  |  | -153.8787 |  |  | -218.6267 |  |  | -292.7024
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8932 |  |  | 48.077 |  |  | 44.8851 |  |  | 37.3213 |  |  | 22.1602 |  |  | -1.4111 |  |  | -30.6174 |  |  | -57.3591 |  |  | -76.4895 |  |  | -80.7713
[13 empty] | C Non choked w/ reducers | 7 |  | 2.3916 |  |  | 19.6176 |  |  | 50.6896 |  |  | 117.7938 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.9229 |  |  | 15.9459 |  |  | 40.9083 |  |  | 87.8993 |  |  | 193.747 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.3916 |  |  | 19.6176 |  |  | 50.6896 |  |  | 117.7938 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.3384 | 13.5805 |  | 8.0176 | 110.4783 |  | 27.6896 | 273.2259 |  | 78.3938 | 532.1743 |  | 5500 | 892.8229 |  | 5500 | 1316.1304 |  | 5500 | 1756.3811 |  | 5500 | 2143.1187 |  | 5500 | 2488.0943 |  | 5500 | 2831.6834
[13 empty] | Next iteration flow rate |  |  | 13.8521 | Abs Value of | Flow this | 111.583 | Abs Value of | Flow this | 275.9582 | Abs Value of | Flow this | 537.496 | Abs Value of | Flow this | 901.7512 | Abs Value of | Flow this | 1329.2917 | Abs Value of | Flow this | 1773.9449 | Abs Value of | Flow this | 2164.5499 | Abs Value of | Flow this | 2512.9752 | Abs Value of | Flow this | 2860.0002 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9097 |  |  | 56.4957 |  |  | 54.3443 |  |  | 47.1592 |  |  | 29.454 |  |  | -2.7602 |  |  | -49.3615 |  |  | -101.3168 |  |  | -156.3579 |  |  | -219.3284
[13 empty] | P2 at this iteration flow rate |  |  | 24.6581 |  |  | 24.7409 |  |  | 25.1711 |  |  | 26.6082 |  |  | 30.1492 |  |  | 36.592 |  |  | 45.9123 |  |  | 56.3034 |  |  | 67.3116 |  |  | 79.9057
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2516 |  |  | 31.7548 |  |  | 29.1731 |  |  | 20.5511 |  |  | -0.69524 |  |  | -39.3522 |  |  | -95.2738 |  |  | -157.6201 |  |  | -223.6695 |  |  | -299.2341
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8929 |  |  | 48.0699 |  |  | 44.8429 |  |  | 37.1683 |  |  | 21.7545 |  |  | -2.2307 |  |  | -31.9613 |  |  | -59.1721 |  |  | -78.5959 |  |  | -82.8226
[13 empty] | C Non choked w/ reducers | 7 |  | 2.4395 |  |  | 19.8169 |  |  | 51.2498 |  |  | 119.6376 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.9613 |  |  | 16.1066 |  |  | 41.3368 |  |  | 88.9608 |  |  | 197.5008 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.4395 |  |  | 19.8169 |  |  | 51.2498 |  |  | 119.6376 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.2905 | 13.8521 |  | 8.2169 | 111.583 |  | 28.2498 | 275.9582 |  | 80.2376 | 537.496 |  | 5500 | 901.7512 |  | 5500 | 1329.2917 |  | 5500 | 1773.9449 |  | 5500 | 2164.5499 |  | 5500 | 2512.9752 |  | 5500 | 2860.0002
[13 empty] | Next iteration flow rate |  |  | 14.1291 | Abs Value of | Flow this | 112.6989 | Abs Value of | Flow this | 278.7177 | Abs Value of | Flow this | 542.871 | Abs Value of | Flow this | 910.7687 | Abs Value of | Flow this | 1342.5846 | Abs Value of | Flow this | 1791.6843 | Abs Value of | Flow this | 2186.1954 | Abs Value of | Flow this | 2538.105 | Abs Value of | Flow this | 2888.6002 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9094 |  |  | 56.4872 |  |  | 54.2926 |  |  | 46.9631 |  |  | 28.902 |  |  | -3.9597 |  |  | -51.4977 |  |  | -104.4972 |  |  | -160.6447 |  |  | -224.8809
[13 empty] | P2 at this iteration flow rate |  |  | 24.6581 |  |  | 24.7426 |  |  | 25.1815 |  |  | 26.6474 |  |  | 30.2596 |  |  | 36.8319 |  |  | 46.3395 |  |  | 56.9394 |  |  | 68.1689 |  |  | 81.0162
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2513 |  |  | 31.7446 |  |  | 29.1111 |  |  | 20.3157 |  |  | -1.3576 |  |  | -40.7916 |  |  | -97.8372 |  |  | -161.4367 |  |  | -228.8137 |  |  | -305.8971
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8927 |  |  | 48.0627 |  |  | 44.7999 |  |  | 37.0123 |  |  | 21.3406 |  |  | -3.0667 |  |  | -33.3323 |  |  | -61.0216 |  |  | -80.7447 |  |  | -84.9152
[13 empty] | C Non choked w/ reducers | 7 |  | 2.4883 |  |  | 20.0183 |  |  | 51.8174 |  |  | 121.5319 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.0006 |  |  | 16.2689 |  |  | 41.7702 |  |  | 90.0396 |  |  | 201.4008 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.4883 |  |  | 20.0183 |  |  | 51.8174 |  |  | 121.5319 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.2417 | 14.1291 |  | 8.4183 | 112.6989 |  | 28.8174 | 278.7177 |  | 82.1319 | 542.871 |  | 5500 | 910.7687 |  | 5500 | 1342.5846 |  | 5500 | 1791.6843 |  | 5500 | 2186.1954 |  | 5500 | 2538.105 |  | 5500 | 2888.6002
[13 empty] | Next iteration flow rate |  |  | 14.4117 | Abs Value of | Flow this | 113.8259 | Abs Value of | Flow this | 281.5049 | Abs Value of | Flow this | 548.2997 | Abs Value of | Flow this | 919.8764 | Abs Value of | Flow this | 1356.0104 | Abs Value of | Flow this | 1809.6012 | Abs Value of | Flow this | 2208.0573 | Abs Value of | Flow this | 2563.486 | Abs Value of | Flow this | 2917.4862 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9091 |  |  | 56.4786 |  |  | 54.2399 |  |  | 46.7631 |  |  | 28.3389 |  |  | -5.1833 |  |  | -53.6768 |  |  | -107.7416 |  |  | -165.0177 |  |  | -230.545
[13 empty] | P2 at this iteration flow rate |  |  | 24.6582 |  |  | 24.7443 |  |  | 25.192 |  |  | 26.6874 |  |  | 30.3722 |  |  | 37.0767 |  |  | 46.7754 |  |  | 57.5883 |  |  | 69.0435 |  |  | 82.149
[13 empty] | Delta P at this iteration flow rate |  |  | 32.251 |  |  | 31.7343 |  |  | 29.0478 |  |  | 20.0757 |  |  | -2.0333 |  |  | -42.26 |  |  | -100.4521 |  |  | -165.33 |  |  | -234.0612 |  |  | -312.6941
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8925 |  |  | 48.0553 |  |  | 44.7561 |  |  | 36.8531 |  |  | 20.9184 |  |  | -3.9196 |  |  | -34.7308 |  |  | -62.9082 |  |  | -82.9367 |  |  | -87.0498
[13 empty] | C Non choked w/ reducers | 7 |  | 2.5381 |  |  | 20.2217 |  |  | 52.3925 |  |  | 123.4789 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.0406 |  |  | 16.4328 |  |  | 42.2085 |  |  | 91.1361 |  |  | 205.4573 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.5381 |  |  | 20.2217 |  |  | 52.3925 |  |  | 123.4789 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.1919 | 14.4117 |  | 8.6217 | 113.8259 |  | 29.3925 | 281.5049 |  | 84.0789 | 548.2997 |  | 5500 | 919.8764 |  | 5500 | 1356.0104 |  | 5500 | 1809.6012 |  | 5500 | 2208.0573 |  | 5500 | 2563.486 |  | 5500 | 2917.4862
[13 empty] | Next iteration flow rate |  |  | 14.6999 | Abs Value of | Flow this | 114.9641 | Abs Value of | Flow this | 284.32 | Abs Value of | Flow this | 553.7827 | Abs Value of | Flow this | 929.0751 | Abs Value of | Flow this | 1369.5705 | Abs Value of | Flow this | 1827.6972 | Abs Value of | Flow this | 2230.1379 | Abs Value of | Flow this | 2589.1209 | Abs Value of | Flow this | 2946.6611 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9088 |  |  | 56.4698 |  |  | 54.1861 |  |  | 46.559 |  |  | 27.7645 |  |  | -6.4315 |  |  | -55.8997 |  |  | -111.0513 |  |  | -169.4786 |  |  | -236.323
[13 empty] | P2 at this iteration flow rate |  |  | 24.6582 |  |  | 24.746 |  |  | 25.2028 |  |  | 26.7282 |  |  | 30.4871 |  |  | 37.3263 |  |  | 47.2199 |  |  | 58.2503 |  |  | 69.9357 |  |  | 83.3046
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2506 |  |  | 31.7237 |  |  | 28.9833 |  |  | 19.8308 |  |  | -2.7226 |  |  | -43.7578 |  |  | -103.1196 |  |  | -169.3015 |  |  | -239.4143 |  |  | -319.6276
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8922 |  |  | 48.0478 |  |  | 44.7113 |  |  | 36.6908 |  |  | 20.4878 |  |  | -4.7896 |  |  | -36.1574 |  |  | -64.8328 |  |  | -85.1727 |  |  | -89.2273
[13 empty] | C Non choked w/ reducers | 7 |  | 2.5888 |  |  | 20.4273 |  |  | 52.9754 |  |  | 125.4814 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.0814 |  |  | 16.5984 |  |  | 42.652 |  |  | 92.2509 |  |  | 209.6817 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.5888 |  |  | 20.4273 |  |  | 52.9754 |  |  | 125.4814 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.1412 | 14.6999 |  | 8.8273 | 114.9641 |  | 29.9754 | 284.32 |  | 86.0814 | 553.7827 |  | 5500 | 929.0751 |  | 5500 | 1369.5705 |  | 5500 | 1827.6972 |  | 5500 | 2230.1379 |  | 5500 | 2589.1209 |  | 5500 | 2946.6611
[13 empty] | Next iteration flow rate |  |  | 14.9939 | Abs Value of | Flow this | 116.1138 | Abs Value of | Flow this | 287.1632 | Abs Value of | Flow this | 559.3205 | Abs Value of | Flow this | 938.3659 | Abs Value of | Flow this | 1383.2662 | Abs Value of | Flow this | 1845.9742 | Abs Value of | Flow this | 2252.4393 | Abs Value of | Flow this | 2615.0121 | Abs Value of | Flow this | 2976.1277 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9086 |  |  | 56.4608 |  |  | 54.1312 |  |  | 46.3508 |  |  | 27.1785 |  |  | -7.7048 |  |  | -58.1673 |  |  | -114.4274 |  |  | -174.0291 |  |  | -242.2171
[13 empty] | P2 at this iteration flow rate |  |  | 24.6583 |  |  | 24.7478 |  |  | 25.2138 |  |  | 26.7698 |  |  | 30.6043 |  |  | 37.581 |  |  | 47.6735 |  |  | 58.9255 |  |  | 70.8458 |  |  | 84.4834
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2503 |  |  | 31.713 |  |  | 28.9174 |  |  | 19.581 |  |  | -3.4258 |  |  | -45.2857 |  |  | -105.8408 |  |  | -173.3529 |  |  | -244.8749 |  |  | -326.7006
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.892 |  |  | 48.0401 |  |  | 44.6657 |  |  | 36.5252 |  |  | 20.0484 |  |  | -5.6772 |  |  | -37.6127 |  |  | -66.796 |  |  | -87.4537 |  |  | -91.4486
[13 empty] | C Non choked w/ reducers | 7 |  | 2.6406 |  |  | 20.6351 |  |  | 53.566 |  |  | 127.5421 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.123 |  |  | 16.7658 |  |  | 43.1005 |  |  | 93.3845 |  |  | 214.0864 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.6406 |  |  | 20.6351 |  |  | 53.566 |  |  | 127.5421 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.0894 | 14.9939 |  | 9.0351 | 116.1138 |  | 30.566 | 287.1632 |  | 88.1421 | 559.3205 |  | 5500 | 938.3659 |  | 5500 | 1383.2662 |  | 5500 | 1845.9742 |  | 5500 | 2252.4393 |  | 5500 | 2615.0121 |  | 5500 | 2976.1277
[13 empty] | Next iteration flow rate |  |  | 15.2938 | Abs Value of | Flow this | 117.2749 | Abs Value of | Flow this | 290.0348 | Abs Value of | Flow this | 564.9137 | Abs Value of | Flow this | 947.7495 | Abs Value of | Flow this | 1397.0989 | Abs Value of | Flow this | 1864.4339 | Abs Value of | Flow this | 2274.9637 | Abs Value of | Flow this | 2641.1622 | Abs Value of | Flow this | 3005.889 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9082 |  |  | 56.4517 |  |  | 54.0752 |  |  | 46.1384 |  |  | 26.5808 |  |  | -9.0037 |  |  | -60.4805 |  |  | -117.8714 |  |  | -178.6711 |  |  | -248.2297
[13 empty] | P2 at this iteration flow rate |  |  | 24.6584 |  |  | 24.7497 |  |  | 25.225 |  |  | 26.8123 |  |  | 30.7238 |  |  | 37.8407 |  |  | 48.1361 |  |  | 59.6143 |  |  | 71.7742 |  |  | 85.6859
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2499 |  |  | 31.702 |  |  | 28.8502 |  |  | 19.3261 |  |  | -4.143 |  |  | -46.8444 |  |  | -108.6166 |  |  | -177.4857 |  |  | -250.4453 |  |  | -333.9156
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8917 |  |  | 48.0322 |  |  | 44.6191 |  |  | 36.3562 |  |  | 19.6002 |  |  | -6.5825 |  |  | -39.0972 |  |  | -68.7987 |  |  | -89.7806 |  |  | -93.7145
[13 empty] | C Non choked w/ reducers | 7 |  | 2.6934 |  |  | 20.8451 |  |  | 54.1646 |  |  | 129.664 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.1655 |  |  | 16.9348 |  |  | 43.5542 |  |  | 94.5372 |  |  | 218.6854 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.6934 |  |  | 20.8451 |  |  | 54.1646 |  |  | 129.664 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.0366 | 15.2938 |  | 9.2451 | 117.2749 |  | 31.1646 | 290.0348 |  | 90.264 | 564.9137 |  | 5500 | 947.7495 |  | 5500 | 1397.0989 |  | 5500 | 1864.4339 |  | 5500 | 2274.9637 |  | 5500 | 2641.1622 |  | 5500 | 3005.889
[13 empty] | Next iteration flow rate |  |  | 15.5997 | Abs Value of | Flow this | 118.4477 | Abs Value of | Flow this | 292.9351 | Abs Value of | Flow this | 570.5629 | Abs Value of | Flow this | 957.227 | Abs Value of | Flow this | 1411.0699 | Abs Value of | Flow this | 1883.0783 | Abs Value of | Flow this | 2297.7133 | Abs Value of | Flow this | 2667.5738 | Abs Value of | Flow this | 3035.9479 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9079 |  |  | 56.4423 |  |  | 54.0181 |  |  | 45.9218 |  |  | 25.9711 |  |  | -10.3286 |  |  | -62.8401 |  |  | -121.3847 |  |  | -183.4064 |  |  | -254.3631
[13 empty] | P2 at this iteration flow rate |  |  | 24.6584 |  |  | 24.7515 |  |  | 25.2364 |  |  | 26.8556 |  |  | 30.8458 |  |  | 38.1057 |  |  | 48.608 |  |  | 60.3169 |  |  | 72.7213 |  |  | 86.9126
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2495 |  |  | 31.6908 |  |  | 28.7817 |  |  | 19.0662 |  |  | -4.8747 |  |  | -48.4344 |  |  | -111.4482 |  |  | -181.7016 |  |  | -256.1277 |  |  | -341.2758
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8914 |  |  | 48.0242 |  |  | 44.5716 |  |  | 36.1839 |  |  | 19.1431 |  |  | -7.5061 |  |  | -40.6116 |  |  | -70.8417 |  |  | -92.1542 |  |  | -96.0259
[13 empty] | C Non choked w/ reducers | 7 |  | 2.7473 |  |  | 21.0573 |  |  | 54.7713 |  |  | 131.8504 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.2088 |  |  | 17.1056 |  |  | 44.0132 |  |  | 95.7097 |  |  | 223.4941 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.7473 |  |  | 21.0573 |  |  | 54.7713 |  |  | 131.8504 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.9827 | 15.5997 |  | 9.4573 | 118.4477 |  | 31.7713 | 292.9351 |  | 92.4504 | 570.5629 |  | 5500 | 957.227 |  | 5500 | 1411.0699 |  | 5500 | 1883.0783 |  | 5500 | 2297.7133 |  | 5500 | 2667.5738 |  | 5500 | 3035.9479
[13 empty] | Next iteration flow rate |  |  | 15.9117 | Abs Value of | Flow this | 119.6321 | Abs Value of | Flow this | 295.8645 | Abs Value of | Flow this | 576.2685 | Abs Value of | Flow this | 966.7993 | Abs Value of | Flow this | 1425.1806 | Abs Value of | Flow this | 1901.909 | Abs Value of | Flow this | 2320.6905 | Abs Value of | Flow this | 2694.2496 | Abs Value of | Flow this | 3066.3073 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9076 |  |  | 56.4328 |  |  | 53.9599 |  |  | 45.7008 |  |  | 25.3491 |  |  | -11.6803 |  |  | -65.2472 |  |  | -124.9685 |  |  | -188.2369 |  |  | -260.6198
[13 empty] | P2 at this iteration flow rate |  |  | 24.6585 |  |  | 24.7534 |  |  | 25.248 |  |  | 26.8998 |  |  | 30.9702 |  |  | 38.3761 |  |  | 49.0894 |  |  | 61.0337 |  |  | 73.6874 |  |  | 88.164
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2491 |  |  | 31.6794 |  |  | 28.7118 |  |  | 18.801 |  |  | -5.6211 |  |  | -50.0563 |  |  | -114.3367 |  |  | -186.0022 |  |  | -261.9242 |  |  | -348.7838
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8911 |  |  | 48.016 |  |  | 44.5231 |  |  | 36.0081 |  |  | 18.6767 |  |  | -8.4482 |  |  | -42.1564 |  |  | -72.9257 |  |  | -94.5755 |  |  | -98.3839
[13 empty] | C Non choked w/ reducers | 7 |  | 2.8023 |  |  | 21.2717 |  |  | 55.3864 |  |  | 134.1048 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.253 |  |  | 17.2781 |  |  | 44.4775 |  |  | 96.9025 |  |  | 228.53 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.8023 |  |  | 21.2717 |  |  | 55.3864 |  |  | 134.1048 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.9277 | 15.9117 |  | 9.6717 | 119.6321 |  | 32.3864 | 295.8645 |  | 94.7048 | 576.2685 |  | 5500 | 966.7993 |  | 5500 | 1425.1806 |  | 5500 | 1901.909 |  | 5500 | 2320.6905 |  | 5500 | 2694.2496 |  | 5500 | 3066.3073
[13 empty] | Next iteration flow rate |  |  | 16.2299 | Abs Value of | Flow this | 120.8284 | Abs Value of | Flow this | 298.8231 | Abs Value of | Flow this | 582.0312 | Abs Value of | Flow this | 976.4673 | Abs Value of | Flow this | 1439.4324 | Abs Value of | Flow this | 1920.9281 | Abs Value of | Flow this | 2343.8974 | Abs Value of | Flow this | 2721.1921 | Abs Value of | Flow this | 3096.9704 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9072 |  |  | 56.4231 |  |  | 53.9004 |  |  | 45.4754 |  |  | 24.7146 |  |  | -13.0591 |  |  | -67.7027 |  |  | -128.6244 |  |  | -193.1644 |  |  | -267.0023
[13 empty] | P2 at this iteration flow rate |  |  | 24.6586 |  |  | 24.7554 |  |  | 25.2599 |  |  | 26.9449 |  |  | 31.0971 |  |  | 38.6518 |  |  | 49.5805 |  |  | 61.7649 |  |  | 74.6729 |  |  | 89.4405
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2487 |  |  | 31.6677 |  |  | 28.6405 |  |  | 18.5305 |  |  | -6.3825 |  |  | -51.7109 |  |  | -117.2833 |  |  | -190.3893 |  |  | -267.8373 |  |  | -356.4428
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8908 |  |  | 48.0077 |  |  | 44.4737 |  |  | 35.8287 |  |  | 18.2009 |  |  | -9.4092 |  |  | -43.7323 |  |  | -75.0516 |  |  | -97.0454 |  |  | -100.7892
[13 empty] | C Non choked w/ reducers | 7 |  | 2.8584 |  |  | 21.4883 |  |  | 56.0098 |  |  | 136.4309 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.2981 |  |  | 17.4524 |  |  | 44.9472 |  |  | 98.1162 |  |  | 233.8124 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.8584 |  |  | 21.4883 |  |  | 56.0098 |  |  | 136.4309 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.8716 | 16.2299 |  | 9.8883 | 120.8284 |  | 33.0098 | 298.8231 |  | 97.0309 | 582.0312 |  | 5500 | 976.4673 |  | 5500 | 1439.4324 |  | 5500 | 1920.9281 |  | 5500 | 2343.8974 |  | 5500 | 2721.1921 |  | 5500 | 3096.9704
[13 empty] | Next iteration flow rate |  |  | 16.5545 | Abs Value of | Flow this | 122.0367 | Abs Value of | Flow this | 301.8114 | Abs Value of | Flow this | 587.8515 | Abs Value of | Flow this | 986.232 | Abs Value of | Flow this | 1453.8267 | Abs Value of | Flow this | 1940.1374 | Abs Value of | Flow this | 2367.3363 | Abs Value of | Flow this | 2748.404 | Abs Value of | Flow this | 3127.9401 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9069 |  |  | 56.4132 |  |  | 53.8398 |  |  | 45.2454 |  |  | 24.0673 |  |  | -14.4656 |  |  | -70.2076 |  |  | -132.3537 |  |  | -198.1911 |  |  | -273.5131
[13 empty] | P2 at this iteration flow rate |  |  | 24.6586 |  |  | 24.7574 |  |  | 25.272 |  |  | 26.9909 |  |  | 31.2265 |  |  | 38.9331 |  |  | 50.0815 |  |  | 62.5107 |  |  | 75.6782 |  |  | 90.7426
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2483 |  |  | 31.6558 |  |  | 28.5678 |  |  | 18.2545 |  |  | -7.1592 |  |  | -53.3987 |  |  | -120.2891 |  |  | -194.8645 |  |  | -273.8693 |  |  | -364.2557
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8905 |  |  | 47.9992 |  |  | 44.4233 |  |  | 35.6458 |  |  | 17.7156 |  |  | -10.3896 |  |  | -45.3398 |  |  | -77.2203 |  |  | -99.5651 |  |  | -103.2428
[13 empty] | C Non choked w/ reducers | 7 |  | 2.9155 |  |  | 21.7073 |  |  | 56.6419 |  |  | 138.8328 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.344 |  |  | 17.6285 |  |  | 45.4225 |  |  | 99.3513 |  |  | 239.3633 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.9155 |  |  | 21.7073 |  |  | 56.6419 |  |  | 138.8328 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.8145 | 16.5545 |  | 10.1073 | 122.0367 |  | 33.6419 | 301.8114 |  | 99.4328 | 587.8515 |  | 5500 | 986.232 |  | 5500 | 1453.8267 |  | 5500 | 1940.1374 |  | 5500 | 2367.3363 |  | 5500 | 2748.404 |  | 5500 | 3127.9401
[13 empty] | Next iteration flow rate |  |  | 16.8856 | Abs Value of | Flow this | 123.2571 | Abs Value of | Flow this | 304.8295 | Abs Value of | Flow this | 593.73 | Abs Value of | Flow this | 996.0943 | Abs Value of | Flow this | 1468.365 | Abs Value of | Flow this | 1959.5388 | Abs Value of | Flow this | 2391.0097 | Abs Value of | Flow this | 2775.888 | Abs Value of | Flow this | 3159.2195 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9065 |  |  | 56.4031 |  |  | 53.778 |  |  | 45.0109 |  |  | 23.4071 |  |  | -15.9003 |  |  | -72.7628 |  |  | -136.1581 |  |  | -203.3187 |  |  | -280.1547
[13 empty] | P2 at this iteration flow rate |  |  | 24.6587 |  |  | 24.7594 |  |  | 25.2844 |  |  | 27.0378 |  |  | 31.3586 |  |  | 39.2201 |  |  | 50.5926 |  |  | 63.2716 |  |  | 76.7037 |  |  | 92.0709
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2478 |  |  | 31.6437 |  |  | 28.4936 |  |  | 17.973 |  |  | -7.9515 |  |  | -55.1204 |  |  | -123.3553 |  |  | -199.4297 |  |  | -280.0225 |  |  | -372.2257
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8902 |  |  | 47.9905 |  |  | 44.3718 |  |  | 35.4591 |  |  | 17.2206 |  |  | -11.3897 |  |  | -46.9797 |  |  | -79.4325 |  |  | -102.1353 |  |  | -105.7458
[13 empty] | C Non choked w/ reducers | 7 |  | 2.9739 |  |  | 21.9286 |  |  | 57.2827 |  |  | 141.315 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.3909 |  |  | 17.8064 |  |  | 45.9033 |  |  | 100.6085 |  |  | 245.2073 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.9739 |  |  | 21.9286 |  |  | 57.2827 |  |  | 141.315 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.7561 | 16.8856 |  | 10.3286 | 123.2571 |  | 34.2827 | 304.8295 |  | 101.915 | 593.73 |  | 5500 | 996.0943 |  | 5500 | 1468.365 |  | 5500 | 1959.5388 |  | 5500 | 2391.0097 |  | 5500 | 2775.888 |  | 5500 | 3159.2195
[13 empty] | Next iteration flow rate |  |  | 17.2233 | Abs Value of | Flow this | 124.4897 | Abs Value of | Flow this | 307.8778 | Abs Value of | Flow this | 599.6673 | Abs Value of | Flow this | 1006.0552 | Abs Value of | Flow this | 1483.0486 | Abs Value of | Flow this | 1979.1342 | Abs Value of | Flow this | 2414.9198 | Abs Value of | Flow this | 2803.6469 | Abs Value of | Flow this | 3190.8117 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9061 |  |  | 56.3927 |  |  | 53.7149 |  |  | 44.7716 |  |  | 22.7335 |  |  | -17.3639 |  |  | -75.3693 |  |  | -140.0389 |  |  | -208.5494 |  |  | -286.9298
[13 empty] | P2 at this iteration flow rate |  |  | 24.6588 |  |  | 24.7615 |  |  | 25.297 |  |  | 27.0857 |  |  | 31.4933 |  |  | 39.5128 |  |  | 51.1139 |  |  | 64.0478 |  |  | 77.7499 |  |  | 93.426
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2473 |  |  | 31.6313 |  |  | 28.4179 |  |  | 17.6859 |  |  | -8.7598 |  |  | -56.8767 |  |  | -126.4832 |  |  | -204.0866 |  |  | -286.2993 |  |  | -380.3558
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8898 |  |  | 47.9817 |  |  | 44.3194 |  |  | 35.2688 |  |  | 16.7156 |  |  | -12.4099 |  |  | -48.6525 |  |  | -81.6892 |  |  | -104.7573 |  |  | -108.2991
[13 empty] | C Non choked w/ reducers | 7 |  | 3.0334 |  |  | 22.1522 |  |  | 57.9326 |  |  | 143.8822 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.4388 |  |  | 17.9861 |  |  | 46.3897 |  |  | 101.8885 |  |  | 251.3727 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.0334 |  |  | 22.1522 |  |  | 57.9326 |  |  | 143.8822 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.6966 | 17.2233 |  | 10.5522 | 124.4897 |  | 34.9326 | 307.8778 |  | 104.4822 | 599.6673 |  | 5500 | 1006.0552 |  | 5500 | 1483.0486 |  | 5500 | 1979.1342 |  | 5500 | 2414.9198 |  | 5500 | 2803.6469 |  | 5500 | 3190.8117
[13 empty] | Next iteration flow rate |  |  | 17.5678 | Abs Value of | Flow this | 125.7346 | Abs Value of | Flow this | 310.9566 | Abs Value of | Flow this | 605.664 | Abs Value of | Flow this | 1016.1158 | Abs Value of | Flow this | 1497.8791 | Abs Value of | Flow this | 1998.9255 | Abs Value of | Flow this | 2439.069 | Abs Value of | Flow this | 2831.6834 | Abs Value of | Flow this | 3222.7198 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9057 |  |  | 56.3822 |  |  | 53.6506 |  |  | 44.5275 |  |  | 22.0465 |  |  | -18.857 |  |  | -78.0282 |  |  | -143.9977 |  |  | -213.8853 |  |  | -293.8411
[13 empty] | P2 at this iteration flow rate |  |  | 24.6589 |  |  | 24.7636 |  |  | 25.3099 |  |  | 27.1345 |  |  | 31.6307 |  |  | 39.8114 |  |  | 51.6456 |  |  | 64.8395 |  |  | 78.8171 |  |  | 94.8082
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2469 |  |  | 31.6187 |  |  | 28.3407 |  |  | 17.393 |  |  | -9.5842 |  |  | -58.6684 |  |  | -129.6739 |  |  | -208.8372 |  |  | -292.7024 |  |  | -388.6494
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8895 |  |  | 47.9727 |  |  | 44.2658 |  |  | 35.0746 |  |  | 16.2004 |  |  | -13.4505 |  |  | -50.3589 |  |  | -83.9912 |  |  | -107.4319 |  |  | -110.9037
[13 empty] | C Non choked w/ reducers | 7 |  | 3.0941 |  |  | 22.3782 |  |  | 58.5915 |  |  | 146.5396 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.4875 |  |  | 18.1677 |  |  | 46.882 |  |  | 103.1919 |  |  | 257.8916 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.0941 |  |  | 22.3782 |  |  | 58.5915 |  |  | 146.5396 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.6359 | 17.5678 |  | 10.7782 | 125.7346 |  | 35.5915 | 310.9566 |  | 107.1396 | 605.664 |  | 5500 | 1016.1158 |  | 5500 | 1497.8791 |  | 5500 | 1998.9255 |  | 5500 | 2439.069 |  | 5500 | 2831.6834 |  | 5500 | 3222.7198
[13 empty] | Next iteration flow rate |  |  | 17.9191 | Abs Value of | Flow this | 126.9919 | Abs Value of | Flow this | 314.0661 | Abs Value of | Flow this | 611.7206 | Abs Value of | Flow this | 1026.2769 | Abs Value of | Flow this | 1512.8579 | Abs Value of | Flow this | 2018.9148 | Abs Value of | Flow this | 2463.4597 | Abs Value of | Flow this | 2860.0002 | Abs Value of | Flow this | 3254.947 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9053 |  |  | 56.3715 |  |  | 53.5849 |  |  | 44.2784 |  |  | 21.3456 |  |  | -20.38 |  |  | -80.7406 |  |  | -148.036 |  |  | -219.3284 |  |  | -300.8914
[13 empty] | P2 at this iteration flow rate |  |  | 24.6589 |  |  | 24.7657 |  |  | 25.323 |  |  | 27.1843 |  |  | 31.7709 |  |  | 40.116 |  |  | 52.1881 |  |  | 65.6472 |  |  | 79.9057 |  |  | 96.2183
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2464 |  |  | 31.6058 |  |  | 28.2619 |  |  | 17.0941 |  |  | -10.4253 |  |  | -60.496 |  |  | -132.9287 |  |  | -213.6832 |  |  | -299.2341 |  |  | -397.1096
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8891 |  |  | 47.9635 |  |  | 44.2112 |  |  | 34.8765 |  |  | 15.6749 |  |  | -14.5121 |  |  | -52.0997 |  |  | -86.3396 |  |  | -110.1603 |  |  | -113.5607
[13 empty] | C Non choked w/ reducers | 7 |  | 3.156 |  |  | 22.6066 |  |  | 59.2599 |  |  | 149.293 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.5373 |  |  | 18.3511 |  |  | 47.38 |  |  | 104.5194 |  |  | 264.8008 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.156 |  |  | 22.6066 |  |  | 59.2599 |  |  | 149.293 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.574 | 17.9191 |  | 11.0066 | 126.9919 |  | 36.2599 | 314.0661 |  | 109.893 | 611.7206 |  | 5500 | 1026.2769 |  | 5500 | 1512.8579 |  | 5500 | 2018.9148 |  | 5500 | 2463.4597 |  | 5500 | 2860.0002 |  | 5500 | 3254.947
[13 empty] | Next iteration flow rate |  |  | 18.2775 | Abs Value of | Flow this | 128.2618 | Abs Value of | Flow this | 317.2068 | Abs Value of | Flow this | 617.8378 | Abs Value of | Flow this | 1036.5397 | Abs Value of | Flow this | 1527.9865 | Abs Value of | Flow this | 2039.1039 | Abs Value of | Flow this | 2488.0943 | Abs Value of | Flow this | 2888.6002 | Abs Value of | Flow this | 3287.4965 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9049 |  |  | 56.3606 |  |  | 53.518 |  |  | 44.0244 |  |  | 20.6306 |  |  | -21.9337 |  |  | -83.5075 |  |  | -152.1556 |  |  | -224.8809 |  |  | -308.0833
[13 empty] | P2 at this iteration flow rate |  |  | 24.659 |  |  | 24.7679 |  |  | 25.3364 |  |  | 27.2351 |  |  | 31.9139 |  |  | 40.4267 |  |  | 52.7415 |  |  | 66.4711 |  |  | 81.0162 |  |  | 97.6567
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2458 |  |  | 31.5927 |  |  | 28.1816 |  |  | 16.7893 |  |  | -11.2833 |  |  | -62.3604 |  |  | -136.249 |  |  | -218.6267 |  |  | -305.8971 |  |  | -405.7399
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8887 |  |  | 47.9541 |  |  | 44.1555 |  |  | 34.6744 |  |  | 15.1388 |  |  | -15.5951 |  |  | -53.8754 |  |  | -88.7351 |  |  | -112.9435 |  |  | -116.2711
[13 empty] | C Non choked w/ reducers | 7 |  | 3.2191 |  |  | 22.8374 |  |  | 59.9377 |  |  | 152.1486 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.5881 |  |  | 18.5364 |  |  | 47.884 |  |  | 105.8718 |  |  | 272.1429 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.2191 |  |  | 22.8374 |  |  | 59.9377 |  |  | 152.1486 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.5109 | 18.2775 |  | 11.2374 | 128.2618 |  | 36.9377 | 317.2068 |  | 112.7486 | 617.8378 |  | 5500 | 1036.5397 |  | 5500 | 1527.9865 |  | 5500 | 2039.1039 |  | 5500 | 2488.0943 |  | 5500 | 2888.6002 |  | 5500 | 3287.4965
[13 empty] | Next iteration flow rate |  |  | 18.6431 | Abs Value of | Flow this | 129.5445 | Abs Value of | Flow this | 320.3788 | Abs Value of | Flow this | 624.0162 | Abs Value of | Flow this | 1046.9051 | Abs Value of | Flow this | 1543.2664 | Abs Value of | Flow this | 2059.495 | Abs Value of | Flow this | 2512.9752 | Abs Value of | Flow this | 2917.4862 | Abs Value of | Flow this | 3320.3715 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9044 |  |  | 56.3494 |  |  | 53.4497 |  |  | 43.7653 |  |  | 19.9013 |  |  | -23.5185 |  |  | -86.33 |  |  | -156.3579 |  |  | -230.545 |  |  | -315.4198
[13 empty] | P2 at this iteration flow rate |  |  | 24.6591 |  |  | 24.7701 |  |  | 25.3501 |  |  | 27.2869 |  |  | 32.0597 |  |  | 40.7437 |  |  | 53.306 |  |  | 67.3116 |  |  | 82.149 |  |  | 99.124
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2453 |  |  | 31.5793 |  |  | 28.0996 |  |  | 16.4784 |  |  | -12.1585 |  |  | -64.2623 |  |  | -139.636 |  |  | -223.6695 |  |  | -312.6941 |  |  | -414.5437
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8883 |  |  | 47.9445 |  |  | 44.0987 |  |  | 34.4682 |  |  | 14.5919 |  |  | -16.6998 |  |  | -55.6868 |  |  | -91.1788 |  |  | -115.7827 |  |  | -119.0359
[13 empty] | C Non choked w/ reducers | 7 |  | 3.2835 |  |  | 23.0706 |  |  | 60.6253 |  |  | 155.1132 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.6398 |  |  | 18.7237 |  |  | 48.394 |  |  | 107.2498 |  |  | 279.9674 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.2835 |  |  | 23.0706 |  |  | 60.6253 |  |  | 155.1132 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.4465 | 18.6431 |  | 11.4706 | 129.5445 |  | 37.6253 | 320.3788 |  | 115.7132 | 624.0162 |  | 5500 | 1046.9051 |  | 5500 | 1543.2664 |  | 5500 | 2059.495 |  | 5500 | 2512.9752 |  | 5500 | 2917.4862 |  | 5500 | 3320.3715
[13 empty] | Next iteration flow rate |  |  | 19.0159 | Abs Value of | Flow this | 130.8399 | Abs Value of | Flow this | 323.5826 | Abs Value of | Flow this | 630.2564 | Abs Value of | Flow this | 1057.3741 | Abs Value of | Flow this | 1558.699 | Abs Value of | Flow this | 2080.0899 | Abs Value of | Flow this | 2538.105 | Abs Value of | Flow this | 2946.6611 | Abs Value of | Flow this | 3353.5752 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9039 |  |  | 56.338 |  |  | 53.38 |  |  | 43.501 |  |  | 19.1573 |  |  | -25.1353 |  |  | -89.2093 |  |  | -160.6447 |  |  | -236.323 |  |  | -322.9037
[13 empty] | P2 at this iteration flow rate |  |  | 24.6592 |  |  | 24.7724 |  |  | 25.364 |  |  | 27.3398 |  |  | 32.2085 |  |  | 41.0671 |  |  | 53.8819 |  |  | 68.1689 |  |  | 83.3046 |  |  | 100.6207
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2447 |  |  | 31.5656 |  |  | 28.016 |  |  | 16.1612 |  |  | -13.0513 |  |  | -66.2023 |  |  | -143.0911 |  |  | -228.8137 |  |  | -319.6276 |  |  | -423.5245
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8879 |  |  | 47.9347 |  |  | 44.0407 |  |  | 34.2579 |  |  | 14.0341 |  |  | -17.8267 |  |  | -57.5346 |  |  | -93.6716 |  |  | -118.6789 |  |  | -121.8564
[13 empty] | C Non choked w/ reducers | 7 |  | 3.3492 |  |  | 23.3064 |  |  | 61.3229 |  |  | 158.1943 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.6926 |  |  | 18.9128 |  |  | 48.9101 |  |  | 108.6542 |  |  | 288.3323 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.3492 |  |  | 23.3064 |  |  | 61.3229 |  |  | 158.1943 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.3808 | 19.0159 |  | 11.7064 | 130.8399 |  | 38.3229 | 323.5826 |  | 118.7943 | 630.2564 |  | 5500 | 1057.3741 |  | 5500 | 1558.699 |  | 5500 | 2080.0899 |  | 5500 | 2538.105 |  | 5500 | 2946.6611 |  | 5500 | 3353.5752
[13 empty] | Next iteration flow rate |  |  | 19.3962 | Abs Value of | Flow this | 132.1483 | Abs Value of | Flow this | 326.8185 | Abs Value of | Flow this | 636.5589 | Abs Value of | Flow this | 1067.9479 | Abs Value of | Flow this | 1574.286 | Abs Value of | Flow this | 2100.8908 | Abs Value of | Flow this | 2563.486 | Abs Value of | Flow this | 2976.1277 | Abs Value of | Flow this | 3387.1109 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9034 |  |  | 56.3264 |  |  | 53.3089 |  |  | 43.2313 |  |  | 18.3983 |  |  | -26.7845 |  |  | -92.1464 |  |  | -165.0177 |  |  | -242.2171 |  |  | -330.5381
[13 empty] | P2 at this iteration flow rate |  |  | 24.6593 |  |  | 24.7747 |  |  | 25.3782 |  |  | 27.3937 |  |  | 32.3603 |  |  | 41.3969 |  |  | 54.4693 |  |  | 69.0435 |  |  | 84.4834 |  |  | 102.1476
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2441 |  |  | 31.5516 |  |  | 27.9307 |  |  | 15.8376 |  |  | -13.962 |  |  | -68.1814 |  |  | -146.6157 |  |  | -234.0612 |  |  | -326.7006 |  |  | -432.6857
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8874 |  |  | 47.9248 |  |  | 43.9816 |  |  | 34.0434 |  |  | 13.465 |  |  | -18.9762 |  |  | -59.4196 |  |  | -96.2145 |  |  | -121.6334 |  |  | -124.7335
[13 empty] | C Non choked w/ reducers | 7 |  | 3.4162 |  |  | 23.5447 |  |  | 62.0306 |  |  | 161.4001 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.7465 |  |  | 19.104 |  |  | 49.4324 |  |  | 110.086 |  |  | 297.3056 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.4162 |  |  | 23.5447 |  |  | 62.0306 |  |  | 161.4001 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.3138 | 19.3962 |  | 11.9447 | 132.1483 |  | 39.0306 | 326.8185 |  | 122.0001 | 636.5589 |  | 5500 | 1067.9479 |  | 5500 | 1574.286 |  | 5500 | 2100.8908 |  | 5500 | 2563.486 |  | 5500 | 2976.1277 |  | 5500 | 3387.1109
[13 empty] | Next iteration flow rate |  |  | 19.7842 | Abs Value of | Flow this | 133.4698 | Abs Value of | Flow this | 330.0866 | Abs Value of | Flow this | 642.9245 | Abs Value of | Flow this | 1078.6274 | Abs Value of | Flow this | 1590.0289 | Abs Value of | Flow this | 2121.8997 | Abs Value of | Flow this | 2589.1209 | Abs Value of | Flow this | 3005.889 | Abs Value of | Flow this | 3420.982 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9029 |  |  | 56.3145 |  |  | 53.2364 |  |  | 42.9563 |  |  | 17.6241 |  |  | -28.4669 |  |  | -95.1426 |  |  | -169.4786 |  |  | -248.2297 |  |  | -338.3259
[13 empty] | P2 at this iteration flow rate |  |  | 24.6594 |  |  | 24.7771 |  |  | 25.3927 |  |  | 27.4487 |  |  | 32.5152 |  |  | 41.7334 |  |  | 55.0685 |  |  | 69.9357 |  |  | 85.6859 |  |  | 103.7052
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2435 |  |  | 31.5374 |  |  | 27.8437 |  |  | 15.5075 |  |  | -14.8911 |  |  | -70.2003 |  |  | -150.2111 |  |  | -239.4143 |  |  | -333.9156 |  |  | -442.0311
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.887 |  |  | 47.9146 |  |  | 43.9213 |  |  | 33.8246 |  |  | 12.8845 |  |  | -20.1489 |  |  | -61.3425 |  |  | -98.8085 |  |  | -124.6472 |  |  | -127.6684
[13 empty] | C Non choked w/ reducers | 7 |  | 3.4846 |  |  | 23.7855 |  |  | 62.7487 |  |  | 164.7399 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.8014 |  |  | 19.297 |  |  | 49.961 |  |  | 111.5459 |  |  | 306.9685 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.4846 |  |  | 23.7855 |  |  | 62.7487 |  |  | 164.7399 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.2454 | 19.7842 |  | 12.1855 | 133.4698 |  | 39.7487 | 330.0866 |  | 125.3399 | 642.9245 |  | 5500 | 1078.6274 |  | 5500 | 1590.0289 |  | 5500 | 2121.8997 |  | 5500 | 2589.1209 |  | 5500 | 3005.889 |  | 5500 | 3420.982
[13 empty] | Next iteration flow rate |  |  | 20.1799 | Abs Value of | Flow this | 134.8045 | Abs Value of | Flow this | 333.3875 | Abs Value of | Flow this | 649.3538 | Abs Value of | Flow this | 1089.4136 | Abs Value of | Flow this | 1605.9292 | Abs Value of | Flow this | 2143.1187 | Abs Value of | Flow this | 2615.0121 | Abs Value of | Flow this | 3035.9479 | Abs Value of | Flow this | 3455.1919 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9024 |  |  | 56.3024 |  |  | 53.1624 |  |  | 42.6757 |  |  | 16.8343 |  |  | -30.1831 |  |  | -98.1989 |  |  | -174.0291 |  |  | -254.3631 |  |  | -346.2703
[13 empty] | P2 at this iteration flow rate |  |  | 24.6595 |  |  | 24.7795 |  |  | 25.4075 |  |  | 27.5049 |  |  | 32.6731 |  |  | 42.0766 |  |  | 55.6798 |  |  | 70.8458 |  |  | 86.9126 |  |  | 105.2941
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2429 |  |  | 31.5229 |  |  | 27.7549 |  |  | 15.1708 |  |  | -15.8388 |  |  | -72.2597 |  |  | -153.8787 |  |  | -244.8749 |  |  | -341.2758 |  |  | -451.5644
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8865 |  |  | 47.9042 |  |  | 43.8598 |  |  | 33.6013 |  |  | 12.2924 |  |  | -21.3451 |  |  | -63.304 |  |  | -101.4547 |  |  | -127.7217 |  |  | -130.6624
[13 empty] | C Non choked w/ reducers | 7 |  | 3.5543 |  |  | 24.0288 |  |  | 63.4775 |  |  | 168.2236 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.8575 |  |  | 19.4921 |  |  | 50.4959 |  |  | 113.035 |  |  | 317.4182 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.5543 |  |  | 24.0288 |  |  | 63.4775 |  |  | 168.2236 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.1757 | 20.1799 |  | 12.4288 | 134.8045 |  | 40.4775 | 333.3875 |  | 128.8236 | 649.3538 |  | 5500 | 1089.4136 |  | 5500 | 1605.9292 |  | 5500 | 2143.1187 |  | 5500 | 2615.0121 |  | 5500 | 3035.9479 |  | 5500 | 3455.1919
[13 empty] | Next iteration flow rate |  |  | 20.5834 | Abs Value of | Flow this | 136.1525 | Abs Value of | Flow this | 336.7214 | Abs Value of | Flow this | 655.8473 | Abs Value of | Flow this | 1100.3078 | Abs Value of | Flow this | 1621.9885 | Abs Value of | Flow this | 2164.5499 | Abs Value of | Flow this | 2641.1622 | Abs Value of | Flow this | 3066.3073 | Abs Value of | Flow this | 3489.7438 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9018 |  |  | 56.2901 |  |  | 53.087 |  |  | 42.3894 |  |  | 16.0287 |  |  | -31.9338 |  |  | -101.3168 |  |  | -178.6711 |  |  | -260.6198 |  |  | -354.3744
[13 empty] | P2 at this iteration flow rate |  |  | 24.6596 |  |  | 24.782 |  |  | 25.4226 |  |  | 27.5621 |  |  | 32.8343 |  |  | 42.4268 |  |  | 56.3034 |  |  | 71.7742 |  |  | 88.164 |  |  | 106.9149
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2422 |  |  | 31.5081 |  |  | 27.6644 |  |  | 14.8273 |  |  | -16.8056 |  |  | -74.3606 |  |  | -157.6201 |  |  | -250.4453 |  |  | -348.7838 |  |  | -461.2892
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.886 |  |  | 47.8937 |  |  | 43.797 |  |  | 33.3736 |  |  | 11.6883 |  |  | -22.5654 |  |  | -65.3049 |  |  | -104.154 |  |  | -130.8579 |  |  | -133.7165
[13 empty] | C Non choked w/ reducers | 7 |  | 3.6255 |  |  | 24.2748 |  |  | 64.2171 |  |  | 171.8625 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.9146 |  |  | 19.6892 |  |  | 51.0374 |  |  | 114.5542 |  |  | 328.7723 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.6255 |  |  | 24.2748 |  |  | 64.2171 |  |  | 171.8625 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.1045 | 20.5834 |  | 12.6748 | 136.1525 |  | 41.2171 | 336.7214 |  | 132.4625 | 655.8473 |  | 5500 | 1100.3078 |  | 5500 | 1621.9885 |  | 5500 | 2164.5499 |  | 5500 | 2641.1622 |  | 5500 | 3066.3073 |  | 5500 | 3489.7438
[13 empty] | Next iteration flow rate |  |  | 20.9951 | Abs Value of | Flow this | 137.514 | Abs Value of | Flow this | 340.0886 | Abs Value of | Flow this | 662.4058 | Abs Value of | Flow this | 1111.3109 | Abs Value of | Flow this | 1638.2083 | Abs Value of | Flow this | 2186.1954 | Abs Value of | Flow this | 2667.5738 | Abs Value of | Flow this | 3096.9704 | Abs Value of | Flow this | 3524.6412 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9013 |  |  | 56.2775 |  |  | 53.01 |  |  | 42.0975 |  |  | 15.2069 |  |  | -33.7197 |  |  | -104.4972 |  |  | -183.4064 |  |  | -267.0023 |  |  | -362.6413
[13 empty] | P2 at this iteration flow rate |  |  | 24.6597 |  |  | 24.7845 |  |  | 25.438 |  |  | 27.6205 |  |  | 32.9986 |  |  | 42.7839 |  |  | 56.9394 |  |  | 72.7213 |  |  | 89.4405 |  |  | 108.5683
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2415 |  |  | 31.493 |  |  | 27.572 |  |  | 14.4769 |  |  | -17.7918 |  |  | -76.5036 |  |  | -161.4367 |  |  | -256.1277 |  |  | -356.4428 |  |  | -471.2096
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8855 |  |  | 47.8829 |  |  | 43.733 |  |  | 33.1413 |  |  | 11.0721 |  |  | -23.8102 |  |  | -67.346 |  |  | -106.9076 |  |  | -134.0571 |  |  | -136.832
[13 empty] | C Non choked w/ reducers | 7 |  | 3.698 |  |  | 24.5235 |  |  | 64.9678 |  |  | 175.6692 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.973 |  |  | 19.8883 |  |  | 51.5855 |  |  | 116.1045 |  |  | 341.1752 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.698 |  |  | 24.5235 |  |  | 64.9678 |  |  | 175.6692 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.032 | 20.9951 |  | 12.9235 | 137.514 |  | 41.9678 | 340.0886 |  | 136.2692 | 662.4058 |  | 5500 | 1111.3109 |  | 5500 | 1638.2083 |  | 5500 | 2186.1954 |  | 5500 | 2667.5738 |  | 5500 | 3096.9704 |  | 5500 | 3524.6412
[13 empty] | Next iteration flow rate |  |  | 21.415 | Abs Value of | Flow this | 138.8892 | Abs Value of | Flow this | 343.4895 | Abs Value of | Flow this | 669.0298 | Abs Value of | Flow this | 1122.424 | Abs Value of | Flow this | 1654.5904 | Abs Value of | Flow this | 2208.0573 | Abs Value of | Flow this | 2694.2496 | Abs Value of | Flow this | 3127.9401 | Abs Value of | Flow this | 3559.8876 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9007 |  |  | 56.2647 |  |  | 52.9315 |  |  | 41.7996 |  |  | 14.3685 |  |  | -35.5415 |  |  | -107.7416 |  |  | -188.2369 |  |  | -273.5131 |  |  | -371.0744
[13 empty] | P2 at this iteration flow rate |  |  | 24.6599 |  |  | 24.7871 |  |  | 25.4537 |  |  | 27.6801 |  |  | 33.1663 |  |  | 43.1483 |  |  | 57.5883 |  |  | 73.6874 |  |  | 90.7426 |  |  | 110.2549
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2408 |  |  | 31.4776 |  |  | 27.4778 |  |  | 14.1195 |  |  | -18.7978 |  |  | -78.6897 |  |  | -165.33 |  |  | -261.9242 |  |  | -364.2557 |  |  | -481.3293
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.885 |  |  | 47.8719 |  |  | 43.6677 |  |  | 32.9044 |  |  | 10.4435 |  |  | -25.0801 |  |  | -69.4282 |  |  | -109.7166 |  |  | -137.3207 |  |  | -140.0101
[13 empty] | C Non choked w/ reducers | 7 |  | 3.772 |  |  | 24.7748 |  |  | 65.7299 |  |  | 179.6576 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.0324 |  |  | 20.0895 |  |  | 52.1403 |  |  | 117.687 |  |  | 354.8059 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.772 |  |  | 24.7748 |  |  | 65.7299 |  |  | 179.6576 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.95799 | 21.415 |  | 13.1748 | 138.8892 |  | 42.7299 | 343.4895 |  | 140.2576 | 669.0298 |  | 5500 | 1122.424 |  | 5500 | 1654.5904 |  | 5500 | 2208.0573 |  | 5500 | 2694.2496 |  | 5500 | 3127.9401 |  | 5500 | 3559.8876
[13 empty] | Next iteration flow rate |  |  | 21.8433 | Abs Value of | Flow this | 140.2781 | Abs Value of | Flow this | 346.9244 | Abs Value of | Flow this | 675.7201 | Abs Value of | Flow this | 1133.6482 | Abs Value of | Flow this | 1671.1363 | Abs Value of | Flow this | 2230.1379 | Abs Value of | Flow this | 2721.1921 | Abs Value of | Flow this | 3159.2195 | Abs Value of | Flow this | 3595.4865 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9 |  |  | 56.2516 |  |  | 52.8514 |  |  | 41.4958 |  |  | 13.5133 |  |  | -37.3999 |  |  | -111.0513 |  |  | -193.1644 |  |  | -280.1547 |  |  | -379.677
[13 empty] | P2 at this iteration flow rate |  |  | 24.66 |  |  | 24.7897 |  |  | 25.4697 |  |  | 27.7408 |  |  | 33.3373 |  |  | 43.52 |  |  | 58.2503 |  |  | 74.6729 |  |  | 92.0709 |  |  | 111.9754
[13 empty] | Delta P at this iteration flow rate |  |  | 32.24 |  |  | 31.4619 |  |  | 27.3817 |  |  | 13.7549 |  |  | -19.824 |  |  | -80.9198 |  |  | -169.3015 |  |  | -267.8373 |  |  | -372.2257 |  |  | -491.6524
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8844 |  |  | 47.8606 |  |  | 43.601 |  |  | 32.6626 |  |  | 9.8023 |  |  | -26.3754 |  |  | -71.5523 |  |  | -112.582 |  |  | -140.6499 |  |  | -143.2521
[13 empty] | C Non choked w/ reducers | 7 |  | 3.8475 |  |  | 25.0287 |  |  | 66.5036 |  |  | 183.8434 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.0931 |  |  | 20.2928 |  |  | 52.702 |  |  | 119.3029 |  |  | 369.8894 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.8475 |  |  | 25.0287 |  |  | 66.5036 |  |  | 183.8434 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.88251 | 21.8433 |  | 13.4287 | 140.2781 |  | 43.5036 | 346.9244 |  | 144.4434 | 675.7201 |  | 5500 | 1133.6482 |  | 5500 | 1671.1363 |  | 5500 | 2230.1379 |  | 5500 | 2721.1921 |  | 5500 | 3159.2195 |  | 5500 | 3595.4865
[13 empty] | Next iteration flow rate |  |  | 22.2802 | Abs Value of | Flow this | 141.6809 | Abs Value of | Flow this | 350.3936 | Abs Value of | Flow this | 682.4773 | Abs Value of | Flow this | 1144.9847 | Abs Value of | Flow this | 1687.8477 | Abs Value of | Flow this | 2252.4393 | Abs Value of | Flow this | 2748.404 | Abs Value of | Flow this | 3190.8117 | Abs Value of | Flow this | 3631.4414 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8994 |  |  | 56.2382 |  |  | 52.7697 |  |  | 41.1858 |  |  | 12.6409 |  |  | -39.2956 |  |  | -114.4274 |  |  | -198.1911 |  |  | -286.9298 |  |  | -388.4525
[13 empty] | P2 at this iteration flow rate |  |  | 24.6601 |  |  | 24.7924 |  |  | 25.4861 |  |  | 27.8028 |  |  | 33.5118 |  |  | 43.8991 |  |  | 58.9255 |  |  | 75.6782 |  |  | 93.426 |  |  | 113.7305
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2393 |  |  | 31.4459 |  |  | 27.2837 |  |  | 13.383 |  |  | -20.8709 |  |  | -83.1947 |  |  | -173.3529 |  |  | -273.8693 |  |  | -380.3558 |  |  | -502.183
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8838 |  |  | 47.8492 |  |  | 43.5331 |  |  | 32.4161 |  |  | 9.1481 |  |  | -27.6968 |  |  | -73.719 |  |  | -115.505 |  |  | -144.0459 |  |  | -146.5593
[13 empty] | C Non choked w/ reducers | 7 |  | 3.9245 |  |  | 25.2855 |  |  | 67.2892 |  |  | 188.2444 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.155 |  |  | 20.4982 |  |  | 53.2705 |  |  | 120.9534 |  |  | 386.7141 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.9245 |  |  | 25.2855 |  |  | 67.2892 |  |  | 188.2444 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.80551 | 22.2802 |  | 13.6855 | 141.6809 |  | 44.2892 | 350.3936 |  | 148.8444 | 682.4773 |  | 5500 | 1144.9847 |  | 5500 | 1687.8477 |  | 5500 | 2252.4393 |  | 5500 | 2748.404 |  | 5500 | 3190.8117 |  | 5500 | 3631.4414
[13 empty] | Next iteration flow rate |  |  | 22.7258 | Abs Value of | Flow this | 143.0977 | Abs Value of | Flow this | 353.8976 | Abs Value of | Flow this | 689.3021 | Abs Value of | Flow this | 1156.4345 | Abs Value of | Flow this | 1704.7262 | Abs Value of | Flow this | 2274.9637 | Abs Value of | Flow this | 2775.888 | Abs Value of | Flow this | 3222.7198 | Abs Value of | Flow this | 3667.7558 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8987 |  |  | 56.2246 |  |  | 52.6864 |  |  | 40.8696 |  |  | 11.751 |  |  | -41.2295 |  |  | -117.8714 |  |  | -203.3187 |  |  | -293.8411 |  |  | -397.4044
[13 empty] | P2 at this iteration flow rate |  |  | 24.6603 |  |  | 24.7951 |  |  | 25.5027 |  |  | 27.8661 |  |  | 33.6898 |  |  | 44.2859 |  |  | 59.6143 |  |  | 76.7037 |  |  | 94.8082 |  |  | 115.5209
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2384 |  |  | 31.4295 |  |  | 27.1836 |  |  | 13.0035 |  |  | -21.9388 |  |  | -85.5154 |  |  | -177.4857 |  |  | -280.0225 |  |  | -388.6494 |  |  | -512.9253
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8832 |  |  | 47.8375 |  |  | 43.4637 |  |  | 32.1645 |  |  | 8.4809 |  |  | -29.0447 |  |  | -75.9293 |  |  | -118.4867 |  |  | -147.5103 |  |  | -149.9329
[13 empty] | C Non choked w/ reducers | 7 |  | 4.003 |  |  | 25.545 |  |  | 68.087 |  |  | 192.8806 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.2181 |  |  | 20.7057 |  |  | 53.8461 |  |  | 122.6397 |  |  | 405.6556 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.003 |  |  | 25.545 |  |  | 68.087 |  |  | 192.8806 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.72697 | 22.7258 |  | 13.945 | 143.0977 |  | 45.087 | 353.8976 |  | 153.4806 | 689.3021 |  | 5500 | 1156.4345 |  | 5500 | 1704.7262 |  | 5500 | 2274.9637 |  | 5500 | 2775.888 |  | 5500 | 3222.7198 |  | 5500 | 3667.7558
[13 empty] | Next iteration flow rate |  |  | 23.1803 | Abs Value of | Flow this | 144.5286 | Abs Value of | Flow this | 357.4365 | Abs Value of | Flow this | 696.1951 | Abs Value of | Flow this | 1167.9989 | Abs Value of | Flow this | 1721.7734 | Abs Value of | Flow this | 2297.7133 | Abs Value of | Flow this | 2803.6469 | Abs Value of | Flow this | 3254.947 | Abs Value of | Flow this | 3704.4333 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.898 |  |  | 56.2107 |  |  | 52.6014 |  |  | 40.5471 |  |  | 10.8431 |  |  | -43.2022 |  |  | -121.3847 |  |  | -208.5494 |  |  | -300.8914 |  |  | -406.5363
[13 empty] | P2 at this iteration flow rate |  |  | 24.6604 |  |  | 24.7979 |  |  | 25.5197 |  |  | 27.9306 |  |  | 33.8714 |  |  | 44.6804 |  |  | 60.3169 |  |  | 77.7499 |  |  | 96.2183 |  |  | 117.3473
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2376 |  |  | 31.4128 |  |  | 27.0816 |  |  | 12.6165 |  |  | -23.0282 |  |  | -87.8826 |  |  | -181.7016 |  |  | -286.2993 |  |  | -397.1096 |  |  | -523.8835
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8826 |  |  | 47.8256 |  |  | 43.393 |  |  | 31.9079 |  |  | 7.8002 |  |  | -30.4198 |  |  | -78.184 |  |  | -121.5284 |  |  | -151.0442 |  |  | -153.3744
[13 empty] | C Non choked w/ reducers | 7 |  | 4.0831 |  |  | 25.8073 |  |  | 68.8973 |  |  | 197.775 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.2825 |  |  | 20.9154 |  |  | 54.4289 |  |  | 124.3632 |  |  | 427.215 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.0831 |  |  | 25.8073 |  |  | 68.8973 |  |  | 197.775 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.64686 | 23.1803 |  | 14.2073 | 144.5286 |  | 45.8973 | 357.4365 |  | 158.375 | 696.1951 |  | 5500 | 1167.9989 |  | 5500 | 1721.7734 |  | 5500 | 2297.7133 |  | 5500 | 2803.6469 |  | 5500 | 3254.947 |  | 5500 | 3704.4333
[13 empty] | Next iteration flow rate |  |  | 23.6439 | Abs Value of | Flow this | 145.9739 | Abs Value of | Flow this | 361.0109 | Abs Value of | Flow this | 703.1571 | Abs Value of | Flow this | 1179.6789 | Abs Value of | Flow this | 1738.9912 | Abs Value of | Flow this | 2320.6905 | Abs Value of | Flow this | 2831.6834 | Abs Value of | Flow this | 3287.4965 | Abs Value of | Flow this | 3741.4777 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8973 |  |  | 56.1965 |  |  | 52.5146 |  |  | 40.2181 |  |  | 9.9171 |  |  | -45.2146 |  |  | -124.9685 |  |  | -213.8853 |  |  | -308.0833 |  |  | -415.8517
[13 empty] | P2 at this iteration flow rate |  |  | 24.6605 |  |  | 24.8007 |  |  | 25.5371 |  |  | 27.9964 |  |  | 34.0566 |  |  | 45.0829 |  |  | 61.0337 |  |  | 78.8171 |  |  | 97.6567 |  |  | 119.2103
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2367 |  |  | 31.3958 |  |  | 26.9776 |  |  | 12.2217 |  |  | -24.1395 |  |  | -90.2975 |  |  | -186.0022 |  |  | -292.7024 |  |  | -405.7399 |  |  | -535.062
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.882 |  |  | 47.8134 |  |  | 43.3209 |  |  | 31.6462 |  |  | 7.1058 |  |  | -31.8225 |  |  | -80.484 |  |  | -124.6313 |  |  | -154.6492 |  |  | -156.885
[13 empty] | C Non choked w/ reducers | 7 |  | 4.1649 |  |  | 26.0724 |  |  | 69.7203 |  |  | 202.9536 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.3481 |  |  | 21.1272 |  |  | 55.0189 |  |  | 126.1252 |  |  | 452.0776 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.1649 |  |  | 26.0724 |  |  | 69.7203 |  |  | 202.9536 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.56514 | 23.6439 |  | 14.4724 | 145.9739 |  | 46.7203 | 361.0109 |  | 163.5536 | 703.1571 |  | 5500 | 1179.6789 |  | 5500 | 1738.9912 |  | 5500 | 2320.6905 |  | 5500 | 2831.6834 |  | 5500 | 3287.4965 |  | 5500 | 3741.4777
[13 empty] | Next iteration flow rate |  |  | 24.1168 | Abs Value of | Flow this | 147.4337 | Abs Value of | Flow this | 364.621 | Abs Value of | Flow this | 710.1887 | Abs Value of | Flow this | 1191.4757 | Abs Value of | Flow this | 1756.3811 | Abs Value of | Flow this | 2343.8974 | Abs Value of | Flow this | 2860.0002 | Abs Value of | Flow this | 3320.3715 | Abs Value of | Flow this | 3778.8925 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8965 |  |  | 56.182 |  |  | 52.4262 |  |  | 39.8824 |  |  | 8.9724 |  |  | -47.2674 |  |  | -128.6244 |  |  | -219.3284 |  |  | -315.4198 |  |  | -425.3543
[13 empty] | P2 at this iteration flow rate |  |  | 24.6607 |  |  | 24.8036 |  |  | 25.5548 |  |  | 28.0635 |  |  | 34.2455 |  |  | 45.4935 |  |  | 61.7649 |  |  | 79.9057 |  |  | 99.124 |  |  | 121.1109
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2358 |  |  | 31.3785 |  |  | 26.8714 |  |  | 11.8189 |  |  | -25.2731 |  |  | -92.7609 |  |  | -190.3893 |  |  | -299.2341 |  |  | -414.5437 |  |  | -546.4652
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8813 |  |  | 47.801 |  |  | 43.2473 |  |  | 31.3791 |  |  | 6.3975 |  |  | -33.2533 |  |  | -82.8302 |  |  | -127.7964 |  |  | -158.3267 |  |  | -160.4662
[13 empty] | C Non choked w/ reducers | 7 |  | 4.2482 |  |  | 26.3404 |  |  | 70.5565 |  |  | 208.4465 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.4151 |  |  | 21.3413 |  |  | 55.6164 |  |  | 127.9273 |  |  | 481.2118 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.2482 |  |  | 26.3404 |  |  | 70.5565 |  |  | 208.4465 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.48178 | 24.1168 |  | 14.7404 | 147.4337 |  | 47.5565 | 364.621 |  | 169.0465 | 710.1887 |  | 5500 | 1191.4757 |  | 5500 | 1756.3811 |  | 5500 | 2343.8974 |  | 5500 | 2860.0002 |  | 5500 | 3320.3715 |  | 5500 | 3778.8925
[13 empty] | Next iteration flow rate |  |  | 24.5991 | Abs Value of | Flow this | 148.908 | Abs Value of | Flow this | 368.2672 | Abs Value of | Flow this | 717.2906 | Abs Value of | Flow this | 1203.3904 | Abs Value of | Flow this | 1773.9449 | Abs Value of | Flow this | 2367.3363 | Abs Value of | Flow this | 2888.6002 | Abs Value of | Flow this | 3353.5752 | Abs Value of | Flow this | 3816.6814 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8957 |  |  | 56.1673 |  |  | 52.3359 |  |  | 39.5401 |  |  | 8.0087 |  |  | -49.3615 |  |  | -132.3537 |  |  | -224.8809 |  |  | -322.9037 |  |  | -435.0479
[13 empty] | P2 at this iteration flow rate |  |  | 24.6609 |  |  | 24.8065 |  |  | 25.5728 |  |  | 28.132 |  |  | 34.4383 |  |  | 45.9123 |  |  | 62.5107 |  |  | 81.0162 |  |  | 100.6207 |  |  | 123.0496
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2348 |  |  | 31.3607 |  |  | 26.7631 |  |  | 11.4081 |  |  | -26.4295 |  |  | -95.2738 |  |  | -194.8645 |  |  | -305.8971 |  |  | -423.5245 |  |  | -558.0975
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8806 |  |  | 47.7884 |  |  | 43.1722 |  |  | 31.1068 |  |  | 5.675 |  |  | -34.713 |  |  | -85.2236 |  |  | -131.0253 |  |  | -162.0781 |  |  | -164.1194
[13 empty] | C Non choked w/ reducers | 7 |  | 4.3332 |  |  | 26.6113 |  |  | 71.4061 |  |  | 214.2885 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.4835 |  |  | 21.5575 |  |  | 56.2214 |  |  | 129.771 |  |  | 516.0382 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.3332 |  |  | 26.6113 |  |  | 71.4061 |  |  | 214.2885 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.39675 | 24.5991 |  | 15.0113 | 148.908 |  | 48.4061 | 368.2672 |  | 174.8885 | 717.2906 |  | 5500 | 1203.3904 |  | 5500 | 1773.9449 |  | 5500 | 2367.3363 |  | 5500 | 2888.6002 |  | 5500 | 3353.5752 |  | 5500 | 3816.6814
[13 empty] | Next iteration flow rate |  |  | 25.0911 | Abs Value of | Flow this | 150.3971 | Abs Value of | Flow this | 371.9499 | Abs Value of | Flow this | 724.4635 | Abs Value of | Flow this | 1215.4243 | Abs Value of | Flow this | 1791.6843 | Abs Value of | Flow this | 2391.0097 | Abs Value of | Flow this | 2917.4862 | Abs Value of | Flow this | 3387.1109 | Abs Value of | Flow this | 3854.8482 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8949 |  |  | 56.1522 |  |  | 52.2438 |  |  | 39.1908 |  |  | 7.0257 |  |  | -51.4977 |  |  | -136.1581 |  |  | -230.545 |  |  | -330.5381 |  |  | -444.9364
[13 empty] | P2 at this iteration flow rate |  |  | 24.661 |  |  | 24.8096 |  |  | 25.5912 |  |  | 28.2018 |  |  | 34.6349 |  |  | 46.3395 |  |  | 63.2716 |  |  | 82.149 |  |  | 102.1476 |  |  | 125.0273
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2339 |  |  | 31.3427 |  |  | 26.6526 |  |  | 10.989 |  |  | -27.6092 |  |  | -97.8372 |  |  | -199.4297 |  |  | -312.6941 |  |  | -432.6857 |  |  | -569.9637
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8799 |  |  | 47.7754 |  |  | 43.0956 |  |  | 30.8289 |  |  | 4.9379 |  |  | -36.2019 |  |  | -87.6651 |  |  | -134.319 |  |  | -165.9048 |  |  | -167.846
[13 empty] | C Non choked w/ reducers | 7 |  | 4.42 |  |  | 26.8852 |  |  | 72.2695 |  |  | 220.52 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.5532 |  |  | 21.776 |  |  | 56.834 |  |  | 131.6581 |  |  | 558.7459 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.42 |  |  | 26.8852 |  |  | 72.2695 |  |  | 220.52 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.31002 | 25.0911 |  | 15.2852 | 150.3971 |  | 49.2695 | 371.9499 |  | 181.12 | 724.4635 |  | 5500 | 1215.4243 |  | 5500 | 1791.6843 |  | 5500 | 2391.0097 |  | 5500 | 2917.4862 |  | 5500 | 3387.1109 |  | 5500 | 3854.8482
[13 empty] | Next iteration flow rate |  |  | 25.5929 | Abs Value of | Flow this | 151.9011 | Abs Value of | Flow this | 375.6694 | Abs Value of | Flow this | 731.7081 | Abs Value of | Flow this | 1227.5786 | Abs Value of | Flow this | 1809.6012 | Abs Value of | Flow this | 2414.9198 | Abs Value of | Flow this | 2946.6611 | Abs Value of | Flow this | 3420.982 | Abs Value of | Flow this | 3893.3967 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.894 |  |  | 56.1369 |  |  | 52.1499 |  |  | 38.8345 |  |  | 6.0229 |  |  | -53.6768 |  |  | -140.0389 |  |  | -236.323 |  |  | -338.3259 |  |  | -455.0237
[13 empty] | P2 at this iteration flow rate |  |  | 24.6612 |  |  | 24.8126 |  |  | 25.61 |  |  | 28.2731 |  |  | 34.8354 |  |  | 46.7754 |  |  | 64.0478 |  |  | 83.3046 |  |  | 103.7052 |  |  | 127.0447
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2328 |  |  | 31.3243 |  |  | 26.5399 |  |  | 10.5614 |  |  | -28.8125 |  |  | -100.4521 |  |  | -204.0866 |  |  | -319.6276 |  |  | -442.0311 |  |  | -582.0684
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8791 |  |  | 47.7623 |  |  | 43.0175 |  |  | 30.5454 |  |  | 4.186 |  |  | -37.7208 |  |  | -90.1557 |  |  | -137.6789 |  |  | -169.8085 |  |  | -171.6475
[13 empty] | C Non choked w/ reducers | 7 |  | 4.5085 |  |  | 27.162 |  |  | 73.147 |  |  | 227.1886 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.6242 |  |  | 21.9968 |  |  | 57.4545 |  |  | 133.5902 |  |  | 612.9246 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.5085 |  |  | 27.162 |  |  | 73.147 |  |  | 227.1886 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.22155 | 25.5929 |  | 15.562 | 151.9011 |  | 50.147 | 375.6694 |  | 187.7886 | 731.7081 |  | 5500 | 1227.5786 |  | 5500 | 1809.6012 |  | 5500 | 2414.9198 |  | 5500 | 2946.6611 |  | 5500 | 3420.982 |  | 5500 | 3893.3967
[13 empty] | Next iteration flow rate |  |  | 26.1048 | Abs Value of | Flow this | 153.4201 | Abs Value of | Flow this | 379.4261 | Abs Value of | Flow this | 739.0252 | Abs Value of | Flow this | 1239.8543 | Abs Value of | Flow this | 1827.6972 | Abs Value of | Flow this | 2439.069 | Abs Value of | Flow this | 2976.1277 | Abs Value of | Flow this | 3455.1919 | Abs Value of | Flow this | 3932.3306 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8931 |  |  | 56.1212 |  |  | 52.0541 |  |  | 38.4711 |  |  | 4.9999 |  |  | -55.8997 |  |  | -143.9977 |  |  | -242.2171 |  |  | -346.2703 |  |  | -465.3137
[13 empty] | P2 at this iteration flow rate |  |  | 24.6614 |  |  | 24.8158 |  |  | 25.6292 |  |  | 28.3458 |  |  | 35.04 |  |  | 47.2199 |  |  | 64.8395 |  |  | 84.4834 |  |  | 105.2941 |  |  | 129.1027
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2318 |  |  | 31.3055 |  |  | 26.425 |  |  | 10.1253 |  |  | -30.0401 |  |  | -103.1196 |  |  | -208.8372 |  |  | -326.7006 |  |  | -451.5644 |  |  | -594.4164
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8783 |  |  | 47.7488 |  |  | 42.9378 |  |  | 30.2563 |  |  | 3.419 |  |  | -39.2703 |  |  | -92.6964 |  |  | -141.1063 |  |  | -173.7907 |  |  | -175.5254
[13 empty] | C Non choked w/ reducers | 7 |  | 4.5987 |  |  | 27.4419 |  |  | 74.039 |  |  | 234.3501 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.6968 |  |  | 22.2199 |  |  | 58.0828 |  |  | 135.5693 |  |  | 684.9819 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.5987 |  |  | 27.4419 |  |  | 74.039 |  |  | 234.3501 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.1313 | 26.1048 |  | 15.8419 | 153.4201 |  | 51.039 | 379.4261 |  | 194.9501 | 739.0252 |  | 5500 | 1239.8543 |  | 5500 | 1827.6972 |  | 5500 | 2439.069 |  | 5500 | 2976.1277 |  | 5500 | 3455.1919 |  | 5500 | 3932.3306
[13 empty] | Next iteration flow rate |  |  | 26.6269 | Abs Value of | Flow this | 154.9543 | Abs Value of | Flow this | 383.2203 | Abs Value of | Flow this | 746.4154 | Abs Value of | Flow this | 1252.2529 | Abs Value of | Flow this | 1845.9742 | Abs Value of | Flow this | 2463.4597 | Abs Value of | Flow this | 3005.889 | Abs Value of | Flow this | 3489.7438 | Abs Value of | Flow this | 3971.654 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8922 |  |  | 56.1052 |  |  | 51.9564 |  |  | 38.1003 |  |  | 3.9564 |  |  | -58.1673 |  |  | -148.036 |  |  | -248.2297 |  |  | -354.3744 |  |  | -475.8105
[13 empty] | P2 at this iteration flow rate |  |  | 24.6616 |  |  | 24.819 |  |  | 25.6487 |  |  | 28.4199 |  |  | 35.2487 |  |  | 47.6735 |  |  | 65.6472 |  |  | 85.6859 |  |  | 106.9149 |  |  | 131.2021
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2306 |  |  | 31.2863 |  |  | 26.3077 |  |  | 9.6804 |  |  | -31.2923 |  |  | -105.8408 |  |  | -213.6832 |  |  | -333.9156 |  |  | -461.2892 |  |  | -607.0126
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8775 |  |  | 47.7351 |  |  | 42.8565 |  |  | 29.9614 |  |  | 2.6366 |  |  | -40.8509 |  |  | -95.2881 |  |  | -144.6027 |  |  | -177.8529 |  |  | -179.4813
[13 empty] | C Non choked w/ reducers | 7 |  | 4.6908 |  |  | 27.7248 |  |  | 74.9458 |  |  | 242.0716 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.7707 |  |  | 22.4453 |  |  | 58.7193 |  |  | 137.5973 |  |  | 787.8259 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.6908 |  |  | 27.7248 |  |  | 74.9458 |  |  | 242.0716 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.039245 | 26.6269 |  | 16.1248 | 154.9543 |  | 51.9458 | 383.2203 |  | 202.6716 | 746.4154 |  | 5500 | 1252.2529 |  | 5500 | 1845.9742 |  | 5500 | 2463.4597 |  | 5500 | 3005.889 |  | 5500 | 3489.7438 |  | 5500 | 3971.654
[13 empty] | Next iteration flow rate |  |  | 27.1594 | Abs Value of | Flow this | 156.5038 | Abs Value of | Flow this | 387.0526 | Abs Value of | Flow this | 753.8796 | Abs Value of | Flow this | 1264.7754 | Abs Value of | Flow this | 1864.4339 | Abs Value of | Flow this | 2488.0943 | Abs Value of | Flow this | 3035.9479 | Abs Value of | Flow this | 3524.6412 | Abs Value of | Flow this | 4011.3705 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8912 |  |  | 56.0889 |  |  | 51.8567 |  |  | 37.7221 |  |  | 2.8919 |  |  | -60.4805 |  |  | -152.1556 |  |  | -254.3631 |  |  | -362.6413 |  |  | -486.5183
[13 empty] | P2 at this iteration flow rate |  |  | 24.6618 |  |  | 24.8222 |  |  | 25.6687 |  |  | 28.4956 |  |  | 35.4616 |  |  | 48.1361 |  |  | 66.4711 |  |  | 86.9126 |  |  | 108.5683 |  |  | 133.3437
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2295 |  |  | 31.2667 |  |  | 26.1881 |  |  | 9.2266 |  |  | -32.5697 |  |  | -108.6166 |  |  | -218.6267 |  |  | -341.2758 |  |  | -471.2096 |  |  | -619.8619
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8766 |  |  | 47.7212 |  |  | 42.7735 |  |  | 29.6605 |  |  | 1.8384 |  |  | -42.4632 |  |  | -97.9319 |  |  | -148.1693 |  |  | -181.9968 |  |  | -183.5167
[13 empty] | C Non choked w/ reducers | 7 |  | 4.7847 |  |  | 28.0108 |  |  | 75.868 |  |  | 250.4331 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.8462 |  |  | 22.6731 |  |  | 59.3639 |  |  | 139.6764 |  |  | 952.9046 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.7847 |  |  | 28.0108 |  |  | 75.868 |  |  | 250.4331 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.054657 | 27.1594 |  | 16.4108 | 156.5038 |  | 52.868 | 387.0526 |  | 211.0331 | 753.8796 |  | 5500 | 1264.7754 |  | 5500 | 1864.4339 |  | 5500 | 2488.0943 |  | 5500 | 3035.9479 |  | 5500 | 3524.6412 |  | 5500 | 4011.3705
[13 empty] | Next iteration flow rate |  |  | 27.7026 | Abs Value of | Flow this | 158.0689 | Abs Value of | Flow this | 390.9231 | Abs Value of | Flow this | 761.4184 | Abs Value of | Flow this | 1277.4232 | Abs Value of | Flow this | 1883.0783 | Abs Value of | Flow this | 2512.9752 | Abs Value of | Flow this | 3066.3073 | Abs Value of | Flow this | 3559.8876 | Abs Value of | Flow this | 4051.4842 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8902 |  |  | 56.0723 |  |  | 51.755 |  |  | 37.3363 |  |  | 1.806 |  |  | -62.8401 |  |  | -156.3579 |  |  | -260.6198 |  |  | -371.0744 |  |  | -497.4413
[13 empty] | P2 at this iteration flow rate |  |  | 24.662 |  |  | 24.8255 |  |  | 25.689 |  |  | 28.5727 |  |  | 35.6788 |  |  | 48.608 |  |  | 67.3116 |  |  | 88.164 |  |  | 110.2549 |  |  | 135.5283
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2283 |  |  | 31.2468 |  |  | 26.066 |  |  | 8.7636 |  |  | -33.8727 |  |  | -111.4482 |  |  | -223.6695 |  |  | -348.7838 |  |  | -481.3293 |  |  | -632.9696
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8758 |  |  | 47.7069 |  |  | 42.6889 |  |  | 29.3535 |  |  | 1.0242 |  |  | -44.1079 |  |  | -100.6289 |  |  | -151.8076 |  |  | -186.2239 |  |  | -187.6331
[13 empty] | C Non choked w/ reducers | 7 |  | 4.8804 |  |  | 28.2999 |  |  | 76.8058 |  |  | 259.5325 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.9231 |  |  | 22.9033 |  |  | 60.017 |  |  | 141.8088 |  |  | 1289.426 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.8804 |  |  | 28.2999 |  |  | 76.8058 |  |  | 259.5325 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.15044 | 27.7026 |  | 16.6999 | 158.0689 |  | 53.8058 | 390.9231 |  | 220.1325 | 761.4184 |  | 5500 | 1277.4232 |  | 5500 | 1883.0783 |  | 5500 | 2512.9752 |  | 5500 | 3066.3073 |  | 5500 | 3559.8876 |  | 5500 | 4051.4842
[13 empty] | Next iteration flow rate |  |  | 28.2567 | Abs Value of | Flow this | 159.6495 | Abs Value of | Flow this | 394.8323 | Abs Value of | Flow this | 769.0326 | Abs Value of | Flow this | 1290.1974 | Abs Value of | Flow this | 1901.909 | Abs Value of | Flow this | 2538.105 | Abs Value of | Flow this | 3096.9704 | Abs Value of | Flow this | 3595.4865 | Abs Value of | Flow this | 4091.999 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8892 |  |  | 56.0554 |  |  | 51.6513 |  |  | 36.9428 |  |  | 0.69833 |  |  | -65.2472 |  |  | -160.6447 |  |  | -267.0023 |  |  | -379.677 |  |  | -508.5839
[13 empty] | P2 at this iteration flow rate |  |  | 24.6622 |  |  | 24.8289 |  |  | 25.7097 |  |  | 28.6514 |  |  | 35.9003 |  |  | 49.0894 |  |  | 68.1689 |  |  | 89.4405 |  |  | 111.9754 |  |  | 137.7568
[13 empty] | Delta P at this iteration flow rate |  |  | 32.227 |  |  | 31.2264 |  |  | 25.9415 |  |  | 8.2913 |  |  | -35.202 |  |  | -114.3367 |  |  | -228.8137 |  |  | -356.4428 |  |  | -491.6524 |  |  | -646.3407
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8748 |  |  | 47.6924 |  |  | 42.6026 |  |  | 29.0404 |  |  | 0.19365 |  |  | -45.7858 |  |  | -103.38 |  |  | -155.5191 |  |  | -190.536 |  |  | -191.8324
[13 empty] | C Non choked w/ reducers | 7 |  | 4.9781 |  |  | 28.5922 |  |  | 77.7598 |  |  | 269.4897 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.0016 |  |  | 23.1358 |  |  | 60.6785 |  |  | 143.9969 |  |  | 2995.0182 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.9781 |  |  | 28.5922 |  |  | 77.7598 |  |  | 269.4897 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.24815 | 28.2567 |  | 16.9922 | 159.6495 |  | 54.7598 | 394.8323 |  | 230.0897 | 769.0326 |  | 5500 | 1290.1974 |  | 5500 | 1901.909 |  | 5500 | 2538.105 |  | 5500 | 3096.9704 |  | 5500 | 3595.4865 |  | 5500 | 4091.999
[13 empty] | Next iteration flow rate |  |  | 28.8218 | Abs Value of | Flow this | 161.246 | Abs Value of | Flow this | 398.7806 | Abs Value of | Flow this | 776.7229 | Abs Value of | Flow this | 1303.0994 | Abs Value of | Flow this | 1920.9281 | Abs Value of | Flow this | 2563.486 | Abs Value of | Flow this | 3127.9401 | Abs Value of | Flow this | 3631.4414 | Abs Value of | Flow this | 4132.919 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8881 |  |  | 56.0381 |  |  | 51.5455 |  |  | 36.5413 |  |  | -0.43164 |  |  | -67.7027 |  |  | -165.0177 |  |  | -273.5131 |  |  | -388.4525 |  |  | -519.9504
[13 empty] | P2 at this iteration flow rate |  |  | 24.6624 |  |  | 24.8324 |  |  | 25.7309 |  |  | 28.7317 |  |  | 36.1263 |  |  | 49.5805 |  |  | 69.0435 |  |  | 90.7426 |  |  | 113.7305 |  |  | 140.0301
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2257 |  |  | 31.2057 |  |  | 25.8145 |  |  | 7.8096 |  |  | -36.558 |  |  | -117.2833 |  |  | -234.0612 |  |  | -364.2557 |  |  | -502.183 |  |  | -659.9805
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8739 |  |  | 47.6775 |  |  | 42.5146 |  |  | 28.721 |  |  | -0.6536 |  |  | -47.4973 |  |  | -106.1865 |  |  | -159.3051 |  |  | -194.9348 |  |  | -196.116
[13 empty] | C Non choked w/ reducers | 7 |  | 5.0778 |  |  | 28.8878 |  |  | 78.7303 |  |  | 280.4542 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.0817 |  |  | 23.3708 |  |  | 61.3487 |  |  | 146.2433 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.0778 |  |  | 28.8878 |  |  | 78.7303 |  |  | 280.4542 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.34781 | 28.8218 |  | 17.2878 | 161.246 |  | 55.7303 | 398.7806 |  | 241.0542 | 776.7229 |  | 5500 | 1303.0994 |  | 5500 | 1920.9281 |  | 5500 | 2563.486 |  | 5500 | 3127.9401 |  | 5500 | 3631.4414 |  | 5500 | 4132.919
[13 empty] | Next iteration flow rate |  |  | 29.3982 | Abs Value of | Flow this | 162.8585 | Abs Value of | Flow this | 402.7684 | Abs Value of | Flow this | 784.4901 | Abs Value of | Flow this | 1316.1304 | Abs Value of | Flow this | 1940.1374 | Abs Value of | Flow this | 2589.1209 | Abs Value of | Flow this | 3159.2195 | Abs Value of | Flow this | 3667.7558 | Abs Value of | Flow this | 4174.2482 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.887 |  |  | 56.0204 |  |  | 51.4375 |  |  | 36.1318 |  |  | -1.5843 |  |  | -70.2076 |  |  | -169.4786 |  |  | -280.1547 |  |  | -397.4044 |  |  | -531.5455
[13 empty] | P2 at this iteration flow rate |  |  | 24.6626 |  |  | 24.8359 |  |  | 25.7525 |  |  | 28.8136 |  |  | 36.3569 |  |  | 50.0815 |  |  | 69.9357 |  |  | 92.0709 |  |  | 115.5209 |  |  | 142.3491
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2243 |  |  | 31.1845 |  |  | 25.685 |  |  | 7.3181 |  |  | -37.9412 |  |  | -120.2891 |  |  | -239.4143 |  |  | -372.2257 |  |  | -512.9253 |  |  | -673.8946
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8729 |  |  | 47.6624 |  |  | 42.4248 |  |  | 28.3952 |  |  | -1.5179 |  |  | -49.2432 |  |  | -109.0494 |  |  | -163.1672 |  |  | -199.422 |  |  | -200.4857
[13 empty] | C Non choked w/ reducers | 7 |  | 5.1795 |  |  | 29.1866 |  |  | 79.7179 |  |  | 292.6152 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.1634 |  |  | 23.6083 |  |  | 62.0277 |  |  | 148.5507 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.1795 |  |  | 29.1866 |  |  | 79.7179 |  |  | 292.6152 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.44948 | 29.3982 |  | 17.5866 | 162.8585 |  | 56.7179 | 402.7684 |  | 253.2152 | 784.4901 |  | 5500 | 1316.1304 |  | 5500 | 1940.1374 |  | 5500 | 2589.1209 |  | 5500 | 3159.2195 |  | 5500 | 3667.7558 |  | 5500 | 4174.2482
[13 empty] | Next iteration flow rate |  |  | 29.9862 | Abs Value of | Flow this | 164.4871 | Abs Value of | Flow this | 406.7961 | Abs Value of | Flow this | 792.335 | Abs Value of | Flow this | 1329.2917 | Abs Value of | Flow this | 1959.5388 | Abs Value of | Flow this | 2615.0121 | Abs Value of | Flow this | 3190.8117 | Abs Value of | Flow this | 3704.4333 | Abs Value of | Flow this | 4215.9907 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8858 |  |  | 56.0024 |  |  | 51.3274 |  |  | 35.714 |  |  | -2.7602 |  |  | -72.7628 |  |  | -174.0291 |  |  | -286.9298 |  |  | -406.5363 |  |  | -543.3735
[13 empty] | P2 at this iteration flow rate |  |  | 24.6628 |  |  | 24.8395 |  |  | 25.7745 |  |  | 28.8972 |  |  | 36.592 |  |  | 50.5926 |  |  | 70.8458 |  |  | 93.426 |  |  | 117.3473 |  |  | 144.7147
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2229 |  |  | 31.1629 |  |  | 25.5529 |  |  | 6.8168 |  |  | -39.3522 |  |  | -123.3553 |  |  | -244.8749 |  |  | -380.3558 |  |  | -523.8835 |  |  | -688.0883
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8718 |  |  | 47.647 |  |  | 42.3332 |  |  | 28.0629 |  |  | -2.3995 |  |  | -51.0243 |  |  | -111.9698 |  |  | -167.107 |  |  | -203.9994 |  |  | -204.9433
[13 empty] | C Non choked w/ reducers | 7 |  | 5.2832 |  |  | 29.4886 |  |  | 80.723 |  |  | 306.2158 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.2467 |  |  | 23.8482 |  |  | 62.7158 |  |  | 150.9221 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.2832 |  |  | 29.4886 |  |  | 80.723 |  |  | 306.2158 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.55318 | 29.9862 |  | 17.8886 | 164.4871 |  | 57.723 | 406.7961 |  | 266.8158 | 792.335 |  | 5500 | 1329.2917 |  | 5500 | 1959.5388 |  | 5500 | 2615.0121 |  | 5500 | 3190.8117 |  | 5500 | 3704.4333 |  | 5500 | 4215.9907
[13 empty] | Next iteration flow rate |  |  | 30.5859 | Abs Value of | Flow this | 166.132 | Abs Value of | Flow this | 410.8641 | Abs Value of | Flow this | 800.2584 | Abs Value of | Flow this | 1342.5846 | Abs Value of | Flow this | 1979.1342 | Abs Value of | Flow this | 2641.1622 | Abs Value of | Flow this | 3222.7198 | Abs Value of | Flow this | 3741.4777 | Abs Value of | Flow this | 4258.1506 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8845 |  |  | 55.984 |  |  | 51.2151 |  |  | 35.2879 |  |  | -3.9597 |  |  | -75.3693 |  |  | -178.6711 |  |  | -293.8411 |  |  | -415.8517 |  |  | -555.4394
[13 empty] | P2 at this iteration flow rate |  |  | 24.6631 |  |  | 24.8432 |  |  | 25.797 |  |  | 28.9824 |  |  | 36.8319 |  |  | 51.1139 |  |  | 71.7742 |  |  | 94.8082 |  |  | 119.2103 |  |  | 147.1279
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2215 |  |  | 31.1408 |  |  | 25.4181 |  |  | 6.3054 |  |  | -40.7916 |  |  | -126.4832 |  |  | -250.4453 |  |  | -388.6494 |  |  | -535.062 |  |  | -702.5672
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8707 |  |  | 47.6312 |  |  | 42.2397 |  |  | 27.7238 |  |  | -3.2989 |  |  | -52.8411 |  |  | -114.9489 |  |  | -171.126 |  |  | -208.6688 |  |  | -209.4905
[13 empty] | C Non choked w/ reducers | 7 |  | 5.389 |  |  | 29.7941 |  |  | 81.7461 |  |  | 321.5753 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.3317 |  |  | 24.0907 |  |  | 63.4129 |  |  | 153.3605 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.389 |  |  | 29.7941 |  |  | 81.7461 |  |  | 321.5753 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.65897 | 30.5859 |  | 18.1941 | 166.132 |  | 58.7461 | 410.8641 |  | 282.1753 | 800.2584 |  | 5500 | 1342.5846 |  | 5500 | 1979.1342 |  | 5500 | 2641.1622 |  | 5500 | 3222.7198 |  | 5500 | 3741.4777 |  | 5500 | 4258.1506
[13 empty] | Next iteration flow rate |  |  | 31.1976 | Abs Value of | Flow this | 167.7933 | Abs Value of | Flow this | 414.9727 | Abs Value of | Flow this | 808.2609 | Abs Value of | Flow this | 1356.0104 | Abs Value of | Flow this | 1998.9255 | Abs Value of | Flow this | 2667.5738 | Abs Value of | Flow this | 3254.947 | Abs Value of | Flow this | 3778.8925 | Abs Value of | Flow this | 4300.7321 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8833 |  |  | 55.9653 |  |  | 51.1005 |  |  | 34.8531 |  |  | -5.1833 |  |  | -78.0282 |  |  | -183.4064 |  |  | -300.8914 |  |  | -425.3543 |  |  | -567.7477
[13 empty] | P2 at this iteration flow rate |  |  | 24.6633 |  |  | 24.8469 |  |  | 25.8199 |  |  | 29.0694 |  |  | 37.0767 |  |  | 51.6456 |  |  | 72.7213 |  |  | 96.2183 |  |  | 121.1109 |  |  | 149.5895
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2199 |  |  | 31.1184 |  |  | 25.2806 |  |  | 5.7838 |  |  | -42.26 |  |  | -129.6739 |  |  | -256.1277 |  |  | -397.1096 |  |  | -546.4652 |  |  | -717.3373
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8696 |  |  | 47.6151 |  |  | 42.1444 |  |  | 27.378 |  |  | -4.2164 |  |  | -54.6944 |  |  | -117.9879 |  |  | -175.2257 |  |  | -213.432 |  |  | -214.129
[13 empty] | C Non choked w/ reducers | 7 |  | 5.4969 |  |  | 30.1029 |  |  | 82.7878 |  |  | 339.1224 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.4184 |  |  | 24.3357 |  |  | 64.1195 |  |  | 155.8694 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.4969 |  |  | 30.1029 |  |  | 82.7878 |  |  | 339.1224 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.76688 | 31.1976 |  | 18.5029 | 167.7933 |  | 59.7878 | 414.9727 |  | 299.7224 | 808.2609 |  | 5500 | 1356.0104 |  | 5500 | 1998.9255 |  | 5500 | 2667.5738 |  | 5500 | 3254.947 |  | 5500 | 3778.8925 |  | 5500 | 4300.7321
[13 empty] | Next iteration flow rate |  |  | 31.8216 | Abs Value of | Flow this | 169.4712 | Abs Value of | Flow this | 419.1225 | Abs Value of | Flow this | 816.3436 | Abs Value of | Flow this | 1369.5705 | Abs Value of | Flow this | 2018.9148 | Abs Value of | Flow this | 2694.2496 | Abs Value of | Flow this | 3287.4965 | Abs Value of | Flow this | 3816.6814 | Abs Value of | Flow this | 4343.7394 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8819 |  |  | 55.9462 |  |  | 50.9836 |  |  | 34.4097 |  |  | -6.4315 |  |  | -80.7406 |  |  | -188.2369 |  |  | -308.0833 |  |  | -435.0479 |  |  | -580.3035
[13 empty] | P2 at this iteration flow rate |  |  | 24.6636 |  |  | 24.8508 |  |  | 25.8433 |  |  | 29.1581 |  |  | 37.3263 |  |  | 52.1881 |  |  | 73.6874 |  |  | 97.6567 |  |  | 123.0496 |  |  | 152.1007
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2183 |  |  | 31.0954 |  |  | 25.1403 |  |  | 5.2516 |  |  | -43.7578 |  |  | -132.9287 |  |  | -261.9242 |  |  | -405.7399 |  |  | -558.0975 |  |  | -732.4041
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8684 |  |  | 47.5987 |  |  | 42.0472 |  |  | 27.0252 |  |  | -5.1523 |  |  | -56.585 |  |  | -121.088 |  |  | -179.4078 |  |  | -218.291 |  |  | -218.8608
[13 empty] | C Non choked w/ reducers | 7 |  | 5.607 |  |  | 30.4151 |  |  | 83.8487 |  |  | 359.4489 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.5068 |  |  | 24.5833 |  |  | 64.8355 |  |  | 158.4524 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.607 |  |  | 30.4151 |  |  | 83.8487 |  |  | 359.4489 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.87696 | 31.8216 |  | 18.8151 | 169.4712 |  | 60.8487 | 419.1225 |  | 320.0489 | 816.3436 |  | 5500 | 1369.5705 |  | 5500 | 2018.9148 |  | 5500 | 2694.2496 |  | 5500 | 3287.4965 |  | 5500 | 3816.6814 |  | 5500 | 4343.7394
[13 empty] | Next iteration flow rate |  |  | 32.458 | Abs Value of | Flow this | 171.1659 | Abs Value of | Flow this | 423.3137 | Abs Value of | Flow this | 824.507 | Abs Value of | Flow this | 1383.2662 | Abs Value of | Flow this | 2039.1039 | Abs Value of | Flow this | 2721.1921 | Abs Value of | Flow this | 3320.3715 | Abs Value of | Flow this | 3854.8482 | Abs Value of | Flow this | 4387.1768 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8806 |  |  | 55.9267 |  |  | 50.8643 |  |  | 33.9573 |  |  | -7.7048 |  |  | -83.5075 |  |  | -193.1644 |  |  | -315.4198 |  |  | -444.9364 |  |  | -593.1116
[13 empty] | P2 at this iteration flow rate |  |  | 24.6639 |  |  | 24.8547 |  |  | 25.8671 |  |  | 29.2485 |  |  | 37.581 |  |  | 52.7415 |  |  | 74.6729 |  |  | 99.124 |  |  | 125.0273 |  |  | 154.6623
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2167 |  |  | 31.072 |  |  | 24.9972 |  |  | 4.7087 |  |  | -45.2857 |  |  | -136.249 |  |  | -267.8373 |  |  | -414.5437 |  |  | -569.9637 |  |  | -747.7739
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8672 |  |  | 47.582 |  |  | 41.948 |  |  | 26.6653 |  |  | -6.107 |  |  | -58.5136 |  |  | -124.2504 |  |  | -183.6741 |  |  | -223.2477 |  |  | -223.6877
[13 empty] | C Non choked w/ reducers | 7 |  | 5.7192 |  |  | 30.7308 |  |  | 84.9292 |  |  | 383.3997 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.597 |  |  | 24.8335 |  |  | 65.5612 |  |  | 161.1133 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.7192 |  |  | 30.7308 |  |  | 84.9292 |  |  | 383.3997 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.98924 | 32.458 |  | 19.1308 | 171.1659 |  | 61.9292 | 423.3137 |  | 343.9997 | 824.507 |  | 5500 | 1383.2662 |  | 5500 | 2039.1039 |  | 5500 | 2721.1921 |  | 5500 | 3320.3715 |  | 5500 | 3854.8482 |  | 5500 | 4387.1768
[13 empty] | Next iteration flow rate |  |  | 33.1072 | Abs Value of | Flow this | 172.8776 | Abs Value of | Flow this | 427.5468 | Abs Value of | Flow this | 832.7521 | Abs Value of | Flow this | 1397.0989 | Abs Value of | Flow this | 2059.495 | Abs Value of | Flow this | 2748.404 | Abs Value of | Flow this | 3353.5752 | Abs Value of | Flow this | 3893.3967 | Abs Value of | Flow this | 4431.0486 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8791 |  |  | 55.9068 |  |  | 50.7427 |  |  | 33.4958 |  |  | -9.0037 |  |  | -86.33 |  |  | -198.1911 |  |  | -322.9037 |  |  | -455.0237 |  |  | -606.1771
[13 empty] | P2 at this iteration flow rate |  |  | 24.6642 |  |  | 24.8586 |  |  | 25.8915 |  |  | 29.3408 |  |  | 37.8407 |  |  | 53.306 |  |  | 75.6782 |  |  | 100.6207 |  |  | 127.0447 |  |  | 157.2754
[13 empty] | Delta P at this iteration flow rate |  |  | 32.215 |  |  | 31.0482 |  |  | 24.8512 |  |  | 4.155 |  |  | -46.8444 |  |  | -139.636 |  |  | -273.8693 |  |  | -423.5245 |  |  | -582.0684 |  |  | -763.4525
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.866 |  |  | 47.565 |  |  | 41.8468 |  |  | 26.2981 |  |  | -7.0809 |  |  | -60.481 |  |  | -127.4763 |  |  | -188.026 |  |  | -228.304 |  |  | -228.6117
[13 empty] | C Non choked w/ reducers | 7 |  | 5.8338 |  |  | 31.0501 |  |  | 86.0301 |  |  | 412.2318 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.689 |  |  | 25.0863 |  |  | 66.2969 |  |  | 163.8563 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.8338 |  |  | 31.0501 |  |  | 86.0301 |  |  | 412.2318 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.1038 | 33.1072 |  | 19.4501 | 172.8776 |  | 63.0301 | 427.5468 |  | 372.8318 | 832.7521 |  | 5500 | 1397.0989 |  | 5500 | 2059.495 |  | 5500 | 2748.404 |  | 5500 | 3353.5752 |  | 5500 | 3893.3967 |  | 5500 | 4431.0486
[13 empty] | Next iteration flow rate |  |  | 33.7693 | Abs Value of | Flow this | 174.6063 | Abs Value of | Flow this | 431.8223 | Abs Value of | Flow this | 841.0796 | Abs Value of | Flow this | 1411.0699 | Abs Value of | Flow this | 2080.0899 | Abs Value of | Flow this | 2775.888 | Abs Value of | Flow this | 3387.1109 | Abs Value of | Flow this | 3932.3306 | Abs Value of | Flow this | 4475.3591 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8776 |  |  | 55.8865 |  |  | 50.6186 |  |  | 33.0251 |  |  | -10.3286 |  |  | -89.2093 |  |  | -203.3187 |  |  | -330.5381 |  |  | -465.3137 |  |  | -619.5053
[13 empty] | P2 at this iteration flow rate |  |  | 24.6645 |  |  | 24.8627 |  |  | 25.9163 |  |  | 29.435 |  |  | 38.1057 |  |  | 53.8819 |  |  | 76.7037 |  |  | 102.1476 |  |  | 129.1027 |  |  | 159.9411
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2132 |  |  | 31.0238 |  |  | 24.7023 |  |  | 3.5901 |  |  | -48.4344 |  |  | -143.0911 |  |  | -280.0225 |  |  | -432.6857 |  |  | -594.4164 |  |  | -779.4464
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8646 |  |  | 47.5476 |  |  | 41.7435 |  |  | 25.9236 |  |  | -8.0743 |  |  | -62.4879 |  |  | -130.7671 |  |  | -192.4654 |  |  | -233.4619 |  |  | -233.6346
[13 empty] | C Non choked w/ reducers | 7 |  | 5.9506 |  |  | 31.3729 |  |  | 87.1518 |  |  | 447.9146 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.7828 |  |  | 25.3418 |  |  | 67.0426 |  |  | 166.686 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.9506 |  |  | 31.3729 |  |  | 87.1518 |  |  | 447.9146 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.2206 | 33.7693 |  | 19.7729 | 174.6063 |  | 64.1518 | 431.8223 |  | 408.5146 | 841.0796 |  | 5500 | 1411.0699 |  | 5500 | 2080.0899 |  | 5500 | 2775.888 |  | 5500 | 3387.1109 |  | 5500 | 3932.3306 |  | 5500 | 4475.3591
[13 empty] | Next iteration flow rate |  |  | 34.4447 | Abs Value of | Flow this | 176.3524 | Abs Value of | Flow this | 436.1405 | Abs Value of | Flow this | 849.4904 | Abs Value of | Flow this | 1425.1806 | Abs Value of | Flow this | 2100.8908 | Abs Value of | Flow this | 2803.6469 | Abs Value of | Flow this | 3420.982 | Abs Value of | Flow this | 3971.654 | Abs Value of | Flow this | 4520.1127 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8761 |  |  | 55.8658 |  |  | 50.492 |  |  | 32.5449 |  |  | -11.6803 |  |  | -92.1464 |  |  | -208.5494 |  |  | -338.3259 |  |  | -475.8105 |  |  | -633.1014
[13 empty] | P2 at this iteration flow rate |  |  | 24.6648 |  |  | 24.8668 |  |  | 25.9416 |  |  | 29.531 |  |  | 38.3761 |  |  | 54.4693 |  |  | 77.7499 |  |  | 103.7052 |  |  | 131.2021 |  |  | 162.6603
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2113 |  |  | 30.999 |  |  | 24.5504 |  |  | 3.0138 |  |  | -50.0563 |  |  | -146.6157 |  |  | -286.2993 |  |  | -442.0311 |  |  | -607.0126 |  |  | -795.7616
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8633 |  |  | 47.5298 |  |  | 41.6382 |  |  | 25.5416 |  |  | -9.0878 |  |  | -64.5352 |  |  | -134.1241 |  |  | -196.9941 |  |  | -238.7235 |  |  | -238.7584
[13 empty] | C Non choked w/ reducers | 7 |  | 6.0698 |  |  | 31.6993 |  |  | 88.2952 |  |  | 493.7527 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.8785 |  |  | 25.6 |  |  | 67.7986 |  |  | 169.6073 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.0698 |  |  | 31.6993 |  |  | 88.2952 |  |  | 493.7527 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.3398 | 34.4447 |  | 20.0993 | 176.3524 |  | 65.2952 | 436.1405 |  | 454.3527 | 849.4904 |  | 5500 | 1425.1806 |  | 5500 | 2100.8908 |  | 5500 | 2803.6469 |  | 5500 | 3420.982 |  | 5500 | 3971.654 |  | 5500 | 4520.1127
[13 empty] | Next iteration flow rate |  |  | 35.1336 | Abs Value of | Flow this | 178.1159 | Abs Value of | Flow this | 440.5019 | Abs Value of | Flow this | 857.9853 | Abs Value of | Flow this | 1439.4324 | Abs Value of | Flow this | 2121.8997 | Abs Value of | Flow this | 2831.6834 | Abs Value of | Flow this | 3455.1919 | Abs Value of | Flow this | 4011.3705 | Abs Value of | Flow this | 4565.3138 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8745 |  |  | 55.8447 |  |  | 50.3629 |  |  | 32.055 |  |  | -13.0591 |  |  | -95.1426 |  |  | -213.8853 |  |  | -346.2703 |  |  | -486.5183 |  |  | -646.9707
[13 empty] | P2 at this iteration flow rate |  |  | 24.6651 |  |  | 24.8711 |  |  | 25.9674 |  |  | 29.629 |  |  | 38.6518 |  |  | 55.0685 |  |  | 78.8171 |  |  | 105.2941 |  |  | 133.3437 |  |  | 165.4341
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2093 |  |  | 30.9736 |  |  | 24.3955 |  |  | 2.426 |  |  | -51.7109 |  |  | -150.2111 |  |  | -292.7024 |  |  | -451.5644 |  |  | -619.8619 |  |  | -812.4049
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8618 |  |  | 47.5117 |  |  | 41.5308 |  |  | 25.1519 |  |  | -10.1216 |  |  | -66.6236 |  |  | -137.5485 |  |  | -201.6138 |  |  | -244.0909 |  |  | -243.9853
[13 empty] | C Non choked w/ reducers | 7 |  | 6.1914 |  |  | 32.0294 |  |  | 89.461 |  |  | 555.8344 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.9762 |  |  | 25.8609 |  |  | 68.5651 |  |  | 172.6254 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.1914 |  |  | 32.0294 |  |  | 89.461 |  |  | 555.8344 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.4614 | 35.1336 |  | 20.4294 | 178.1159 |  | 66.461 | 440.5019 |  | 516.4344 | 857.9853 |  | 5500 | 1439.4324 |  | 5500 | 2121.8997 |  | 5500 | 2831.6834 |  | 5500 | 3455.1919 |  | 5500 | 4011.3705 |  | 5500 | 4565.3138
[13 empty] | Next iteration flow rate |  |  | 35.8363 | Abs Value of | Flow this | 179.8971 | Abs Value of | Flow this | 444.9069 | Abs Value of | Flow this | 866.5651 | Abs Value of | Flow this | 1453.8267 | Abs Value of | Flow this | 2143.1187 | Abs Value of | Flow this | 2860.0002 | Abs Value of | Flow this | 3489.7438 | Abs Value of | Flow this | 4051.4842 | Abs Value of | Flow this | 4610.9669 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8728 |  |  | 55.8232 |  |  | 50.2312 |  |  | 31.5553 |  |  | -14.4656 |  |  | -98.1989 |  |  | -219.3284 |  |  | -354.3744 |  |  | -497.4413 |  |  | -661.1188
[13 empty] | P2 at this iteration flow rate |  |  | 24.6654 |  |  | 24.8754 |  |  | 25.9938 |  |  | 29.7289 |  |  | 38.9331 |  |  | 55.6798 |  |  | 79.9057 |  |  | 106.9149 |  |  | 135.5283 |  |  | 168.2638
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2073 |  |  | 30.9478 |  |  | 24.2374 |  |  | 1.8263 |  |  | -53.3987 |  |  | -153.8787 |  |  | -299.2341 |  |  | -461.2892 |  |  | -632.9696 |  |  | -829.3826
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8603 |  |  | 47.4933 |  |  | 41.4212 |  |  | 24.7543 |  |  | -11.1762 |  |  | -68.754 |  |  | -141.0417 |  |  | -206.3263 |  |  | -249.5661 |  |  | -249.3172
[13 empty] | C Non choked w/ reducers | 7 |  | 6.3154 |  |  | 32.3632 |  |  | 90.6497 |  |  | 647.0245 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.0758 |  |  | 26.1246 |  |  | 69.3423 |  |  | 175.7461 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.3154 |  |  | 32.3632 |  |  | 90.6497 |  |  | 647.0245 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.5854 | 35.8363 |  | 20.7632 | 179.8971 |  | 67.6497 | 444.9069 |  | 607.6245 | 866.5651 |  | 5500 | 1453.8267 |  | 5500 | 2143.1187 |  | 5500 | 2860.0002 |  | 5500 | 3489.7438 |  | 5500 | 4051.4842 |  | 5500 | 4610.9669
[13 empty] | Next iteration flow rate |  |  | 36.553 | Abs Value of | Flow this | 181.6961 | Abs Value of | Flow this | 449.356 | Abs Value of | Flow this | 875.2308 | Abs Value of | Flow this | 1468.365 | Abs Value of | Flow this | 2164.5499 | Abs Value of | Flow this | 2888.6002 | Abs Value of | Flow this | 3524.6412 | Abs Value of | Flow this | 4091.999 | Abs Value of | Flow this | 4657.0766 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.871 |  |  | 55.8012 |  |  | 50.0968 |  |  | 31.0455 |  |  | -15.9003 |  |  | -101.3168 |  |  | -224.8809 |  |  | -362.6413 |  |  | -508.5839 |  |  | -675.5514
[13 empty] | P2 at this iteration flow rate |  |  | 24.6658 |  |  | 24.8798 |  |  | 26.0206 |  |  | 29.8309 |  |  | 39.2201 |  |  | 56.3034 |  |  | 81.0162 |  |  | 108.5683 |  |  | 137.7568 |  |  | 171.1503
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2052 |  |  | 30.9214 |  |  | 24.0762 |  |  | 1.2146 |  |  | -55.1204 |  |  | -157.6201 |  |  | -305.8971 |  |  | -471.2096 |  |  | -646.3407 |  |  | -846.7016
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8588 |  |  | 47.4744 |  |  | 41.3095 |  |  | 24.3488 |  |  | -12.252 |  |  | -70.9271 |  |  | -144.6052 |  |  | -211.1336 |  |  | -255.1514 |  |  | -254.7563
[13 empty] | C Non choked w/ reducers | 7 |  | 6.4419 |  |  | 32.7007 |  |  | 91.8623 |  |  | 801.3274 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.1774 |  |  | 26.3911 |  |  | 70.1304 |  |  | 178.9757 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.4419 |  |  | 32.7007 |  |  | 91.8623 |  |  | 801.3274 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.7119 | 36.553 |  | 21.1007 | 181.6961 |  | 68.8623 | 449.356 |  | 761.9274 | 875.2308 |  | 5500 | 1468.365 |  | 5500 | 2164.5499 |  | 5500 | 2888.6002 |  | 5500 | 3524.6412 |  | 5500 | 4091.999 |  | 5500 | 4657.0766
[13 empty] | Next iteration flow rate |  |  | 37.2841 | Abs Value of | Flow this | 183.513 | Abs Value of | Flow this | 453.8496 | Abs Value of | Flow this | 883.9831 | Abs Value of | Flow this | 1483.0486 | Abs Value of | Flow this | 2186.1954 | Abs Value of | Flow this | 2917.4862 | Abs Value of | Flow this | 3559.8876 | Abs Value of | Flow this | 4132.919 | Abs Value of | Flow this | 4703.6474 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8692 |  |  | 55.7788 |  |  | 49.9597 |  |  | 30.5255 |  |  | -17.3639 |  |  | -104.4972 |  |  | -230.545 |  |  | -371.0744 |  |  | -519.9504 |  |  | -690.2739
[13 empty] | P2 at this iteration flow rate |  |  | 24.6662 |  |  | 24.8842 |  |  | 26.0481 |  |  | 29.9349 |  |  | 39.5128 |  |  | 56.9394 |  |  | 82.149 |  |  | 110.2549 |  |  | 140.0301 |  |  | 174.0948
[13 empty] | Delta P at this iteration flow rate |  |  | 32.203 |  |  | 30.8945 |  |  | 23.9117 |  |  | 0.59063 |  |  | -56.8767 |  |  | -161.4367 |  |  | -312.6941 |  |  | -481.3293 |  |  | -659.9805 |  |  | -864.3687
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8572 |  |  | 47.4552 |  |  | 41.1954 |  |  | 23.9351 |  |  | -13.3494 |  |  | -73.144 |  |  | -148.2403 |  |  | -216.0375 |  |  | -260.8489 |  |  | -260.3047
[13 empty] | C Non choked w/ reducers | 7 |  | 6.571 |  |  | 33.0421 |  |  | 93.0995 |  |  | 1160.6327 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.281 |  |  | 26.6604 |  |  | 70.9296 |  |  | 182.321 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.571 |  |  | 33.0421 |  |  | 93.0995 |  |  | 1160.6327 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.841 | 37.2841 |  | 21.4421 | 183.513 |  | 70.0995 | 453.8496 |  | 1121.2327 | 883.9831 |  | 5500 | 1483.0486 |  | 5500 | 2186.1954 |  | 5500 | 2917.4862 |  | 5500 | 3559.8876 |  | 5500 | 4132.919 |  | 5500 | 4703.6474
[13 empty] | Next iteration flow rate |  |  | 38.0298 | Abs Value of | Flow this | 185.3482 | Abs Value of | Flow this | 458.3881 | Abs Value of | Flow this | 892.8229 | Abs Value of | Flow this | 1497.8791 | Abs Value of | Flow this | 2208.0573 | Abs Value of | Flow this | 2946.6611 | Abs Value of | Flow this | 3595.4865 | Abs Value of | Flow this | 4174.2482 | Abs Value of | Flow this | 4750.6838 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8673 |  |  | 55.7559 |  |  | 49.8199 |  |  | 29.9951 |  |  | -18.857 |  |  | -107.7416 |  |  | -236.323 |  |  | -379.677 |  |  | -531.5455 |  |  | -705.2925
[13 empty] | P2 at this iteration flow rate |  |  | 24.6665 |  |  | 24.8888 |  |  | 26.076 |  |  | 30.041 |  |  | 39.8114 |  |  | 57.5883 |  |  | 83.3046 |  |  | 111.9754 |  |  | 142.3491 |  |  | 177.0985
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2008 |  |  | 30.8671 |  |  | 23.7439 |  |  | -0.045908 |  |  | -58.6684 |  |  | -165.33 |  |  | -319.6276 |  |  | -491.6524 |  |  | -673.8946 |  |  | -882.391
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8555 |  |  | 47.4356 |  |  | 41.0791 |  |  | 23.5131 |  |  | -14.4688 |  |  | -75.4055 |  |  | -151.9484 |  |  | -221.0399 |  |  | -266.661 |  |  | -265.9646
[13 empty] | C Non choked w/ reducers | 7 |  | 6.7027 |  |  | 33.3874 |  |  | 94.3621 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.3867 |  |  | 26.9326 |  |  | 71.7403 |  |  | 185.7893 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.7027 |  |  | 33.3874 |  |  | 94.3621 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.9727 | 38.0298 |  | 21.7874 | 185.3482 |  | 71.3621 | 458.3881 |  | 5500 | 892.8229 |  | 5500 | 1497.8791 |  | 5500 | 2208.0573 |  | 5500 | 2946.6611 |  | 5500 | 3595.4865 |  | 5500 | 4174.2482 |  | 5500 | 4750.6838
[13 empty] | Next iteration flow rate |  |  | 38.7903 | Abs Value of | Flow this | 187.2016 | Abs Value of | Flow this | 462.9719 | Abs Value of | Flow this | 901.7512 | Abs Value of | Flow this | 1512.8579 | Abs Value of | Flow this | 2230.1379 | Abs Value of | Flow this | 2976.1277 | Abs Value of | Flow this | 3631.4414 | Abs Value of | Flow this | 4215.9907 | Abs Value of | Flow this | 4798.1907 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8653 |  |  | 55.7326 |  |  | 49.6773 |  |  | 29.454 |  |  | -20.38 |  |  | -111.0513 |  |  | -242.2171 |  |  | -388.4525 |  |  | -543.3735 |  |  | -720.6129
[13 empty] | P2 at this iteration flow rate |  |  | 24.6669 |  |  | 24.8935 |  |  | 26.1045 |  |  | 30.1492 |  |  | 40.116 |  |  | 58.2503 |  |  | 84.4834 |  |  | 113.7305 |  |  | 144.7147 |  |  | 180.1626
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1984 |  |  | 30.8391 |  |  | 23.5727 |  |  | -0.69524 |  |  | -60.496 |  |  | -169.3015 |  |  | -326.7006 |  |  | -502.183 |  |  | -688.0883 |  |  | -900.7754
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8538 |  |  | 47.4156 |  |  | 40.9605 |  |  | 23.0826 |  |  | -15.6108 |  |  | -77.7124 |  |  | -155.7311 |  |  | -226.143 |  |  | -272.5899 |  |  | -271.7383
[13 empty] | C Non choked w/ reducers | 7 |  | 6.837 |  |  | 33.7365 |  |  | 95.6511 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.4945 |  |  | 27.2076 |  |  | 72.5626 |  |  | 189.3889 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.837 |  |  | 33.7365 |  |  | 95.6511 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.107 | 38.7903 |  | 22.1365 | 187.2016 |  | 72.6511 | 462.9719 |  | 5500 | 901.7512 |  | 5500 | 1512.8579 |  | 5500 | 2230.1379 |  | 5500 | 2976.1277 |  | 5500 | 3631.4414 |  | 5500 | 4215.9907 |  | 5500 | 4798.1907
[13 empty] | Next iteration flow rate |  |  | 39.5662 | Abs Value of | Flow this | 189.0737 | Abs Value of | Flow this | 467.6017 | Abs Value of | Flow this | 910.7687 | Abs Value of | Flow this | 1527.9865 | Abs Value of | Flow this | 2252.4393 | Abs Value of | Flow this | 3005.889 | Abs Value of | Flow this | 3667.7558 | Abs Value of | Flow this | 4258.1506 | Abs Value of | Flow this | 4846.1726 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8633 |  |  | 55.7088 |  |  | 49.5318 |  |  | 28.902 |  |  | -21.9337 |  |  | -114.4274 |  |  | -248.2297 |  |  | -397.4044 |  |  | -555.4394 |  |  | -736.2412
[13 empty] | P2 at this iteration flow rate |  |  | 24.6673 |  |  | 24.8982 |  |  | 26.1336 |  |  | 30.2596 |  |  | 40.4267 |  |  | 58.9255 |  |  | 85.6859 |  |  | 115.5209 |  |  | 147.1279 |  |  | 183.2882
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1959 |  |  | 30.8106 |  |  | 23.3981 |  |  | -1.3576 |  |  | -62.3604 |  |  | -173.3529 |  |  | -333.9156 |  |  | -512.9253 |  |  | -702.5672 |  |  | -919.5294
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8519 |  |  | 47.3952 |  |  | 40.8394 |  |  | 22.6434 |  |  | -16.7757 |  |  | -80.0656 |  |  | -159.5898 |  |  | -231.3485 |  |  | -278.638 |  |  | -277.628
[13 empty] | C Non choked w/ reducers | 7 |  | 6.974 |  |  | 34.0897 |  |  | 96.9674 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.6045 |  |  | 27.4856 |  |  | 73.3967 |  |  | 193.1288 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.974 |  |  | 34.0897 |  |  | 96.9674 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.244 | 39.5662 |  | 22.4897 | 189.0737 |  | 73.9674 | 467.6017 |  | 5500 | 910.7687 |  | 5500 | 1527.9865 |  | 5500 | 2252.4393 |  | 5500 | 3005.889 |  | 5500 | 3667.7558 |  | 5500 | 4258.1506 |  | 5500 | 4846.1726
[13 empty] | Next iteration flow rate |  |  | 40.3575 | Abs Value of | Flow this | 190.9644 | Abs Value of | Flow this | 472.2777 | Abs Value of | Flow this | 919.8764 | Abs Value of | Flow this | 1543.2664 | Abs Value of | Flow this | 2274.9637 | Abs Value of | Flow this | 3035.9479 | Abs Value of | Flow this | 3704.4333 | Abs Value of | Flow this | 4300.7321 | Abs Value of | Flow this | 4894.6343 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8611 |  |  | 55.6846 |  |  | 49.3833 |  |  | 28.3389 |  |  | -23.5185 |  |  | -117.8714 |  |  | -254.3631 |  |  | -406.5363 |  |  | -567.7477 |  |  | -752.1837
[13 empty] | P2 at this iteration flow rate |  |  | 24.6678 |  |  | 24.9031 |  |  | 26.1633 |  |  | 30.3722 |  |  | 40.7437 |  |  | 59.6143 |  |  | 86.9126 |  |  | 117.3473 |  |  | 149.5895 |  |  | 186.4767
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1934 |  |  | 30.7815 |  |  | 23.22 |  |  | -2.0333 |  |  | -64.2623 |  |  | -177.4857 |  |  | -341.2758 |  |  | -523.8835 |  |  | -717.3373 |  |  | -938.6604
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8501 |  |  | 47.3744 |  |  | 40.7159 |  |  | 22.1954 |  |  | -17.9641 |  |  | -82.4662 |  |  | -163.5261 |  |  | -236.6588 |  |  | -284.8076 |  |  | -283.6361
[13 empty] | C Non choked w/ reducers | 7 |  | 7.1137 |  |  | 34.4468 |  |  | 98.312 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.7167 |  |  | 27.7666 |  |  | 74.243 |  |  | 197.0187 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 7.1137 |  |  | 34.4468 |  |  | 98.312 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.3837 | 40.3575 |  | 22.8468 | 190.9644 |  | 75.312 | 472.2777 |  | 5500 | 919.8764 |  | 5500 | 1543.2664 |  | 5500 | 2274.9637 |  | 5500 | 3035.9479 |  | 5500 | 3704.4333 |  | 5500 | 4300.7321 |  | 5500 | 4894.6343
[13 empty] | Next iteration flow rate |  |  | 41.1646 | Abs Value of | Flow this | 192.874 | Abs Value of | Flow this | 477.0004 | Abs Value of | Flow this | 929.0751 | Abs Value of | Flow this | 1558.699 | Abs Value of | Flow this | 2297.7133 | Abs Value of | Flow this | 3066.3073 | Abs Value of | Flow this | 3741.4777 | Abs Value of | Flow this | 4343.7394 | Abs Value of | Flow this | 4943.5807 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8589 |  |  | 55.6598 |  |  | 49.2319 |  |  | 27.7645 |  |  | -25.1353 |  |  | -121.3847 |  |  | -260.6198 |  |  | -415.8517 |  |  | -580.3035 |  |  | -768.4466
[13 empty] | P2 at this iteration flow rate |  |  | 24.6682 |  |  | 24.908 |  |  | 26.1936 |  |  | 30.4871 |  |  | 41.0671 |  |  | 60.3169 |  |  | 88.164 |  |  | 119.2103 |  |  | 152.1007 |  |  | 189.7293
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1907 |  |  | 30.7518 |  |  | 23.0383 |  |  | -2.7226 |  |  | -66.2023 |  |  | -181.7016 |  |  | -348.7838 |  |  | -535.062 |  |  | -732.4041 |  |  | -958.1759
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8481 |  |  | 47.3532 |  |  | 40.59 |  |  | 21.7385 |  |  | -19.1763 |  |  | -84.915 |  |  | -167.5415 |  |  | -242.0757 |  |  | -291.1013 |  |  | -289.765
[13 empty] | C Non choked w/ reducers | 7 |  | 7.2563 |  |  | 34.8081 |  |  | 99.6859 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.8312 |  |  | 28.0505 |  |  | 75.1017 |  |  | 201.0696 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 7.2563 |  |  | 34.8081 |  |  | 99.6859 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.5263 | 41.1646 |  | 23.2081 | 192.874 |  | 76.6859 | 477.0004 |  | 5500 | 929.0751 |  | 5500 | 1558.699 |  | 5500 | 2297.7133 |  | 5500 | 3066.3073 |  | 5500 | 3741.4777 |  | 5500 | 4343.7394 |  | 5500 | 4943.5807
[13 empty] | Next iteration flow rate |  |  | 41.9879 | Abs Value of | Flow this | 194.8028 | Abs Value of | Flow this | 481.7705 | Abs Value of | Flow this | 938.3659 | Abs Value of | Flow this | 1574.286 | Abs Value of | Flow this | 2320.6905 | Abs Value of | Flow this | 3096.9704 | Abs Value of | Flow this | 3778.8925 | Abs Value of | Flow this | 4387.1768 | Abs Value of | Flow this | 4993.0165 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8566 |  |  | 55.6345 |  |  | 49.0775 |  |  | 27.1785 |  |  | -26.7845 |  |  | -124.9685 |  |  | -267.0023 |  |  | -425.3543 |  |  | -593.1116 |  |  | -785.0364
[13 empty] | P2 at this iteration flow rate |  |  | 24.6687 |  |  | 24.9131 |  |  | 26.2245 |  |  | 30.6043 |  |  | 41.3969 |  |  | 61.0337 |  |  | 89.4405 |  |  | 121.1109 |  |  | 154.6623 |  |  | 193.0473
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1879 |  |  | 30.7215 |  |  | 22.853 |  |  | -3.4258 |  |  | -68.1814 |  |  | -186.0022 |  |  | -356.4428 |  |  | -546.4652 |  |  | -747.7739 |  |  | -978.0836
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8461 |  |  | 47.3315 |  |  | 40.4615 |  |  | 21.2723 |  |  | -20.4129 |  |  | -87.413 |  |  | -171.6376 |  |  | -247.6015 |  |  | -297.5214 |  |  | -296.0171
[13 empty] | C Non choked w/ reducers | 7 |  | 7.4018 |  |  | 35.1735 |  |  | 101.0902 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.9479 |  |  | 28.3375 |  |  | 75.973 |  |  | 205.2933 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 7.4018 |  |  | 35.1735 |  |  | 101.0902 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.6718 | 41.9879 |  | 23.5735 | 194.8028 |  | 78.0902 | 481.7705 |  | 5500 | 938.3659 |  | 5500 | 1574.286 |  | 5500 | 2320.6905 |  | 5500 | 3096.9704 |  | 5500 | 3778.8925 |  | 5500 | 4387.1768 |  | 5500 | 4993.0165
[13 empty] | Next iteration flow rate |  |  | 42.8277 | Abs Value of | Flow this | 196.7508 | Abs Value of | Flow this | 486.5882 | Abs Value of | Flow this | 947.7495 | Abs Value of | Flow this | 1590.0289 | Abs Value of | Flow this | 2343.8974 | Abs Value of | Flow this | 3127.9401 | Abs Value of | Flow this | 3816.6814 | Abs Value of | Flow this | 4431.0486 | Abs Value of | Flow this | 5042.9466 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8542 |  |  | 55.6088 |  |  | 48.9199 |  |  | 26.5808 |  |  | -28.4669 |  |  | -128.6244 |  |  | -273.5131 |  |  | -435.0479 |  |  | -606.1771 |  |  | -801.9596
[13 empty] | P2 at this iteration flow rate |  |  | 24.6692 |  |  | 24.9182 |  |  | 26.256 |  |  | 30.7238 |  |  | 41.7334 |  |  | 61.7649 |  |  | 90.7426 |  |  | 123.0496 |  |  | 157.2754 |  |  | 196.4319
[13 empty] | Delta P at this iteration flow rate |  |  | 32.185 |  |  | 30.6905 |  |  | 22.6639 |  |  | -4.143 |  |  | -70.2003 |  |  | -190.3893 |  |  | -364.2557 |  |  | -558.0975 |  |  | -763.4525 |  |  | -998.3915
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8439 |  |  | 47.3094 |  |  | 40.3304 |  |  | 20.7968 |  |  | -21.6743 |  |  | -89.9613 |  |  | -175.816 |  |  | -253.2384 |  |  | -304.0706 |  |  | -302.3949
[13 empty] | C Non choked w/ reducers | 7 |  | 7.5501 |  |  | 35.5432 |  |  | 102.5261 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.067 |  |  | 28.6276 |  |  | 76.8574 |  |  | 209.7034 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 7.5501 |  |  | 35.5432 |  |  | 102.5261 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.8201 | 42.8277 |  | 23.9432 | 196.7508 |  | 79.5261 | 486.5882 |  | 5500 | 947.7495 |  | 5500 | 1590.0289 |  | 5500 | 2343.8974 |  | 5500 | 3127.9401 |  | 5500 | 3816.6814 |  | 5500 | 4431.0486 |  | 5500 | 5042.9466
[13 empty] | Next iteration flow rate |  |  | 43.6842 | Abs Value of | Flow this | 198.7183 | Abs Value of | Flow this | 491.454 | Abs Value of | Flow this | 957.227 | Abs Value of | Flow this | 1605.9292 | Abs Value of | Flow this | 2367.3363 | Abs Value of | Flow this | 3159.2195 | Abs Value of | Flow this | 3854.8482 | Abs Value of | Flow this | 4475.3591 | Abs Value of | Flow this | 5093.3761 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8517 |  |  | 55.5825 |  |  | 48.7592 |  |  | 25.9711 |  |  | -30.1831 |  |  | -132.3537 |  |  | -280.1547 |  |  | -444.9364 |  |  | -619.5053 |  |  | -819.223
[13 empty] | P2 at this iteration flow rate |  |  | 24.6697 |  |  | 24.9235 |  |  | 26.2882 |  |  | 30.8458 |  |  | 42.0766 |  |  | 62.5107 |  |  | 92.0709 |  |  | 125.0273 |  |  | 159.9411 |  |  | 199.8846
[13 empty] | Delta P at this iteration flow rate |  |  | 32.182 |  |  | 30.659 |  |  | 22.471 |  |  | -4.8747 |  |  | -72.2597 |  |  | -194.8645 |  |  | -372.2257 |  |  | -569.9637 |  |  | -779.4464 |  |  | -1019.1076
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8417 |  |  | 47.2869 |  |  | 40.1967 |  |  | 20.3117 |  |  | -22.9611 |  |  | -92.5607 |  |  | -180.0785 |  |  | -258.9886 |  |  | -310.7514 |  |  | -308.9008
[13 empty] | C Non choked w/ reducers | 7 |  | 7.7015 |  |  | 35.917 |  |  | 103.9948 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.1885 |  |  | 28.9207 |  |  | 77.7549 |  |  | 214.3147 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 7.7015 |  |  | 35.917 |  |  | 103.9948 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.9715 | 43.6842 |  | 24.317 | 198.7183 |  | 80.9948 | 491.454 |  | 5500 | 957.227 |  | 5500 | 1605.9292 |  | 5500 | 2367.3363 |  | 5500 | 3159.2195 |  | 5500 | 3854.8482 |  | 5500 | 4475.3591 |  | 5500 | 5093.3761
[13 empty] | Next iteration flow rate |  |  | 44.5579 | Abs Value of | Flow this | 200.7055 | Abs Value of | Flow this | 496.3686 | Abs Value of | Flow this | 966.7993 | Abs Value of | Flow this | 1621.9885 | Abs Value of | Flow this | 2391.0097 | Abs Value of | Flow this | 3190.8117 | Abs Value of | Flow this | 3893.3967 | Abs Value of | Flow this | 4520.1127 | Abs Value of | Flow this | 5144.3099 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8491 |  |  | 55.5557 |  |  | 48.5952 |  |  | 25.3491 |  |  | -31.9338 |  |  | -136.1581 |  |  | -286.9298 |  |  | -455.0237 |  |  | -633.1014 |  |  | -836.8334
[13 empty] | P2 at this iteration flow rate |  |  | 24.6702 |  |  | 24.9289 |  |  | 26.321 |  |  | 30.9702 |  |  | 42.4268 |  |  | 63.2716 |  |  | 93.426 |  |  | 127.0447 |  |  | 162.6603 |  |  | 203.4067
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1789 |  |  | 30.6268 |  |  | 22.2743 |  |  | -5.6211 |  |  | -74.3606 |  |  | -199.4297 |  |  | -380.3558 |  |  | -582.0684 |  |  | -795.7616 |  |  | -1040.2401
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8394 |  |  | 47.2639 |  |  | 40.0603 |  |  | 19.8168 |  |  | -24.2738 |  |  | -95.2124 |  |  | -184.4266 |  |  | -264.8544 |  |  | -317.5665 |  |  | -315.5375
[13 empty] | C Non choked w/ reducers | 7 |  | 7.8559 |  |  | 36.2953 |  |  | 105.4976 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.3124 |  |  | 29.217 |  |  | 78.6661 |  |  | 219.1437 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 7.8559 |  |  | 36.2953 |  |  | 105.4976 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.1259 | 44.5579 |  | 24.6953 | 200.7055 |  | 82.4976 | 496.3686 |  | 5500 | 966.7993 |  | 5500 | 1621.9885 |  | 5500 | 2391.0097 |  | 5500 | 3190.8117 |  | 5500 | 3893.3967 |  | 5500 | 4520.1127 |  | 5500 | 5144.3099
[13 empty] | Next iteration flow rate |  |  | 45.4491 | Abs Value of | Flow this | 202.7126 | Abs Value of | Flow this | 501.3323 | Abs Value of | Flow this | 976.4673 | Abs Value of | Flow this | 1638.2083 | Abs Value of | Flow this | 2414.9198 | Abs Value of | Flow this | 3222.7198 | Abs Value of | Flow this | 3932.3306 | Abs Value of | Flow this | 4565.3138 | Abs Value of | Flow this | 5195.753 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8464 |  |  | 55.5284 |  |  | 48.428 |  |  | 24.7146 |  |  | -33.7197 |  |  | -140.0389 |  |  | -293.8411 |  |  | -465.3137 |  |  | -646.9707 |  |  | -854.7978
[13 empty] | P2 at this iteration flow rate |  |  | 24.6707 |  |  | 24.9343 |  |  | 26.3544 |  |  | 31.0971 |  |  | 42.7839 |  |  | 64.0478 |  |  | 94.8082 |  |  | 129.1027 |  |  | 165.4341 |  |  | 206.9996
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1757 |  |  | 30.594 |  |  | 22.0736 |  |  | -6.3825 |  |  | -76.5036 |  |  | -204.0866 |  |  | -388.6494 |  |  | -594.4164 |  |  | -812.4049 |  |  | -1061.7973
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.837 |  |  | 47.2404 |  |  | 39.9212 |  |  | 19.3121 |  |  | -25.6128 |  |  | -97.9175 |  |  | -188.8621 |  |  | -270.8381 |  |  | -324.5186 |  |  | -322.3076
[13 empty] | C Non choked w/ reducers | 7 |  | 8.0134 |  |  | 36.6779 |  |  | 107.0359 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.4388 |  |  | 29.5165 |  |  | 79.5911 |  |  | 224.2092 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 8.0134 |  |  | 36.6779 |  |  | 107.0359 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.2834 | 45.4491 |  | 25.0779 | 202.7126 |  | 84.0359 | 501.3323 |  | 5500 | 976.4673 |  | 5500 | 1638.2083 |  | 5500 | 2414.9198 |  | 5500 | 3222.7198 |  | 5500 | 3932.3306 |  | 5500 | 4565.3138 |  | 5500 | 5195.753
[13 empty] | Next iteration flow rate |  |  | 46.3581 | Abs Value of | Flow this | 204.7397 | Abs Value of | Flow this | 506.3456 | Abs Value of | Flow this | 986.232 | Abs Value of | Flow this | 1654.5904 | Abs Value of | Flow this | 2439.069 | Abs Value of | Flow this | 3254.947 | Abs Value of | Flow this | 3971.654 | Abs Value of | Flow this | 4610.9669 | Abs Value of | Flow this | 5247.7105 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8436 |  |  | 55.5005 |  |  | 48.2574 |  |  | 24.0673 |  |  | -35.5415 |  |  | -143.9977 |  |  | -300.8914 |  |  | -475.8105 |  |  | -661.1188 |  |  | -873.1232
[13 empty] | P2 at this iteration flow rate |  |  | 24.6713 |  |  | 24.9399 |  |  | 26.3885 |  |  | 31.2265 |  |  | 43.1483 |  |  | 64.8395 |  |  | 96.2183 |  |  | 131.2021 |  |  | 168.2638 |  |  | 210.6646
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1723 |  |  | 30.5606 |  |  | 21.8689 |  |  | -7.1592 |  |  | -78.6897 |  |  | -208.8372 |  |  | -397.1096 |  |  | -607.0126 |  |  | -829.3826 |  |  | -1083.7879
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8345 |  |  | 47.2165 |  |  | 39.7792 |  |  | 18.7971 |  |  | -26.9788 |  |  | -100.6768 |  |  | -193.3867 |  |  | -276.942 |  |  | -331.6105 |  |  | -329.2138
[13 empty] | C Non choked w/ reducers | 7 |  | 8.1741 |  |  | 37.0649 |  |  | 108.6111 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.5678 |  |  | 29.8193 |  |  | 80.5303 |  |  | 229.5321 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 8.1741 |  |  | 37.0649 |  |  | 108.6111 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.4441 | 46.3581 |  | 25.4649 | 204.7397 |  | 85.6111 | 506.3456 |  | 5500 | 986.232 |  | 5500 | 1654.5904 |  | 5500 | 2439.069 |  | 5500 | 3254.947 |  | 5500 | 3971.654 |  | 5500 | 4610.9669 |  | 5500 | 5247.7105
[13 empty] | Next iteration flow rate |  |  | 47.2852 | Abs Value of | Flow this | 206.7871 | Abs Value of | Flow this | 511.409 | Abs Value of | Flow this | 996.0943 | Abs Value of | Flow this | 1671.1363 | Abs Value of | Flow this | 2463.4597 | Abs Value of | Flow this | 3287.4965 | Abs Value of | Flow this | 4011.3705 | Abs Value of | Flow this | 4657.0766 | Abs Value of | Flow this | 5300.1876 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8406 |  |  | 55.472 |  |  | 48.0833 |  |  | 23.4071 |  |  | -37.3999 |  |  | -148.036 |  |  | -308.0833 |  |  | -486.5183 |  |  | -675.5514 |  |  | -891.817
[13 empty] | P2 at this iteration flow rate |  |  | 24.6719 |  |  | 24.9456 |  |  | 26.4233 |  |  | 31.3586 |  |  | 43.52 |  |  | 65.6472 |  |  | 97.6567 |  |  | 133.3437 |  |  | 171.1503 |  |  | 214.4034
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1688 |  |  | 30.5264 |  |  | 21.66 |  |  | -7.9515 |  |  | -80.9198 |  |  | -213.6832 |  |  | -405.7399 |  |  | -619.8619 |  |  | -846.7016 |  |  | -1106.2204
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8319 |  |  | 47.1921 |  |  | 39.6345 |  |  | 18.2718 |  |  | -28.3722 |  |  | -103.4917 |  |  | -198.0023 |  |  | -283.1687 |  |  | -338.8449 |  |  | -336.2588
[13 empty] | C Non choked w/ reducers | 7 |  | 8.3381 |  |  | 37.4565 |  |  | 110.2248 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.6993 |  |  | 30.1252 |  |  | 81.484 |  |  | 235.1361 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 8.3381 |  |  | 37.4565 |  |  | 110.2248 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.6081 | 47.2852 |  | 25.8565 | 206.7871 |  | 87.2248 | 511.409 |  | 5500 | 996.0943 |  | 5500 | 1671.1363 |  | 5500 | 2463.4597 |  | 5500 | 3287.4965 |  | 5500 | 4011.3705 |  | 5500 | 4657.0766 |  | 5500 | 5300.1876
[13 empty] | Next iteration flow rate |  |  | 48.2309 | Abs Value of | Flow this | 208.8549 | Abs Value of | Flow this | 516.5231 | Abs Value of | Flow this | 1006.0552 | Abs Value of | Flow this | 1687.8477 | Abs Value of | Flow this | 2488.0943 | Abs Value of | Flow this | 3320.3715 | Abs Value of | Flow this | 4051.4842 | Abs Value of | Flow this | 4703.6474 | Abs Value of | Flow this | 5353.1895 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8376 |  |  | 55.443 |  |  | 47.9058 |  |  | 22.7335 |  |  | -39.2956 |  |  | -152.1556 |  |  | -315.4198 |  |  | -497.4413 |  |  | -690.2739 |  |  | -910.8865
[13 empty] | P2 at this iteration flow rate |  |  | 24.6725 |  |  | 24.9514 |  |  | 26.4588 |  |  | 31.4933 |  |  | 43.8991 |  |  | 66.4711 |  |  | 99.124 |  |  | 135.5283 |  |  | 174.0948 |  |  | 218.2173
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1651 |  |  | 30.4916 |  |  | 21.447 |  |  | -8.7598 |  |  | -83.1947 |  |  | -218.6267 |  |  | -414.5437 |  |  | -632.9696 |  |  | -864.3687 |  |  | -1129.1039
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8292 |  |  | 47.1672 |  |  | 39.4868 |  |  | 17.736 |  |  | -29.7937 |  |  | -106.3631 |  |  | -202.7107 |  |  | -289.5205 |  |  | -346.2246 |  |  | -343.4454
[13 empty] | C Non choked w/ reducers | 7 |  | 8.5053 |  |  | 37.8527 |  |  | 111.8786 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.8335 |  |  | 30.4345 |  |  | 82.4526 |  |  | 241.0482 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 8.5053 |  |  | 37.8527 |  |  | 111.8786 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.7753 | 48.2309 |  | 26.2527 | 208.8549 |  | 88.8786 | 516.5231 |  | 5500 | 1006.0552 |  | 5500 | 1687.8477 |  | 5500 | 2488.0943 |  | 5500 | 3320.3715 |  | 5500 | 4051.4842 |  | 5500 | 4703.6474 |  | 5500 | 5353.1895
[13 empty] | Next iteration flow rate |  |  | 49.1955 | Abs Value of | Flow this | 210.9435 | Abs Value of | Flow this | 521.6884 | Abs Value of | Flow this | 1016.1158 | Abs Value of | Flow this | 1704.7262 | Abs Value of | Flow this | 2512.9752 | Abs Value of | Flow this | 3353.5752 | Abs Value of | Flow this | 4091.999 | Abs Value of | Flow this | 4750.6838 | Abs Value of | Flow this | 5406.7214 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8344 |  |  | 55.4134 |  |  | 47.7247 |  |  | 22.0465 |  |  | -41.2295 |  |  | -156.3579 |  |  | -322.9037 |  |  | -508.5839 |  |  | -705.2925 |  |  | -930.3394
[13 empty] | P2 at this iteration flow rate |  |  | 24.6731 |  |  | 24.9573 |  |  | 26.4951 |  |  | 31.6307 |  |  | 44.2859 |  |  | 67.3116 |  |  | 100.6207 |  |  | 137.7568 |  |  | 177.0985 |  |  | 222.1079
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1613 |  |  | 30.456 |  |  | 21.2296 |  |  | -9.5842 |  |  | -85.5154 |  |  | -223.6695 |  |  | -423.5245 |  |  | -646.3407 |  |  | -882.391 |  |  | -1152.4473
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8264 |  |  | 47.1418 |  |  | 39.3361 |  |  | 17.1894 |  |  | -31.2436 |  |  | -109.2923 |  |  | -207.5137 |  |  | -295.9999 |  |  | -353.7528 |  |  | -350.7765
[13 empty] | C Non choked w/ reducers | 7 |  | 8.6759 |  |  | 38.2535 |  |  | 113.5743 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.9703 |  |  | 30.7471 |  |  | 83.4364 |  |  | 247.2993 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 8.6759 |  |  | 38.2535 |  |  | 113.5743 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.9459 | 49.1955 |  | 26.6535 | 210.9435 |  | 90.5743 | 521.6884 |  | 5500 | 1016.1158 |  | 5500 | 1704.7262 |  | 5500 | 2512.9752 |  | 5500 | 3353.5752 |  | 5500 | 4091.999 |  | 5500 | 4750.6838 |  | 5500 | 5406.7214
[13 empty] | Next iteration flow rate |  |  | 50.1794 | Abs Value of | Flow this | 213.0529 | Abs Value of | Flow this | 526.9052 | Abs Value of | Flow this | 1026.2769 | Abs Value of | Flow this | 1721.7734 | Abs Value of | Flow this | 2538.105 | Abs Value of | Flow this | 3387.1109 | Abs Value of | Flow this | 4132.919 | Abs Value of | Flow this | 4798.1907 | Abs Value of | Flow this | 5460.7886 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8311 |  |  | 55.3832 |  |  | 47.5399 |  |  | 21.3456 |  |  | -43.2022 |  |  | -160.6447 |  |  | -330.5381 |  |  | -519.9504 |  |  | -720.6129 |  |  | -950.1832
[13 empty] | P2 at this iteration flow rate |  |  | 24.6738 |  |  | 24.9634 |  |  | 26.532 |  |  | 31.7709 |  |  | 44.6804 |  |  | 68.1689 |  |  | 102.1476 |  |  | 140.0301 |  |  | 180.1626 |  |  | 226.0766
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1573 |  |  | 30.4198 |  |  | 21.0079 |  |  | -10.4253 |  |  | -87.8826 |  |  | -228.8137 |  |  | -432.6857 |  |  | -659.9805 |  |  | -900.7754 |  |  | -1176.2599
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8235 |  |  | 47.1159 |  |  | 39.1824 |  |  | 16.6318 |  |  | -32.7228 |  |  | -112.2803 |  |  | -212.4132 |  |  | -302.6096 |  |  | -361.4322 |  |  | -358.2549
[13 empty] | C Non choked w/ reducers | 7 |  | 8.85 |  |  | 38.659 |  |  | 115.3138 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 7.1099 |  |  | 31.0631 |  |  | 84.4359 |  |  | 253.9248 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 8.85 |  |  | 38.659 |  |  | 115.3138 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.12 | 50.1794 |  | 27.059 | 213.0529 |  | 92.3138 | 526.9052 |  | 5500 | 1026.2769 |  | 5500 | 1721.7734 |  | 5500 | 2538.105 |  | 5500 | 3387.1109 |  | 5500 | 4132.919 |  | 5500 | 4798.1907 |  | 5500 | 5460.7886
[13 empty] | Next iteration flow rate |  |  | 51.183 | Abs Value of | Flow this | 215.1835 | Abs Value of | Flow this | 532.1743 | Abs Value of | Flow this | 1036.5397 | Abs Value of | Flow this | 1738.9912 | Abs Value of | Flow this | 2563.486 | Abs Value of | Flow this | 3420.982 | Abs Value of | Flow this | 4174.2482 | Abs Value of | Flow this | 4846.1726 | Abs Value of | Flow this | 5515.3965 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8277 |  |  | 55.3523 |  |  | 47.3515 |  |  | 20.6306 |  |  | -45.2146 |  |  | -165.0177 |  |  | -338.3259 |  |  | -531.5455 |  |  | -736.2412 |  |  | -970.4259
[13 empty] | P2 at this iteration flow rate |  |  | 24.6745 |  |  | 24.9695 |  |  | 26.5697 |  |  | 31.9139 |  |  | 45.0829 |  |  | 69.0435 |  |  | 103.7052 |  |  | 142.3491 |  |  | 183.2882 |  |  | 230.1252
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1532 |  |  | 30.3828 |  |  | 20.7818 |  |  | -11.2833 |  |  | -90.2975 |  |  | -234.0612 |  |  | -442.0311 |  |  | -673.8946 |  |  | -919.5294 |  |  | -1200.5511
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8205 |  |  | 47.0895 |  |  | 39.0256 |  |  | 16.063 |  |  | -34.2317 |  |  | -115.3284 |  |  | -217.4113 |  |  | -309.3522 |  |  | -369.266 |  |  | -365.8836
[13 empty] | C Non choked w/ reducers | 7 |  | 9.0276 |  |  | 39.0694 |  |  | 117.0989 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 7.2524 |  |  | 31.3826 |  |  | 85.4514 |  |  | 260.9653 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 9.0276 |  |  | 39.0694 |  |  | 117.0989 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2976 | 51.183 |  | 27.4694 | 215.1835 |  | 94.0989 | 532.1743 |  | 5500 | 1036.5397 |  | 5500 | 1738.9912 |  | 5500 | 2563.486 |  | 5500 | 3420.982 |  | 5500 | 4174.2482 |  | 5500 | 4846.1726 |  | 5500 | 5515.3965
[13 empty] | Next iteration flow rate |  |  | 52.2067 | Abs Value of | Flow this | 217.3353 | Abs Value of | Flow this | 537.496 | Abs Value of | Flow this | 1046.9051 | Abs Value of | Flow this | 1756.3811 | Abs Value of | Flow this | 2589.1209 | Abs Value of | Flow this | 3455.1919 | Abs Value of | Flow this | 4215.9907 | Abs Value of | Flow this | 4894.6343 | Abs Value of | Flow this | 5570.5504 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8241 |  |  | 55.3209 |  |  | 47.1592 |  |  | 19.9013 |  |  | -47.2674 |  |  | -169.4786 |  |  | -346.2703 |  |  | -543.3735 |  |  | -752.1837 |  |  | -991.0755
[13 empty] | P2 at this iteration flow rate |  |  | 24.6752 |  |  | 24.9758 |  |  | 26.6082 |  |  | 32.0597 |  |  | 45.4935 |  |  | 69.9357 |  |  | 105.2941 |  |  | 144.7147 |  |  | 186.4767 |  |  | 234.2551
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1489 |  |  | 30.3451 |  |  | 20.5511 |  |  | -12.1585 |  |  | -92.7609 |  |  | -239.4143 |  |  | -451.5644 |  |  | -688.0883 |  |  | -938.6604 |  |  | -1225.3306
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8173 |  |  | 47.0626 |  |  | 38.8657 |  |  | 15.4827 |  |  | -35.7709 |  |  | -118.4377 |  |  | -222.5098 |  |  | -316.2303 |  |  | -377.2573 |  |  | -373.6657
[13 empty] | C Non choked w/ reducers | 7 |  | 9.2087 |  |  | 39.4846 |  |  | 118.9319 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 7.3976 |  |  | 31.7055 |  |  | 86.4833 |  |  | 268.4685 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 9.2087 |  |  | 39.4846 |  |  | 118.9319 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4787 | 52.2067 |  | 27.8846 | 217.3353 |  | 95.9319 | 537.496 |  | 5500 | 1046.9051 |  | 5500 | 1756.3811 |  | 5500 | 2589.1209 |  | 5500 | 3455.1919 |  | 5500 | 4215.9907 |  | 5500 | 4894.6343 |  | 5500 | 5570.5504
[13 empty] | Next iteration flow rate |  |  | 53.2508 | Abs Value of | Flow this | 219.5086 | Abs Value of | Flow this | 542.871 | Abs Value of | Flow this | 1057.3741 | Abs Value of | Flow this | 1773.9449 | Abs Value of | Flow this | 2615.0121 | Abs Value of | Flow this | 3489.7438 | Abs Value of | Flow this | 4258.1506 | Abs Value of | Flow this | 4943.5807 | Abs Value of | Flow this | 5626.2559 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8204 |  |  | 55.2889 |  |  | 46.9631 |  |  | 19.1573 |  |  | -49.3615 |  |  | -174.0291 |  |  | -354.3744 |  |  | -555.4394 |  |  | -768.4466 |  |  | -1012.1401
[13 empty] | P2 at this iteration flow rate |  |  | 24.6759 |  |  | 24.9822 |  |  | 26.6474 |  |  | 32.2085 |  |  | 45.9123 |  |  | 70.8458 |  |  | 106.9149 |  |  | 147.1279 |  |  | 189.7293 |  |  | 238.468
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1445 |  |  | 30.3066 |  |  | 20.3157 |  |  | -13.0513 |  |  | -95.2738 |  |  | -244.8749 |  |  | -461.2892 |  |  | -702.5672 |  |  | -958.1759 |  |  | -1250.6081
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.814 |  |  | 47.0351 |  |  | 38.7026 |  |  | 14.8908 |  |  | -37.341 |  |  | -121.6095 |  |  | -227.7107 |  |  | -323.2466 |  |  | -385.4091 |  |  | -381.6042
[13 empty] | C Non choked w/ reducers | 7 |  | 9.3936 |  |  | 39.9047 |  |  | 120.8149 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 7.5458 |  |  | 32.0319 |  |  | 87.5321 |  |  | 276.4898 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 9.3936 |  |  | 39.9047 |  |  | 120.8149 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6636 | 53.2508 |  | 28.3047 | 219.5086 |  | 97.8149 | 542.871 |  | 5500 | 1057.3741 |  | 5500 | 1773.9449 |  | 5500 | 2615.0121 |  | 5500 | 3489.7438 |  | 5500 | 4258.1506 |  | 5500 | 4943.5807 |  | 5500 | 5626.2559
[13 empty] | Next iteration flow rate |  |  | 54.3158 | Abs Value of | Flow this | 221.7037 | Abs Value of | Flow this | 548.2997 | Abs Value of | Flow this | 1067.9479 | Abs Value of | Flow this | 1791.6843 | Abs Value of | Flow this | 2641.1622 | Abs Value of | Flow this | 3524.6412 | Abs Value of | Flow this | 4300.7321 | Abs Value of | Flow this | 4993.0165 | Abs Value of | Flow this | 5682.5185 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8165 |  |  | 55.2561 |  |  | 46.7631 |  |  | 18.3983 |  |  | -51.4977 |  |  | -178.6711 |  |  | -362.6413 |  |  | -567.7477 |  |  | -785.0364 |  |  | -1033.6281
[13 empty] | P2 at this iteration flow rate |  |  | 24.6767 |  |  | 24.9888 |  |  | 26.6874 |  |  | 32.3603 |  |  | 46.3395 |  |  | 71.7742 |  |  | 108.5683 |  |  | 149.5895 |  |  | 193.0473 |  |  | 242.7656
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1398 |  |  | 30.2674 |  |  | 20.0757 |  |  | -13.962 |  |  | -97.8372 |  |  | -250.4453 |  |  | -471.2096 |  |  | -717.3373 |  |  | -978.0836 |  |  | -1276.3938
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8106 |  |  | 47.007 |  |  | 38.5361 |  |  | 14.287 |  |  | -38.9427 |  |  | -124.8451 |  |  | -233.0162 |  |  | -330.404 |  |  | -393.7249 |  |  | -389.7022
[13 empty] | C Non choked w/ reducers | 7 |  | 9.5821 |  |  | 40.3299 |  |  | 122.7505 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 7.697 |  |  | 32.3619 |  |  | 88.5981 |  |  | 285.0945 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 9.5821 |  |  | 40.3299 |  |  | 122.7505 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8521 | 54.3158 |  | 28.7299 | 221.7037 |  | 99.7505 | 548.2997 |  | 5500 | 1067.9479 |  | 5500 | 1791.6843 |  | 5500 | 2641.1622 |  | 5500 | 3524.6412 |  | 5500 | 4300.7321 |  | 5500 | 4993.0165 |  | 5500 | 5682.5185
[13 empty] | Next iteration flow rate |  |  | 55.4022 | Abs Value of | Flow this | 223.9208 | Abs Value of | Flow this | 553.7827 | Abs Value of | Flow this | 1078.6274 | Abs Value of | Flow this | 1809.6012 | Abs Value of | Flow this | 2667.5738 | Abs Value of | Flow this | 3559.8876 | Abs Value of | Flow this | 4343.7394 | Abs Value of | Flow this | 5042.9466 | Abs Value of | Flow this | 5739.3437 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8125 |  |  | 55.2228 |  |  | 46.559 |  |  | 17.6241 |  |  | -53.6768 |  |  | -183.4064 |  |  | -371.0744 |  |  | -580.3035 |  |  | -801.9596 |  |  | -1055.5481
[13 empty] | P2 at this iteration flow rate |  |  | 24.6775 |  |  | 24.9954 |  |  | 26.7282 |  |  | 32.5152 |  |  | 46.7754 |  |  | 72.7213 |  |  | 110.2549 |  |  | 152.1007 |  |  | 196.4319 |  |  | 247.1496
[13 empty] | Delta P at this iteration flow rate |  |  | 32.135 |  |  | 30.2273 |  |  | 19.8308 |  |  | -14.8911 |  |  | -100.4521 |  |  | -256.1277 |  |  | -481.3293 |  |  | -732.4041 |  |  | -998.3915 |  |  | -1302.6977
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8071 |  |  | 46.9784 |  |  | 38.3664 |  |  | 13.6711 |  |  | -40.5766 |  |  | -128.1458 |  |  | -238.4284 |  |  | -337.7052 |  |  | -402.2078 |  |  | -397.963
[13 empty] | C Non choked w/ reducers | 7 |  | 9.7745 |  |  | 40.7602 |  |  | 124.7411 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 7.8512 |  |  | 32.6954 |  |  | 89.6818 |  |  | 294.3606 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 9.7745 |  |  | 40.7602 |  |  | 124.7411 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5.0445 | 55.4022 |  | 29.1602 | 223.9208 |  | 101.7411 | 553.7827 |  | 5500 | 1078.6274 |  | 5500 | 1809.6012 |  | 5500 | 2667.5738 |  | 5500 | 3559.8876 |  | 5500 | 4343.7394 |  | 5500 | 5042.9466 |  | 5500 | 5739.3437
[13 empty] | Next iteration flow rate |  |  | 56.5102 | Abs Value of | Flow this | 226.16 | Abs Value of | Flow this | 559.3205 | Abs Value of | Flow this | 1089.4136 | Abs Value of | Flow this | 1827.6972 | Abs Value of | Flow this | 2694.2496 | Abs Value of | Flow this | 3595.4865 | Abs Value of | Flow this | 4387.1768 | Abs Value of | Flow this | 5093.3761 | Abs Value of | Flow this | 5796.7371 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8083 |  |  | 55.1887 |  |  | 46.3508 |  |  | 16.8343 |  |  | -55.8997 |  |  | -188.2369 |  |  | -379.677 |  |  | -593.1116 |  |  | -819.223 |  |  | -1077.9086
[13 empty] | P2 at this iteration flow rate |  |  | 24.6783 |  |  | 25.0023 |  |  | 26.7698 |  |  | 32.6731 |  |  | 47.2199 |  |  | 73.6874 |  |  | 111.9754 |  |  | 154.6623 |  |  | 199.8846 |  |  | 251.6217
[13 empty] | Delta P at this iteration flow rate |  |  | 32.13 |  |  | 30.1865 |  |  | 19.581 |  |  | -15.8388 |  |  | -103.1196 |  |  | -261.9242 |  |  | -491.6524 |  |  | -747.7739 |  |  | -1019.1076 |  |  | -1329.5303
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.8034 |  |  | 46.9492 |  |  | 38.1932 |  |  | 13.0428 |  |  | -42.2433 |  |  | -131.5127 |  |  | -243.9493 |  |  | -345.1532 |  |  | -410.8611 |  |  | -406.3899
[13 empty] | C Non choked w/ reducers | 7 |  | 9.9708 |  |  | 41.1956 |  |  | 126.7897 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 8.0086 |  |  | 33.0326 |  |  | 90.7838 |  |  | 304.381 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 9.9708 |  |  | 41.1956 |  |  | 126.7897 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5.2408 | 56.5102 |  | 29.5956 | 226.16 |  | 103.7897 | 559.3205 |  | 5500 | 1089.4136 |  | 5500 | 1827.6972 |  | 5500 | 2694.2496 |  | 5500 | 3595.4865 |  | 5500 | 4387.1768 |  | 5500 | 5093.3761 |  | 5500 | 5796.7371
[13 empty] | Next iteration flow rate |  |  | 57.6404 | Abs Value of | Flow this | 228.4216 | Abs Value of | Flow this | 564.9137 | Abs Value of | Flow this | 1100.3078 | Abs Value of | Flow this | 1845.9742 | Abs Value of | Flow this | 2721.1921 | Abs Value of | Flow this | 3631.4414 | Abs Value of | Flow this | 4431.0486 | Abs Value of | Flow this | 5144.3099 | Abs Value of | Flow this | 5854.7045 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8039 |  |  | 55.154 |  |  | 46.1384 |  |  | 16.0287 |  |  | -58.1673 |  |  | -193.1644 |  |  | -388.4525 |  |  | -606.1771 |  |  | -836.8334 |  |  | -1100.7186
[13 empty] | P2 at this iteration flow rate |  |  | 24.6792 |  |  | 25.0092 |  |  | 26.8123 |  |  | 32.8343 |  |  | 47.6735 |  |  | 74.6729 |  |  | 113.7305 |  |  | 157.2754 |  |  | 203.4067 |  |  | 256.1837
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1247 |  |  | 30.1448 |  |  | 19.3261 |  |  | -16.8056 |  |  | -105.8408 |  |  | -267.8373 |  |  | -502.183 |  |  | -763.4525 |  |  | -1040.2401 |  |  | -1356.9023
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7995 |  |  | 46.9194 |  |  | 38.0165 |  |  | 12.4018 |  |  | -43.9436 |  |  | -134.9474 |  |  | -249.5812 |  |  | -352.7509 |  |  | -419.6885 |  |  | -414.9861
[13 empty] | C Non choked w/ reducers | 7 |  | 10.171 |  |  | 41.6363 |  |  | 128.8991 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 8.169 |  |  | 33.3736 |  |  | 91.9044 |  |  | 315.2689 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 10.171 |  |  | 41.6363 |  |  | 128.8991 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5.441 | 57.6404 |  | 30.0363 | 228.4216 |  | 105.8991 | 564.9137 |  | 5500 | 1100.3078 |  | 5500 | 1845.9742 |  | 5500 | 2721.1921 |  | 5500 | 3631.4414 |  | 5500 | 4431.0486 |  | 5500 | 5144.3099 |  | 5500 | 5854.7045
[13 empty] | Next iteration flow rate |  |  | 58.7932 | Abs Value of | Flow this | 230.7058 | Abs Value of | Flow this | 570.5629 | Abs Value of | Flow this | 1111.3109 | Abs Value of | Flow this | 1864.4339 | Abs Value of | Flow this | 2748.404 | Abs Value of | Flow this | 3667.7558 | Abs Value of | Flow this | 4475.3591 | Abs Value of | Flow this | 5195.753 | Abs Value of | Flow this | 5913.2515 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7994 |  |  | 55.1186 |  |  | 45.9218 |  |  | 15.2069 |  |  | -60.4805 |  |  | -198.1911 |  |  | -397.4044 |  |  | -619.5053 |  |  | -854.7978 |  |  | -1123.9871
[13 empty] | P2 at this iteration flow rate |  |  | 24.6801 |  |  | 25.0163 |  |  | 26.8556 |  |  | 32.9986 |  |  | 48.1361 |  |  | 75.6782 |  |  | 115.5209 |  |  | 159.9411 |  |  | 206.9996 |  |  | 260.8374
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1193 |  |  | 30.1023 |  |  | 19.0662 |  |  | -17.7918 |  |  | -108.6166 |  |  | -273.8693 |  |  | -512.9253 |  |  | -779.4464 |  |  | -1061.7973 |  |  | -1384.8245
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7955 |  |  | 46.8891 |  |  | 37.8363 |  |  | 11.748 |  |  | -45.678 |  |  | -138.4511 |  |  | -255.3263 |  |  | -360.5013 |  |  | -428.6932 |  |  | -423.7551
[13 empty] | C Non choked w/ reducers | 7 |  | 10.3753 |  |  | 42.0824 |  |  | 131.0726 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 8.3328 |  |  | 33.7182 |  |  | 93.0443 |  |  | 327.1624 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 10.3753 |  |  | 42.0824 |  |  | 131.0726 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5.6453 | 58.7932 |  | 30.4824 | 230.7058 |  | 108.0726 | 570.5629 |  | 5500 | 1111.3109 |  | 5500 | 1864.4339 |  | 5500 | 2748.404 |  | 5500 | 3667.7558 |  | 5500 | 4475.3591 |  | 5500 | 5195.753 |  | 5500 | 5913.2515
[13 empty] | Next iteration flow rate |  |  | 59.9691 | Abs Value of | Flow this | 233.0129 | Abs Value of | Flow this | 576.2685 | Abs Value of | Flow this | 1122.424 | Abs Value of | Flow this | 1883.0783 | Abs Value of | Flow this | 2775.888 | Abs Value of | Flow this | 3704.4333 | Abs Value of | Flow this | 4520.1127 | Abs Value of | Flow this | 5247.7105 | Abs Value of | Flow this | 5972.384 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7947 |  |  | 55.0825 |  |  | 45.7008 |  |  | 14.3685 |  |  | -62.8401 |  |  | -203.3187 |  |  | -406.5363 |  |  | -633.1014 |  |  | -873.1232 |  |  | -1147.7232
[13 empty] | P2 at this iteration flow rate |  |  | 24.6811 |  |  | 25.0235 |  |  | 26.8998 |  |  | 33.1663 |  |  | 48.608 |  |  | 76.7037 |  |  | 117.3473 |  |  | 162.6603 |  |  | 210.6646 |  |  | 265.5846
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1136 |  |  | 30.059 |  |  | 18.801 |  |  | -18.7978 |  |  | -111.4482 |  |  | -280.0225 |  |  | -523.8835 |  |  | -795.7616 |  |  | -1083.7879 |  |  | -1413.3078
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7913 |  |  | 46.8581 |  |  | 37.6525 |  |  | 11.081 |  |  | -47.4473 |  |  | -142.0252 |  |  | -261.1869 |  |  | -368.4075 |  |  | -437.879 |  |  | -432.7004
[13 empty] | C Non choked w/ reducers | 7 |  | 10.5838 |  |  | 42.5338 |  |  | 133.3137 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 8.4998 |  |  | 34.0666 |  |  | 94.2038 |  |  | 340.2331 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 10.5838 |  |  | 42.5338 |  |  | 133.3137 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5.8538 | 59.9691 |  | 30.9338 | 233.0129 |  | 110.3137 | 576.2685 |  | 5500 | 1122.424 |  | 5500 | 1883.0783 |  | 5500 | 2775.888 |  | 5500 | 3704.4333 |  | 5500 | 4520.1127 |  | 5500 | 5247.7105 |  | 5500 | 5972.384
[13 empty] | Next iteration flow rate |  |  | 61.1685 | Abs Value of | Flow this | 235.343 | Abs Value of | Flow this | 582.0312 | Abs Value of | Flow this | 1133.6482 | Abs Value of | Flow this | 1901.909 | Abs Value of | Flow this | 2803.6469 | Abs Value of | Flow this | 3741.4777 | Abs Value of | Flow this | 4565.3138 | Abs Value of | Flow this | 5300.1876 | Abs Value of | Flow this | 6032.1079 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7898 |  |  | 55.0456 |  |  | 45.4754 |  |  | 13.5133 |  |  | -65.2472 |  |  | -208.5494 |  |  | -415.8517 |  |  | -646.9707 |  |  | -891.817 |  |  | -1171.9365
[13 empty] | P2 at this iteration flow rate |  |  | 24.682 |  |  | 25.0309 |  |  | 26.9449 |  |  | 33.3373 |  |  | 49.0894 |  |  | 77.7499 |  |  | 119.2103 |  |  | 165.4341 |  |  | 214.4034 |  |  | 270.4273
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1077 |  |  | 30.0147 |  |  | 18.5305 |  |  | -19.824 |  |  | -114.3367 |  |  | -286.2993 |  |  | -535.062 |  |  | -812.4049 |  |  | -1106.2204 |  |  | -1442.3638
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.787 |  |  | 46.8265 |  |  | 37.4649 |  |  | 10.4007 |  |  | -49.2521 |  |  | -145.6711 |  |  | -267.1653 |  |  | -376.4726 |  |  | -447.2493 |  |  | -441.8255
[13 empty] | C Non choked w/ reducers | 7 |  | 10.7964 |  |  | 42.9908 |  |  | 135.6261 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 8.6701 |  |  | 34.4189 |  |  | 95.3837 |  |  | 354.6972 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 10.7964 |  |  | 42.9908 |  |  | 135.6261 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 6.0664 | 61.1685 |  | 31.3908 | 235.343 |  | 112.6261 | 582.0312 |  | 5500 | 1133.6482 |  | 5500 | 1901.909 |  | 5500 | 2803.6469 |  | 5500 | 3741.4777 |  | 5500 | 4565.3138 |  | 5500 | 5300.1876 |  | 5500 | 6032.1079
[13 empty] | Next iteration flow rate |  |  | 62.3918 | Abs Value of | Flow this | 237.6964 | Abs Value of | Flow this | 587.8515 | Abs Value of | Flow this | 1144.9847 | Abs Value of | Flow this | 1920.9281 | Abs Value of | Flow this | 2831.6834 | Abs Value of | Flow this | 3778.8925 | Abs Value of | Flow this | 4610.9669 | Abs Value of | Flow this | 5353.1895 | Abs Value of | Flow this | 6092.429 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7847 |  |  | 55.008 |  |  | 45.2454 |  |  | 12.6409 |  |  | -67.7027 |  |  | -213.8853 |  |  | -425.3543 |  |  | -661.1188 |  |  | -910.8865 |  |  | -1196.6364
[13 empty] | P2 at this iteration flow rate |  |  | 24.6831 |  |  | 25.0384 |  |  | 26.9909 |  |  | 33.5118 |  |  | 49.5805 |  |  | 78.8171 |  |  | 121.1109 |  |  | 168.2638 |  |  | 218.2173 |  |  | 275.3673
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1016 |  |  | 29.9696 |  |  | 18.2545 |  |  | -20.8709 |  |  | -117.2833 |  |  | -292.7024 |  |  | -546.4652 |  |  | -829.3826 |  |  | -1129.1039 |  |  | -1472.0037
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7825 |  |  | 46.7942 |  |  | 37.2736 |  |  | 9.7066 |  |  | -51.0932 |  |  | -149.3904 |  |  | -273.2638 |  |  | -384.6998 |  |  | -456.8081 |  |  | -451.134
[13 empty] | C Non choked w/ reducers | 7 |  | 11.0134 |  |  | 43.4534 |  |  | 138.0138 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 8.8439 |  |  | 34.7751 |  |  | 96.5844 |  |  | 370.8308 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 11.0134 |  |  | 43.4534 |  |  | 138.0138 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 6.2834 | 62.3918 |  | 31.8534 | 237.6964 |  | 115.0138 | 587.8515 |  | 5500 | 1144.9847 |  | 5500 | 1920.9281 |  | 5500 | 2831.6834 |  | 5500 | 3778.8925 |  | 5500 | 4610.9669 |  | 5500 | 5353.1895 |  | 5500 | 6092.429
[13 empty] | Next iteration flow rate |  |  | 63.6397 | Abs Value of | Flow this | 240.0734 | Abs Value of | Flow this | 593.73 | Abs Value of | Flow this | 1156.4345 | Abs Value of | Flow this | 1940.1374 | Abs Value of | Flow this | 2860.0002 | Abs Value of | Flow this | 3816.6814 | Abs Value of | Flow this | 4657.0766 | Abs Value of | Flow this | 5406.7214 | Abs Value of | Flow this | 6153.3533 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7794 |  |  | 54.9697 |  |  | 45.0109 |  |  | 11.751 |  |  | -70.2076 |  |  | -219.3284 |  |  | -435.0479 |  |  | -675.5514 |  |  | -930.3394 |  |  | -1221.8328
[13 empty] | P2 at this iteration flow rate |  |  | 24.6841 |  |  | 25.0461 |  |  | 27.0378 |  |  | 33.6898 |  |  | 50.0815 |  |  | 79.9057 |  |  | 123.0496 |  |  | 171.1503 |  |  | 222.1079 |  |  | 280.4066
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0952 |  |  | 29.9236 |  |  | 17.973 |  |  | -21.9388 |  |  | -120.2891 |  |  | -299.2341 |  |  | -558.0975 |  |  | -846.7016 |  |  | -1152.4473 |  |  | -1502.2394
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7778 |  |  | 46.7613 |  |  | 37.0785 |  |  | 8.9986 |  |  | -52.9713 |  |  | -153.1843 |  |  | -279.4849 |  |  | -393.0923 |  |  | -466.5589 |  |  | -460.6296
[13 empty] | C Non choked w/ reducers | 7 |  | 11.2348 |  |  | 43.9217 |  |  | 140.4813 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 9.0213 |  |  | 35.1352 |  |  | 97.8067 |  |  | 388.9943 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 11.2348 |  |  | 43.9217 |  |  | 140.4813 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 6.5048 | 63.6397 |  | 32.3217 | 240.0734 |  | 117.4813 | 593.73 |  | 5500 | 1156.4345 |  | 5500 | 1940.1374 |  | 5500 | 2860.0002 |  | 5500 | 3816.6814 |  | 5500 | 4657.0766 |  | 5500 | 5406.7214 |  | 5500 | 6153.3533
[13 empty] | Next iteration flow rate |  |  | 64.9125 | Abs Value of | Flow this | 242.4741 | Abs Value of | Flow this | 599.6673 | Abs Value of | Flow this | 1167.9989 | Abs Value of | Flow this | 1959.5388 | Abs Value of | Flow this | 2888.6002 | Abs Value of | Flow this | 3854.8482 | Abs Value of | Flow this | 4703.6474 | Abs Value of | Flow this | 5460.7886 | Abs Value of | Flow this | 6214.8868 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7738 |  |  | 54.9305 |  |  | 44.7716 |  |  | 10.8431 |  |  | -72.7628 |  |  | -224.8809 |  |  | -444.9364 |  |  | -690.2739 |  |  | -950.1832 |  |  | -1247.5357
[13 empty] | P2 at this iteration flow rate |  |  | 24.6852 |  |  | 25.0539 |  |  | 27.0857 |  |  | 33.8714 |  |  | 50.5926 |  |  | 81.0162 |  |  | 125.0273 |  |  | 174.0948 |  |  | 226.0766 |  |  | 285.5471
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0886 |  |  | 29.8766 |  |  | 17.6859 |  |  | -23.0282 |  |  | -123.3553 |  |  | -305.8971 |  |  | -569.9637 |  |  | -864.3687 |  |  | -1176.2599 |  |  | -1533.0828
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7729 |  |  | 46.7278 |  |  | 36.8794 |  |  | 8.2764 |  |  | -54.8872 |  |  | -157.0546 |  |  | -285.8311 |  |  | -401.6536 |  |  | -476.5058 |  |  | -470.3161
[13 empty] | C Non choked w/ reducers | 7 |  | 11.4607 |  |  | 44.3957 |  |  | 143.0334 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 9.2021 |  |  | 35.4993 |  |  | 99.051 |  |  | 409.6682 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 11.4607 |  |  | 44.3957 |  |  | 143.0334 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 6.7307 | 64.9125 |  | 32.7957 | 242.4741 |  | 120.0334 | 599.6673 |  | 5500 | 1167.9989 |  | 5500 | 1959.5388 |  | 5500 | 2888.6002 |  | 5500 | 3854.8482 |  | 5500 | 4703.6474 |  | 5500 | 5460.7886 |  | 5500 | 6214.8868
[13 empty] | Next iteration flow rate |  |  | 66.2107 | Abs Value of | Flow this | 244.8988 | Abs Value of | Flow this | 605.664 | Abs Value of | Flow this | 1179.6789 | Abs Value of | Flow this | 1979.1342 | Abs Value of | Flow this | 2917.4862 | Abs Value of | Flow this | 3893.3967 | Abs Value of | Flow this | 4750.6838 | Abs Value of | Flow this | 5515.3965 | Abs Value of | Flow this | 6277.0357 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7681 |  |  | 54.8906 |  |  | 44.5275 |  |  | 9.9171 |  |  | -75.3693 |  |  | -230.545 |  |  | -455.0237 |  |  | -705.2925 |  |  | -970.4259 |  |  | -1273.7551
[13 empty] | P2 at this iteration flow rate |  |  | 24.6864 |  |  | 25.0619 |  |  | 27.1345 |  |  | 34.0566 |  |  | 51.1139 |  |  | 82.149 |  |  | 127.0447 |  |  | 177.0985 |  |  | 230.1252 |  |  | 290.791
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0817 |  |  | 29.8288 |  |  | 17.393 |  |  | -24.1395 |  |  | -126.4832 |  |  | -312.6941 |  |  | -582.0684 |  |  | -882.391 |  |  | -1200.5511 |  |  | -1564.5462
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7678 |  |  | 46.6936 |  |  | 36.6763 |  |  | 7.5396 |  |  | -56.8416 |  |  | -161.0026 |  |  | -292.3048 |  |  | -410.3869 |  |  | -486.6525 |  |  | -480.1972
[13 empty] | C Non choked w/ reducers | 7 |  | 11.6911 |  |  | 44.8757 |  |  | 145.6751 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 9.3867 |  |  | 35.8674 |  |  | 100.3181 |  |  | 433.5097 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 11.6911 |  |  | 44.8757 |  |  | 145.6751 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 6.9611 | 66.2107 |  | 33.2757 | 244.8988 |  | 122.6751 | 605.664 |  | 5500 | 1179.6789 |  | 5500 | 1979.1342 |  | 5500 | 2917.4862 |  | 5500 | 3893.3967 |  | 5500 | 4750.6838 |  | 5500 | 5515.3965 |  | 5500 | 6277.0357
[13 empty] | Next iteration flow rate |  |  | 67.5349 | Abs Value of | Flow this | 247.3478 | Abs Value of | Flow this | 611.7206 | Abs Value of | Flow this | 1191.4757 | Abs Value of | Flow this | 1998.9255 | Abs Value of | Flow this | 2946.6611 | Abs Value of | Flow this | 3932.3306 | Abs Value of | Flow this | 4798.1907 | Abs Value of | Flow this | 5570.5504 | Abs Value of | Flow this | 6339.806 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7621 |  |  | 54.8499 |  |  | 44.2784 |  |  | 8.9724 |  |  | -78.0282 |  |  | -236.323 |  |  | -465.3137 |  |  | -720.6129 |  |  | -991.0755 |  |  | -1300.5016
[13 empty] | P2 at this iteration flow rate |  |  | 24.6876 |  |  | 25.07 |  |  | 27.1843 |  |  | 34.2455 |  |  | 51.6456 |  |  | 83.3046 |  |  | 129.1027 |  |  | 180.1626 |  |  | 234.2551 |  |  | 296.1403
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0745 |  |  | 29.7799 |  |  | 17.0941 |  |  | -25.2731 |  |  | -129.6739 |  |  | -319.6276 |  |  | -594.4164 |  |  | -900.7754 |  |  | -1225.3306 |  |  | -1596.642
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7626 |  |  | 46.6587 |  |  | 36.4692 |  |  | 6.7881 |  |  | -58.8352 |  |  | -165.03 |  |  | -298.9087 |  |  | -419.2958 |  |  | -497.0033 |  |  | -490.277
[13 empty] | C Non choked w/ reducers | 7 |  | 11.9263 |  |  | 45.3616 |  |  | 148.4123 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 9.5749 |  |  | 36.2396 |  |  | 101.6086 |  |  | 461.4473 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 11.9263 |  |  | 45.3616 |  |  | 148.4123 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 7.1963 | 67.5349 |  | 33.7616 | 247.3478 |  | 125.4123 | 611.7206 |  | 5500 | 1191.4757 |  | 5500 | 1998.9255 |  | 5500 | 2946.6611 |  | 5500 | 3932.3306 |  | 5500 | 4798.1907 |  | 5500 | 5570.5504 |  | 5500 | 6339.806
[13 empty] | Next iteration flow rate |  |  | 68.8856 | Abs Value of | Flow this | 249.8213 | Abs Value of | Flow this | 617.8378 | Abs Value of | Flow this | 1203.3904 | Abs Value of | Flow this | 2018.9148 | Abs Value of | Flow this | 2976.1277 | Abs Value of | Flow this | 3971.654 | Abs Value of | Flow this | 4846.1726 | Abs Value of | Flow this | 5626.2559 | Abs Value of | Flow this | 6403.2041 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7559 |  |  | 54.8084 |  |  | 44.0244 |  |  | 8.0087 |  |  | -80.7406 |  |  | -242.2171 |  |  | -475.8105 |  |  | -736.2412 |  |  | -1012.1401 |  |  | -1327.7857
[13 empty] | P2 at this iteration flow rate |  |  | 24.6888 |  |  | 25.0783 |  |  | 27.2351 |  |  | 34.4383 |  |  | 52.1881 |  |  | 84.4834 |  |  | 131.2021 |  |  | 183.2882 |  |  | 238.468 |  |  | 301.5971
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0671 |  |  | 29.7301 |  |  | 16.7893 |  |  | -26.4295 |  |  | -132.9287 |  |  | -326.7006 |  |  | -607.0126 |  |  | -919.5294 |  |  | -1250.6081 |  |  | -1629.3829
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7571 |  |  | 46.623 |  |  | 36.2579 |  |  | 6.0214 |  |  | -60.869 |  |  | -169.1384 |  |  | -305.6453 |  |  | -428.3838 |  |  | -507.562 |  |  | -500.5594
[13 empty] | C Non choked w/ reducers | 7 |  | 12.1662 |  |  | 45.8536 |  |  | 151.251 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 9.7669 |  |  | 36.616 |  |  | 102.9233 |  |  | 494.8433 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 12.1662 |  |  | 45.8536 |  |  | 151.251 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 7.4362 | 68.8856 |  | 34.2536 | 249.8213 |  | 128.251 | 617.8378 |  | 5500 | 1203.3904 |  | 5500 | 2018.9148 |  | 5500 | 2976.1277 |  | 5500 | 3971.654 |  | 5500 | 4846.1726 |  | 5500 | 5626.2559 |  | 5500 | 6403.2041
[13 empty] | Next iteration flow rate |  |  | 70.2633 | Abs Value of | Flow this | 252.3195 | Abs Value of | Flow this | 624.0162 | Abs Value of | Flow this | 1215.4243 | Abs Value of | Flow this | 2039.1039 | Abs Value of | Flow this | 3005.889 | Abs Value of | Flow this | 4011.3705 | Abs Value of | Flow this | 4894.6343 | Abs Value of | Flow this | 5682.5185 | Abs Value of | Flow this | 6467.2361 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7494 |  |  | 54.766 |  |  | 43.7653 |  |  | 7.0257 |  |  | -83.5075 |  |  | -248.2297 |  |  | -486.5183 |  |  | -752.1837 |  |  | -1033.6281 |  |  | -1355.6182
[13 empty] | P2 at this iteration flow rate |  |  | 24.6901 |  |  | 25.0868 |  |  | 27.2869 |  |  | 34.6349 |  |  | 52.7415 |  |  | 85.6859 |  |  | 133.3437 |  |  | 186.4767 |  |  | 242.7656 |  |  | 307.1636
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0593 |  |  | 29.6792 |  |  | 16.4784 |  |  | -27.6092 |  |  | -136.249 |  |  | -333.9156 |  |  | -619.8619 |  |  | -938.6604 |  |  | -1276.3938 |  |  | -1662.7819
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7513 |  |  | 46.5867 |  |  | 36.0423 |  |  | 5.2393 |  |  | -62.9436 |  |  | -173.3293 |  |  | -312.5173 |  |  | -437.6544 |  |  | -518.333 |  |  | -511.0484
[13 empty] | C Non choked w/ reducers | 7 |  | 12.4111 |  |  | 46.3518 |  |  | 154.1981 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 9.9628 |  |  | 36.9966 |  |  | 104.263 |  |  | 535.7968 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 12.4111 |  |  | 46.3518 |  |  | 154.1981 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 7.6811 | 70.2633 |  | 34.7518 | 252.3195 |  | 131.1981 | 624.0162 |  | 5500 | 1215.4243 |  | 5500 | 2039.1039 |  | 5500 | 3005.889 |  | 5500 | 4011.3705 |  | 5500 | 4894.6343 |  | 5500 | 5682.5185 |  | 5500 | 6467.2361
[13 empty] | Next iteration flow rate |  |  | 71.6686 | Abs Value of | Flow this | 254.8427 | Abs Value of | Flow this | 630.2564 | Abs Value of | Flow this | 1227.5786 | Abs Value of | Flow this | 2059.495 | Abs Value of | Flow this | 3035.9479 | Abs Value of | Flow this | 4051.4842 | Abs Value of | Flow this | 4943.5807 | Abs Value of | Flow this | 5739.3437 | Abs Value of | Flow this | 6531.9085 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7427 |  |  | 54.7228 |  |  | 43.501 |  |  | 6.0229 |  |  | -86.33 |  |  | -254.3631 |  |  | -497.4413 |  |  | -768.4466 |  |  | -1055.5481 |  |  | -1384.0102
[13 empty] | P2 at this iteration flow rate |  |  | 24.6915 |  |  | 25.0954 |  |  | 27.3398 |  |  | 34.8354 |  |  | 53.306 |  |  | 86.9126 |  |  | 135.5283 |  |  | 189.7293 |  |  | 247.1496 |  |  | 312.842
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0512 |  |  | 29.6274 |  |  | 16.1612 |  |  | -28.8125 |  |  | -139.636 |  |  | -341.2758 |  |  | -632.9696 |  |  | -958.1759 |  |  | -1302.6977 |  |  | -1696.8522
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7454 |  |  | 46.5496 |  |  | 35.8224 |  |  | 4.4415 |  |  | -65.0599 |  |  | -177.6045 |  |  | -319.5274 |  |  | -447.1114 |  |  | -529.3206 |  |  | -521.7483
[13 empty] | C Non choked w/ reducers | 7 |  | 12.6609 |  |  | 46.8562 |  |  | 157.261 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 10.1627 |  |  | 37.3814 |  |  | 105.6283 |  |  | 587.7503 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 12.6609 |  |  | 46.8562 |  |  | 157.261 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 7.9309 | 71.6686 |  | 35.2562 | 254.8427 |  | 134.261 | 630.2564 |  | 5500 | 1227.5786 |  | 5500 | 2059.495 |  | 5500 | 3035.9479 |  | 5500 | 4051.4842 |  | 5500 | 4943.5807 |  | 5500 | 5739.3437 |  | 5500 | 6531.9085
[13 empty] | Next iteration flow rate |  |  | 73.102 | Abs Value of | Flow this | 257.3912 | Abs Value of | Flow this | 636.5589 | Abs Value of | Flow this | 1239.8543 | Abs Value of | Flow this | 2080.0899 | Abs Value of | Flow this | 3066.3073 | Abs Value of | Flow this | 4091.999 | Abs Value of | Flow this | 4993.0165 | Abs Value of | Flow this | 5796.7371 | Abs Value of | Flow this | 6597.2276 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7357 |  |  | 54.6787 |  |  | 43.2313 |  |  | 4.9999 |  |  | -89.2093 |  |  | -260.6198 |  |  | -508.5839 |  |  | -785.0364 |  |  | -1077.9086 |  |  | -1412.9728
[13 empty] | P2 at this iteration flow rate |  |  | 24.6929 |  |  | 25.1043 |  |  | 27.3937 |  |  | 35.04 |  |  | 53.8819 |  |  | 88.164 |  |  | 137.7568 |  |  | 193.0473 |  |  | 251.6217 |  |  | 318.6346
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0428 |  |  | 29.5745 |  |  | 15.8376 |  |  | -30.0401 |  |  | -143.0911 |  |  | -348.7838 |  |  | -646.3407 |  |  | -978.0836 |  |  | -1329.5303 |  |  | -1731.6074
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7392 |  |  | 46.5118 |  |  | 35.5981 |  |  | 3.6277 |  |  | -67.2187 |  |  | -181.9655 |  |  | -326.6784 |  |  | -456.7584 |  |  | -540.5289 |  |  | -532.6632
[13 empty] | C Non choked w/ reducers | 7 |  | 12.9158 |  |  | 47.3671 |  |  | 160.448 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 10.3666 |  |  | 37.7706 |  |  | 107.0202 |  |  | 656.848 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 12.9158 |  |  | 47.3671 |  |  | 160.448 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 8.1858 | 73.102 |  | 35.7671 | 257.3912 |  | 137.448 | 636.5589 |  | 5500 | 1239.8543 |  | 5500 | 2080.0899 |  | 5500 | 3066.3073 |  | 5500 | 4091.999 |  | 5500 | 4993.0165 |  | 5500 | 5796.7371 |  | 5500 | 6597.2276
[13 empty] | Next iteration flow rate |  |  | 74.564 | Abs Value of | Flow this | 259.9651 | Abs Value of | Flow this | 642.9245 | Abs Value of | Flow this | 1252.2529 | Abs Value of | Flow this | 2100.8908 | Abs Value of | Flow this | 3096.9704 | Abs Value of | Flow this | 4132.919 | Abs Value of | Flow this | 5042.9466 | Abs Value of | Flow this | 5854.7045 | Abs Value of | Flow this | 6663.1998 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7284 |  |  | 54.6337 |  |  | 42.9563 |  |  | 3.9564 |  |  | -92.1464 |  |  | -267.0023 |  |  | -519.9504 |  |  | -801.9596 |  |  | -1100.7186 |  |  | -1442.5176
[13 empty] | P2 at this iteration flow rate |  |  | 24.6943 |  |  | 25.1133 |  |  | 27.4487 |  |  | 35.2487 |  |  | 54.4693 |  |  | 89.4405 |  |  | 140.0301 |  |  | 196.4319 |  |  | 256.1837 |  |  | 324.5435
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0341 |  |  | 29.5205 |  |  | 15.5075 |  |  | -31.2923 |  |  | -146.6157 |  |  | -356.4428 |  |  | -659.9805 |  |  | -998.3915 |  |  | -1356.9023 |  |  | -1767.0611
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7328 |  |  | 46.4733 |  |  | 35.3692 |  |  | 2.7975 |  |  | -69.421 |  |  | -186.4143 |  |  | -333.9732 |  |  | -466.5994 |  |  | -551.9625 |  |  | -543.7976
[13 empty] | C Non choked w/ reducers | 7 |  | 13.1759 |  |  | 47.8845 |  |  | 163.768 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 10.5746 |  |  | 38.1641 |  |  | 108.4395 |  |  | 755.4679 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 13.1759 |  |  | 47.8845 |  |  | 163.768 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 8.4459 | 74.564 |  | 36.2845 | 259.9651 |  | 140.768 | 642.9245 |  | 5500 | 1252.2529 |  | 5500 | 2100.8908 |  | 5500 | 3096.9704 |  | 5500 | 4132.919 |  | 5500 | 5042.9466 |  | 5500 | 5854.7045 |  | 5500 | 6663.1998
[13 empty] | Next iteration flow rate |  |  | 76.0553 | Abs Value of | Flow this | 262.5647 | Abs Value of | Flow this | 649.3538 | Abs Value of | Flow this | 1264.7754 | Abs Value of | Flow this | 2121.8997 | Abs Value of | Flow this | 3127.9401 | Abs Value of | Flow this | 4174.2482 | Abs Value of | Flow this | 5093.3761 | Abs Value of | Flow this | 5913.2515 | Abs Value of | Flow this | 6729.8318 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7208 |  |  | 54.5879 |  |  | 42.6757 |  |  | 2.8919 |  |  | -95.1426 |  |  | -273.5131 |  |  | -531.5455 |  |  | -819.223 |  |  | -1123.9871 |  |  | -1472.6562
[13 empty] | P2 at this iteration flow rate |  |  | 24.6958 |  |  | 25.1224 |  |  | 27.5049 |  |  | 35.4616 |  |  | 55.0685 |  |  | 90.7426 |  |  | 142.3491 |  |  | 199.8846 |  |  | 260.8374 |  |  | 330.5712
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0249 |  |  | 29.4654 |  |  | 15.1708 |  |  | -32.5697 |  |  | -150.2111 |  |  | -364.2557 |  |  | -673.8946 |  |  | -1019.1076 |  |  | -1384.8245 |  |  | -1803.2274
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7261 |  |  | 46.4339 |  |  | 35.1358 |  |  | 1.9506 |  |  | -71.6675 |  |  | -190.9525 |  |  | -341.4146 |  |  | -476.6381 |  |  | -563.626 |  |  | -555.1557
[13 empty] | C Non choked w/ reducers | 7 |  | 13.4413 |  |  | 48.4085 |  |  | 167.2312 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 10.7868 |  |  | 38.5621 |  |  | 109.8871 |  |  | 913.7665 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 13.4413 |  |  | 48.4085 |  |  | 167.2312 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 8.7113 | 76.0553 |  | 36.8085 | 262.5647 |  | 144.2312 | 649.3538 |  | 5500 | 1264.7754 |  | 5500 | 2121.8997 |  | 5500 | 3127.9401 |  | 5500 | 4174.2482 |  | 5500 | 5093.3761 |  | 5500 | 5913.2515 |  | 5500 | 6729.8318
[13 empty] | Next iteration flow rate |  |  | 77.5764 | Abs Value of | Flow this | 265.1904 | Abs Value of | Flow this | 655.8473 | Abs Value of | Flow this | 1277.4232 | Abs Value of | Flow this | 2143.1187 | Abs Value of | Flow this | 3159.2195 | Abs Value of | Flow this | 4215.9907 | Abs Value of | Flow this | 5144.3099 | Abs Value of | Flow this | 5972.384 | Abs Value of | Flow this | 6797.1302 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7129 |  |  | 54.5411 |  |  | 42.3894 |  |  | 1.806 |  |  | -98.1989 |  |  | -280.1547 |  |  | -543.3735 |  |  | -836.8334 |  |  | -1147.7232 |  |  | -1503.4006
[13 empty] | P2 at this iteration flow rate |  |  | 24.6974 |  |  | 25.1318 |  |  | 27.5621 |  |  | 35.6788 |  |  | 55.6798 |  |  | 92.0709 |  |  | 144.7147 |  |  | 203.4067 |  |  | 265.5846 |  |  | 336.7201
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0155 |  |  | 29.4093 |  |  | 14.8273 |  |  | -33.8727 |  |  | -153.8787 |  |  | -372.2257 |  |  | -688.0883 |  |  | -1040.2401 |  |  | -1413.3078 |  |  | -1840.1207
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7191 |  |  | 46.3938 |  |  | 34.8977 |  |  | 1.0867 |  |  | -73.9592 |  |  | -195.5819 |  |  | -349.0055 |  |  | -486.8786 |  |  | -575.5239 |  |  | -566.7421
[13 empty] | C Non choked w/ reducers | 7 |  | 13.7122 |  |  | 48.9392 |  |  | 170.8487 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 11.0034 |  |  | 38.9645 |  |  | 111.364 |  |  | 1236.4662 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 13.7122 |  |  | 48.9392 |  |  | 170.8487 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 8.9822 | 77.5764 |  | 37.3392 | 265.1904 |  | 147.8487 | 655.8473 |  | 5500 | 1277.4232 |  | 5500 | 2143.1187 |  | 5500 | 3159.2195 |  | 5500 | 4215.9907 |  | 5500 | 5144.3099 |  | 5500 | 5972.384 |  | 5500 | 6797.1302
[13 empty] | Next iteration flow rate |  |  | 79.1279 | Abs Value of | Flow this | 267.8423 | Abs Value of | Flow this | 662.4058 | Abs Value of | Flow this | 1290.1974 | Abs Value of | Flow this | 2164.5499 | Abs Value of | Flow this | 3190.8117 | Abs Value of | Flow this | 4258.1506 | Abs Value of | Flow this | 5195.753 | Abs Value of | Flow this | 6032.1079 | Abs Value of | Flow this | 6865.1015 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7047 |  |  | 54.4933 |  |  | 42.0975 |  |  | 0.69833 |  |  | -101.3168 |  |  | -286.9298 |  |  | -555.4394 |  |  | -854.7978 |  |  | -1171.9365 |  |  | -1534.7629
[13 empty] | P2 at this iteration flow rate |  |  | 24.6991 |  |  | 25.1413 |  |  | 27.6205 |  |  | 35.9003 |  |  | 56.3034 |  |  | 93.426 |  |  | 147.1279 |  |  | 206.9996 |  |  | 270.4273 |  |  | 342.9926
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0056 |  |  | 29.352 |  |  | 14.4769 |  |  | -35.202 |  |  | -157.6201 |  |  | -380.3558 |  |  | -702.5672 |  |  | -1061.7973 |  |  | -1442.3638 |  |  | -1877.7555
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7118 |  |  | 46.3529 |  |  | 34.6548 |  |  | 0.20548 |  |  | -76.2969 |  |  | -200.3043 |  |  | -356.749 |  |  | -497.325 |  |  | -587.6609 |  |  | -578.5614
[13 empty] | C Non choked w/ reducers | 7 |  | 13.9886 |  |  | 49.4768 |  |  | 174.6329 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 11.2242 |  |  | 39.3716 |  |  | 112.8711 |  |  | 2872.0055 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 13.9886 |  |  | 49.4768 |  |  | 174.6329 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 9.2586 | 79.1279 |  | 37.8768 | 267.8423 |  | 151.6329 | 662.4058 |  | 5500 | 1290.1974 |  | 5500 | 2164.5499 |  | 5500 | 3190.8117 |  | 5500 | 4258.1506 |  | 5500 | 5195.753 |  | 5500 | 6032.1079 |  | 5500 | 6865.1015
[13 empty] | Next iteration flow rate |  |  | 80.7105 | Abs Value of | Flow this | 270.5207 | Abs Value of | Flow this | 669.0298 | Abs Value of | Flow this | 1303.0994 | Abs Value of | Flow this | 2186.1954 | Abs Value of | Flow this | 3222.7198 | Abs Value of | Flow this | 4300.7321 | Abs Value of | Flow this | 5247.7105 | Abs Value of | Flow this | 6092.429 | Abs Value of | Flow this | 6933.7525 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6961 |  |  | 54.4446 |  |  | 41.7996 |  |  | -0.43164 |  |  | -104.4972 |  |  | -293.8411 |  |  | -567.7477 |  |  | -873.1232 |  |  | -1196.6364 |  |  | -1566.7557
[13 empty] | P2 at this iteration flow rate |  |  | 24.7008 |  |  | 25.1511 |  |  | 27.6801 |  |  | 36.1263 |  |  | 56.9394 |  |  | 94.8082 |  |  | 149.5895 |  |  | 210.6646 |  |  | 275.3673 |  |  | 349.3911
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9954 |  |  | 29.2936 |  |  | 14.1195 |  |  | -36.558 |  |  | -161.4367 |  |  | -388.6494 |  |  | -717.3373 |  |  | -1083.7879 |  |  | -1472.0037 |  |  | -1916.1468
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.7043 |  |  | 46.3111 |  |  | 34.407 |  |  | -0.6935 |  |  | -78.6816 |  |  | -205.1217 |  |  | -364.6482 |  |  | -507.9814 |  |  | -600.0419 |  |  | -590.6183
[13 empty] | C Non choked w/ reducers | 7 |  | 14.2706 |  |  | 50.0214 |  |  | 178.5977 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 11.4496 |  |  | 39.7832 |  |  | 114.4096 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 14.2706 |  |  | 50.0214 |  |  | 178.5977 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 9.5406 | 80.7105 |  | 38.4214 | 270.5207 |  | 155.5977 | 669.0298 |  | 5500 | 1303.0994 |  | 5500 | 2186.1954 |  | 5500 | 3222.7198 |  | 5500 | 4300.7321 |  | 5500 | 5247.7105 |  | 5500 | 6092.429 |  | 5500 | 6933.7525
[13 empty] | Next iteration flow rate |  |  | 82.3247 | Abs Value of | Flow this | 273.2259 | Abs Value of | Flow this | 675.7201 | Abs Value of | Flow this | 1316.1304 | Abs Value of | Flow this | 2208.0573 | Abs Value of | Flow this | 3254.947 | Abs Value of | Flow this | 4343.7394 | Abs Value of | Flow this | 5300.1876 | Abs Value of | Flow this | 6153.3533 | Abs Value of | Flow this | 7003.09 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6873 |  |  | 54.395 |  |  | 41.4958 |  |  | -1.5843 |  |  | -107.7416 |  |  | -300.8914 |  |  | -580.3035 |  |  | -891.817 |  |  | -1221.8328 |  |  | -1599.3915
[13 empty] | P2 at this iteration flow rate |  |  | 24.7025 |  |  | 25.161 |  |  | 27.7408 |  |  | 36.3569 |  |  | 57.5883 |  |  | 96.2183 |  |  | 152.1007 |  |  | 214.4034 |  |  | 280.4066 |  |  | 355.9183
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9847 |  |  | 29.2339 |  |  | 13.7549 |  |  | -37.9412 |  |  | -165.33 |  |  | -397.1096 |  |  | -732.4041 |  |  | -1106.2204 |  |  | -1502.2394 |  |  | -1955.3098
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.6964 |  |  | 46.2685 |  |  | 34.1542 |  |  | -1.6105 |  |  | -81.1142 |  |  | -210.0358 |  |  | -372.7062 |  |  | -518.8519 |  |  | -612.6718 |  |  | -602.9176
[13 empty] | C Non choked w/ reducers | 7 |  | 14.5585 |  |  | 50.5731 |  |  | 182.7588 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 11.6795 |  |  | 40.1995 |  |  | 115.9805 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 14.5585 |  |  | 50.5731 |  |  | 182.7588 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 9.8285 | 82.3247 |  | 38.9731 | 273.2259 |  | 159.7588 | 675.7201 |  | 5500 | 1316.1304 |  | 5500 | 2208.0573 |  | 5500 | 3254.947 |  | 5500 | 4343.7394 |  | 5500 | 5300.1876 |  | 5500 | 6153.3533 |  | 5500 | 7003.09
[13 empty] | Next iteration flow rate |  |  | 83.9712 | Abs Value of | Flow this | 275.9582 | Abs Value of | Flow this | 682.4773 | Abs Value of | Flow this | 1329.2917 | Abs Value of | Flow this | 2230.1379 | Abs Value of | Flow this | 3287.4965 | Abs Value of | Flow this | 4387.1768 | Abs Value of | Flow this | 5353.1895 | Abs Value of | Flow this | 6214.8868 | Abs Value of | Flow this | 7073.1209 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.678 |  |  | 54.3443 |  |  | 41.1858 |  |  | -2.7602 |  |  | -111.0513 |  |  | -308.0833 |  |  | -593.1116 |  |  | -910.8865 |  |  | -1247.5357 |  |  | -1632.6833
[13 empty] | P2 at this iteration flow rate |  |  | 24.7044 |  |  | 25.1711 |  |  | 27.8028 |  |  | 36.592 |  |  | 58.2503 |  |  | 97.6567 |  |  | 154.6623 |  |  | 218.2173 |  |  | 285.5471 |  |  | 362.5767
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9736 |  |  | 29.1731 |  |  | 13.383 |  |  | -39.3522 |  |  | -169.3015 |  |  | -405.7399 |  |  | -747.7739 |  |  | -1129.1039 |  |  | -1533.0828 |  |  | -1995.2599
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.6883 |  |  | 46.2251 |  |  | 33.8964 |  |  | -2.546 |  |  | -83.5958 |  |  | -215.0488 |  |  | -380.9261 |  |  | -529.9409 |  |  | -625.5555 |  |  | -615.464
[13 empty] | C Non choked w/ reducers | 7 |  | 14.8522 |  |  | 51.1321 |  |  | 187.1339 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 11.9141 |  |  | 40.6206 |  |  | 117.585 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 14.8522 |  |  | 51.1321 |  |  | 187.1339 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 10.1222 | 83.9712 |  | 39.5321 | 275.9582 |  | 164.1339 | 682.4773 |  | 5500 | 1329.2917 |  | 5500 | 2230.1379 |  | 5500 | 3287.4965 |  | 5500 | 4387.1768 |  | 5500 | 5353.1895 |  | 5500 | 6214.8868 |  | 5500 | 7073.1209
[13 empty] | Next iteration flow rate |  |  | 85.6506 | Abs Value of | Flow this | 278.7177 | Abs Value of | Flow this | 689.3021 | Abs Value of | Flow this | 1342.5846 | Abs Value of | Flow this | 2252.4393 | Abs Value of | Flow this | 3320.3715 | Abs Value of | Flow this | 4431.0486 | Abs Value of | Flow this | 5406.7214 | Abs Value of | Flow this | 6277.0357 | Abs Value of | Flow this | 7143.8521 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6684 |  |  | 54.2926 |  |  | 40.8696 |  |  | -3.9597 |  |  | -114.4274 |  |  | -315.4198 |  |  | -606.1771 |  |  | -930.3394 |  |  | -1273.7551 |  |  | -1666.6442
[13 empty] | P2 at this iteration flow rate |  |  | 24.7063 |  |  | 25.1815 |  |  | 27.8661 |  |  | 36.8319 |  |  | 58.9255 |  |  | 99.124 |  |  | 157.2754 |  |  | 222.1079 |  |  | 290.791 |  |  | 369.3688
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9621 |  |  | 29.1111 |  |  | 13.0035 |  |  | -40.7916 |  |  | -173.3529 |  |  | -414.5437 |  |  | -763.4525 |  |  | -1152.4473 |  |  | -1564.5462 |  |  | -2036.0131
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.6798 |  |  | 46.1807 |  |  | 33.6334 |  |  | -3.5003 |  |  | -86.1272 |  |  | -220.1625 |  |  | -389.3112 |  |  | -541.2528 |  |  | -638.6982 |  |  | -628.2626
[13 empty] | C Non choked w/ reducers | 7 |  | 15.152 |  |  | 51.6984 |  |  | 191.7428 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 12.1534 |  |  | 41.0465 |  |  | 119.2243 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 15.152 |  |  | 51.6984 |  |  | 191.7428 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 10.422 | 85.6506 |  | 40.0984 | 278.7177 |  | 168.7428 | 689.3021 |  | 5500 | 1342.5846 |  | 5500 | 2252.4393 |  | 5500 | 3320.3715 |  | 5500 | 4431.0486 |  | 5500 | 5406.7214 |  | 5500 | 6277.0357 |  | 5500 | 7143.8521
[13 empty] | Next iteration flow rate |  |  | 87.3636 | Abs Value of | Flow this | 281.5049 | Abs Value of | Flow this | 696.1951 | Abs Value of | Flow this | 1356.0104 | Abs Value of | Flow this | 2274.9637 | Abs Value of | Flow this | 3353.5752 | Abs Value of | Flow this | 4475.3591 | Abs Value of | Flow this | 5460.7886 | Abs Value of | Flow this | 6339.806 | Abs Value of | Flow this | 7215.2906 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6584 |  |  | 54.2399 |  |  | 40.5471 |  |  | -5.1833 |  |  | -117.8714 |  |  | -322.9037 |  |  | -619.5053 |  |  | -950.1832 |  |  | -1300.5016 |  |  | -1701.2878
[13 empty] | P2 at this iteration flow rate |  |  | 24.7083 |  |  | 25.192 |  |  | 27.9306 |  |  | 37.0767 |  |  | 59.6143 |  |  | 100.6207 |  |  | 159.9411 |  |  | 226.0766 |  |  | 296.1403 |  |  | 376.2976
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9501 |  |  | 29.0478 |  |  | 12.6165 |  |  | -42.26 |  |  | -177.4857 |  |  | -423.5245 |  |  | -779.4464 |  |  | -1176.2599 |  |  | -1596.642 |  |  | -2077.5854
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.6709 |  |  | 46.1355 |  |  | 33.3651 |  |  | -4.4738 |  |  | -88.7095 |  |  | -225.379 |  |  | -397.8649 |  |  | -552.7921 |  |  | -652.105 |  |  | -641.3185
[13 empty] | C Non choked w/ reducers | 7 |  | 15.4579 |  |  | 52.2722 |  |  | 196.6082 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 12.3976 |  |  | 41.4773 |  |  | 120.8997 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 15.4579 |  |  | 52.2722 |  |  | 196.6082 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 10.7279 | 87.3636 |  | 40.6722 | 281.5049 |  | 173.6082 | 696.1951 |  | 5500 | 1356.0104 |  | 5500 | 2274.9637 |  | 5500 | 3353.5752 |  | 5500 | 4475.3591 |  | 5500 | 5460.7886 |  | 5500 | 6339.806 |  | 5500 | 7215.2906
[13 empty] | Next iteration flow rate |  |  | 89.1109 | Abs Value of | Flow this | 284.32 | Abs Value of | Flow this | 703.1571 | Abs Value of | Flow this | 1369.5705 | Abs Value of | Flow this | 2297.7133 | Abs Value of | Flow this | 3387.1109 | Abs Value of | Flow this | 4520.1127 | Abs Value of | Flow this | 5515.3965 | Abs Value of | Flow this | 6403.2041 | Abs Value of | Flow this | 7287.4435 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.648 |  |  | 54.1861 |  |  | 40.2181 |  |  | -6.4315 |  |  | -121.3847 |  |  | -330.5381 |  |  | -633.1014 |  |  | -970.4259 |  |  | -1327.7857 |  |  | -1736.6277
[13 empty] | P2 at this iteration flow rate |  |  | 24.7104 |  |  | 25.2028 |  |  | 27.9964 |  |  | 37.3263 |  |  | 60.3169 |  |  | 102.1476 |  |  | 162.6603 |  |  | 230.1252 |  |  | 301.5971 |  |  | 383.3655
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9376 |  |  | 28.9833 |  |  | 12.2217 |  |  | -43.7578 |  |  | -181.7016 |  |  | -432.6857 |  |  | -795.7616 |  |  | -1200.5511 |  |  | -1629.3829 |  |  | -2119.9932
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.6617 |  |  | 46.0894 |  |  | 33.0913 |  |  | -5.4668 |  |  | -91.3437 |  |  | -230.7004 |  |  | -406.5905 |  |  | -564.5633 |  |  | -665.7813 |  |  | -654.6368
[13 empty] | C Non choked w/ reducers | 7 |  | 15.7702 |  |  | 52.8537 |  |  | 201.7563 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 12.6467 |  |  | 41.913 |  |  | 122.6127 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 15.7702 |  |  | 52.8537 |  |  | 201.7563 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 11.0402 | 89.1109 |  | 41.2537 | 284.32 |  | 178.7563 | 703.1571 |  | 5500 | 1369.5705 |  | 5500 | 2297.7133 |  | 5500 | 3387.1109 |  | 5500 | 4520.1127 |  | 5500 | 5515.3965 |  | 5500 | 6403.2041 |  | 5500 | 7287.4435
[13 empty] | Next iteration flow rate |  |  | 90.8931 | Abs Value of | Flow this | 287.1632 | Abs Value of | Flow this | 710.1887 | Abs Value of | Flow this | 1383.2662 | Abs Value of | Flow this | 2320.6905 | Abs Value of | Flow this | 3420.982 | Abs Value of | Flow this | 4565.3138 | Abs Value of | Flow this | 5570.5504 | Abs Value of | Flow this | 6467.2361 | Abs Value of | Flow this | 7360.318 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6371 |  |  | 54.1312 |  |  | 39.8824 |  |  | -7.7048 |  |  | -124.9685 |  |  | -338.3259 |  |  | -646.9707 |  |  | -991.0755 |  |  | -1355.6182 |  |  | -1772.6779
[13 empty] | P2 at this iteration flow rate |  |  | 24.7126 |  |  | 25.2138 |  |  | 28.0635 |  |  | 37.581 |  |  | 61.0337 |  |  | 103.7052 |  |  | 165.4341 |  |  | 234.2551 |  |  | 307.1636 |  |  | 390.5756
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9246 |  |  | 28.9174 |  |  | 11.8189 |  |  | -45.2857 |  |  | -186.0022 |  |  | -442.0311 |  |  | -812.4049 |  |  | -1225.3306 |  |  | -1662.7819 |  |  | -2163.2535
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.6521 |  |  | 46.0423 |  |  | 32.8121 |  |  | -6.4798 |  |  | -94.0309 |  |  | -236.1287 |  |  | -415.4915 |  |  | -576.5712 |  |  | -679.7326 |  |  | -668.2228
[13 empty] | C Non choked w/ reducers | 7 |  | 16.0889 |  |  | 53.443 |  |  | 207.2168 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 12.9009 |  |  | 42.3538 |  |  | 124.3646 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 16.0889 |  |  | 53.443 |  |  | 207.2168 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 11.3589 | 90.8931 |  | 41.843 | 287.1632 |  | 184.2168 | 710.1887 |  | 5500 | 1383.2662 |  | 5500 | 2320.6905 |  | 5500 | 3420.982 |  | 5500 | 4565.3138 |  | 5500 | 5570.5504 |  | 5500 | 6467.2361 |  | 5500 | 7360.318
[13 empty] | Next iteration flow rate |  |  | 92.711 | Abs Value of | Flow this | 290.0348 | Abs Value of | Flow this | 717.2906 | Abs Value of | Flow this | 1397.0989 | Abs Value of | Flow this | 2343.8974 | Abs Value of | Flow this | 3455.1919 | Abs Value of | Flow this | 4610.9669 | Abs Value of | Flow this | 5626.2559 | Abs Value of | Flow this | 6531.9085 | Abs Value of | Flow this | 7433.9211 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6259 |  |  | 54.0752 |  |  | 39.5401 |  |  | -9.0037 |  |  | -128.6244 |  |  | -346.2703 |  |  | -661.1188 |  |  | -1012.1401 |  |  | -1384.0102 |  |  | -1809.4528
[13 empty] | P2 at this iteration flow rate |  |  | 24.7148 |  |  | 25.225 |  |  | 28.132 |  |  | 37.8407 |  |  | 61.7649 |  |  | 105.2941 |  |  | 168.2638 |  |  | 238.468 |  |  | 312.842 |  |  | 397.9306
[13 empty] | Delta P at this iteration flow rate |  |  | 31.911 |  |  | 28.8502 |  |  | 11.4081 |  |  | -46.8444 |  |  | -190.3893 |  |  | -451.5644 |  |  | -829.3826 |  |  | -1250.6081 |  |  | -1696.8522 |  |  | -2207.3833
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.6422 |  |  | 45.9943 |  |  | 32.5273 |  |  | -7.5131 |  |  | -96.772 |  |  | -241.6661 |  |  | -424.5714 |  |  | -588.8204 |  |  | -693.9642 |  |  | -682.0819
[13 empty] | C Non choked w/ reducers | 7 |  | 16.4141 |  |  | 54.0402 |  |  | 213.0243 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 13.1602 |  |  | 42.7996 |  |  | 126.157 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 16.4141 |  |  | 54.0402 |  |  | 213.0243 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 11.6841 | 92.711 |  | 42.4402 | 290.0348 |  | 190.0243 | 717.2906 |  | 5500 | 1397.0989 |  | 5500 | 2343.8974 |  | 5500 | 3455.1919 |  | 5500 | 4610.9669 |  | 5500 | 5626.2559 |  | 5500 | 6531.9085 |  | 5500 | 7433.9211
[13 empty] | Next iteration flow rate |  |  | 94.5652 | Abs Value of | Flow this | 292.9351 | Abs Value of | Flow this | 724.4635 | Abs Value of | Flow this | 1411.0699 | Abs Value of | Flow this | 2367.3363 | Abs Value of | Flow this | 3489.7438 | Abs Value of | Flow this | 4657.0766 | Abs Value of | Flow this | 5682.5185 | Abs Value of | Flow this | 6597.2276 | Abs Value of | Flow this | 7508.2604 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6141 |  |  | 54.0181 |  |  | 39.1908 |  |  | -10.3286 |  |  | -132.3537 |  |  | -354.3744 |  |  | -675.5514 |  |  | -1033.6281 |  |  | -1412.9728 |  |  | -1846.9668
[13 empty] | P2 at this iteration flow rate |  |  | 24.7172 |  |  | 25.2364 |  |  | 28.2018 |  |  | 38.1057 |  |  | 62.5107 |  |  | 106.9149 |  |  | 171.1503 |  |  | 242.7656 |  |  | 318.6346 |  |  | 405.4334
[13 empty] | Delta P at this iteration flow rate |  |  | 31.897 |  |  | 28.7817 |  |  | 10.989 |  |  | -48.4344 |  |  | -194.8645 |  |  | -461.2892 |  |  | -846.7016 |  |  | -1276.3938 |  |  | -1731.6074 |  |  | -2252.4001
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.6318 |  |  | 45.9453 |  |  | 32.2368 |  |  | -8.5672 |  |  | -99.5683 |  |  | -247.3149 |  |  | -433.8338 |  |  | -601.3158 |  |  | -708.4819 |  |  | -696.2196
[13 empty] | C Non choked w/ reducers | 7 |  | 16.7461 |  |  | 54.6455 |  |  | 219.2191 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 13.4248 |  |  | 43.2506 |  |  | 127.9915 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 16.7461 |  |  | 54.6455 |  |  | 219.2191 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 12.0161 | 94.5652 |  | 43.0455 | 292.9351 |  | 196.2191 | 724.4635 |  | 5500 | 1411.0699 |  | 5500 | 2367.3363 |  | 5500 | 3489.7438 |  | 5500 | 4657.0766 |  | 5500 | 5682.5185 |  | 5500 | 6597.2276 |  | 5500 | 7508.2604
[13 empty] | Next iteration flow rate |  |  | 96.4565 | Abs Value of | Flow this | 295.8645 | Abs Value of | Flow this | 731.7081 | Abs Value of | Flow this | 1425.1806 | Abs Value of | Flow this | 2391.0097 | Abs Value of | Flow this | 3524.6412 | Abs Value of | Flow this | 4703.6474 | Abs Value of | Flow this | 5739.3437 | Abs Value of | Flow this | 6663.1998 | Abs Value of | Flow this | 7583.343 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6019 |  |  | 53.9599 |  |  | 38.8345 |  |  | -11.6803 |  |  | -136.1581 |  |  | -362.6413 |  |  | -690.2739 |  |  | -1055.5481 |  |  | -1442.5176 |  |  | -1885.2348
[13 empty] | P2 at this iteration flow rate |  |  | 24.7196 |  |  | 25.248 |  |  | 28.2731 |  |  | 38.3761 |  |  | 63.2716 |  |  | 108.5683 |  |  | 174.0948 |  |  | 247.1496 |  |  | 324.5435 |  |  | 413.087
[13 empty] | Delta P at this iteration flow rate |  |  | 31.8823 |  |  | 28.7118 |  |  | 10.5614 |  |  | -50.0563 |  |  | -199.4297 |  |  | -471.2096 |  |  | -864.3687 |  |  | -1302.6977 |  |  | -1767.0611 |  |  | -2298.3218
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.621 |  |  | 45.8954 |  |  | 31.9404 |  |  | -9.6426 |  |  | -102.4208 |  |  | -253.0772 |  |  | -443.2824 |  |  | -614.0623 |  |  | -723.2914 |  |  | -710.6414
[13 empty] | C Non choked w/ reducers | 7 |  | 17.0849 |  |  | 55.2591 |  |  | 225.8483 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 13.6948 |  |  | 43.7069 |  |  | 129.8698 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 17.0849 |  |  | 55.2591 |  |  | 225.8483 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 12.3549 | 96.4565 |  | 43.6591 | 295.8645 |  | 202.8483 | 731.7081 |  | 5500 | 1425.1806 |  | 5500 | 2391.0097 |  | 5500 | 3524.6412 |  | 5500 | 4703.6474 |  | 5500 | 5739.3437 |  | 5500 | 6663.1998 |  | 5500 | 7583.343
[13 empty] | Next iteration flow rate |  |  | 98.3856 | Abs Value of | Flow this | 298.8231 | Abs Value of | Flow this | 739.0252 | Abs Value of | Flow this | 1439.4324 | Abs Value of | Flow this | 2414.9198 | Abs Value of | Flow this | 3559.8876 | Abs Value of | Flow this | 4750.6838 | Abs Value of | Flow this | 5796.7371 | Abs Value of | Flow this | 6729.8318 | Abs Value of | Flow this | 7659.1764 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.5892 |  |  | 53.9004 |  |  | 38.4711 |  |  | -13.0591 |  |  | -140.0389 |  |  | -371.0744 |  |  | -705.2925 |  |  | -1077.9086 |  |  | -1472.6562 |  |  | -1924.2721
[13 empty] | P2 at this iteration flow rate |  |  | 24.7222 |  |  | 25.2599 |  |  | 28.3458 |  |  | 38.6518 |  |  | 64.0478 |  |  | 110.2549 |  |  | 177.0985 |  |  | 251.6217 |  |  | 330.5712 |  |  | 420.8944
[13 empty] | Delta P at this iteration flow rate |  |  | 31.8671 |  |  | 28.6405 |  |  | 10.1253 |  |  | -51.7109 |  |  | -204.0866 |  |  | -481.3293 |  |  | -882.391 |  |  | -1329.5303 |  |  | -1803.2274 |  |  | -2345.1665
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.6098 |  |  | 45.8444 |  |  | 31.638 |  |  | -10.7395 |  |  | -105.3306 |  |  | -258.9552 |  |  | -452.9209 |  |  | -627.0651 |  |  | -738.3985 |  |  | -725.3531
[13 empty] | C Non choked w/ reducers | 7 |  | 17.4308 |  |  | 55.8812 |  |  | 232.9676 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 13.9703 |  |  | 44.1685 |  |  | 131.7938 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 17.4308 |  |  | 55.8812 |  |  | 232.9676 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 12.7008 | 98.3856 |  | 44.2812 | 298.8231 |  | 209.9676 | 739.0252 |  | 5500 | 1439.4324 |  | 5500 | 2414.9198 |  | 5500 | 3559.8876 |  | 5500 | 4750.6838 |  | 5500 | 5796.7371 |  | 5500 | 6729.8318 |  | 5500 | 7659.1764
[13 empty] | Next iteration flow rate |  |  | 100.3534 | Abs Value of | Flow this | 301.8114 | Abs Value of | Flow this | 746.4154 | Abs Value of | Flow this | 1453.8267 | Abs Value of | Flow this | 2439.069 | Abs Value of | Flow this | 3595.4865 | Abs Value of | Flow this | 4798.1907 | Abs Value of | Flow this | 5854.7045 | Abs Value of | Flow this | 6797.1302 | Abs Value of | Flow this | 7735.7682 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.576 |  |  | 53.8398 |  |  | 38.1003 |  |  | -14.4656 |  |  | -143.9977 |  |  | -379.677 |  |  | -720.6129 |  |  | -1100.7186 |  |  | -1503.4006 |  |  | -1964.094
[13 empty] | P2 at this iteration flow rate |  |  | 24.7248 |  |  | 25.272 |  |  | 28.4199 |  |  | 38.9331 |  |  | 64.8395 |  |  | 111.9754 |  |  | 180.1626 |  |  | 256.1837 |  |  | 336.7201 |  |  | 428.8588
[13 empty] | Delta P at this iteration flow rate |  |  | 31.8512 |  |  | 28.5678 |  |  | 9.6804 |  |  | -53.3987 |  |  | -208.8372 |  |  | -491.6524 |  |  | -900.7754 |  |  | -1356.9023 |  |  | -1840.1207 |  |  | -2392.9527
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.5982 |  |  | 45.7925 |  |  | 31.3296 |  |  | -11.8584 |  |  | -108.2989 |  |  | -264.9515 |  |  | -462.7531 |  |  | -640.3292 |  |  | -753.8094 |  |  | -740.3605
[13 empty] | C Non choked w/ reducers | 7 |  | 17.7838 |  |  | 56.5118 |  |  | 240.6435 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 14.2513 |  |  | 44.6355 |  |  | 133.7653 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 17.7838 |  |  | 56.5118 |  |  | 240.6435 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 13.0538 | 100.3534 |  | 44.9118 | 301.8114 |  | 217.6435 | 746.4154 |  | 5500 | 1453.8267 |  | 5500 | 2439.069 |  | 5500 | 3595.4865 |  | 5500 | 4798.1907 |  | 5500 | 5854.7045 |  | 5500 | 6797.1302 |  | 5500 | 7735.7682
[13 empty] | Next iteration flow rate |  |  | 102.3604 | Abs Value of | Flow this | 304.8295 | Abs Value of | Flow this | 753.8796 | Abs Value of | Flow this | 1468.365 | Abs Value of | Flow this | 2463.4597 | Abs Value of | Flow this | 3631.4414 | Abs Value of | Flow this | 4846.1726 | Abs Value of | Flow this | 5913.2515 | Abs Value of | Flow this | 6865.1015 | Abs Value of | Flow this | 7813.1258 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.5623 |  |  | 53.778 |  |  | 37.7221 |  |  | -15.9003 |  |  | -148.036 |  |  | -388.4525 |  |  | -736.2412 |  |  | -1123.9871 |  |  | -1534.7629 |  |  | -2004.7163
[13 empty] | P2 at this iteration flow rate |  |  | 24.7275 |  |  | 25.2844 |  |  | 28.4956 |  |  | 39.2201 |  |  | 65.6472 |  |  | 113.7305 |  |  | 183.2882 |  |  | 260.8374 |  |  | 342.9926 |  |  | 436.9833
[13 empty] | Delta P at this iteration flow rate |  |  | 31.8347 |  |  | 28.4936 |  |  | 9.2266 |  |  | -55.1204 |  |  | -213.6832 |  |  | -502.183 |  |  | -919.5294 |  |  | -1384.8245 |  |  | -1877.7555 |  |  | -2441.6995
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.586 |  |  | 45.7394 |  |  | 31.015 |  |  | -12.9999 |  |  | -111.3268 |  |  | -271.0683 |  |  | -472.783 |  |  | -653.8599 |  |  | -769.5299 |  |  | -755.6695
[13 empty] | C Non choked w/ reducers | 7 |  | 18.1442 |  |  | 57.1512 |  |  | 248.9558 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 14.5382 |  |  | 45.108 |  |  | 135.7865 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 18.1442 |  |  | 57.1512 |  |  | 248.9558 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 13.4142 | 102.3604 |  | 45.5512 | 304.8295 |  | 225.9558 | 753.8796 |  | 5500 | 1468.365 |  | 5500 | 2463.4597 |  | 5500 | 3631.4414 |  | 5500 | 4846.1726 |  | 5500 | 5913.2515 |  | 5500 | 6865.1015 |  | 5500 | 7813.1258
[13 empty] | Next iteration flow rate |  |  | 104.4076 | Abs Value of | Flow this | 307.8778 | Abs Value of | Flow this | 761.4184 | Abs Value of | Flow this | 1483.0486 | Abs Value of | Flow this | 2488.0943 | Abs Value of | Flow this | 3667.7558 | Abs Value of | Flow this | 4894.6343 | Abs Value of | Flow this | 5972.384 | Abs Value of | Flow this | 6933.7525 | Abs Value of | Flow this | 7891.2571 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.548 |  |  | 53.7149 |  |  | 37.3363 |  |  | -17.3639 |  |  | -152.1556 |  |  | -397.4044 |  |  | -752.1837 |  |  | -1147.7232 |  |  | -1566.7557 |  |  | -2046.1551
[13 empty] | P2 at this iteration flow rate |  |  | 24.7304 |  |  | 25.297 |  |  | 28.5727 |  |  | 39.5128 |  |  | 66.4711 |  |  | 115.5209 |  |  | 186.4767 |  |  | 265.5846 |  |  | 349.3911 |  |  | 445.271
[13 empty] | Delta P at this iteration flow rate |  |  | 31.8176 |  |  | 28.4179 |  |  | 8.7636 |  |  | -56.8767 |  |  | -218.6267 |  |  | -512.9253 |  |  | -938.6604 |  |  | -1413.3078 |  |  | -1916.1468 |  |  | -2491.4261
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.5734 |  |  | 45.6853 |  |  | 30.694 |  |  | -14.1643 |  |  | -114.4156 |  |  | -277.308 |  |  | -483.0145 |  |  | -667.6626 |  |  | -785.5665 |  |  | -771.2863
[13 empty] | C Non choked w/ reducers | 7 |  | 18.5121 |  |  | 57.7995 |  |  | 258.0015 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 14.8308 |  |  | 45.586 |  |  | 137.8595 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 18.5121 |  |  | 57.7995 |  |  | 258.0015 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 13.7821 | 104.4076 |  | 46.1995 | 307.8778 |  | 235.0015 | 761.4184 |  | 5500 | 1483.0486 |  | 5500 | 2488.0943 |  | 5500 | 3667.7558 |  | 5500 | 4894.6343 |  | 5500 | 5972.384 |  | 5500 | 6933.7525 |  | 5500 | 7891.2571
[13 empty] | Next iteration flow rate |  |  | 106.4958 | Abs Value of | Flow this | 310.9566 | Abs Value of | Flow this | 769.0326 | Abs Value of | Flow this | 1497.8791 | Abs Value of | Flow this | 2512.9752 | Abs Value of | Flow this | 3704.4333 | Abs Value of | Flow this | 4943.5807 | Abs Value of | Flow this | 6032.1079 | Abs Value of | Flow this | 7003.09 | Abs Value of | Flow this | 7970.1697 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.5331 |  |  | 53.6506 |  |  | 36.9428 |  |  | -18.857 |  |  | -156.3579 |  |  | -406.5363 |  |  | -768.4466 |  |  | -1171.9365 |  |  | -1599.3915 |  |  | -2088.4268
[13 empty] | P2 at this iteration flow rate |  |  | 24.7334 |  |  | 25.3099 |  |  | 28.6514 |  |  | 39.8114 |  |  | 67.3116 |  |  | 117.3473 |  |  | 189.7293 |  |  | 270.4273 |  |  | 355.9183 |  |  | 453.7254
[13 empty] | Delta P at this iteration flow rate |  |  | 31.7997 |  |  | 28.3407 |  |  | 8.2913 |  |  | -58.6684 |  |  | -223.6695 |  |  | -523.8835 |  |  | -958.1759 |  |  | -1442.3638 |  |  | -1955.3098 |  |  | -2542.1522
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.5602 |  |  | 45.6302 |  |  | 30.3666 |  |  | -15.3521 |  |  | -117.5665 |  |  | -283.6731 |  |  | -493.4516 |  |  | -681.7427 |  |  | -801.9254 |  |  | -787.217
[13 empty] | C Non choked w/ reducers | 7 |  | 18.8876 |  |  | 58.457 |  |  | 267.8999 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 15.1294 |  |  | 46.0697 |  |  | 139.9867 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 18.8876 |  |  | 58.457 |  |  | 267.8999 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 14.1576 | 106.4958 |  | 46.857 | 310.9566 |  | 244.8999 | 769.0326 |  | 5500 | 1497.8791 |  | 5500 | 2512.9752 |  | 5500 | 3704.4333 |  | 5500 | 4943.5807 |  | 5500 | 6032.1079 |  | 5500 | 7003.09 |  | 5500 | 7970.1697
[13 empty] | Next iteration flow rate |  |  | 108.6257 | Abs Value of | Flow this | 314.0661 | Abs Value of | Flow this | 776.7229 | Abs Value of | Flow this | 1512.8579 | Abs Value of | Flow this | 2538.105 | Abs Value of | Flow this | 3741.4777 | Abs Value of | Flow this | 4993.0165 | Abs Value of | Flow this | 6092.429 | Abs Value of | Flow this | 7073.1209 | Abs Value of | Flow this | 8049.8714 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.5176 |  |  | 53.5849 |  |  | 36.5413 |  |  | -20.38 |  |  | -160.6447 |  |  | -415.8517 |  |  | -785.0364 |  |  | -1196.6364 |  |  | -1632.6833 |  |  | -2131.5482
[13 empty] | P2 at this iteration flow rate |  |  | 24.7365 |  |  | 25.323 |  |  | 28.7317 |  |  | 40.116 |  |  | 68.1689 |  |  | 119.2103 |  |  | 193.0473 |  |  | 275.3673 |  |  | 362.5767 |  |  | 462.3496
[13 empty] | Delta P at this iteration flow rate |  |  | 31.7812 |  |  | 28.2619 |  |  | 7.8096 |  |  | -60.496 |  |  | -228.8137 |  |  | -535.062 |  |  | -978.0836 |  |  | -1472.0037 |  |  | -1995.2599 |  |  | -2593.8978
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.5466 |  |  | 45.5739 |  |  | 30.0327 |  |  | -16.5638 |  |  | -120.7808 |  |  | -290.1662 |  |  | -504.0985 |  |  | -696.1059 |  |  | -818.6131 |  |  | -803.4678
[13 empty] | C Non choked w/ reducers | 7 |  | 19.271 |  |  | 59.1238 |  |  | 278.7998 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 15.4341 |  |  | 46.5591 |  |  | 142.1705 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 19.271 |  |  | 59.1238 |  |  | 278.7998 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 14.541 | 108.6257 |  | 47.5238 | 314.0661 |  | 255.7998 | 776.7229 |  | 5500 | 1512.8579 |  | 5500 | 2538.105 |  | 5500 | 3741.4777 |  | 5500 | 4993.0165 |  | 5500 | 6092.429 |  | 5500 | 7073.1209 |  | 5500 | 8049.8714
[13 empty] | Next iteration flow rate |  |  | 110.7982 | Abs Value of | Flow this | 317.2068 | Abs Value of | Flow this | 784.4901 | Abs Value of | Flow this | 1527.9865 | Abs Value of | Flow this | 2563.486 | Abs Value of | Flow this | 3778.8925 | Abs Value of | Flow this | 5042.9466 | Abs Value of | Flow this | 6153.3533 | Abs Value of | Flow this | 7143.8521 | Abs Value of | Flow this | 8130.3701 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.5015 |  |  | 53.518 |  |  | 36.1318 |  |  | -21.9337 |  |  | -165.0177 |  |  | -425.3543 |  |  | -801.9596 |  |  | -1221.8328 |  |  | -1666.6442 |  |  | -2175.5363
[13 empty] | P2 at this iteration flow rate |  |  | 24.7397 |  |  | 25.3364 |  |  | 28.8136 |  |  | 40.4267 |  |  | 69.0435 |  |  | 121.1109 |  |  | 196.4319 |  |  | 280.4066 |  |  | 369.3688 |  |  | 471.1473
[13 empty] | Delta P at this iteration flow rate |  |  | 31.7619 |  |  | 28.1816 |  |  | 7.3181 |  |  | -62.3604 |  |  | -234.0612 |  |  | -546.4652 |  |  | -998.3915 |  |  | -1502.2394 |  |  | -2036.0131 |  |  | -2646.6836
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.5323 |  |  | 45.5165 |  |  | 29.692 |  |  | -17.7998 |  |  | -124.0596 |  |  | -296.7898 |  |  | -514.9594 |  |  | -710.7577 |  |  | -835.6363 |  |  | -820.0453
[13 empty] | C Non choked w/ reducers | 7 |  | 19.6624 |  |  | 59.8001 |  |  | 290.889 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 15.7451 |  |  | 47.0544 |  |  | 144.4137 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 19.6624 |  |  | 59.8001 |  |  | 290.889 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 14.9324 | 110.7982 |  | 48.2001 | 317.2068 |  | 267.889 | 784.4901 |  | 5500 | 1527.9865 |  | 5500 | 2563.486 |  | 5500 | 3778.8925 |  | 5500 | 5042.9466 |  | 5500 | 6153.3533 |  | 5500 | 7143.8521 |  | 5500 | 8130.3701
[13 empty] | Next iteration flow rate |  |  | 113.0142 | Abs Value of | Flow this | 320.3788 | Abs Value of | Flow this | 792.335 | Abs Value of | Flow this | 1543.2664 | Abs Value of | Flow this | 2589.1209 | Abs Value of | Flow this | 3816.6814 | Abs Value of | Flow this | 5093.3761 | Abs Value of | Flow this | 6214.8868 | Abs Value of | Flow this | 7215.2906 | Abs Value of | Flow this | 8211.6738 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.4848 |  |  | 53.4497 |  |  | 35.714 |  |  | -23.5185 |  |  | -169.4786 |  |  | -435.0479 |  |  | -819.223 |  |  | -1247.5357 |  |  | -1701.2878 |  |  | -2220.4086
[13 empty] | P2 at this iteration flow rate |  |  | 24.743 |  |  | 25.3501 |  |  | 28.8972 |  |  | 40.7437 |  |  | 69.9357 |  |  | 123.0496 |  |  | 199.8846 |  |  | 285.5471 |  |  | 376.2976 |  |  | 480.1217
[13 empty] | Delta P at this iteration flow rate |  |  | 31.7418 |  |  | 28.0996 |  |  | 6.8168 |  |  | -64.2623 |  |  | -239.4143 |  |  | -558.0975 |  |  | -1019.1076 |  |  | -1533.0828 |  |  | -2077.5854 |  |  | -2700.5303
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.5175 |  |  | 45.4579 |  |  | 29.3444 |  |  | -19.0607 |  |  | -127.4043 |  |  | -303.5465 |  |  | -526.0386 |  |  | -725.704 |  |  | -853.0016 |  |  | -836.956
[13 empty] | C Non choked w/ reducers | 7 |  | 20.062 |  |  | 60.4861 |  |  | 304.4094 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 16.0624 |  |  | 47.5555 |  |  | 146.719 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 20.062 |  |  | 60.4861 |  |  | 304.4094 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 15.332 | 113.0142 |  | 48.8861 | 320.3788 |  | 281.4094 | 792.335 |  | 5500 | 1543.2664 |  | 5500 | 2589.1209 |  | 5500 | 3816.6814 |  | 5500 | 5093.3761 |  | 5500 | 6214.8868 |  | 5500 | 7215.2906 |  | 5500 | 8211.6738
[13 empty] | Next iteration flow rate |  |  | 115.2745 | Abs Value of | Flow this | 323.5826 | Abs Value of | Flow this | 800.2584 | Abs Value of | Flow this | 1558.699 | Abs Value of | Flow this | 2615.0121 | Abs Value of | Flow this | 3854.8482 | Abs Value of | Flow this | 5144.3099 | Abs Value of | Flow this | 6277.0357 | Abs Value of | Flow this | 7287.4435 | Abs Value of | Flow this | 8293.7905 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.4674 |  |  | 53.38 |  |  | 35.2879 |  |  | -25.1353 |  |  | -174.0291 |  |  | -444.9364 |  |  | -836.8334 |  |  | -1273.7551 |  |  | -1736.6277 |  |  | -2266.1828
[13 empty] | P2 at this iteration flow rate |  |  | 24.7465 |  |  | 25.364 |  |  | 28.9824 |  |  | 41.0671 |  |  | 70.8458 |  |  | 125.0273 |  |  | 203.4067 |  |  | 290.791 |  |  | 383.3655 |  |  | 489.2766
[13 empty] | Delta P at this iteration flow rate |  |  | 31.7208 |  |  | 28.016 |  |  | 6.3054 |  |  | -66.2023 |  |  | -244.8749 |  |  | -569.9637 |  |  | -1040.2401 |  |  | -1564.5462 |  |  | -2119.9932 |  |  | -2755.4594
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.5022 |  |  | 45.3981 |  |  | 28.9899 |  |  | -20.3469 |  |  | -130.8163 |  |  | -310.439 |  |  | -537.3405 |  |  | -740.9508 |  |  | -870.7159 |  |  | -854.2067
[13 empty] | C Non choked w/ reducers | 7 |  | 20.47 |  |  | 61.1821 |  |  | 319.6783 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 16.3862 |  |  | 48.0627 |  |  | 149.0895 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 20.47 |  |  | 61.1821 |  |  | 319.6783 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 15.74 | 115.2745 |  | 49.5821 | 323.5826 |  | 296.6783 | 800.2584 |  | 5500 | 1558.699 |  | 5500 | 2615.0121 |  | 5500 | 3854.8482 |  | 5500 | 5144.3099 |  | 5500 | 6277.0357 |  | 5500 | 7287.4435 |  | 5500 | 8293.7905
[13 empty] | Next iteration flow rate |  |  | 117.5799 | Abs Value of | Flow this | 326.8185 | Abs Value of | Flow this | 808.2609 | Abs Value of | Flow this | 1574.286 | Abs Value of | Flow this | 2641.1622 | Abs Value of | Flow this | 3893.3967 | Abs Value of | Flow this | 5195.753 | Abs Value of | Flow this | 6339.806 | Abs Value of | Flow this | 7360.318 | Abs Value of | Flow this | 8376.7284 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.4492 |  |  | 53.3089 |  |  | 34.8531 |  |  | -26.7845 |  |  | -178.6711 |  |  | -455.0237 |  |  | -854.7978 |  |  | -1300.5016 |  |  | -1772.6779 |  |  | -2312.8771
[13 empty] | P2 at this iteration flow rate |  |  | 24.7502 |  |  | 25.3782 |  |  | 29.0694 |  |  | 41.3969 |  |  | 71.7742 |  |  | 127.0447 |  |  | 206.9996 |  |  | 296.1403 |  |  | 390.5756 |  |  | 498.6154
[13 empty] | Delta P at this iteration flow rate |  |  | 31.6991 |  |  | 27.9307 |  |  | 5.7838 |  |  | -68.1814 |  |  | -250.4453 |  |  | -582.0684 |  |  | -1061.7973 |  |  | -1596.642 |  |  | -2163.2535 |  |  | -2811.4926
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.4861 |  |  | 45.3372 |  |  | 28.6282 |  |  | -21.659 |  |  | -134.2969 |  |  | -317.4701 |  |  | -548.8695 |  |  | -756.504 |  |  | -888.7863 |  |  | -871.804
[13 empty] | C Non choked w/ reducers | 7 |  | 20.8866 |  |  | 61.8881 |  |  | 337.1218 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 16.7166 |  |  | 48.5759 |  |  | 151.5286 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 20.8866 |  |  | 61.8881 |  |  | 337.1218 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 16.1566 | 117.5799 |  | 50.2881 | 326.8185 |  | 314.1218 | 808.2609 |  | 5500 | 1574.286 |  | 5500 | 2641.1622 |  | 5500 | 3893.3967 |  | 5500 | 5195.753 |  | 5500 | 6339.806 |  | 5500 | 7360.318 |  | 5500 | 8376.7284
[13 empty] | Next iteration flow rate |  |  | 119.9315 | Abs Value of | Flow this | 330.0866 | Abs Value of | Flow this | 816.3436 | Abs Value of | Flow this | 1590.0289 | Abs Value of | Flow this | 2667.5738 | Abs Value of | Flow this | 3932.3306 | Abs Value of | Flow this | 5247.7105 | Abs Value of | Flow this | 6403.2041 | Abs Value of | Flow this | 7433.9211 | Abs Value of | Flow this | 8460.4957 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.4304 |  |  | 53.2364 |  |  | 34.4097 |  |  | -28.4669 |  |  | -183.4064 |  |  | -465.3137 |  |  | -873.1232 |  |  | -1327.7857 |  |  | -1809.4528 |  |  | -2360.51
[13 empty] | P2 at this iteration flow rate |  |  | 24.7539 |  |  | 25.3927 |  |  | 29.1581 |  |  | 41.7334 |  |  | 72.7213 |  |  | 129.1027 |  |  | 210.6646 |  |  | 301.5971 |  |  | 397.9306 |  |  | 508.142
[13 empty] | Delta P at this iteration flow rate |  |  | 31.6765 |  |  | 27.8437 |  |  | 5.2516 |  |  | -70.2003 |  |  | -256.1277 |  |  | -594.4164 |  |  | -1083.7879 |  |  | -1629.3829 |  |  | -2207.3833 |  |  | -2868.652
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.4695 |  |  | 45.275 |  |  | 28.2593 |  |  | -22.9975 |  |  | -137.8474 |  |  | -324.6425 |  |  | -560.6303 |  |  | -772.3698 |  |  | -907.2199 |  |  | -889.7551
[13 empty] | C Non choked w/ reducers | 7 |  | 21.3119 |  |  | 62.6046 |  |  | 357.3284 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 17.0538 |  |  | 49.0954 |  |  | 154.0396 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 21.3119 |  |  | 62.6046 |  |  | 357.3284 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 16.5819 | 119.9315 |  | 51.0046 | 330.0866 |  | 334.3284 | 816.3436 |  | 5500 | 1590.0289 |  | 5500 | 2667.5738 |  | 5500 | 3932.3306 |  | 5500 | 5247.7105 |  | 5500 | 6403.2041 |  | 5500 | 7433.9211 |  | 5500 | 8460.4957
[13 empty] | Next iteration flow rate |  |  | 122.3302 | Abs Value of | Flow this | 333.3875 | Abs Value of | Flow this | 824.507 | Abs Value of | Flow this | 1605.9292 | Abs Value of | Flow this | 2694.2496 | Abs Value of | Flow this | 3971.654 | Abs Value of | Flow this | 5300.1876 | Abs Value of | Flow this | 6467.2361 | Abs Value of | Flow this | 7508.2604 | Abs Value of | Flow this | 8545.1007 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.4108 |  |  | 53.1624 |  |  | 33.9573 |  |  | -30.1831 |  |  | -188.2369 |  |  | -475.8105 |  |  | -891.817 |  |  | -1355.6182 |  |  | -1846.9668 |  |  | -2409.1002
[13 empty] | P2 at this iteration flow rate |  |  | 24.7578 |  |  | 25.4075 |  |  | 29.2485 |  |  | 42.0766 |  |  | 73.6874 |  |  | 131.2021 |  |  | 214.4034 |  |  | 307.1636 |  |  | 405.4334 |  |  | 517.86
[13 empty] | Delta P at this iteration flow rate |  |  | 31.6529 |  |  | 27.7549 |  |  | 4.7087 |  |  | -72.2597 |  |  | -261.9242 |  |  | -607.0126 |  |  | -1106.2204 |  |  | -1662.7819 |  |  | -2252.4001 |  |  | -2926.9603
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.4521 |  |  | 45.2116 |  |  | 27.883 |  |  | -24.3628 |  |  | -141.4693 |  |  | -331.959 |  |  | -572.6275 |  |  | -788.5546 |  |  | -926.024 |  |  | -908.067
[13 empty] | C Non choked w/ reducers | 7 |  | 21.7462 |  |  | 63.3317 |  |  | 381.138 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 17.3979 |  |  | 49.6211 |  |  | 156.6264 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 21.7462 |  |  | 63.3317 |  |  | 381.138 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 17.0162 | 122.3302 |  | 51.7317 | 333.3875 |  | 358.138 | 824.507 |  | 5500 | 1605.9292 |  | 5500 | 2694.2496 |  | 5500 | 3971.654 |  | 5500 | 5300.1876 |  | 5500 | 6467.2361 |  | 5500 | 7508.2604 |  | 5500 | 8545.1007
[13 empty] | Next iteration flow rate |  |  | 124.7768 | Abs Value of | Flow this | 336.7214 | Abs Value of | Flow this | 832.7521 | Abs Value of | Flow this | 1621.9885 | Abs Value of | Flow this | 2721.1921 | Abs Value of | Flow this | 4011.3705 | Abs Value of | Flow this | 5353.1895 | Abs Value of | Flow this | 6531.9085 | Abs Value of | Flow this | 7583.343 | Abs Value of | Flow this | 8630.5517 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.3903 |  |  | 53.087 |  |  | 33.4958 |  |  | -31.9338 |  |  | -193.1644 |  |  | -486.5183 |  |  | -910.8865 |  |  | -1384.0102 |  |  | -1885.2348 |  |  | -2458.6672
[13 empty] | P2 at this iteration flow rate |  |  | 24.7619 |  |  | 25.4226 |  |  | 29.3408 |  |  | 42.4268 |  |  | 74.6729 |  |  | 133.3437 |  |  | 218.2173 |  |  | 312.842 |  |  | 413.087 |  |  | 527.7734
[13 empty] | Delta P at this iteration flow rate |  |  | 31.6284 |  |  | 27.6644 |  |  | 4.155 |  |  | -74.3606 |  |  | -267.8373 |  |  | -619.8619 |  |  | -1129.1039 |  |  | -1696.8522 |  |  | -2298.3218 |  |  | -2986.4406
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.4341 |  |  | 45.1469 |  |  | 27.4991 |  |  | -25.7556 |  |  | -145.1639 |  |  | -339.4226 |  |  | -584.8659 |  |  | -805.0646 |  |  | -945.2061 |  |  | -926.7469
[13 empty] | C Non choked w/ reducers | 7 |  | 22.1897 |  |  | 64.0696 |  |  | 409.7999 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 17.7491 |  |  | 50.1532 |  |  | 159.2931 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 22.1897 |  |  | 64.0696 |  |  | 409.7999 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 17.4597 | 124.7768 |  | 52.4696 | 336.7214 |  | 386.7999 | 832.7521 |  | 5500 | 1621.9885 |  | 5500 | 2721.1921 |  | 5500 | 4011.3705 |  | 5500 | 5353.1895 |  | 5500 | 6531.9085 |  | 5500 | 7583.343 |  | 5500 | 8630.5517
[13 empty] | Next iteration flow rate |  |  | 127.2723 | Abs Value of | Flow this | 340.0886 | Abs Value of | Flow this | 841.0796 | Abs Value of | Flow this | 1638.2083 | Abs Value of | Flow this | 2748.404 | Abs Value of | Flow this | 4051.4842 | Abs Value of | Flow this | 5406.7214 | Abs Value of | Flow this | 6597.2276 | Abs Value of | Flow this | 7659.1764 | Abs Value of | Flow this | 8716.8572 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.3691 |  |  | 53.01 |  |  | 33.0251 |  |  | -33.7197 |  |  | -198.1911 |  |  | -497.4413 |  |  | -930.3394 |  |  | -1412.9728 |  |  | -1924.2721 |  |  | -2509.2304
[13 empty] | P2 at this iteration flow rate |  |  | 24.7662 |  |  | 25.438 |  |  | 29.435 |  |  | 42.7839 |  |  | 75.6782 |  |  | 135.5283 |  |  | 222.1079 |  |  | 318.6346 |  |  | 420.8944 |  |  | 537.8861
[13 empty] | Delta P at this iteration flow rate |  |  | 31.6029 |  |  | 27.572 |  |  | 3.5901 |  |  | -76.5036 |  |  | -273.8693 |  |  | -632.9696 |  |  | -1152.4473 |  |  | -1731.6074 |  |  | -2345.1665 |  |  | -3047.1165
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.4153 |  |  | 45.0809 |  |  | 27.1075 |  |  | -27.1764 |  |  | -148.9329 |  |  | -347.0363 |  |  | -597.3502 |  |  | -821.9065 |  |  | -964.7738 |  |  | -945.8023
[13 empty] | C Non choked w/ reducers | 7 |  | 22.6427 |  |  | 64.8186 |  |  | 445.2722 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 18.1076 |  |  | 50.6918 |  |  | 162.044 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 22.6427 |  |  | 64.8186 |  |  | 445.2722 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 17.9127 | 127.2723 |  | 53.2186 | 340.0886 |  | 422.2722 | 841.0796 |  | 5500 | 1638.2083 |  | 5500 | 2748.404 |  | 5500 | 4051.4842 |  | 5500 | 5406.7214 |  | 5500 | 6597.2276 |  | 5500 | 7659.1764 |  | 5500 | 8716.8572
[13 empty] | Next iteration flow rate |  |  | 129.8178 | Abs Value of | Flow this | 343.4895 | Abs Value of | Flow this | 849.4904 | Abs Value of | Flow this | 1654.5904 | Abs Value of | Flow this | 2775.888 | Abs Value of | Flow this | 4091.999 | Abs Value of | Flow this | 5460.7886 | Abs Value of | Flow this | 6663.1998 | Abs Value of | Flow this | 7735.7682 | Abs Value of | Flow this | 8804.0258 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.347 |  |  | 52.9315 |  |  | 32.5449 |  |  | -35.5415 |  |  | -203.3187 |  |  | -508.5839 |  |  | -950.1832 |  |  | -1442.5176 |  |  | -1964.094 |  |  | -2560.8099
[13 empty] | P2 at this iteration flow rate |  |  | 24.7706 |  |  | 25.4537 |  |  | 29.531 |  |  | 43.1483 |  |  | 76.7037 |  |  | 137.7568 |  |  | 226.0766 |  |  | 324.5435 |  |  | 428.8588 |  |  | 548.202
[13 empty] | Delta P at this iteration flow rate |  |  | 31.5764 |  |  | 27.4778 |  |  | 3.0138 |  |  | -78.6897 |  |  | -280.0225 |  |  | -646.3407 |  |  | -1176.2599 |  |  | -1767.0611 |  |  | -2392.9527 |  |  | -3109.0119
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.3958 |  |  | 45.0135 |  |  | 26.708 |  |  | -28.6258 |  |  | -152.7776 |  |  | -354.8029 |  |  | -610.0855 |  |  | -839.087 |  |  | -984.7348 |  |  | -965.2408
[13 empty] | C Non choked w/ reducers | 7 |  | 23.1052 |  |  | 65.5789 |  |  | 490.8399 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 18.4734 |  |  | 51.237 |  |  | 164.8839 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 23.1052 |  |  | 65.5789 |  |  | 490.8399 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 18.3752 | 129.8178 |  | 53.9789 | 343.4895 |  | 467.8399 | 849.4904 |  | 5500 | 1654.5904 |  | 5500 | 2775.888 |  | 5500 | 4091.999 |  | 5500 | 5460.7886 |  | 5500 | 6663.1998 |  | 5500 | 7735.7682 |  | 5500 | 8804.0258
[13 empty] | Next iteration flow rate |  |  | 132.4141 | Abs Value of | Flow this | 346.9244 | Abs Value of | Flow this | 857.9853 | Abs Value of | Flow this | 1671.1363 | Abs Value of | Flow this | 2803.6469 | Abs Value of | Flow this | 4132.919 | Abs Value of | Flow this | 5515.3965 | Abs Value of | Flow this | 6729.8318 | Abs Value of | Flow this | 7813.1258 | Abs Value of | Flow this | 8892.066 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.324 |  |  | 52.8514 |  |  | 32.055 |  |  | -37.3999 |  |  | -208.5494 |  |  | -519.9504 |  |  | -970.4259 |  |  | -1472.6562 |  |  | -2004.7163 |  |  | -2613.4262
[13 empty] | P2 at this iteration flow rate |  |  | 24.7752 |  |  | 25.4697 |  |  | 29.629 |  |  | 43.52 |  |  | 77.7499 |  |  | 140.0301 |  |  | 230.1252 |  |  | 330.5712 |  |  | 436.9833 |  |  | 558.7252
[13 empty] | Delta P at this iteration flow rate |  |  | 31.5488 |  |  | 27.3817 |  |  | 2.426 |  |  | -80.9198 |  |  | -286.2993 |  |  | -659.9805 |  |  | -1200.5511 |  |  | -1803.2274 |  |  | -2441.6995 |  |  | -3172.1515
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.3755 |  |  | 44.9449 |  |  | 26.3005 |  |  | -30.1043 |  |  | -156.6995 |  |  | -362.7257 |  |  | -623.0767 |  |  | -856.6127 |  |  | -1005.0969 |  |  | -985.0699
[13 empty] | C Non choked w/ reducers | 7 |  | 23.5776 |  |  | 66.3508 |  |  | 552.5554 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 18.8467 |  |  | 51.7889 |  |  | 167.8179 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 23.5776 |  |  | 66.3508 |  |  | 552.5554 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 18.8476 | 132.4141 |  | 54.7508 | 346.9244 |  | 529.5554 | 857.9853 |  | 5500 | 1671.1363 |  | 5500 | 2803.6469 |  | 5500 | 4132.919 |  | 5500 | 5515.3965 |  | 5500 | 6729.8318 |  | 5500 | 7813.1258 |  | 5500 | 8892.066
[13 empty] | Next iteration flow rate |  |  | 135.0624 | Abs Value of | Flow this | 350.3936 | Abs Value of | Flow this | 866.5651 | Abs Value of | Flow this | 1687.8477 | Abs Value of | Flow this | 2831.6834 | Abs Value of | Flow this | 4174.2482 | Abs Value of | Flow this | 5570.5504 | Abs Value of | Flow this | 6797.1302 | Abs Value of | Flow this | 7891.2571 | Abs Value of | Flow this | 8980.9867 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.3001 |  |  | 52.7697 |  |  | 31.5553 |  |  | -39.2956 |  |  | -213.8853 |  |  | -531.5455 |  |  | -991.0755 |  |  | -1503.4006 |  |  | -2046.1551 |  |  | -2667.1001
[13 empty] | P2 at this iteration flow rate |  |  | 24.78 |  |  | 25.4861 |  |  | 29.7289 |  |  | 43.8991 |  |  | 78.8171 |  |  | 142.3491 |  |  | 234.2551 |  |  | 336.7201 |  |  | 445.271 |  |  | 569.46
[13 empty] | Delta P at this iteration flow rate |  |  | 31.5201 |  |  | 27.2837 |  |  | 1.8263 |  |  | -83.1947 |  |  | -292.7024 |  |  | -673.8946 |  |  | -1225.3306 |  |  | -1840.1207 |  |  | -2491.4261 |  |  | -3236.5601
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.3543 |  |  | 44.8748 |  |  | 25.8848 |  |  | -31.6125 |  |  | -160.7004 |  |  | -370.8078 |  |  | -636.3291 |  |  | -874.4907 |  |  | -1025.8684 |  |  | -1005.2976
[13 empty] | C Non choked w/ reducers | 7 |  | 24.0601 |  |  | 67.1346 |  |  | 643.2075 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 19.2278 |  |  | 52.3476 |  |  | 170.8517 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 24.0601 |  |  | 67.1346 |  |  | 643.2075 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 19.3301 | 135.0624 |  | 55.5346 | 350.3936 |  | 620.2075 | 866.5651 |  | 5500 | 1687.8477 |  | 5500 | 2831.6834 |  | 5500 | 4174.2482 |  | 5500 | 5570.5504 |  | 5500 | 6797.1302 |  | 5500 | 7891.2571 |  | 5500 | 8980.9867
[13 empty] | Next iteration flow rate |  |  | 137.7637 | Abs Value of | Flow this | 353.8976 | Abs Value of | Flow this | 875.2308 | Abs Value of | Flow this | 1704.7262 | Abs Value of | Flow this | 2860.0002 | Abs Value of | Flow this | 4215.9907 | Abs Value of | Flow this | 5626.2559 | Abs Value of | Flow this | 6865.1015 | Abs Value of | Flow this | 7970.1697 | Abs Value of | Flow this | 9070.7965 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.2752 |  |  | 52.6864 |  |  | 31.0455 |  |  | -41.2295 |  |  | -219.3284 |  |  | -543.3735 |  |  | -1012.1401 |  |  | -1534.7629 |  |  | -2088.4268 |  |  | -2721.8528
[13 empty] | P2 at this iteration flow rate |  |  | 24.785 |  |  | 25.5027 |  |  | 29.8309 |  |  | 44.2859 |  |  | 79.9057 |  |  | 144.7147 |  |  | 238.468 |  |  | 342.9926 |  |  | 453.7254 |  |  | 580.4106
[13 empty] | Delta P at this iteration flow rate |  |  | 31.4902 |  |  | 27.1836 |  |  | 1.2146 |  |  | -85.5154 |  |  | -299.2341 |  |  | -688.0883 |  |  | -1250.6081 |  |  | -1877.7555 |  |  | -2542.1522 |  |  | -3302.2634
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.3323 |  |  | 44.8033 |  |  | 25.4607 |  |  | -33.151 |  |  | -164.7816 |  |  | -379.0522 |  |  | -649.8478 |  |  | -892.7281 |  |  | -1047.0574 |  |  | -1025.9319
[13 empty] | C Non choked w/ reducers | 7 |  | 24.5529 |  |  | 67.9306 |  |  | 796.6001 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 19.6167 |  |  | 52.9132 |  |  | 173.9914 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 24.5529 |  |  | 67.9306 |  |  | 796.6001 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 19.8229 | 137.7637 |  | 56.3306 | 353.8976 |  | 773.6001 | 875.2308 |  | 5500 | 1704.7262 |  | 5500 | 2860.0002 |  | 5500 | 4215.9907 |  | 5500 | 5626.2559 |  | 5500 | 6865.1015 |  | 5500 | 7970.1697 |  | 5500 | 9070.7965
[13 empty] | Next iteration flow rate |  |  | 140.5189 | Abs Value of | Flow this | 357.4365 | Abs Value of | Flow this | 883.9831 | Abs Value of | Flow this | 1721.7734 | Abs Value of | Flow this | 2888.6002 | Abs Value of | Flow this | 4258.1506 | Abs Value of | Flow this | 5682.5185 | Abs Value of | Flow this | 6933.7525 | Abs Value of | Flow this | 8049.8714 | Abs Value of | Flow this | 9161.5045 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.2493 |  |  | 52.6014 |  |  | 30.5255 |  |  | -43.2022 |  |  | -224.8809 |  |  | -555.4394 |  |  | -1033.6281 |  |  | -1566.7557 |  |  | -2131.5482 |  |  | -2777.7061
[13 empty] | P2 at this iteration flow rate |  |  | 24.7901 |  |  | 25.5197 |  |  | 29.9349 |  |  | 44.6804 |  |  | 81.0162 |  |  | 147.1279 |  |  | 242.7656 |  |  | 349.3911 |  |  | 462.3496 |  |  | 591.5812
[13 empty] | Delta P at this iteration flow rate |  |  | 31.4591 |  |  | 27.0816 |  |  | 0.59063 |  |  | -87.8826 |  |  | -305.8971 |  |  | -702.5672 |  |  | -1276.3938 |  |  | -1916.1468 |  |  | -2593.8978 |  |  | -3369.2873
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.3095 |  |  | 44.7304 |  |  | 25.0281 |  |  | -34.7204 |  |  | -168.9448 |  |  | -387.4624 |  |  | -663.6383 |  |  | -911.3321 |  |  | -1068.6722 |  |  | -1046.9809
[13 empty] | C Non choked w/ reducers | 7 |  | 25.0564 |  |  | 68.739 |  |  | 1153.7858 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 20.0137 |  |  | 53.4859 |  |  | 177.2435 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 25.0564 |  |  | 68.739 |  |  | 1153.7858 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 20.3264 | 140.5189 |  | 57.139 | 357.4365 |  | 1130.7858 | 883.9831 |  | 5500 | 1721.7734 |  | 5500 | 2888.6002 |  | 5500 | 4258.1506 |  | 5500 | 5682.5185 |  | 5500 | 6933.7525 |  | 5500 | 8049.8714 |  | 5500 | 9161.5045
[13 empty] | Next iteration flow rate |  |  | 143.3293 | Abs Value of | Flow this | 361.0109 | Abs Value of | Flow this | 892.8229 | Abs Value of | Flow this | 1738.9912 | Abs Value of | Flow this | 2917.4862 | Abs Value of | Flow this | 4300.7321 | Abs Value of | Flow this | 5739.3437 | Abs Value of | Flow this | 7003.09 | Abs Value of | Flow this | 8130.3701 | Abs Value of | Flow this | 9253.1195 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.2223 |  |  | 52.5146 |  |  | 29.9951 |  |  | -45.2146 |  |  | -230.545 |  |  | -567.7477 |  |  | -1055.5481 |  |  | -1599.3915 |  |  | -2175.5363 |  |  | -2834.682
[13 empty] | P2 at this iteration flow rate |  |  | 24.7955 |  |  | 25.5371 |  |  | 30.041 |  |  | 45.0829 |  |  | 82.149 |  |  | 149.5895 |  |  | 247.1496 |  |  | 355.9183 |  |  | 471.1473 |  |  | 602.9764
[13 empty] | Delta P at this iteration flow rate |  |  | 31.4268 |  |  | 26.9776 |  |  | -0.045908 |  |  | -90.2975 |  |  | -312.6941 |  |  | -717.3373 |  |  | -1302.6977 |  |  | -1955.3098 |  |  | -2646.6836 |  |  | -3437.6584
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.2857 |  |  | 44.6561 |  |  | 24.5868 |  |  | -36.3214 |  |  | -173.1918 |  |  | -396.0417 |  |  | -677.7059 |  |  | -930.3099 |  |  | -1090.7215 |  |  | -1068.453
[13 empty] | C Non choked w/ reducers | 7 |  | 25.5706 |  |  | 69.5602 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 20.4189 |  |  | 54.0657 |  |  | 180.6152 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 25.5706 |  |  | 69.5602 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 20.8406 | 143.3293 |  | 57.9602 | 361.0109 |  | 5500 | 892.8229 |  | 5500 | 1738.9912 |  | 5500 | 2917.4862 |  | 5500 | 4300.7321 |  | 5500 | 5739.3437 |  | 5500 | 7003.09 |  | 5500 | 8130.3701 |  | 5500 | 9253.1195
[13 empty] | Next iteration flow rate |  |  | 146.1959 | Abs Value of | Flow this | 364.621 | Abs Value of | Flow this | 901.7512 | Abs Value of | Flow this | 1756.3811 | Abs Value of | Flow this | 2946.6611 | Abs Value of | Flow this | 4343.7394 | Abs Value of | Flow this | 5796.7371 | Abs Value of | Flow this | 7073.1209 | Abs Value of | Flow this | 8211.6738 | Abs Value of | Flow this | 9345.6507 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.1943 |  |  | 52.4262 |  |  | 29.454 |  |  | -47.2674 |  |  | -236.323 |  |  | -580.3035 |  |  | -1077.9086 |  |  | -1632.6833 |  |  | -2220.4086 |  |  | -2892.8031
[13 empty] | P2 at this iteration flow rate |  |  | 24.8011 |  |  | 25.5548 |  |  | 30.1492 |  |  | 45.4935 |  |  | 83.3046 |  |  | 152.1007 |  |  | 251.6217 |  |  | 362.5767 |  |  | 480.1217 |  |  | 614.6006
[13 empty] | Delta P at this iteration flow rate |  |  | 31.3932 |  |  | 26.8714 |  |  | -0.69524 |  |  | -92.7609 |  |  | -319.6276 |  |  | -732.4041 |  |  | -1329.5303 |  |  | -1995.2599 |  |  | -2700.5303 |  |  | -3507.4038
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.2609 |  |  | 44.5802 |  |  | 24.1367 |  |  | -37.9546 |  |  | -177.5241 |  |  | -404.7933 |  |  | -692.0563 |  |  | -949.6693 |  |  | -1113.2141 |  |  | -1090.3568
[13 empty] | C Non choked w/ reducers | 7 |  | 26.096 |  |  | 70.3944 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 20.8325 |  |  | 54.6528 |  |  | 184.1146 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 26.096 |  |  | 70.3944 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 21.366 | 146.1959 |  | 58.7944 | 364.621 |  | 5500 | 901.7512 |  | 5500 | 1756.3811 |  | 5500 | 2946.6611 |  | 5500 | 4343.7394 |  | 5500 | 5796.7371 |  | 5500 | 7073.1209 |  | 5500 | 8211.6738 |  | 5500 | 9345.6507
[13 empty] | Next iteration flow rate |  |  | 149.1198 | Abs Value of | Flow this | 368.2672 | Abs Value of | Flow this | 910.7687 | Abs Value of | Flow this | 1773.9449 | Abs Value of | Flow this | 2976.1277 | Abs Value of | Flow this | 4387.1768 | Abs Value of | Flow this | 5854.7045 | Abs Value of | Flow this | 7143.8521 | Abs Value of | Flow this | 8293.7905 | Abs Value of | Flow this | 9439.1072 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.1652 |  |  | 52.3359 |  |  | 28.902 |  |  | -49.3615 |  |  | -242.2171 |  |  | -593.1116 |  |  | -1100.7186 |  |  | -1666.6442 |  |  | -2266.1828 |  |  | -2952.0925
[13 empty] | P2 at this iteration flow rate |  |  | 24.807 |  |  | 25.5728 |  |  | 30.2596 |  |  | 45.9123 |  |  | 84.4834 |  |  | 154.6623 |  |  | 256.1837 |  |  | 369.3688 |  |  | 489.2766 |  |  | 626.4585
[13 empty] | Delta P at this iteration flow rate |  |  | 31.3582 |  |  | 26.7631 |  |  | -1.3576 |  |  | -95.2738 |  |  | -326.7006 |  |  | -747.7739 |  |  | -1356.9023 |  |  | -2036.0131 |  |  | -2755.4594 |  |  | -3578.551
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.2351 |  |  | 44.5028 |  |  | 23.6775 |  |  | -39.6206 |  |  | -181.9434 |  |  | -413.7209 |  |  | -706.6952 |  |  | -969.4177 |  |  | -1136.1587 |  |  | -1112.7007
[13 empty] | C Non choked w/ reducers | 7 |  | 26.6328 |  |  | 71.2421 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 21.2547 |  |  | 55.2473 |  |  | 187.7503 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 26.6328 |  |  | 71.2421 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 21.9028 | 149.1198 |  | 59.6421 | 368.2672 |  | 5500 | 910.7687 |  | 5500 | 1773.9449 |  | 5500 | 2976.1277 |  | 5500 | 4387.1768 |  | 5500 | 5854.7045 |  | 5500 | 7143.8521 |  | 5500 | 8293.7905 |  | 5500 | 9439.1072
[13 empty] | Next iteration flow rate |  |  | 152.1022 | Abs Value of | Flow this | 371.9499 | Abs Value of | Flow this | 919.8764 | Abs Value of | Flow this | 1791.6843 | Abs Value of | Flow this | 3005.889 | Abs Value of | Flow this | 4431.0486 | Abs Value of | Flow this | 5913.2515 | Abs Value of | Flow this | 7215.2906 | Abs Value of | Flow this | 8376.7284 | Abs Value of | Flow this | 9533.4983 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.1348 |  |  | 52.2438 |  |  | 28.3389 |  |  | -51.4977 |  |  | -248.2297 |  |  | -606.1771 |  |  | -1123.9871 |  |  | -1701.2878 |  |  | -2312.8771 |  |  | -3012.5736
[13 empty] | P2 at this iteration flow rate |  |  | 24.813 |  |  | 25.5912 |  |  | 30.3722 |  |  | 46.3395 |  |  | 85.6859 |  |  | 157.2754 |  |  | 260.8374 |  |  | 376.2976 |  |  | 498.6154 |  |  | 638.5547
[13 empty] | Delta P at this iteration flow rate |  |  | 31.3218 |  |  | 26.6526 |  |  | -2.0333 |  |  | -97.8372 |  |  | -333.9156 |  |  | -763.4525 |  |  | -1384.8245 |  |  | -2077.5854 |  |  | -2811.4926 |  |  | -3651.1283
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.2083 |  |  | 44.4238 |  |  | 23.209 |  |  | -41.32 |  |  | -186.4517 |  |  | -422.828 |  |  | -721.6283 |  |  | -989.5631 |  |  | -1159.5645 |  |  | -1135.4938
[13 empty] | C Non choked w/ reducers | 7 |  | 27.1812 |  |  | 72.1035 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 21.6857 |  |  | 55.8493 |  |  | 191.5319 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 27.1812 |  |  | 72.1035 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 22.4512 | 152.1022 |  | 60.5035 | 371.9499 |  | 5500 | 919.8764 |  | 5500 | 1791.6843 |  | 5500 | 3005.889 |  | 5500 | 4431.0486 |  | 5500 | 5913.2515 |  | 5500 | 7215.2906 |  | 5500 | 8376.7284 |  | 5500 | 9533.4983
[13 empty] | Next iteration flow rate |  |  | 155.1442 | Abs Value of | Flow this | 375.6694 | Abs Value of | Flow this | 929.0751 | Abs Value of | Flow this | 1809.6012 | Abs Value of | Flow this | 3035.9479 | Abs Value of | Flow this | 4475.3591 | Abs Value of | Flow this | 5972.384 | Abs Value of | Flow this | 7287.4435 | Abs Value of | Flow this | 8460.4957 | Abs Value of | Flow this | 9628.8333 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.1033 |  |  | 52.1499 |  |  | 27.7645 |  |  | -53.6768 |  |  | -254.3631 |  |  | -619.5053 |  |  | -1147.7232 |  |  | -1736.6277 |  |  | -2360.51 |  |  | -3074.2703
[13 empty] | P2 at this iteration flow rate |  |  | 24.8193 |  |  | 25.61 |  |  | 30.4871 |  |  | 46.7754 |  |  | 86.9126 |  |  | 159.9411 |  |  | 265.5846 |  |  | 383.3655 |  |  | 508.142 |  |  | 650.8941
[13 empty] | Delta P at this iteration flow rate |  |  | 31.2839 |  |  | 26.5399 |  |  | -2.7226 |  |  | -100.4521 |  |  | -341.2758 |  |  | -779.4464 |  |  | -1413.3078 |  |  | -2119.9932 |  |  | -2868.652 |  |  | -3725.1644
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.1804 |  |  | 44.3433 |  |  | 22.7312 |  |  | -43.0537 |  |  | -191.0505 |  |  | -432.118 |  |  | -736.8615 |  |  | -1010.1135 |  |  | -1183.4407 |  |  | -1158.745
[13 empty] | C Non choked w/ reducers | 7 |  | 27.7416 |  |  | 72.979 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 22.1257 |  |  | 56.459 |  |  | 195.4699 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 27.7416 |  |  | 72.979 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 23.0116 | 155.1442 |  | 61.379 | 375.6694 |  | 5500 | 929.0751 |  | 5500 | 1809.6012 |  | 5500 | 3035.9479 |  | 5500 | 4475.3591 |  | 5500 | 5972.384 |  | 5500 | 7287.4435 |  | 5500 | 8460.4957 |  | 5500 | 9628.8333
[13 empty] | Next iteration flow rate |  |  | 158.2471 | Abs Value of | Flow this | 379.4261 | Abs Value of | Flow this | 938.3659 | Abs Value of | Flow this | 1827.6972 | Abs Value of | Flow this | 3066.3073 | Abs Value of | Flow this | 4520.1127 | Abs Value of | Flow this | 6032.1079 | Abs Value of | Flow this | 7360.318 | Abs Value of | Flow this | 8545.1007 | Abs Value of | Flow this | 9725.1216 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.0704 |  |  | 52.0541 |  |  | 27.1785 |  |  | -55.8997 |  |  | -260.6198 |  |  | -633.1014 |  |  | -1171.9365 |  |  | -1772.6779 |  |  | -2409.1002 |  |  | -3137.2072
[13 empty] | P2 at this iteration flow rate |  |  | 24.8259 |  |  | 25.6292 |  |  | 30.6043 |  |  | 47.2199 |  |  | 88.164 |  |  | 162.6603 |  |  | 270.4273 |  |  | 390.5756 |  |  | 517.86 |  |  | 663.4814
[13 empty] | Delta P at this iteration flow rate |  |  | 31.2445 |  |  | 26.425 |  |  | -3.4258 |  |  | -103.1196 |  |  | -348.7838 |  |  | -795.7616 |  |  | -1442.3638 |  |  | -2163.2535 |  |  | -2926.9603 |  |  | -3800.6886
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.1514 |  |  | 44.2612 |  |  | 22.2437 |  |  | -44.8222 |  |  | -195.7417 |  |  | -441.5949 |  |  | -752.401 |  |  | -1031.0769 |  |  | -1207.7969 |  |  | -1182.4636
[13 empty] | C Non choked w/ reducers | 7 |  | 28.3143 |  |  | 73.8689 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 22.5748 |  |  | 57.0765 |  |  | 199.5761 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 28.3143 |  |  | 73.8689 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 23.5843 | 158.2471 |  | 62.2689 | 379.4261 |  | 5500 | 938.3659 |  | 5500 | 1827.6972 |  | 5500 | 3066.3073 |  | 5500 | 4520.1127 |  | 5500 | 6032.1079 |  | 5500 | 7360.318 |  | 5500 | 8545.1007 |  | 5500 | 9725.1216
[13 empty] | Next iteration flow rate |  |  | 161.4121 | Abs Value of | Flow this | 383.2203 | Abs Value of | Flow this | 947.7495 | Abs Value of | Flow this | 1845.9742 | Abs Value of | Flow this | 3096.9704 | Abs Value of | Flow this | 4565.3138 | Abs Value of | Flow this | 6092.429 | Abs Value of | Flow this | 7433.9211 | Abs Value of | Flow this | 8630.5517 | Abs Value of | Flow this | 9822.3729 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.0362 |  |  | 51.9564 |  |  | 26.5808 |  |  | -58.1673 |  |  | -267.0023 |  |  | -646.9707 |  |  | -1196.6364 |  |  | -1809.4528 |  |  | -2458.6672 |  |  | -3201.409
[13 empty] | P2 at this iteration flow rate |  |  | 24.8328 |  |  | 25.6487 |  |  | 30.7238 |  |  | 47.6735 |  |  | 89.4405 |  |  | 165.4341 |  |  | 275.3673 |  |  | 397.9306 |  |  | 527.7734 |  |  | 676.3218
[13 empty] | Delta P at this iteration flow rate |  |  | 31.2035 |  |  | 26.3077 |  |  | -4.143 |  |  | -105.8408 |  |  | -356.4428 |  |  | -812.4049 |  |  | -1472.0037 |  |  | -2207.3833 |  |  | -2986.4406 |  |  | -3877.7308
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.1212 |  |  | 44.1774 |  |  | 21.7465 |  |  | -46.6262 |  |  | -200.5273 |  |  | -451.2622 |  |  | -768.2527 |  |  | -1052.4616 |  |  | -1232.6426 |  |  | -1206.6589
[13 empty] | C Non choked w/ reducers | 7 |  | 28.8996 |  |  | 74.7737 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 23.0334 |  |  | 57.7019 |  |  | 203.8634 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 28.8996 |  |  | 74.7737 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 24.1696 | 161.4121 |  | 63.1737 | 383.2203 |  | 5500 | 947.7495 |  | 5500 | 1845.9742 |  | 5500 | 3096.9704 |  | 5500 | 4565.3138 |  | 5500 | 6092.429 |  | 5500 | 7433.9211 |  | 5500 | 8630.5517 |  | 5500 | 9822.3729
[13 empty] | Next iteration flow rate |  |  | 164.6403 | Abs Value of | Flow this | 387.0526 | Abs Value of | Flow this | 957.227 | Abs Value of | Flow this | 1864.4339 | Abs Value of | Flow this | 3127.9401 | Abs Value of | Flow this | 4610.9669 | Abs Value of | Flow this | 6153.3533 | Abs Value of | Flow this | 7508.2604 | Abs Value of | Flow this | 8716.8572 | Abs Value of | Flow this | 9920.5966 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.0007 |  |  | 51.8567 |  |  | 25.9711 |  |  | -60.4805 |  |  | -273.5131 |  |  | -661.1188 |  |  | -1221.8328 |  |  | -1846.9668 |  |  | -2509.2304 |  |  | -3266.9014
[13 empty] | P2 at this iteration flow rate |  |  | 24.8399 |  |  | 25.6687 |  |  | 30.8458 |  |  | 48.1361 |  |  | 90.7426 |  |  | 168.2638 |  |  | 280.4066 |  |  | 405.4334 |  |  | 537.8861 |  |  | 689.4203
[13 empty] | Delta P at this iteration flow rate |  |  | 31.1608 |  |  | 26.1881 |  |  | -4.8747 |  |  | -108.6166 |  |  | -364.2557 |  |  | -829.3826 |  |  | -1502.2394 |  |  | -2252.4001 |  |  | -3047.1165 |  |  | -3956.3216
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.0898 |  |  | 44.0919 |  |  | 21.2393 |  |  | -48.4665 |  |  | -205.409 |  |  | -461.1238 |  |  | -784.4231 |  |  | -1074.2762 |  |  | -1257.9877 |  |  | -1231.3406
[13 empty] | C Non choked w/ reducers | 7 |  | 29.4977 |  |  | 75.6937 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 23.5016 |  |  | 58.3354 |  |  | 208.3462 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 29.4977 |  |  | 75.6937 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 24.7677 | 164.6403 |  | 64.0937 | 387.0526 |  | 5500 | 957.227 |  | 5500 | 1864.4339 |  | 5500 | 3127.9401 |  | 5500 | 4610.9669 |  | 5500 | 6153.3533 |  | 5500 | 7508.2604 |  | 5500 | 8716.8572 |  | 5500 | 9920.5966
[13 empty] | Next iteration flow rate |  |  | 167.9331 | Abs Value of | Flow this | 390.9231 | Abs Value of | Flow this | 966.7993 | Abs Value of | Flow this | 1883.0783 | Abs Value of | Flow this | 3159.2195 | Abs Value of | Flow this | 4657.0766 | Abs Value of | Flow this | 6214.8868 | Abs Value of | Flow this | 7583.343 | Abs Value of | Flow this | 8804.0258 | Abs Value of | Flow this | 10019.8025 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.9637 |  |  | 51.755 |  |  | 25.3491 |  |  | -62.8401 |  |  | -280.1547 |  |  | -675.5514 |  |  | -1247.5357 |  |  | -1885.2348 |  |  | -2560.8099 |  |  | -3333.7101
[13 empty] | P2 at this iteration flow rate |  |  | 24.8473 |  |  | 25.689 |  |  | 30.9702 |  |  | 48.608 |  |  | 92.0709 |  |  | 171.1503 |  |  | 285.5471 |  |  | 413.087 |  |  | 548.202 |  |  | 702.782
[13 empty] | Delta P at this iteration flow rate |  |  | 31.1165 |  |  | 26.066 |  |  | -5.6211 |  |  | -111.4482 |  |  | -372.2257 |  |  | -846.7016 |  |  | -1533.0828 |  |  | -2298.3218 |  |  | -3109.0119 |  |  | -4036.4921
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.0572 |  |  | 44.0047 |  |  | 20.7218 |  |  | -50.3438 |  |  | -210.3889 |  |  | -471.1836 |  |  | -800.9186 |  |  | -1096.5292 |  |  | -1283.8423 |  |  | -1256.5183
[13 empty] | C Non choked w/ reducers | 7 |  | 30.1091 |  |  | 76.6294 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 23.9796 |  |  | 58.9771 |  |  | 213.0408 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 30.1091 |  |  | 76.6294 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 25.3791 | 167.9331 |  | 65.0294 | 390.9231 |  | 5500 | 966.7993 |  | 5500 | 1883.0783 |  | 5500 | 3159.2195 |  | 5500 | 4657.0766 |  | 5500 | 6214.8868 |  | 5500 | 7583.343 |  | 5500 | 8804.0258 |  | 5500 | 10019.8025
[13 empty] | Next iteration flow rate |  |  | 171.2918 | Abs Value of | Flow this | 394.8323 | Abs Value of | Flow this | 976.4673 | Abs Value of | Flow this | 1901.909 | Abs Value of | Flow this | 3190.8117 | Abs Value of | Flow this | 4703.6474 | Abs Value of | Flow this | 6277.0357 | Abs Value of | Flow this | 7659.1764 | Abs Value of | Flow this | 8892.066 | Abs Value of | Flow this | 10120.0006 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.9252 |  |  | 51.6513 |  |  | 24.7146 |  |  | -65.2472 |  |  | -286.9298 |  |  | -690.2739 |  |  | -1273.7551 |  |  | -1924.2721 |  |  | -2613.4262 |  |  | -3401.8617
[13 empty] | P2 at this iteration flow rate |  |  | 24.855 |  |  | 25.7097 |  |  | 31.0971 |  |  | 49.0894 |  |  | 93.426 |  |  | 174.0948 |  |  | 290.791 |  |  | 420.8944 |  |  | 558.7252 |  |  | 716.4123
[13 empty] | Delta P at this iteration flow rate |  |  | 31.0703 |  |  | 25.9415 |  |  | -6.3825 |  |  | -114.3367 |  |  | -380.3558 |  |  | -864.3687 |  |  | -1564.5462 |  |  | -2345.1665 |  |  | -3172.1515 |  |  | -4118.274
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 49.0232 |  |  | 43.9157 |  |  | 20.194 |  |  | -52.2588 |  |  | -215.4689 |  |  | -481.4456 |  |  | -817.7456 |  |  | -1119.2296 |  |  | -1310.2166 |  |  | -1282.2022
[13 empty] | C Non choked w/ reducers | 7 |  | 30.7341 |  |  | 77.5812 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 24.4677 |  |  | 59.6272 |  |  | 217.9651 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 30.7341 |  |  | 77.5812 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 26.0041 | 171.2918 |  | 65.9812 | 394.8323 |  | 5500 | 976.4673 |  | 5500 | 1901.909 |  | 5500 | 3190.8117 |  | 5500 | 4703.6474 |  | 5500 | 6277.0357 |  | 5500 | 7659.1764 |  | 5500 | 8892.066 |  | 5500 | 10120.0006
[13 empty] | Next iteration flow rate |  |  | 174.7176 | Abs Value of | Flow this | 398.7806 | Abs Value of | Flow this | 986.232 | Abs Value of | Flow this | 1920.9281 | Abs Value of | Flow this | 3222.7198 | Abs Value of | Flow this | 4750.6838 | Abs Value of | Flow this | 6339.806 | Abs Value of | Flow this | 7735.7682 | Abs Value of | Flow this | 8980.9867 | Abs Value of | Flow this | 10221.2006 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.8852 |  |  | 51.5455 |  |  | 24.0673 |  |  | -67.7027 |  |  | -293.8411 |  |  | -705.2925 |  |  | -1300.5016 |  |  | -1964.094 |  |  | -2667.1001 |  |  | -3471.3831
[13 empty] | P2 at this iteration flow rate |  |  | 24.863 |  |  | 25.7309 |  |  | 31.2265 |  |  | 49.5805 |  |  | 94.8082 |  |  | 177.0985 |  |  | 296.1403 |  |  | 428.8588 |  |  | 569.46 |  |  | 730.3166
[13 empty] | Delta P at this iteration flow rate |  |  | 31.0222 |  |  | 25.8145 |  |  | -7.1592 |  |  | -117.2833 |  |  | -388.6494 |  |  | -882.391 |  |  | -1596.642 |  |  | -2392.9527 |  |  | -3236.5601 |  |  | -4201.6997
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.9878 |  |  | 43.8249 |  |  | 19.6555 |  |  | -54.2123 |  |  | -220.6509 |  |  | -491.9139 |  |  | -834.9108 |  |  | -1142.3862 |  |  | -1337.1209 |  |  | -1308.4022
[13 empty] | C Non choked w/ reducers | 7 |  | 31.3731 |  |  | 78.5495 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 24.966 |  |  | 60.2858 |  |  | 223.1398 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 31.3731 |  |  | 78.5495 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 26.6431 | 174.7176 |  | 66.9495 | 398.7806 |  | 5500 | 986.232 |  | 5500 | 1920.9281 |  | 5500 | 3222.7198 |  | 5500 | 4750.6838 |  | 5500 | 6339.806 |  | 5500 | 7735.7682 |  | 5500 | 8980.9867 |  | 5500 | 10221.2006
[13 empty] | Next iteration flow rate |  |  | 178.212 | Abs Value of | Flow this | 402.7684 | Abs Value of | Flow this | 996.0943 | Abs Value of | Flow this | 1940.1374 | Abs Value of | Flow this | 3254.947 | Abs Value of | Flow this | 4798.1907 | Abs Value of | Flow this | 6403.2041 | Abs Value of | Flow this | 7813.1258 | Abs Value of | Flow this | 9070.7965 | Abs Value of | Flow this | 10323.4126 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.8435 |  |  | 51.4375 |  |  | 23.4071 |  |  | -70.2076 |  |  | -300.8914 |  |  | -720.6129 |  |  | -1327.7857 |  |  | -2004.7163 |  |  | -2721.8528 |  |  | -3542.3019
[13 empty] | P2 at this iteration flow rate |  |  | 24.8713 |  |  | 25.7525 |  |  | 31.3586 |  |  | 50.0815 |  |  | 96.2183 |  |  | 180.1626 |  |  | 301.5971 |  |  | 436.9833 |  |  | 580.4106 |  |  | 744.5004
[13 empty] | Delta P at this iteration flow rate |  |  | 30.9723 |  |  | 25.685 |  |  | -7.9515 |  |  | -120.2891 |  |  | -397.1096 |  |  | -900.7754 |  |  | -1629.3829 |  |  | -2441.6995 |  |  | -3302.2634 |  |  | -4286.8023
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.951 |  |  | 43.7324 |  |  | 19.1063 |  |  | -56.2051 |  |  | -225.9372 |  |  | -502.5926 |  |  | -852.421 |  |  | -1166.0083 |  |  | -1364.5661 |  |  | -1335.1289
[13 empty] | C Non choked w/ reducers | 7 |  | 32.0263 |  |  | 79.5348 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 25.4749 |  |  | 60.9531 |  |  | 228.5877 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 32.0263 |  |  | 79.5348 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 27.2963 | 178.212 |  | 67.9348 | 402.7684 |  | 5500 | 996.0943 |  | 5500 | 1940.1374 |  | 5500 | 3254.947 |  | 5500 | 4798.1907 |  | 5500 | 6403.2041 |  | 5500 | 7813.1258 |  | 5500 | 9070.7965 |  | 5500 | 10323.4126
[13 empty] | Next iteration flow rate |  |  | 181.7762 | Abs Value of | Flow this | 406.7961 | Abs Value of | Flow this | 1006.0552 | Abs Value of | Flow this | 1959.5388 | Abs Value of | Flow this | 3287.4965 | Abs Value of | Flow this | 4846.1726 | Abs Value of | Flow this | 6467.2361 | Abs Value of | Flow this | 7891.2571 | Abs Value of | Flow this | 9161.5045 | Abs Value of | Flow this | 10426.6467 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.8002 |  |  | 51.3274 |  |  | 22.7335 |  |  | -72.7628 |  |  | -308.0833 |  |  | -736.2412 |  |  | -1355.6182 |  |  | -2046.1551 |  |  | -2777.7061 |  |  | -3614.6462
[13 empty] | P2 at this iteration flow rate |  |  | 24.88 |  |  | 25.7745 |  |  | 31.4933 |  |  | 50.5926 |  |  | 97.6567 |  |  | 183.2882 |  |  | 307.1636 |  |  | 445.271 |  |  | 591.5812 |  |  | 758.9692
[13 empty] | Delta P at this iteration flow rate |  |  | 30.9203 |  |  | 25.5529 |  |  | -8.7598 |  |  | -123.3553 |  |  | -405.7399 |  |  | -919.5294 |  |  | -1662.7819 |  |  | -2491.4261 |  |  | -3369.2873 |  |  | -4373.6155
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.9127 |  |  | 43.6379 |  |  | 18.5459 |  |  | -58.2379 |  |  | -231.3297 |  |  | -513.486 |  |  | -870.2832 |  |  | -1190.1052 |  |  | -1392.5628 |  |  | -1362.3928
[13 empty] | C Non choked w/ reducers | 7 |  | 32.6943 |  |  | 80.5376 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 25.9946 |  |  | 61.6292 |  |  | 234.3352 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 32.6943 |  |  | 80.5376 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 27.9643 | 181.7762 |  | 68.9376 | 406.7961 |  | 5500 | 1006.0552 |  | 5500 | 1959.5388 |  | 5500 | 3287.4965 |  | 5500 | 4846.1726 |  | 5500 | 6467.2361 |  | 5500 | 7891.2571 |  | 5500 | 9161.5045 |  | 5500 | 10426.6467
[13 empty] | Next iteration flow rate |  |  | 185.4117 | Abs Value of | Flow this | 410.8641 | Abs Value of | Flow this | 1016.1158 | Abs Value of | Flow this | 1979.1342 | Abs Value of | Flow this | 3320.3715 | Abs Value of | Flow this | 4894.6343 | Abs Value of | Flow this | 6531.9085 | Abs Value of | Flow this | 7970.1697 | Abs Value of | Flow this | 9253.1195 | Abs Value of | Flow this | 10530.9132 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.7551 |  |  | 51.2151 |  |  | 22.0465 |  |  | -75.3693 |  |  | -315.4198 |  |  | -752.1837 |  |  | -1384.0102 |  |  | -2088.4268 |  |  | -2834.682 |  |  | -3688.4446
[13 empty] | P2 at this iteration flow rate |  |  | 24.889 |  |  | 25.797 |  |  | 31.6307 |  |  | 51.1139 |  |  | 99.124 |  |  | 186.4767 |  |  | 312.842 |  |  | 453.7254 |  |  | 602.9764 |  |  | 773.7289
[13 empty] | Delta P at this iteration flow rate |  |  | 30.8662 |  |  | 25.4181 |  |  | -9.5842 |  |  | -126.4832 |  |  | -414.5437 |  |  | -938.6604 |  |  | -1696.8522 |  |  | -2542.1522 |  |  | -3437.6584 |  |  | -4462.1736
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.8729 |  |  | 43.5416 |  |  | 17.9744 |  |  | -60.3116 |  |  | -236.8305 |  |  | -524.5983 |  |  | -888.5044 |  |  | -1214.6864 |  |  | -1421.1224 |  |  | -1390.2047
[13 empty] | C Non choked w/ reducers | 7 |  | 33.3774 |  |  | 81.5584 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 26.5253 |  |  | 62.3143 |  |  | 240.4123 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 33.3774 |  |  | 81.5584 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 28.6474 | 185.4117 |  | 69.9584 | 410.8641 |  | 5500 | 1016.1158 |  | 5500 | 1979.1342 |  | 5500 | 3320.3715 |  | 5500 | 4894.6343 |  | 5500 | 6531.9085 |  | 5500 | 7970.1697 |  | 5500 | 9253.1195 |  | 5500 | 10530.9132
[13 empty] | Next iteration flow rate |  |  | 189.12 | Abs Value of | Flow this | 414.9727 | Abs Value of | Flow this | 1026.2769 | Abs Value of | Flow this | 1998.9255 | Abs Value of | Flow this | 3353.5752 | Abs Value of | Flow this | 4943.5807 | Abs Value of | Flow this | 6597.2276 | Abs Value of | Flow this | 8049.8714 | Abs Value of | Flow this | 9345.6507 | Abs Value of | Flow this | 10636.2223 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.7082 |  |  | 51.1005 |  |  | 21.3456 |  |  | -78.0282 |  |  | -322.9037 |  |  | -768.4466 |  |  | -1412.9728 |  |  | -2131.5482 |  |  | -2892.8031 |  |  | -3763.7264
[13 empty] | P2 at this iteration flow rate |  |  | 24.8984 |  |  | 25.8199 |  |  | 31.7709 |  |  | 51.6456 |  |  | 100.6207 |  |  | 189.7293 |  |  | 318.6346 |  |  | 462.3496 |  |  | 614.6006 |  |  | 788.7853
[13 empty] | Delta P at this iteration flow rate |  |  | 30.8099 |  |  | 25.2806 |  |  | -10.4253 |  |  | -129.6739 |  |  | -423.5245 |  |  | -958.1759 |  |  | -1731.6074 |  |  | -2593.8978 |  |  | -3507.4038 |  |  | -4552.5117
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.8314 |  |  | 43.4433 |  |  | 17.3913 |  |  | -62.4269 |  |  | -242.442 |  |  | -535.934 |  |  | -907.0918 |  |  | -1239.7617 |  |  | -1450.2559 |  |  | -1418.5756
[13 empty] | C Non choked w/ reducers | 7 |  | 34.0761 |  |  | 82.5977 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 27.0673 |  |  | 63.0086 |  |  | 246.8532 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 34.0761 |  |  | 82.5977 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 29.3461 | 189.12 |  | 70.9977 | 414.9727 |  | 5500 | 1026.2769 |  | 5500 | 1998.9255 |  | 5500 | 3353.5752 |  | 5500 | 4943.5807 |  | 5500 | 6597.2276 |  | 5500 | 8049.8714 |  | 5500 | 9345.6507 |  | 5500 | 10636.2223
[13 empty] | Next iteration flow rate |  |  | 192.9024 | Abs Value of | Flow this | 419.1225 | Abs Value of | Flow this | 1036.5397 | Abs Value of | Flow this | 2018.9148 | Abs Value of | Flow this | 3387.1109 | Abs Value of | Flow this | 4993.0165 | Abs Value of | Flow this | 6663.1998 | Abs Value of | Flow this | 8130.3701 | Abs Value of | Flow this | 9439.1072 | Abs Value of | Flow this | 10742.5845 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.6594 |  |  | 50.9836 |  |  | 20.6306 |  |  | -80.7406 |  |  | -330.5381 |  |  | -785.0364 |  |  | -1442.5176 |  |  | -2175.5363 |  |  | -2952.0925 |  |  | -3840.5213
[13 empty] | P2 at this iteration flow rate |  |  | 24.9081 |  |  | 25.8433 |  |  | 31.9139 |  |  | 52.1881 |  |  | 102.1476 |  |  | 193.0473 |  |  | 324.5435 |  |  | 471.1473 |  |  | 626.4585 |  |  | 804.1443
[13 empty] | Delta P at this iteration flow rate |  |  | 30.7513 |  |  | 25.1403 |  |  | -11.2833 |  |  | -132.9287 |  |  | -432.6857 |  |  | -978.0836 |  |  | -1767.0611 |  |  | -2646.6836 |  |  | -3578.551 |  |  | -4644.6655
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.7883 |  |  | 43.3431 |  |  | 16.7965 |  |  | -64.5848 |  |  | -248.1662 |  |  | -547.4975 |  |  | -926.0529 |  |  | -1265.341 |  |  | -1479.9751 |  |  | -1447.5168
[13 empty] | C Non choked w/ reducers | 7 |  | 34.7907 |  |  | 83.6561 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 27.6208 |  |  | 63.7122 |  |  | 253.6977 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 34.7907 |  |  | 83.6561 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 30.0607 | 192.9024 |  | 72.0561 | 419.1225 |  | 5500 | 1036.5397 |  | 5500 | 2018.9148 |  | 5500 | 3387.1109 |  | 5500 | 4993.0165 |  | 5500 | 6663.1998 |  | 5500 | 8130.3701 |  | 5500 | 9439.1072 |  | 5500 | 10742.5845
[13 empty] | Next iteration flow rate |  |  | 196.7604 | Abs Value of | Flow this | 423.3137 | Abs Value of | Flow this | 1046.9051 | Abs Value of | Flow this | 2039.1039 | Abs Value of | Flow this | 3420.982 | Abs Value of | Flow this | 5042.9466 | Abs Value of | Flow this | 6729.8318 | Abs Value of | Flow this | 8211.6738 | Abs Value of | Flow this | 9533.4983 | Abs Value of | Flow this | 10850.0104 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.6087 |  |  | 50.8643 |  |  | 19.9013 |  |  | -83.5075 |  |  | -338.3259 |  |  | -801.9596 |  |  | -1472.6562 |  |  | -2220.4086 |  |  | -3012.5736 |  |  | -3918.8598
[13 empty] | P2 at this iteration flow rate |  |  | 24.9183 |  |  | 25.8671 |  |  | 32.0597 |  |  | 52.7415 |  |  | 103.7052 |  |  | 196.4319 |  |  | 330.5712 |  |  | 480.1217 |  |  | 638.5547 |  |  | 819.812
[13 empty] | Delta P at this iteration flow rate |  |  | 30.6904 |  |  | 24.9972 |  |  | -12.1585 |  |  | -136.249 |  |  | -442.0311 |  |  | -998.3915 |  |  | -1803.2274 |  |  | -2700.5303 |  |  | -3651.1283 |  |  | -4738.6717
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.7434 |  |  | 43.2408 |  |  | 16.1898 |  |  | -66.7861 |  |  | -254.0055 |  |  | -559.2934 |  |  | -945.3951 |  |  | -1291.4345 |  |  | -1510.2916 |  |  | -1477.0397
[13 empty] | C Non choked w/ reducers | 7 |  | 35.5217 |  |  | 84.7341 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 28.1862 |  |  | 64.4254 |  |  | 260.9919 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 35.5217 |  |  | 84.7341 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 30.7917 | 196.7604 |  | 73.1341 | 423.3137 |  | 5500 | 1046.9051 |  | 5500 | 2039.1039 |  | 5500 | 3420.982 |  | 5500 | 5042.9466 |  | 5500 | 6729.8318 |  | 5500 | 8211.6738 |  | 5500 | 9533.4983 |  | 5500 | 10850.0104
[13 empty] | Next iteration flow rate |  |  | 200.6956 | Abs Value of | Flow this | 427.5468 | Abs Value of | Flow this | 1057.3741 | Abs Value of | Flow this | 2059.495 | Abs Value of | Flow this | 3455.1919 | Abs Value of | Flow this | 5093.3761 | Abs Value of | Flow this | 6797.1302 | Abs Value of | Flow this | 8293.7905 | Abs Value of | Flow this | 9628.8333 | Abs Value of | Flow this | 10958.5105 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.5558 |  |  | 50.7427 |  |  | 19.1573 |  |  | -86.33 |  |  | -346.2703 |  |  | -819.223 |  |  | -1503.4006 |  |  | -2266.1828 |  |  | -3074.2703 |  |  | -3998.7729
[13 empty] | P2 at this iteration flow rate |  |  | 24.9288 |  |  | 25.8915 |  |  | 32.2085 |  |  | 53.306 |  |  | 105.2941 |  |  | 199.8846 |  |  | 336.7201 |  |  | 489.2766 |  |  | 650.8941 |  |  | 835.7946
[13 empty] | Delta P at this iteration flow rate |  |  | 30.627 |  |  | 24.8512 |  |  | -13.0513 |  |  | -139.636 |  |  | -451.5644 |  |  | -1019.1076 |  |  | -1840.1207 |  |  | -2755.4594 |  |  | -3725.1644 |  |  | -4834.5675
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6968 |  |  | 43.1365 |  |  | 15.5709 |  |  | -69.0316 |  |  | -259.9621 |  |  | -571.3265 |  |  | -965.1261 |  |  | -1318.0524 |  |  | -1541.2175 |  |  | -1507.156
[13 empty] | C Non choked w/ reducers | 7 |  | 36.2696 |  |  | 85.8325 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 28.7637 |  |  | 65.1483 |  |  | 268.7898 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 36.2696 |  |  | 85.8325 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 31.5396 | 200.6956 |  | 74.2325 | 427.5468 |  | 5500 | 1057.3741 |  | 5500 | 2059.495 |  | 5500 | 3455.1919 |  | 5500 | 5093.3761 |  | 5500 | 6797.1302 |  | 5500 | 8293.7905 |  | 5500 | 9628.8333 |  | 5500 | 10958.5105
[13 empty] | Next iteration flow rate |  |  | 204.7095 | Abs Value of | Flow this | 431.8223 | Abs Value of | Flow this | 1067.9479 | Abs Value of | Flow this | 2080.0899 | Abs Value of | Flow this | 3489.7438 | Abs Value of | Flow this | 5144.3099 | Abs Value of | Flow this | 6865.1015 | Abs Value of | Flow this | 8376.7284 | Abs Value of | Flow this | 9725.1216 | Abs Value of | Flow this | 11068.0956 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.5009 |  |  | 50.6186 |  |  | 18.3983 |  |  | -89.2093 |  |  | -354.3744 |  |  | -836.8334 |  |  | -1534.7629 |  |  | -2312.8771 |  |  | -3137.2072 |  |  | -4080.2922
[13 empty] | P2 at this iteration flow rate |  |  | 24.9398 |  |  | 25.9163 |  |  | 32.3603 |  |  | 53.8819 |  |  | 106.9149 |  |  | 203.4067 |  |  | 342.9926 |  |  | 498.6154 |  |  | 663.4814 |  |  | 852.0984
[13 empty] | Delta P at this iteration flow rate |  |  | 30.5611 |  |  | 24.7023 |  |  | -13.962 |  |  | -143.0911 |  |  | -461.2892 |  |  | -1040.2401 |  |  | -1877.7555 |  |  | -2811.4926 |  |  | -3800.6886 |  |  | -4932.3907
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.6482 |  |  | 43.0301 |  |  | 14.9395 |  |  | -71.3222 |  |  | -266.0385 |  |  | -583.6014 |  |  | -985.2536 |  |  | -1345.2054 |  |  | -1572.765 |  |  | -1537.8776
[13 empty] | C Non choked w/ reducers | 7 |  | 37.0349 |  |  | 86.9517 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 29.3536 |  |  | 65.881 |  |  | 277.1549 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 37.0349 |  |  | 86.9517 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 32.3049 | 204.7095 |  | 75.3517 | 431.8223 |  | 5500 | 1067.9479 |  | 5500 | 2080.0899 |  | 5500 | 3489.7438 |  | 5500 | 5144.3099 |  | 5500 | 6865.1015 |  | 5500 | 8376.7284 |  | 5500 | 9725.1216 |  | 5500 | 11068.0956
[13 empty] | Next iteration flow rate |  |  | 208.8037 | Abs Value of | Flow this | 436.1405 | Abs Value of | Flow this | 1078.6274 | Abs Value of | Flow this | 2100.8908 | Abs Value of | Flow this | 3524.6412 | Abs Value of | Flow this | 5195.753 | Abs Value of | Flow this | 6933.7525 | Abs Value of | Flow this | 8460.4957 | Abs Value of | Flow this | 9822.3729 | Abs Value of | Flow this | 11178.7765 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.4437 |  |  | 50.492 |  |  | 17.6241 |  |  | -92.1464 |  |  | -362.6413 |  |  | -854.7978 |  |  | -1566.7557 |  |  | -2360.51 |  |  | -3201.409 |  |  | -4163.4501
[13 empty] | P2 at this iteration flow rate |  |  | 24.9513 |  |  | 25.9416 |  |  | 32.5152 |  |  | 54.4693 |  |  | 108.5683 |  |  | 206.9996 |  |  | 349.3911 |  |  | 508.142 |  |  | 676.3218 |  |  | 868.73
[13 empty] | Delta P at this iteration flow rate |  |  | 30.4924 |  |  | 24.5504 |  |  | -14.8911 |  |  | -146.6157 |  |  | -471.2096 |  |  | -1061.7973 |  |  | -1916.1468 |  |  | -2868.652 |  |  | -3877.7308 |  |  | -5032.1801
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.5977 |  |  | 42.9216 |  |  | 14.2954 |  |  | -73.6589 |  |  | -272.237 |  |  | -596.123 |  |  | -1005.7857 |  |  | -1372.9041 |  |  | -1604.9465 |  |  | -1569.2168
[13 empty] | C Non choked w/ reducers | 7 |  | 37.818 |  |  | 88.0925 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 29.9562 |  |  | 66.6239 |  |  | 286.1629 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 37.818 |  |  | 88.0925 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 33.088 | 208.8037 |  | 76.4925 | 436.1405 |  | 5500 | 1078.6274 |  | 5500 | 2100.8908 |  | 5500 | 3524.6412 |  | 5500 | 5195.753 |  | 5500 | 6933.7525 |  | 5500 | 8460.4957 |  | 5500 | 9822.3729 |  | 5500 | 11178.7765
[13 empty] | Next iteration flow rate |  |  | 212.9798 | Abs Value of | Flow this | 440.5019 | Abs Value of | Flow this | 1089.4136 | Abs Value of | Flow this | 2121.8997 | Abs Value of | Flow this | 3559.8876 | Abs Value of | Flow this | 5247.7105 | Abs Value of | Flow this | 7003.09 | Abs Value of | Flow this | 8545.1007 | Abs Value of | Flow this | 9920.5966 | Abs Value of | Flow this | 11290.5643 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.3842 |  |  | 50.3629 |  |  | 16.8343 |  |  | -95.1426 |  |  | -371.0744 |  |  | -873.1232 |  |  | -1599.3915 |  |  | -2409.1002 |  |  | -3266.9014 |  |  | -4248.2795
[13 empty] | P2 at this iteration flow rate |  |  | 24.9632 |  |  | 25.9674 |  |  | 32.6731 |  |  | 55.0685 |  |  | 110.2549 |  |  | 210.6646 |  |  | 355.9183 |  |  | 517.86 |  |  | 689.4203 |  |  | 885.6959
[13 empty] | Delta P at this iteration flow rate |  |  | 30.4211 |  |  | 24.3955 |  |  | -15.8388 |  |  | -150.2111 |  |  | -481.3293 |  |  | -1083.7879 |  |  | -1955.3098 |  |  | -2926.9603 |  |  | -3956.3216 |  |  | -5133.9754
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.5451 |  |  | 42.8108 |  |  | 13.6384 |  |  | -76.0426 |  |  | -278.5602 |  |  | -608.8963 |  |  | -1026.7306 |  |  | -1401.1596 |  |  | -1637.775 |  |  | -1601.1858
[13 empty] | C Non choked w/ reducers | 7 |  | 38.6196 |  |  | 89.2555 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 30.5719 |  |  | 67.3771 |  |  | 295.9043 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 38.6196 |  |  | 89.2555 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 33.8896 | 212.9798 |  | 77.6555 | 440.5019 |  | 5500 | 1089.4136 |  | 5500 | 2121.8997 |  | 5500 | 3559.8876 |  | 5500 | 5247.7105 |  | 5500 | 7003.09 |  | 5500 | 8545.1007 |  | 5500 | 9920.5966 |  | 5500 | 11290.5643
[13 empty] | Next iteration flow rate |  |  | 217.2394 | Abs Value of | Flow this | 444.9069 | Abs Value of | Flow this | 1100.3078 | Abs Value of | Flow this | 2143.1187 | Abs Value of | Flow this | 3595.4865 | Abs Value of | Flow this | 5300.1876 | Abs Value of | Flow this | 7073.1209 | Abs Value of | Flow this | 8630.5517 | Abs Value of | Flow this | 10019.8025 | Abs Value of | Flow this | 11403.47 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.3223 |  |  | 50.2312 |  |  | 16.0287 |  |  | -98.1989 |  |  | -379.677 |  |  | -891.817 |  |  | -1632.6833 |  |  | -2458.6672 |  |  | -3333.7101 |  |  | -4334.8139
[13 empty] | P2 at this iteration flow rate |  |  | 24.9755 |  |  | 25.9938 |  |  | 32.8343 |  |  | 55.6798 |  |  | 111.9754 |  |  | 214.4034 |  |  | 362.5767 |  |  | 527.7734 |  |  | 702.782 |  |  | 903.0028
[13 empty] | Delta P at this iteration flow rate |  |  | 30.3468 |  |  | 24.2374 |  |  | -16.8056 |  |  | -153.8787 |  |  | -491.6524 |  |  | -1106.2204 |  |  | -1995.2599 |  |  | -2986.4406 |  |  | -4036.4921 |  |  | -5237.8167
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.4905 |  |  | 42.6979 |  |  | 12.9682 |  |  | -78.4741 |  |  | -285.0104 |  |  | -621.9264 |  |  | -1048.0964 |  |  | -1429.983 |  |  | -1671.2633 |  |  | -1633.7975
[13 empty] | C Non choked w/ reducers | 7 |  | 39.4402 |  |  | 90.4415 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 31.2009 |  |  | 68.1409 |  |  | 306.4889 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 39.4402 |  |  | 90.4415 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 34.7102 | 217.2394 |  | 78.8415 | 444.9069 |  | 5500 | 1100.3078 |  | 5500 | 2143.1187 |  | 5500 | 3595.4865 |  | 5500 | 5300.1876 |  | 5500 | 7073.1209 |  | 5500 | 8630.5517 |  | 5500 | 10019.8025 |  | 5500 | 11403.47
[13 empty] | Next iteration flow rate |  |  | 221.5842 | Abs Value of | Flow this | 449.356 | Abs Value of | Flow this | 1111.3109 | Abs Value of | Flow this | 2164.5499 | Abs Value of | Flow this | 3631.4414 | Abs Value of | Flow this | 5353.1895 | Abs Value of | Flow this | 7143.8521 | Abs Value of | Flow this | 8716.8572 | Abs Value of | Flow this | 10120.0006 | Abs Value of | Flow this | 11517.5046 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.2579 |  |  | 50.0968 |  |  | 15.2069 |  |  | -101.3168 |  |  | -388.4525 |  |  | -910.8865 |  |  | -1666.6442 |  |  | -2509.2304 |  |  | -3401.8617 |  |  | -4423.0877
[13 empty] | P2 at this iteration flow rate |  |  | 24.9884 |  |  | 26.0206 |  |  | 32.9986 |  |  | 56.3034 |  |  | 113.7305 |  |  | 218.2173 |  |  | 369.3688 |  |  | 537.8861 |  |  | 716.4123 |  |  | 920.6575
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2695 |  |  | 24.0762 |  |  | -17.7918 |  |  | -157.6201 |  |  | -502.183 |  |  | -1129.1039 |  |  | -2036.0131 |  |  | -3047.1165 |  |  | -4118.274 |  |  | -5343.7452
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.4336 |  |  | 42.5827 |  |  | 12.2845 |  |  | -80.9546 |  |  | -291.5902 |  |  | -635.2184 |  |  | -1069.8916 |  |  | -1459.3857 |  |  | -1705.4247 |  |  | -1667.0646
[13 empty] | C Non choked w/ reducers | 7 |  | 40.2803 |  |  | 91.6513 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 31.8436 |  |  | 68.9153 |  |  | 318.0512 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 40.2803 |  |  | 91.6513 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 35.5503 | 221.5842 |  | 80.0513 | 449.356 |  | 5500 | 1111.3109 |  | 5500 | 2164.5499 |  | 5500 | 3631.4414 |  | 5500 | 5353.1895 |  | 5500 | 7143.8521 |  | 5500 | 8716.8572 |  | 5500 | 10120.0006 |  | 5500 | 11517.5046
[13 empty] | Next iteration flow rate |  |  | 226.0159 | Abs Value of | Flow this | 453.8496 | Abs Value of | Flow this | 1122.424 | Abs Value of | Flow this | 2186.1954 | Abs Value of | Flow this | 3667.7558 | Abs Value of | Flow this | 5406.7214 | Abs Value of | Flow this | 7215.2906 | Abs Value of | Flow this | 8804.0258 | Abs Value of | Flow this | 10221.2006 | Abs Value of | Flow this | 11632.6797 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.1909 |  |  | 49.9597 |  |  | 14.3685 |  |  | -104.4972 |  |  | -397.4044 |  |  | -930.3394 |  |  | -1701.2878 |  |  | -2560.8099 |  |  | -3471.3831 |  |  | -4513.1358
[13 empty] | P2 at this iteration flow rate |  |  | 25.0018 |  |  | 26.0481 |  |  | 33.1663 |  |  | 56.9394 |  |  | 115.5209 |  |  | 222.1079 |  |  | 376.2976 |  |  | 548.202 |  |  | 730.3166 |  |  | 938.6672
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1891 |  |  | 23.9117 |  |  | -18.7978 |  |  | -161.4367 |  |  | -512.9253 |  |  | -1152.4473 |  |  | -2077.5854 |  |  | -3109.0119 |  |  | -4201.6997 |  |  | -5451.8029
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.3744 |  |  | 42.4651 |  |  | 11.5871 |  |  | -83.4849 |  |  | -298.3023 |  |  | -648.7775 |  |  | -1092.125 |  |  | -1489.3795 |  |  | -1740.2727 |  |  | -1701.0004
[13 empty] | C Non choked w/ reducers | 7 |  | 41.1406 |  |  | 92.8857 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 32.5004 |  |  | 69.7007 |  |  | 330.7579 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 41.1406 |  |  | 92.8857 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 36.4106 | 226.0159 |  | 81.2857 | 453.8496 |  | 5500 | 1122.424 |  | 5500 | 2186.1954 |  | 5500 | 3667.7558 |  | 5500 | 5406.7214 |  | 5500 | 7215.2906 |  | 5500 | 8804.0258 |  | 5500 | 10221.2006 |  | 5500 | 11632.6797
[13 empty] | Next iteration flow rate |  |  | 230.5362 | Abs Value of | Flow this | 458.3881 | Abs Value of | Flow this | 1133.6482 | Abs Value of | Flow this | 2208.0573 | Abs Value of | Flow this | 3704.4333 | Abs Value of | Flow this | 5460.7886 | Abs Value of | Flow this | 7287.4435 | Abs Value of | Flow this | 8892.066 | Abs Value of | Flow this | 10323.4126 | Abs Value of | Flow this | 11749.0065 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.1212 |  |  | 49.8199 |  |  | 13.5133 |  |  | -107.7416 |  |  | -406.5363 |  |  | -950.1832 |  |  | -1736.6277 |  |  | -2613.4262 |  |  | -3542.3019 |  |  | -4604.9938
[13 empty] | P2 at this iteration flow rate |  |  | 25.0158 |  |  | 26.076 |  |  | 33.3373 |  |  | 57.5883 |  |  | 117.3473 |  |  | 226.0766 |  |  | 383.3655 |  |  | 558.7252 |  |  | 744.5004 |  |  | 957.0388
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1055 |  |  | 23.7439 |  |  | -19.824 |  |  | -165.33 |  |  | -523.8835 |  |  | -1176.2599 |  |  | -2119.9932 |  |  | -3172.1515 |  |  | -4286.8023 |  |  | -5562.0326
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.3128 |  |  | 42.3452 |  |  | 10.8756 |  |  | -86.066 |  |  | -305.1493 |  |  | -662.6092 |  |  | -1114.8052 |  |  | -1519.9761 |  |  | -1775.8212 |  |  | -1735.6183
[13 empty] | C Non choked w/ reducers | 7 |  | 42.0216 |  |  | 94.1454 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 33.1715 |  |  | 70.4974 |  |  | 344.8191 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 42.0216 |  |  | 94.1454 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 37.2916 | 230.5362 |  | 82.5454 | 458.3881 |  | 5500 | 1133.6482 |  | 5500 | 2208.0573 |  | 5500 | 3704.4333 |  | 5500 | 5460.7886 |  | 5500 | 7287.4435 |  | 5500 | 8892.066 |  | 5500 | 10323.4126 |  | 5500 | 11749.0065
[13 empty] | Next iteration flow rate |  |  | 235.1469 | Abs Value of | Flow this | 462.9719 | Abs Value of | Flow this | 1144.9847 | Abs Value of | Flow this | 2230.1379 | Abs Value of | Flow this | 3741.4777 | Abs Value of | Flow this | 5515.3965 | Abs Value of | Flow this | 7360.318 | Abs Value of | Flow this | 8980.9867 | Abs Value of | Flow this | 10426.6467 | Abs Value of | Flow this | 11866.4966 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.0487 |  |  | 49.6773 |  |  | 12.6409 |  |  | -111.0513 |  |  | -415.8517 |  |  | -970.4259 |  |  | -1772.6779 |  |  | -2667.1001 |  |  | -3614.6462 |  |  | -4698.6982
[13 empty] | P2 at this iteration flow rate |  |  | 25.0303 |  |  | 26.1045 |  |  | 33.5118 |  |  | 58.2503 |  |  | 119.2103 |  |  | 230.1252 |  |  | 390.5756 |  |  | 569.46 |  |  | 758.9692 |  |  | 975.7796
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0185 |  |  | 23.5727 |  |  | -20.8709 |  |  | -169.3015 |  |  | -535.062 |  |  | -1200.5511 |  |  | -2163.2535 |  |  | -3236.5601 |  |  | -4373.6155 |  |  | -5674.4778
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.2487 |  |  | 42.2229 |  |  | 10.1499 |  |  | -88.699 |  |  | -312.134 |  |  | -676.7188 |  |  | -1137.9413 |  |  | -1551.1878 |  |  | -1812.0842 |  |  | -1770.9321
[13 empty] | C Non choked w/ reducers | 7 |  | 42.9242 |  |  | 95.4314 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 33.8574 |  |  | 71.3054 |  |  | 360.5035 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 42.9242 |  |  | 95.4314 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 38.1942 | 235.1469 |  | 83.8314 | 462.9719 |  | 5500 | 1144.9847 |  | 5500 | 2230.1379 |  | 5500 | 3741.4777 |  | 5500 | 5515.3965 |  | 5500 | 7360.318 |  | 5500 | 8980.9867 |  | 5500 | 10426.6467 |  | 5500 | 11866.4966
[13 empty] | Next iteration flow rate |  |  | 239.8499 | Abs Value of | Flow this | 467.6017 | Abs Value of | Flow this | 1156.4345 | Abs Value of | Flow this | 2252.4393 | Abs Value of | Flow this | 3778.8925 | Abs Value of | Flow this | 5570.5504 | Abs Value of | Flow this | 7433.9211 | Abs Value of | Flow this | 9070.7965 | Abs Value of | Flow this | 10530.9132 | Abs Value of | Flow this | 11985.1615 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.9733 |  |  | 49.5318 |  |  | 11.751 |  |  | -114.4274 |  |  | -425.3543 |  |  | -991.0755 |  |  | -1809.4528 |  |  | -2721.8528 |  |  | -3688.4446 |  |  | -4794.286
[13 empty] | P2 at this iteration flow rate |  |  | 25.0453 |  |  | 26.1336 |  |  | 33.6898 |  |  | 58.9255 |  |  | 121.1109 |  |  | 234.2551 |  |  | 397.9306 |  |  | 580.4106 |  |  | 773.7289 |  |  | 994.8972
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9279 |  |  | 23.3981 |  |  | -21.9388 |  |  | -173.3529 |  |  | -546.4652 |  |  | -1225.3306 |  |  | -2207.3833 |  |  | -3302.2634 |  |  | -4462.1736 |  |  | -5789.1833
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.1821 |  |  | 42.0981 |  |  | 9.4095 |  |  | -91.385 |  |  | -319.259 |  |  | -691.1121 |  |  | -1161.5425 |  |  | -1583.0267 |  |  | -1849.0761 |  |  | -1806.9556
[13 empty] | C Non choked w/ reducers | 7 |  | 43.8488 |  |  | 96.7447 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 34.5584 |  |  | 72.1251 |  |  | 378.1612 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 43.8488 |  |  | 96.7447 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 39.1188 | 239.8499 |  | 85.1447 | 467.6017 |  | 5500 | 1156.4345 |  | 5500 | 2252.4393 |  | 5500 | 3778.8925 |  | 5500 | 5570.5504 |  | 5500 | 7433.9211 |  | 5500 | 9070.7965 |  | 5500 | 10530.9132 |  | 5500 | 11985.1615
[13 empty] | Next iteration flow rate |  |  | 244.6468 | Abs Value of | Flow this | 472.2777 | Abs Value of | Flow this | 1167.9989 | Abs Value of | Flow this | 2274.9637 | Abs Value of | Flow this | 3816.6814 | Abs Value of | Flow this | 5626.2559 | Abs Value of | Flow this | 7508.2604 | Abs Value of | Flow this | 9161.5045 | Abs Value of | Flow this | 10636.2223 | Abs Value of | Flow this | 12105.0131 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.8948 |  |  | 49.3833 |  |  | 10.8431 |  |  | -117.8714 |  |  | -435.0479 |  |  | -1012.1401 |  |  | -1846.9668 |  |  | -2777.7061 |  |  | -3763.7264 |  |  | -4891.7952
[13 empty] | P2 at this iteration flow rate |  |  | 25.061 |  |  | 26.1633 |  |  | 33.8714 |  |  | 59.6143 |  |  | 123.0496 |  |  | 238.468 |  |  | 405.4334 |  |  | 591.5812 |  |  | 788.7853 |  |  | 1014.399
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8338 |  |  | 23.22 |  |  | -23.0282 |  |  | -177.4857 |  |  | -558.0975 |  |  | -1250.6081 |  |  | -2252.4001 |  |  | -3369.2873 |  |  | -4552.5117 |  |  | -5906.1942
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.1127 |  |  | 41.9708 |  |  | 8.6543 |  |  | -94.1249 |  |  | -326.5273 |  |  | -705.7947 |  |  | -1185.618 |  |  | -1615.5057 |  |  | -1886.8116 |  |  | -1843.7032
[13 empty] | C Non choked w/ reducers | 7 |  | 44.7963 |  |  | 98.0862 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 35.275 |  |  | 72.9567 |  |  | 398.2593 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 44.7963 |  |  | 98.0862 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 40.0663 | 244.6468 |  | 86.4862 | 472.2777 |  | 5500 | 1167.9989 |  | 5500 | 2274.9637 |  | 5500 | 3816.6814 |  | 5500 | 5626.2559 |  | 5500 | 7508.2604 |  | 5500 | 9161.5045 |  | 5500 | 10636.2223 |  | 5500 | 12105.0131
[13 empty] | Next iteration flow rate |  |  | 249.5398 | Abs Value of | Flow this | 477.0004 | Abs Value of | Flow this | 1179.6789 | Abs Value of | Flow this | 2297.7133 | Abs Value of | Flow this | 3854.8482 | Abs Value of | Flow this | 5682.5185 | Abs Value of | Flow this | 7583.343 | Abs Value of | Flow this | 9253.1195 | Abs Value of | Flow this | 10742.5845 | Abs Value of | Flow this | 12226.0633 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.8131 |  |  | 49.2319 |  |  | 9.9171 |  |  | -121.3847 |  |  | -444.9364 |  |  | -1033.6281 |  |  | -1885.2348 |  |  | -2834.682 |  |  | -3840.5213 |  |  | -4991.2643
[13 empty] | P2 at this iteration flow rate |  |  | 25.0774 |  |  | 26.1936 |  |  | 34.0566 |  |  | 60.3169 |  |  | 125.0273 |  |  | 242.7656 |  |  | 413.087 |  |  | 602.9764 |  |  | 804.1443 |  |  | 1034.2929
[13 empty] | Delta P at this iteration flow rate |  |  | 29.7358 |  |  | 23.0383 |  |  | -24.1395 |  |  | -181.7016 |  |  | -569.9637 |  |  | -1276.3938 |  |  | -2298.3218 |  |  | -3437.6584 |  |  | -4644.6655 |  |  | -6025.5572
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 48.0406 |  |  | 41.841 |  |  | 7.8839 |  |  | -96.92 |  |  | -333.9416 |  |  | -720.7724 |  |  | -1210.1774 |  |  | -1648.6375 |  |  | -1925.3055 |  |  | -1881.1895
[13 empty] | C Non choked w/ reducers | 7 |  | 45.7675 |  |  | 99.4569 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 36.0075 |  |  | 73.8005 |  |  | 421.4368 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 45.7675 |  |  | 99.4569 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 41.0375 | 249.5398 |  | 87.8569 | 477.0004 |  | 5500 | 1179.6789 |  | 5500 | 2297.7133 |  | 5500 | 3854.8482 |  | 5500 | 5682.5185 |  | 5500 | 7583.343 |  | 5500 | 9253.1195 |  | 5500 | 10742.5845 |  | 5500 | 12226.0633
[13 empty] | Next iteration flow rate |  |  | 254.5306 | Abs Value of | Flow this | 481.7705 | Abs Value of | Flow this | 1191.4757 | Abs Value of | Flow this | 2320.6905 | Abs Value of | Flow this | 3893.3967 | Abs Value of | Flow this | 5739.3437 | Abs Value of | Flow this | 7659.1764 | Abs Value of | Flow this | 9345.6507 | Abs Value of | Flow this | 10850.0104 | Abs Value of | Flow this | 12348.3239 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.7282 |  |  | 49.0775 |  |  | 8.9724 |  |  | -124.9685 |  |  | -455.0237 |  |  | -1055.5481 |  |  | -1924.2721 |  |  | -2892.8031 |  |  | -3918.8598 |  |  | -5092.7327
[13 empty] | P2 at this iteration flow rate |  |  | 25.0944 |  |  | 26.2245 |  |  | 34.2455 |  |  | 61.0337 |  |  | 127.0447 |  |  | 247.1496 |  |  | 420.8944 |  |  | 614.6006 |  |  | 819.812 |  |  | 1054.5865
[13 empty] | Delta P at this iteration flow rate |  |  | 29.6338 |  |  | 22.853 |  |  | -25.2731 |  |  | -186.0022 |  |  | -582.0684 |  |  | -1302.6977 |  |  | -2345.1665 |  |  | -3507.4038 |  |  | -4738.6717 |  |  | -6147.3193
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 47.9655 |  |  | 41.7086 |  |  | 7.0981 |  |  | -99.7712 |  |  | -341.505 |  |  | -736.0512 |  |  | -1235.2305 |  |  | -1682.4352 |  |  | -1964.5731 |  |  | -1919.4292
[13 empty] | C Non choked w/ reducers | 7 |  | 46.7631 |  |  | 100.858 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 36.7563 |  |  | 74.6568 |  |  | 448.5963 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 46.7631 |  |  | 100.858 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 42.0331 | 254.5306 |  | 89.258 | 481.7705 |  | 5500 | 1191.4757 |  | 5500 | 2320.6905 |  | 5500 | 3893.3967 |  | 5500 | 5739.3437 |  | 5500 | 7659.1764 |  | 5500 | 9345.6507 |  | 5500 | 10850.0104 |  | 5500 | 12348.3239
[13 empty] | Next iteration flow rate |  |  | 259.6212 | Abs Value of | Flow this | 486.5882 | Abs Value of | Flow this | 1203.3904 | Abs Value of | Flow this | 2343.8974 | Abs Value of | Flow this | 3932.3306 | Abs Value of | Flow this | 5796.7371 | Abs Value of | Flow this | 7735.7682 | Abs Value of | Flow this | 9439.1072 | Abs Value of | Flow this | 10958.5105 | Abs Value of | Flow this | 12471.8071 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.6398 |  |  | 48.9199 |  |  | 8.0087 |  |  | -128.6244 |  |  | -465.3137 |  |  | -1077.9086 |  |  | -1964.094 |  |  | -2952.0925 |  |  | -3998.7729 |  |  | -5196.2407
[13 empty] | P2 at this iteration flow rate |  |  | 25.112 |  |  | 26.256 |  |  | 34.4383 |  |  | 61.7649 |  |  | 129.1027 |  |  | 251.6217 |  |  | 428.8588 |  |  | 626.4585 |  |  | 835.7946 |  |  | 1075.2881
[13 empty] | Delta P at this iteration flow rate |  |  | 29.5277 |  |  | 22.6639 |  |  | -26.4295 |  |  | -190.3893 |  |  | -594.4164 |  |  | -1329.5303 |  |  | -2392.9527 |  |  | -3578.551 |  |  | -4834.5675 |  |  | -6271.5288
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 47.8874 |  |  | 41.5734 |  |  | 6.2964 |  |  | -102.6797 |  |  | -349.2204 |  |  | -751.6371 |  |  | -1260.7872 |  |  | -1716.9122 |  |  | -2004.6301 |  |  | -1958.4375
[13 empty] | C Non choked w/ reducers | 7 |  | 47.7839 |  |  | 102.2906 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 37.522 |  |  | 75.5258 |  |  | 481.0623 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 47.7839 |  |  | 102.2906 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 43.0539 | 259.6212 |  | 90.6906 | 486.5882 |  | 5500 | 1203.3904 |  | 5500 | 2343.8974 |  | 5500 | 3932.3306 |  | 5500 | 5796.7371 |  | 5500 | 7735.7682 |  | 5500 | 9439.1072 |  | 5500 | 10958.5105 |  | 5500 | 12471.8071
[13 empty] | Next iteration flow rate |  |  | 264.8136 | Abs Value of | Flow this | 491.454 | Abs Value of | Flow this | 1215.4243 | Abs Value of | Flow this | 2367.3363 | Abs Value of | Flow this | 3971.654 | Abs Value of | Flow this | 5854.7045 | Abs Value of | Flow this | 7813.1258 | Abs Value of | Flow this | 9533.4983 | Abs Value of | Flow this | 11068.0956 | Abs Value of | Flow this | 12596.5252 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.5478 |  |  | 48.7592 |  |  | 7.0257 |  |  | -132.3537 |  |  | -475.8105 |  |  | -1100.7186 |  |  | -2004.7163 |  |  | -3012.5736 |  |  | -4080.2922 |  |  | -5301.8291
[13 empty] | P2 at this iteration flow rate |  |  | 25.1304 |  |  | 26.2882 |  |  | 34.6349 |  |  | 62.5107 |  |  | 131.2021 |  |  | 256.1837 |  |  | 436.9833 |  |  | 638.5547 |  |  | 852.0984 |  |  | 1096.4058
[13 empty] | Delta P at this iteration flow rate |  |  | 29.4174 |  |  | 22.471 |  |  | -27.6092 |  |  | -194.8645 |  |  | -607.0126 |  |  | -1356.9023 |  |  | -2441.6995 |  |  | -3651.1283 |  |  | -4932.3907 |  |  | -6398.235
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 47.8062 |  |  | 41.4356 |  |  | 5.4786 |  |  | -105.6466 |  |  | -357.0909 |  |  | -767.5362 |  |  | -1286.8575 |  |  | -1752.0823 |  |  | -2045.4922 |  |  | -1998.2299
[13 empty] | C Non choked w/ reducers | 7 |  | 48.831 |  |  | 103.756 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 38.305 |  |  | 76.4078 |  |  | 520.8753 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 48.831 |  |  | 103.756 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 44.101 | 264.8136 |  | 92.156 | 491.454 |  | 5500 | 1215.4243 |  | 5500 | 2367.3363 |  | 5500 | 3971.654 |  | 5500 | 5854.7045 |  | 5500 | 7813.1258 |  | 5500 | 9533.4983 |  | 5500 | 11068.0956 |  | 5500 | 12596.5252
[13 empty] | Next iteration flow rate |  |  | 270.1099 | Abs Value of | Flow this | 496.3686 | Abs Value of | Flow this | 1227.5786 | Abs Value of | Flow this | 2391.0097 | Abs Value of | Flow this | 4011.3705 | Abs Value of | Flow this | 5913.2515 | Abs Value of | Flow this | 7891.2571 | Abs Value of | Flow this | 9628.8333 | Abs Value of | Flow this | 11178.7765 | Abs Value of | Flow this | 12722.4905 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.4521 |  |  | 48.5952 |  |  | 6.0229 |  |  | -136.1581 |  |  | -486.5183 |  |  | -1123.9871 |  |  | -2046.1551 |  |  | -3074.2703 |  |  | -4163.4501 |  |  | -5409.5399
[13 empty] | P2 at this iteration flow rate |  |  | 25.1496 |  |  | 26.321 |  |  | 34.8354 |  |  | 63.2716 |  |  | 133.3437 |  |  | 260.8374 |  |  | 445.271 |  |  | 650.8941 |  |  | 868.73 |  |  | 1117.948
[13 empty] | Delta P at this iteration flow rate |  |  | 29.3026 |  |  | 22.2743 |  |  | -28.8125 |  |  | -199.4297 |  |  | -619.8619 |  |  | -1384.8245 |  |  | -2491.4261 |  |  | -3725.1644 |  |  | -5032.1801 |  |  | -6527.4879
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 47.7216 |  |  | 41.295 |  |  | 4.6444 |  |  | -108.6732 |  |  | -365.1195 |  |  | -783.755 |  |  | -1313.4519 |  |  | -1787.9592 |  |  | -2087.1756 |  |  | -2038.8221
[13 empty] | C Non choked w/ reducers | 7 |  | 49.9051 |  |  | 105.2553 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 39.1057 |  |  | 77.3031 |  |  | 571.382 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 49.9051 |  |  | 105.2553 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 45.1751 | 270.1099 |  | 93.6553 | 496.3686 |  | 5500 | 1227.5786 |  | 5500 | 2391.0097 |  | 5500 | 4011.3705 |  | 5500 | 5913.2515 |  | 5500 | 7891.2571 |  | 5500 | 9628.8333 |  | 5500 | 11178.7765 |  | 5500 | 12722.4905
[13 empty] | Next iteration flow rate |  |  | 275.5121 | Abs Value of | Flow this | 501.3323 | Abs Value of | Flow this | 1239.8543 | Abs Value of | Flow this | 2414.9198 | Abs Value of | Flow this | 4051.4842 | Abs Value of | Flow this | 5972.384 | Abs Value of | Flow this | 7970.1697 | Abs Value of | Flow this | 9725.1216 | Abs Value of | Flow this | 11290.5643 | Abs Value of | Flow this | 12849.7154 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.3526 |  |  | 48.428 |  |  | 4.9999 |  |  | -140.0389 |  |  | -497.4413 |  |  | -1147.7232 |  |  | -2088.4268 |  |  | -3137.2072 |  |  | -4248.2795 |  |  | -5519.4157
[13 empty] | P2 at this iteration flow rate |  |  | 25.1695 |  |  | 26.3544 |  |  | 35.04 |  |  | 64.0478 |  |  | 135.5283 |  |  | 265.5846 |  |  | 453.7254 |  |  | 663.4814 |  |  | 885.6959 |  |  | 1139.9231
[13 empty] | Delta P at this iteration flow rate |  |  | 29.1831 |  |  | 22.0736 |  |  | -30.0401 |  |  | -204.0866 |  |  | -632.9696 |  |  | -1413.3078 |  |  | -2542.1522 |  |  | -3800.6886 |  |  | -5133.9754 |  |  | -6659.3388
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 47.6337 |  |  | 41.1516 |  |  | 3.7934 |  |  | -111.7607 |  |  | -373.3096 |  |  | -800.2997 |  |  | -1340.5808 |  |  | -1824.5573 |  |  | -2129.6968 |  |  | -2080.2302
[13 empty] | C Non choked w/ reducers | 7 |  | 51.0072 |  |  | 106.7901 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 39.9246 |  |  | 78.2121 |  |  | 638.5554 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 51.0072 |  |  | 106.7901 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 46.2772 | 275.5121 |  | 95.1901 | 501.3323 |  | 5500 | 1239.8543 |  | 5500 | 2414.9198 |  | 5500 | 4051.4842 |  | 5500 | 5972.384 |  | 5500 | 7970.1697 |  | 5500 | 9725.1216 |  | 5500 | 11290.5643 |  | 5500 | 12849.7154
[13 empty] | Next iteration flow rate |  |  | 281.0223 | Abs Value of | Flow this | 506.3456 | Abs Value of | Flow this | 1252.2529 | Abs Value of | Flow this | 2439.069 | Abs Value of | Flow this | 4091.999 | Abs Value of | Flow this | 6032.1079 | Abs Value of | Flow this | 8049.8714 | Abs Value of | Flow this | 9822.3729 | Abs Value of | Flow this | 11403.47 | Abs Value of | Flow this | 12978.2125 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.249 |  |  | 48.2574 |  |  | 3.9564 |  |  | -143.9977 |  |  | -508.5839 |  |  | -1171.9365 |  |  | -2131.5482 |  |  | -3201.409 |  |  | -4334.8139 |  |  | -5631.4999
[13 empty] | P2 at this iteration flow rate |  |  | 25.1902 |  |  | 26.3885 |  |  | 35.2487 |  |  | 64.8395 |  |  | 137.7568 |  |  | 270.4273 |  |  | 462.3496 |  |  | 676.3218 |  |  | 903.0028 |  |  | 1162.34
[13 empty] | Delta P at this iteration flow rate |  |  | 29.0588 |  |  | 21.8689 |  |  | -31.2923 |  |  | -208.8372 |  |  | -646.3407 |  |  | -1442.3638 |  |  | -2593.8978 |  |  | -3877.7308 |  |  | -5237.8167 |  |  | -6793.8399
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5422 |  |  | 41.0053 |  |  | 2.9253 |  |  | -114.9102 |  |  | -381.6643 |  |  | -817.1769 |  |  | -1368.255 |  |  | -1861.891 |  |  | -2173.0727 |  |  | -2122.4707
[13 empty] | C Non choked w/ reducers | 7 |  | 52.1385 |  |  | 108.3617 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 40.7623 |  |  | 79.135 |  |  | 734.4288 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 52.1385 |  |  | 108.3617 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 47.4085 | 281.0223 |  | 96.7617 | 506.3456 |  | 5500 | 1252.2529 |  | 5500 | 2439.069 |  | 5500 | 4091.999 |  | 5500 | 6032.1079 |  | 5500 | 8049.8714 |  | 5500 | 9822.3729 |  | 5500 | 11403.47 |  | 5500 | 12978.2125
[13 empty] | Next iteration flow rate |  |  | 286.6428 | Abs Value of | Flow this | 511.409 | Abs Value of | Flow this | 1264.7754 | Abs Value of | Flow this | 2463.4597 | Abs Value of | Flow this | 4132.919 | Abs Value of | Flow this | 6092.429 | Abs Value of | Flow this | 8130.3701 | Abs Value of | Flow this | 9920.5966 | Abs Value of | Flow this | 11517.5046 | Abs Value of | Flow this | 13107.9946 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.1413 |  |  | 48.0833 |  |  | 2.8919 |  |  | -148.036 |  |  | -519.9504 |  |  | -1196.6364 |  |  | -2175.5363 |  |  | -3266.9014 |  |  | -4423.0877 |  |  | -5745.8371
[13 empty] | P2 at this iteration flow rate |  |  | 25.2117 |  |  | 26.4233 |  |  | 35.4616 |  |  | 65.6472 |  |  | 140.0301 |  |  | 275.3673 |  |  | 471.1473 |  |  | 689.4203 |  |  | 920.6575 |  |  | 1185.2074
[13 empty] | Delta P at this iteration flow rate |  |  | 28.9295 |  |  | 21.66 |  |  | -32.5697 |  |  | -213.6832 |  |  | -659.9805 |  |  | -1472.0037 |  |  | -2646.6836 |  |  | -3956.3216 |  |  | -5343.7452 |  |  | -6931.0445
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 47.447 |  |  | 40.856 |  |  | 2.0397 |  |  | -118.123 |  |  | -390.1869 |  |  | -834.3934 |  |  | -1396.4854 |  |  | -1899.9752 |  |  | -2217.3205 |  |  | -2165.5601
[13 empty] | C Non choked w/ reducers | 7 |  | 53.3 |  |  | 109.9717 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 41.6192 |  |  | 80.0722 |  |  | 888.3189 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 53.3 |  |  | 109.9717 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 48.57 | 286.6428 |  | 98.3717 | 511.409 |  | 5500 | 1264.7754 |  | 5500 | 2463.4597 |  | 5500 | 4132.919 |  | 5500 | 6092.429 |  | 5500 | 8130.3701 |  | 5500 | 9920.5966 |  | 5500 | 11517.5046 |  | 5500 | 13107.9946
[13 empty] | Next iteration flow rate |  |  | 292.3756 | Abs Value of | Flow this | 516.5231 | Abs Value of | Flow this | 1277.4232 | Abs Value of | Flow this | 2488.0943 | Abs Value of | Flow this | 4174.2482 | Abs Value of | Flow this | 6153.3533 | Abs Value of | Flow this | 8211.6738 | Abs Value of | Flow this | 10019.8025 | Abs Value of | Flow this | 11632.6797 | Abs Value of | Flow this | 13239.0746 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.0292 |  |  | 47.9058 |  |  | 1.806 |  |  | -152.1556 |  |  | -531.5455 |  |  | -1221.8328 |  |  | -2220.4086 |  |  | -3333.7101 |  |  | -4513.1358 |  |  | -5862.4724
[13 empty] | P2 at this iteration flow rate |  |  | 25.2342 |  |  | 26.4588 |  |  | 35.6788 |  |  | 66.4711 |  |  | 142.3491 |  |  | 280.4066 |  |  | 480.1217 |  |  | 702.782 |  |  | 938.6672 |  |  | 1208.5345
[13 empty] | Delta P at this iteration flow rate |  |  | 28.795 |  |  | 21.447 |  |  | -33.8727 |  |  | -218.6267 |  |  | -673.8946 |  |  | -1502.2394 |  |  | -2700.5303 |  |  | -4036.4921 |  |  | -5451.8029 |  |  | -7071.0069
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 47.3479 |  |  | 40.7038 |  |  | 1.1364 |  |  | -121.4003 |  |  | -398.8808 |  |  | -851.956 |  |  | -1425.2833 |  |  | -1938.8248 |  |  | -2262.4576 |  |  | -2209.5157
[13 empty] | C Non choked w/ reducers | 7 |  | 54.4929 |  |  | 111.6217 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 42.496 |  |  | 81.0241 |  |  | 1202.0316 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 54.4929 |  |  | 111.6217 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 49.7629 | 292.3756 |  | 100.0217 | 516.5231 |  | 5500 | 1277.4232 |  | 5500 | 2488.0943 |  | 5500 | 4174.2482 |  | 5500 | 6153.3533 |  | 5500 | 8211.6738 |  | 5500 | 10019.8025 |  | 5500 | 11632.6797 |  | 5500 | 13239.0746
[13 empty] | Next iteration flow rate |  |  | 298.2231 | Abs Value of | Flow this | 521.6884 | Abs Value of | Flow this | 1290.1974 | Abs Value of | Flow this | 2512.9752 | Abs Value of | Flow this | 4215.9907 | Abs Value of | Flow this | 6214.8868 | Abs Value of | Flow this | 8293.7905 | Abs Value of | Flow this | 10120.0006 | Abs Value of | Flow this | 11749.0065 | Abs Value of | Flow this | 13371.4653 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.9125 |  |  | 47.7247 |  |  | 0.69833 |  |  | -156.3579 |  |  | -543.3735 |  |  | -1247.5357 |  |  | -2266.1828 |  |  | -3401.8617 |  |  | -4604.9938 |  |  | -5981.4522
[13 empty] | P2 at this iteration flow rate |  |  | 25.2575 |  |  | 26.4951 |  |  | 35.9003 |  |  | 67.3116 |  |  | 144.7147 |  |  | 285.5471 |  |  | 489.2766 |  |  | 716.4123 |  |  | 957.0388 |  |  | 1232.3304
[13 empty] | Delta P at this iteration flow rate |  |  | 28.655 |  |  | 21.2296 |  |  | -35.202 |  |  | -223.6695 |  |  | -688.0883 |  |  | -1533.0828 |  |  | -2755.4594 |  |  | -4118.274 |  |  | -5562.0326 |  |  | -7213.7826
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 47.2449 |  |  | 40.5485 |  |  | 0.21486 |  |  | -124.7436 |  |  | -407.7494 |  |  | -869.8715 |  |  | -1454.66 |  |  | -1978.4552 |  |  | -2308.502 |  |  | -2254.3548
[13 empty] | C Non choked w/ reducers | 7 |  | 55.7183 |  |  | 113.3135 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 43.3931 |  |  | 81.9909 |  |  | 2792.0226 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 55.7183 |  |  | 113.3135 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 50.9883 | 298.2231 |  | 101.7135 | 521.6884 |  | 5500 | 1290.1974 |  | 5500 | 2512.9752 |  | 5500 | 4215.9907 |  | 5500 | 6214.8868 |  | 5500 | 8293.7905 |  | 5500 | 10120.0006 |  | 5500 | 11749.0065 |  | 5500 | 13371.4653
[13 empty] | Next iteration flow rate |  |  | 304.1876 | Abs Value of | Flow this | 526.9052 | Abs Value of | Flow this | 1303.0994 | Abs Value of | Flow this | 2538.105 | Abs Value of | Flow this | 4258.1506 | Abs Value of | Flow this | 6277.0357 | Abs Value of | Flow this | 8376.7284 | Abs Value of | Flow this | 10221.2006 | Abs Value of | Flow this | 11866.4966 | Abs Value of | Flow this | 13505.18 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.7912 |  |  | 47.5399 |  |  | -0.43164 |  |  | -160.6447 |  |  | -555.4394 |  |  | -1273.7551 |  |  | -2312.8771 |  |  | -3471.3831 |  |  | -4698.6982 |  |  | -6102.8234
[13 empty] | P2 at this iteration flow rate |  |  | 25.2818 |  |  | 26.532 |  |  | 36.1263 |  |  | 68.1689 |  |  | 147.1279 |  |  | 290.791 |  |  | 498.6154 |  |  | 730.3166 |  |  | 975.7796 |  |  | 1256.6047
[13 empty] | Delta P at this iteration flow rate |  |  | 28.5094 |  |  | 21.0079 |  |  | -36.558 |  |  | -228.8137 |  |  | -702.5672 |  |  | -1564.5462 |  |  | -2811.4926 |  |  | -4201.6997 |  |  | -5674.4778 |  |  | -7359.428
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 47.1376 |  |  | 40.3901 |  |  | -0.72517 |  |  | -128.154 |  |  | -416.7963 |  |  | -888.1472 |  |  | -1484.6272 |  |  | -2018.8823 |  |  | -2355.4719 |  |  | -2300.0951
[13 empty] | C Non choked w/ reducers | 7 |  | 56.9776 |  |  | 115.0489 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 44.3113 |  |  | 82.973 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 56.9776 |  |  | 115.0489 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 52.2476 | 304.1876 |  | 103.4489 | 526.9052 |  | 5500 | 1303.0994 |  | 5500 | 2538.105 |  | 5500 | 4258.1506 |  | 5500 | 6277.0357 |  | 5500 | 8376.7284 |  | 5500 | 10221.2006 |  | 5500 | 11866.4966 |  | 5500 | 13505.18
[13 empty] | Next iteration flow rate |  |  | 310.2714 | Abs Value of | Flow this | 532.1743 | Abs Value of | Flow this | 1316.1304 | Abs Value of | Flow this | 2563.486 | Abs Value of | Flow this | 4300.7321 | Abs Value of | Flow this | 6339.806 | Abs Value of | Flow this | 8460.4957 | Abs Value of | Flow this | 10323.4126 | Abs Value of | Flow this | 11985.1615 | Abs Value of | Flow this | 13640.2318 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.6649 |  |  | 47.3515 |  |  | -1.5843 |  |  | -165.0177 |  |  | -567.7477 |  |  | -1300.5016 |  |  | -2360.51 |  |  | -3542.3019 |  |  | -4794.286 |  |  | -6226.6341
[13 empty] | P2 at this iteration flow rate |  |  | 25.307 |  |  | 26.5697 |  |  | 36.3569 |  |  | 69.0435 |  |  | 149.5895 |  |  | 296.1403 |  |  | 508.142 |  |  | 744.5004 |  |  | 994.8972 |  |  | 1281.3668
[13 empty] | Delta P at this iteration flow rate |  |  | 28.3579 |  |  | 20.7818 |  |  | -37.9412 |  |  | -234.0612 |  |  | -717.3373 |  |  | -1596.642 |  |  | -2868.652 |  |  | -4286.8023 |  |  | -5789.1833 |  |  | -7508.0009
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 47.0261 |  |  | 40.2284 |  |  | -1.6841 |  |  | -131.633 |  |  | -426.0251 |  |  | -906.7902 |  |  | -1515.1967 |  |  | -2060.1219 |  |  | -2403.3859 |  |  | -2346.7548
[13 empty] | C Non choked w/ reducers | 7 |  | 58.2722 |  |  | 116.83 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 45.2511 |  |  | 83.9709 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 58.2722 |  |  | 116.83 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 53.5422 | 310.2714 |  | 105.23 | 532.1743 |  | 5500 | 1316.1304 |  | 5500 | 2563.486 |  | 5500 | 4300.7321 |  | 5500 | 6339.806 |  | 5500 | 8460.4957 |  | 5500 | 10323.4126 |  | 5500 | 11985.1615 |  | 5500 | 13640.2318
[13 empty] | Next iteration flow rate |  |  | 316.4768 | Abs Value of | Flow this | 537.496 | Abs Value of | Flow this | 1329.2917 | Abs Value of | Flow this | 2589.1209 | Abs Value of | Flow this | 4343.7394 | Abs Value of | Flow this | 6403.2041 | Abs Value of | Flow this | 8545.1007 | Abs Value of | Flow this | 10426.6467 | Abs Value of | Flow this | 12105.0131 | Abs Value of | Flow this | 13776.6341 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.5336 |  |  | 47.1592 |  |  | -2.7602 |  |  | -169.4786 |  |  | -580.3035 |  |  | -1327.7857 |  |  | -2409.1002 |  |  | -3614.6462 |  |  | -4891.7952 |  |  | -6352.9335
[13 empty] | P2 at this iteration flow rate |  |  | 25.3333 |  |  | 26.6082 |  |  | 36.592 |  |  | 69.9357 |  |  | 152.1007 |  |  | 301.5971 |  |  | 517.86 |  |  | 758.9692 |  |  | 1014.399 |  |  | 1306.6267
[13 empty] | Delta P at this iteration flow rate |  |  | 28.2003 |  |  | 20.5511 |  |  | -39.3522 |  |  | -239.4143 |  |  | -732.4041 |  |  | -1629.3829 |  |  | -2926.9603 |  |  | -4373.6155 |  |  | -5906.1942 |  |  | -7659.5602
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.91 |  |  | 40.0636 |  |  | -2.6623 |  |  | -135.182 |  |  | -435.4393 |  |  | -925.8079 |  |  | -1546.3807 |  |  | -2102.1905 |  |  | -2452.263 |  |  | -2394.3524
[13 empty] | C Non choked w/ reducers | 7 |  | 59.6035 |  |  | 118.6587 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 46.2132 |  |  | 84.985 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 59.6035 |  |  | 118.6587 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 54.8735 | 316.4768 |  | 107.0587 | 537.496 |  | 5500 | 1329.2917 |  | 5500 | 2589.1209 |  | 5500 | 4343.7394 |  | 5500 | 6403.2041 |  | 5500 | 8545.1007 |  | 5500 | 10426.6467 |  | 5500 | 12105.0131 |  | 5500 | 13776.6341
[13 empty] | Next iteration flow rate |  |  | 322.8063 | Abs Value of | Flow this | 542.871 | Abs Value of | Flow this | 1342.5846 | Abs Value of | Flow this | 2615.0121 | Abs Value of | Flow this | 4387.1768 | Abs Value of | Flow this | 6467.2361 | Abs Value of | Flow this | 8630.5517 | Abs Value of | Flow this | 10530.9132 | Abs Value of | Flow this | 12226.0633 | Abs Value of | Flow this | 13914.4005 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.3969 |  |  | 46.9631 |  |  | -3.9597 |  |  | -174.0291 |  |  | -593.1116 |  |  | -1355.6182 |  |  | -2458.6672 |  |  | -3688.4446 |  |  | -4991.2643 |  |  | -6481.7715
[13 empty] | P2 at this iteration flow rate |  |  | 25.3606 |  |  | 26.6474 |  |  | 36.8319 |  |  | 70.8458 |  |  | 154.6623 |  |  | 307.1636 |  |  | 527.7734 |  |  | 773.7289 |  |  | 1034.2929 |  |  | 1332.3943
[13 empty] | Delta P at this iteration flow rate |  |  | 28.0363 |  |  | 20.3157 |  |  | -40.7916 |  |  | -244.8749 |  |  | -747.7739 |  |  | -1662.7819 |  |  | -2986.4406 |  |  | -4462.1736 |  |  | -6025.5572 |  |  | -7814.1658
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7893 |  |  | 39.8954 |  |  | -3.6602 |  |  | -138.8022 |  |  | -445.0428 |  |  | -945.2079 |  |  | -1578.1915 |  |  | -2145.1046 |  |  | -2502.1225 |  |  | -2442.9067
[13 empty] | C Non choked w/ reducers | 7 |  | 60.9731 |  |  | 120.5374 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 47.1982 |  |  | 86.0155 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 60.9731 |  |  | 120.5374 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 56.2431 | 322.8063 |  | 108.9374 | 542.871 |  | 5500 | 1342.5846 |  | 5500 | 2615.0121 |  | 5500 | 4387.1768 |  | 5500 | 6467.2361 |  | 5500 | 8630.5517 |  | 5500 | 10530.9132 |  | 5500 | 12226.0633 |  | 5500 | 13914.4005
[13 empty] | Next iteration flow rate |  |  | 329.2624 | Abs Value of | Flow this | 548.2997 | Abs Value of | Flow this | 1356.0104 | Abs Value of | Flow this | 2641.1622 | Abs Value of | Flow this | 4431.0486 | Abs Value of | Flow this | 6531.9085 | Abs Value of | Flow this | 8716.8572 | Abs Value of | Flow this | 10636.2223 | Abs Value of | Flow this | 12348.3239 | Abs Value of | Flow this | 14053.5445 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.2548 |  |  | 46.7631 |  |  | -5.1833 |  |  | -178.6711 |  |  | -606.1771 |  |  | -1384.0102 |  |  | -2509.2304 |  |  | -3763.7264 |  |  | -5092.7327 |  |  | -6613.1991
[13 empty] | P2 at this iteration flow rate |  |  | 25.389 |  |  | 26.6874 |  |  | 37.0767 |  |  | 71.7742 |  |  | 157.2754 |  |  | 312.842 |  |  | 537.8861 |  |  | 788.7853 |  |  | 1054.5865 |  |  | 1358.6798
[13 empty] | Delta P at this iteration flow rate |  |  | 27.8657 |  |  | 20.0757 |  |  | -42.26 |  |  | -250.4453 |  |  | -763.4525 |  |  | -1696.8522 |  |  | -3047.1165 |  |  | -4552.5117 |  |  | -6147.3193 |  |  | -7971.8789
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6637 |  |  | 39.7239 |  |  | -4.6781 |  |  | -142.4953 |  |  | -454.8393 |  |  | -964.9978 |  |  | -1610.6416 |  |  | -2188.8813 |  |  | -2552.9842 |  |  | -2492.4369
[13 empty] | C Non choked w/ reducers | 7 |  | 62.3827 |  |  | 122.4686 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 48.2069 |  |  | 87.0631 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 62.3827 |  |  | 122.4686 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 57.6527 | 329.2624 |  | 110.8686 | 548.2997 |  | 5500 | 1356.0104 |  | 5500 | 2641.1622 |  | 5500 | 4431.0486 |  | 5500 | 6531.9085 |  | 5500 | 8716.8572 |  | 5500 | 10636.2223 |  | 5500 | 12348.3239 |  | 5500 | 14053.5445
[13 empty] | Next iteration flow rate |  |  | 335.8477 | Abs Value of | Flow this | 553.7827 | Abs Value of | Flow this | 1369.5705 | Abs Value of | Flow this | 2667.5738 | Abs Value of | Flow this | 4475.3591 | Abs Value of | Flow this | 6597.2276 | Abs Value of | Flow this | 8804.0258 | Abs Value of | Flow this | 10742.5845 | Abs Value of | Flow this | 12471.8071 | Abs Value of | Flow this | 14194.0799 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.1068 |  |  | 46.559 |  |  | -6.4315 |  |  | -183.4064 |  |  | -619.5053 |  |  | -1412.9728 |  |  | -2560.8099 |  |  | -3840.5213 |  |  | -5196.2407 |  |  | -6747.2684
[13 empty] | P2 at this iteration flow rate |  |  | 25.4186 |  |  | 26.7282 |  |  | 37.3263 |  |  | 72.7213 |  |  | 159.9411 |  |  | 318.6346 |  |  | 548.202 |  |  | 804.1443 |  |  | 1075.2881 |  |  | 1385.4937
[13 empty] | Delta P at this iteration flow rate |  |  | 27.6882 |  |  | 19.8308 |  |  | -43.7578 |  |  | -256.1277 |  |  | -779.4464 |  |  | -1731.6074 |  |  | -3109.0119 |  |  | -4644.6655 |  |  | -6271.5288 |  |  | -8132.7621
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.533 |  |  | 39.5489 |  |  | -5.7164 |  |  | -146.2625 |  |  | -464.8327 |  |  | -985.1855 |  |  | -1643.7441 |  |  | -2233.538 |  |  | -2604.8682 |  |  | -2542.9627
[13 empty] | C Non choked w/ reducers | 7 |  | 63.834 |  |  | 124.4546 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 49.2401 |  |  | 88.1281 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 63.834 |  |  | 124.4546 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 59.104 | 335.8477 |  | 112.8546 | 553.7827 |  | 5500 | 1369.5705 |  | 5500 | 2667.5738 |  | 5500 | 4475.3591 |  | 5500 | 6597.2276 |  | 5500 | 8804.0258 |  | 5500 | 10742.5845 |  | 5500 | 12471.8071 |  | 5500 | 14194.0799
[13 empty] | Next iteration flow rate |  |  | 342.5647 | Abs Value of | Flow this | 559.3205 | Abs Value of | Flow this | 1383.2662 | Abs Value of | Flow this | 2694.2496 | Abs Value of | Flow this | 4520.1127 | Abs Value of | Flow this | 6663.1998 | Abs Value of | Flow this | 8892.066 | Abs Value of | Flow this | 10850.0104 | Abs Value of | Flow this | 12596.5252 | Abs Value of | Flow this | 14336.0207 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 52.9529 |  |  | 46.3508 |  |  | -7.7048 |  |  | -188.2369 |  |  | -633.1014 |  |  | -1442.5176 |  |  | -2613.4262 |  |  | -3918.8598 |  |  | -5301.8291 |  |  | -6884.0325
[13 empty] | P2 at this iteration flow rate |  |  | 25.4494 |  |  | 26.7698 |  |  | 37.581 |  |  | 73.6874 |  |  | 162.6603 |  |  | 324.5435 |  |  | 558.7252 |  |  | 819.812 |  |  | 1096.4058 |  |  | 1412.8465
[13 empty] | Delta P at this iteration flow rate |  |  | 27.5035 |  |  | 19.581 |  |  | -45.2857 |  |  | -261.9242 |  |  | -795.7616 |  |  | -1767.0611 |  |  | -3172.1515 |  |  | -4738.6717 |  |  | -6398.235 |  |  | -8296.879
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.397 |  |  | 39.3703 |  |  | -6.7757 |  |  | -150.1055 |  |  | -475.027 |  |  | -1005.779 |  |  | -1677.5118 |  |  | -2279.0922 |  |  | -2657.795 |  |  | -2594.504
[13 empty] | C Non choked w/ reducers | 7 |  | 65.3289 |  |  | 126.4985 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 50.2984 |  |  | 89.2109 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 65.3289 |  |  | 126.4985 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 60.5989 | 342.5647 |  | 114.8985 | 559.3205 |  | 5500 | 1383.2662 |  | 5500 | 2694.2496 |  | 5500 | 4520.1127 |  | 5500 | 6663.1998 |  | 5500 | 8892.066 |  | 5500 | 10850.0104 |  | 5500 | 12596.5252 |  | 5500 | 14336.0207
[13 empty] | Next iteration flow rate |  |  | 349.4159 | Abs Value of | Flow this | 564.9137 | Abs Value of | Flow this | 1397.0989 | Abs Value of | Flow this | 2721.1921 | Abs Value of | Flow this | 4565.3138 | Abs Value of | Flow this | 6729.8318 | Abs Value of | Flow this | 8980.9867 | Abs Value of | Flow this | 10958.5105 | Abs Value of | Flow this | 12722.4905 | Abs Value of | Flow this | 14479.3809 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 52.7928 |  |  | 46.1384 |  |  | -9.0037 |  |  | -193.1644 |  |  | -646.9707 |  |  | -1472.6562 |  |  | -2667.1001 |  |  | -3998.7729 |  |  | -5409.5399 |  |  | -7023.5456
[13 empty] | P2 at this iteration flow rate |  |  | 25.4814 |  |  | 26.8123 |  |  | 37.8407 |  |  | 74.6729 |  |  | 165.4341 |  |  | 330.5712 |  |  | 569.46 |  |  | 835.7946 |  |  | 1117.948 |  |  | 1440.7491
[13 empty] | Delta P at this iteration flow rate |  |  | 27.3114 |  |  | 19.3261 |  |  | -46.8444 |  |  | -267.8373 |  |  | -812.4049 |  |  | -1803.2274 |  |  | -3236.5601 |  |  | -4834.5675 |  |  | -6527.4879 |  |  | -8464.2947
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.2556 |  |  | 39.1882 |  |  | -7.8562 |  |  | -154.0257 |  |  | -485.4262 |  |  | -1026.7864 |  |  | -1711.9584 |  |  | -2325.562 |  |  | -2711.7857 |  |  | -2647.0814
[13 empty] | C Non choked w/ reducers | 7 |  | 66.8694 |  |  | 128.6031 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 51.3828 |  |  | 90.3121 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 66.8694 |  |  | 128.6031 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 62.1394 | 349.4159 |  | 117.0031 | 564.9137 |  | 5500 | 1397.0989 |  | 5500 | 2721.1921 |  | 5500 | 4565.3138 |  | 5500 | 6729.8318 |  | 5500 | 8980.9867 |  | 5500 | 10958.5105 |  | 5500 | 12722.4905 |  | 5500 | 14479.3809
[13 empty] | Next iteration flow rate |  |  | 356.4043 | Abs Value of | Flow this | 570.5629 | Abs Value of | Flow this | 1411.0699 | Abs Value of | Flow this | 2748.404 | Abs Value of | Flow this | 4610.9669 | Abs Value of | Flow this | 6797.1302 | Abs Value of | Flow this | 9070.7965 | Abs Value of | Flow this | 11068.0956 | Abs Value of | Flow this | 12849.7154 | Abs Value of | Flow this | 14624.1747 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 52.6262 |  |  | 45.9218 |  |  | -10.3286 |  |  | -198.1911 |  |  | -661.1188 |  |  | -1503.4006 |  |  | -2721.8528 |  |  | -4080.2922 |  |  | -5519.4157 |  |  | -7165.8629
[13 empty] | P2 at this iteration flow rate |  |  | 25.5148 |  |  | 26.8556 |  |  | 38.1057 |  |  | 75.6782 |  |  | 168.2638 |  |  | 336.7201 |  |  | 580.4106 |  |  | 852.0984 |  |  | 1139.9231 |  |  | 1469.2126
[13 empty] | Delta P at this iteration flow rate |  |  | 27.1115 |  |  | 19.0662 |  |  | -48.4344 |  |  | -273.8693 |  |  | -829.3826 |  |  | -1840.1207 |  |  | -3302.2634 |  |  | -4932.3907 |  |  | -6659.3388 |  |  | -8635.0754
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.1084 |  |  | 39.0024 |  |  | -8.9585 |  |  | -158.0248 |  |  | -496.0344 |  |  | -1048.2161 |  |  | -1747.0972 |  |  | -2372.9659 |  |  | -2766.8616 |  |  | -2700.7155
[13 empty] | C Non choked w/ reducers | 7 |  | 68.4578 |  |  | 130.7716 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 52.494 |  |  | 91.4322 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 68.4578 |  |  | 130.7716 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 63.7278 | 356.4043 |  | 119.1716 | 570.5629 |  | 5500 | 1411.0699 |  | 5500 | 2748.404 |  | 5500 | 4610.9669 |  | 5500 | 6797.1302 |  | 5500 | 9070.7965 |  | 5500 | 11068.0956 |  | 5500 | 12849.7154 |  | 5500 | 14624.1747
[13 empty] | Next iteration flow rate |  |  | 363.5323 | Abs Value of | Flow this | 576.2685 | Abs Value of | Flow this | 1425.1806 | Abs Value of | Flow this | 2775.888 | Abs Value of | Flow this | 4657.0766 | Abs Value of | Flow this | 6865.1015 | Abs Value of | Flow this | 9161.5045 | Abs Value of | Flow this | 11178.7765 | Abs Value of | Flow this | 12978.2125 | Abs Value of | Flow this | 14770.4165 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 52.4529 |  |  | 45.7008 |  |  | -11.6803 |  |  | -203.3187 |  |  | -675.5514 |  |  | -1534.7629 |  |  | -2777.7061 |  |  | -4163.4501 |  |  | -5631.4999 |  |  | -7311.0407
[13 empty] | P2 at this iteration flow rate |  |  | 25.5494 |  |  | 26.8998 |  |  | 38.3761 |  |  | 76.7037 |  |  | 171.1503 |  |  | 342.9926 |  |  | 591.5812 |  |  | 868.73 |  |  | 1162.34 |  |  | 1498.2481
[13 empty] | Delta P at this iteration flow rate |  |  | 26.9035 |  |  | 18.801 |  |  | -50.0563 |  |  | -280.0225 |  |  | -846.7016 |  |  | -1877.7555 |  |  | -3369.2873 |  |  | -5032.1801 |  |  | -6793.8399 |  |  | -8809.2889
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.9552 |  |  | 38.8129 |  |  | -10.0829 |  |  | -162.1042 |  |  | -506.8558 |  |  | -1070.0764 |  |  | -1782.9424 |  |  | -2421.3227 |  |  | -2823.0446 |  |  | -2755.4277
[13 empty] | C Non choked w/ reducers | 7 |  | 70.0963 |  |  | 133.0075 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 53.633 |  |  | 92.5717 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 70.0963 |  |  | 133.0075 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 65.3663 | 363.5323 |  | 121.4075 | 576.2685 |  | 5500 | 1425.1806 |  | 5500 | 2775.888 |  | 5500 | 4657.0766 |  | 5500 | 6865.1015 |  | 5500 | 9161.5045 |  | 5500 | 11178.7765 |  | 5500 | 12978.2125 |  | 5500 | 14770.4165
[13 empty] | Next iteration flow rate |  |  | 370.803 | Abs Value of | Flow this | 582.0312 | Abs Value of | Flow this | 1439.4324 | Abs Value of | Flow this | 2803.6469 | Abs Value of | Flow this | 4703.6474 | Abs Value of | Flow this | 6933.7525 | Abs Value of | Flow this | 9253.1195 | Abs Value of | Flow this | 11290.5643 | Abs Value of | Flow this | 13107.9946 | Abs Value of | Flow this | 14918.1206 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 52.2726 |  |  | 45.4754 |  |  | -13.0591 |  |  | -208.5494 |  |  | -690.2739 |  |  | -1566.7557 |  |  | -2834.682 |  |  | -4248.2795 |  |  | -5745.8371 |  |  | -7459.1366
[13 empty] | P2 at this iteration flow rate |  |  | 25.5855 |  |  | 26.9449 |  |  | 38.6518 |  |  | 77.7499 |  |  | 174.0948 |  |  | 349.3911 |  |  | 602.9764 |  |  | 885.6959 |  |  | 1185.2074 |  |  | 1527.8673
[13 empty] | Delta P at this iteration flow rate |  |  | 26.6871 |  |  | 18.5305 |  |  | -51.7109 |  |  | -286.2993 |  |  | -864.3687 |  |  | -1916.1468 |  |  | -3437.6584 |  |  | -5133.9754 |  |  | -6931.0445 |  |  | -8987.004
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.7959 |  |  | 38.6196 |  |  | -11.2299 |  |  | -166.2656 |  |  | -517.8948 |  |  | -1092.3762 |  |  | -1819.5081 |  |  | -2470.6514 |  |  | -2880.3568 |  |  | -2811.2396
[13 empty] | C Non choked w/ reducers | 7 |  | 71.7875 |  |  | 135.3146 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 54.8008 |  |  | 93.7311 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 71.7875 |  |  | 135.3146 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 67.0575 | 370.803 |  | 123.7146 | 582.0312 |  | 5500 | 1439.4324 |  | 5500 | 2803.6469 |  | 5500 | 4703.6474 |  | 5500 | 6933.7525 |  | 5500 | 9253.1195 |  | 5500 | 11290.5643 |  | 5500 | 13107.9946 |  | 5500 | 14918.1206
[13 empty] | Next iteration flow rate |  |  | 378.2191 | Abs Value of | Flow this | 587.8515 | Abs Value of | Flow this | 1453.8267 | Abs Value of | Flow this | 2831.6834 | Abs Value of | Flow this | 4750.6838 | Abs Value of | Flow this | 7003.09 | Abs Value of | Flow this | 9345.6507 | Abs Value of | Flow this | 11403.47 | Abs Value of | Flow this | 13239.0746 | Abs Value of | Flow this | 15067.3018 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 52.085 |  |  | 45.2454 |  |  | -14.4656 |  |  | -213.8853 |  |  | -705.2925 |  |  | -1599.3915 |  |  | -2892.8031 |  |  | -4334.8139 |  |  | -5862.4724 |  |  | -7610.2093
[13 empty] | P2 at this iteration flow rate |  |  | 25.623 |  |  | 26.9909 |  |  | 38.9331 |  |  | 78.8171 |  |  | 177.0985 |  |  | 355.9183 |  |  | 614.6006 |  |  | 903.0028 |  |  | 1208.5345 |  |  | 1558.0819
[13 empty] | Delta P at this iteration flow rate |  |  | 26.462 |  |  | 18.2545 |  |  | -53.3987 |  |  | -292.7024 |  |  | -882.391 |  |  | -1955.3098 |  |  | -3507.4038 |  |  | -5237.8167 |  |  | -7071.0069 |  |  | -9168.2912
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.6302 |  |  | 38.4224 |  |  | -12.4 |  |  | -170.5106 |  |  | -529.1556 |  |  | -1115.1242 |  |  | -1856.8087 |  |  | -2520.9716 |  |  | -2938.8209 |  |  | -2868.1733
[13 empty] | C Non choked w/ reducers | 7 |  | 73.5341 |  |  | 137.6968 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 55.9982 |  |  | 94.9111 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 73.5341 |  |  | 137.6968 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 68.8041 | 378.2191 |  | 126.0968 | 587.8515 |  | 5500 | 1453.8267 |  | 5500 | 2831.6834 |  | 5500 | 4750.6838 |  | 5500 | 7003.09 |  | 5500 | 9345.6507 |  | 5500 | 11403.47 |  | 5500 | 13239.0746 |  | 5500 | 15067.3018
[13 empty] | Next iteration flow rate |  |  | 385.7834 | Abs Value of | Flow this | 593.73 | Abs Value of | Flow this | 1468.365 | Abs Value of | Flow this | 2860.0002 | Abs Value of | Flow this | 4798.1907 | Abs Value of | Flow this | 7073.1209 | Abs Value of | Flow this | 9439.1072 | Abs Value of | Flow this | 11517.5046 | Abs Value of | Flow this | 13371.4653 | Abs Value of | Flow this | 15217.9749 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 51.8898 |  |  | 45.0109 |  |  | -15.9003 |  |  | -219.3284 |  |  | -720.6129 |  |  | -1632.6833 |  |  | -2952.0925 |  |  | -4423.0877 |  |  | -5981.4522 |  |  | -7764.3185
[13 empty] | P2 at this iteration flow rate |  |  | 25.662 |  |  | 27.0378 |  |  | 39.2201 |  |  | 79.9057 |  |  | 180.1626 |  |  | 362.5767 |  |  | 626.4585 |  |  | 920.6575 |  |  | 1232.3304 |  |  | 1588.9037
[13 empty] | Delta P at this iteration flow rate |  |  | 26.2278 |  |  | 17.973 |  |  | -55.1204 |  |  | -299.2341 |  |  | -900.7754 |  |  | -1995.2599 |  |  | -3578.551 |  |  | -5343.7452 |  |  | -7213.7826 |  |  | -9353.2222
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.4577 |  |  | 38.2213 |  |  | -13.5936 |  |  | -174.841 |  |  | -540.6428 |  |  | -1138.3295 |  |  | -1894.8591 |  |  | -2572.3032 |  |  | -2998.4603 |  |  | -2926.2514
[13 empty] | C Non choked w/ reducers | 7 |  | 75.3389 |  |  | 140.1587 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 57.2264 |  |  | 96.1121 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 75.3389 |  |  | 140.1587 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 70.6089 | 385.7834 |  | 128.5587 | 593.73 |  | 5500 | 1468.365 |  | 5500 | 2860.0002 |  | 5500 | 4798.1907 |  | 5500 | 7073.1209 |  | 5500 | 9439.1072 |  | 5500 | 11517.5046 |  | 5500 | 13371.4653 |  | 5500 | 15217.9749
[13 empty] | Next iteration flow rate |  |  | 393.4991 | Abs Value of | Flow this | 599.6673 | Abs Value of | Flow this | 1483.0486 | Abs Value of | Flow this | 2888.6002 | Abs Value of | Flow this | 4846.1726 | Abs Value of | Flow this | 7143.8521 | Abs Value of | Flow this | 9533.4983 | Abs Value of | Flow this | 11632.6797 | Abs Value of | Flow this | 13505.18 | Abs Value of | Flow this | 15370.1546 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 51.6868 |  |  | 44.7716 |  |  | -17.3639 |  |  | -224.8809 |  |  | -736.2412 |  |  | -1666.6442 |  |  | -3012.5736 |  |  | -4513.1358 |  |  | -6102.8234 |  |  | -7921.5253
[13 empty] | P2 at this iteration flow rate |  |  | 25.7026 |  |  | 27.0857 |  |  | 39.5128 |  |  | 81.0162 |  |  | 183.2882 |  |  | 369.3688 |  |  | 638.5547 |  |  | 938.6672 |  |  | 1256.6047 |  |  | 1620.3451
[13 empty] | Delta P at this iteration flow rate |  |  | 25.9841 |  |  | 17.6859 |  |  | -56.8767 |  |  | -305.8971 |  |  | -919.5294 |  |  | -2036.0131 |  |  | -3651.1283 |  |  | -5451.8029 |  |  | -7359.428 |  |  | -9541.8704
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.2783 |  |  | 38.0161 |  |  | -14.8112 |  |  | -179.2584 |  |  | -552.3609 |  |  | -1162.0011 |  |  | -1933.6743 |  |  | -2624.6666 |  |  | -3059.2983 |  |  | -2985.4969
[13 empty] | C Non choked w/ reducers | 7 |  | 77.2052 |  |  | 142.7049 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 58.4865 |  |  | 97.3349 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 77.2052 |  |  | 142.7049 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 72.4752 | 393.4991 |  | 131.1049 | 599.6673 |  | 5500 | 1483.0486 |  | 5500 | 2888.6002 |  | 5500 | 4846.1726 |  | 5500 | 7143.8521 |  | 5500 | 9533.4983 |  | 5500 | 11632.6797 |  | 5500 | 13505.18 |  | 5500 | 15370.1546
[13 empty] | Next iteration flow rate |  |  | 401.3691 | Abs Value of | Flow this | 605.664 | Abs Value of | Flow this | 1497.8791 | Abs Value of | Flow this | 2917.4862 | Abs Value of | Flow this | 4894.6343 | Abs Value of | Flow this | 7215.2906 | Abs Value of | Flow this | 9628.8333 | Abs Value of | Flow this | 11749.0065 | Abs Value of | Flow this | 13640.2318 | Abs Value of | Flow this | 15523.8561 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 51.4755 |  |  | 44.5275 |  |  | -18.857 |  |  | -230.545 |  |  | -752.1837 |  |  | -1701.2878 |  |  | -3074.2703 |  |  | -4604.9938 |  |  | -6226.6341 |  |  | -8081.892
[13 empty] | P2 at this iteration flow rate |  |  | 25.7449 |  |  | 27.1345 |  |  | 39.8114 |  |  | 82.149 |  |  | 186.4767 |  |  | 376.2976 |  |  | 650.8941 |  |  | 957.0388 |  |  | 1281.3668 |  |  | 1652.4184
[13 empty] | Delta P at this iteration flow rate |  |  | 25.7306 |  |  | 17.393 |  |  | -58.6684 |  |  | -312.6941 |  |  | -938.6604 |  |  | -2077.5854 |  |  | -3725.1644 |  |  | -5562.0326 |  |  | -7508.0009 |  |  | -9734.3104
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.0917 |  |  | 37.8067 |  |  | -16.0532 |  |  | -183.7646 |  |  | -564.3144 |  |  | -1186.1486 |  |  | -1973.2697 |  |  | -2678.0825 |  |  | -3121.3592 |  |  | -3045.9332
[13 empty] | C Non choked w/ reducers | 7 |  | 79.1363 |  |  | 145.3406 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 59.7796 |  |  | 98.58 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 79.1363 |  |  | 145.3406 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 74.4063 | 401.3691 |  | 133.7406 | 605.664 |  | 5500 | 1497.8791 |  | 5500 | 2917.4862 |  | 5500 | 4894.6343 |  | 5500 | 7215.2906 |  | 5500 | 9628.8333 |  | 5500 | 11749.0065 |  | 5500 | 13640.2318 |  | 5500 | 15523.8561
[13 empty] | Next iteration flow rate |  |  | 409.3965 | Abs Value of | Flow this | 611.7206 | Abs Value of | Flow this | 1512.8579 | Abs Value of | Flow this | 2946.6611 | Abs Value of | Flow this | 4943.5807 | Abs Value of | Flow this | 7287.4435 | Abs Value of | Flow this | 9725.1216 | Abs Value of | Flow this | 11866.4966 | Abs Value of | Flow this | 13776.6341 | Abs Value of | Flow this | 15679.0947 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 51.2557 |  |  | 44.2784 |  |  | -20.38 |  |  | -236.323 |  |  | -768.4466 |  |  | -1736.6277 |  |  | -3137.2072 |  |  | -4698.6982 |  |  | -6352.9335 |  |  | -8245.4821
[13 empty] | P2 at this iteration flow rate |  |  | 25.7889 |  |  | 27.1843 |  |  | 40.116 |  |  | 83.3046 |  |  | 189.7293 |  |  | 383.3655 |  |  | 663.4814 |  |  | 975.7796 |  |  | 1306.6267 |  |  | 1685.1364
[13 empty] | Delta P at this iteration flow rate |  |  | 25.4669 |  |  | 17.0941 |  |  | -60.496 |  |  | -319.6276 |  |  | -958.1759 |  |  | -2119.9932 |  |  | -3800.6886 |  |  | -5674.4778 |  |  | -7659.5602 |  |  | -9930.6185
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.8975 |  |  | 37.5932 |  |  | -17.3202 |  |  | -188.3614 |  |  | -576.5083 |  |  | -1210.7814 |  |  | -2013.6609 |  |  | -2732.5721 |  |  | -3184.6676 |  |  | -3107.5842
[13 empty] | C Non choked w/ reducers | 7 |  | 81.136 |  |  | 148.0714 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 61.1069 |  |  | 99.8482 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 81.136 |  |  | 148.0714 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 76.406 | 409.3965 |  | 136.4714 | 611.7206 |  | 5500 | 1512.8579 |  | 5500 | 2946.6611 |  | 5500 | 4943.5807 |  | 5500 | 7287.4435 |  | 5500 | 9725.1216 |  | 5500 | 11866.4966 |  | 5500 | 13776.6341 |  | 5500 | 15679.0947
[13 empty] | Next iteration flow rate |  |  | 417.5844 | Abs Value of | Flow this | 617.8378 | Abs Value of | Flow this | 1527.9865 | Abs Value of | Flow this | 2976.1277 | Abs Value of | Flow this | 4993.0165 | Abs Value of | Flow this | 7360.318 | Abs Value of | Flow this | 9822.3729 | Abs Value of | Flow this | 11985.1615 | Abs Value of | Flow this | 13914.4005 | Abs Value of | Flow this | 15835.8857 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 51.027 |  |  | 44.0244 |  |  | -21.9337 |  |  | -242.2171 |  |  | -785.0364 |  |  | -1772.6779 |  |  | -3201.409 |  |  | -4794.286 |  |  | -6481.7715 |  |  | -8412.3603
[13 empty] | P2 at this iteration flow rate |  |  | 25.8346 |  |  | 27.2351 |  |  | 40.4267 |  |  | 84.4834 |  |  | 193.0473 |  |  | 390.5756 |  |  | 676.3218 |  |  | 994.8972 |  |  | 1332.3943 |  |  | 1718.5121
[13 empty] | Delta P at this iteration flow rate |  |  | 25.1924 |  |  | 16.7893 |  |  | -62.3604 |  |  | -326.7006 |  |  | -978.0836 |  |  | -2163.2535 |  |  | -3877.7308 |  |  | -5789.1833 |  |  | -7814.1658 |  |  | -10130.8723
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.6954 |  |  | 37.3754 |  |  | -18.6127 |  |  | -193.0505 |  |  | -588.9473 |  |  | -1235.9094 |  |  | -2054.864 |  |  | -2788.1569 |  |  | -3249.2484 |  |  | -3170.4745
[13 empty] | C Non choked w/ reducers | 7 |  | 83.2082 |  |  | 150.9036 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 62.4697 |  |  | 101.1401 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 83.2082 |  |  | 150.9036 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 78.4782 | 417.5844 |  | 139.3036 | 617.8378 |  | 5500 | 1527.9865 |  | 5500 | 2976.1277 |  | 5500 | 4993.0165 |  | 5500 | 7360.318 |  | 5500 | 9822.3729 |  | 5500 | 11985.1615 |  | 5500 | 13914.4005 |  | 5500 | 15835.8857
[13 empty] | Next iteration flow rate |  |  | 425.9361 | Abs Value of | Flow this | 624.0162 | Abs Value of | Flow this | 1543.2664 | Abs Value of | Flow this | 3005.889 | Abs Value of | Flow this | 5042.9466 | Abs Value of | Flow this | 7433.9211 | Abs Value of | Flow this | 9920.5966 | Abs Value of | Flow this | 12105.0131 | Abs Value of | Flow this | 14053.5445 | Abs Value of | Flow this | 15994.2445 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 50.7891 |  |  | 43.7653 |  |  | -23.5185 |  |  | -248.2297 |  |  | -801.9596 |  |  | -1809.4528 |  |  | -3266.9014 |  |  | -4891.7952 |  |  | -6613.1991 |  |  | -8582.5927
[13 empty] | P2 at this iteration flow rate |  |  | 25.8822 |  |  | 27.2869 |  |  | 40.7437 |  |  | 85.6859 |  |  | 196.4319 |  |  | 397.9306 |  |  | 689.4203 |  |  | 1014.399 |  |  | 1358.6798 |  |  | 1752.5585
[13 empty] | Delta P at this iteration flow rate |  |  | 24.9069 |  |  | 16.4784 |  |  | -64.2623 |  |  | -333.9156 |  |  | -998.3915 |  |  | -2207.3833 |  |  | -3956.3216 |  |  | -5906.1942 |  |  | -7971.8789 |  |  | -10335.1513
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.4852 |  |  | 37.1532 |  |  | -19.9312 |  |  | -197.8339 |  |  | -601.6363 |  |  | -1261.5424 |  |  | -2096.8953 |  |  | -2844.8589 |  |  | -3315.1273 |  |  | -3234.6288
[13 empty] | C Non choked w/ reducers | 7 |  | 85.3574 |  |  | 153.844 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 63.8695 |  |  | 102.4566 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 85.3574 |  |  | 153.844 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 80.6274 | 425.9361 |  | 142.244 | 624.0162 |  | 5500 | 1543.2664 |  | 5500 | 3005.889 |  | 5500 | 5042.9466 |  | 5500 | 7433.9211 |  | 5500 | 9920.5966 |  | 5500 | 12105.0131 |  | 5500 | 14053.5445 |  | 5500 | 15994.2445
[13 empty] | Next iteration flow rate |  |  | 434.4548 | Abs Value of | Flow this | 630.2564 | Abs Value of | Flow this | 1558.699 | Abs Value of | Flow this | 3035.9479 | Abs Value of | Flow this | 5093.3761 | Abs Value of | Flow this | 7508.2604 | Abs Value of | Flow this | 10019.8025 | Abs Value of | Flow this | 12226.0633 | Abs Value of | Flow this | 14194.0799 | Abs Value of | Flow this | 16154.187 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 50.5416 |  |  | 43.501 |  |  | -25.1353 |  |  | -254.3631 |  |  | -819.223 |  |  | -1846.9668 |  |  | -3333.7101 |  |  | -4991.2643 |  |  | -6747.2684 |  |  | -8756.2469
[13 empty] | P2 at this iteration flow rate |  |  | 25.9317 |  |  | 27.3398 |  |  | 41.0671 |  |  | 86.9126 |  |  | 199.8846 |  |  | 405.4334 |  |  | 702.782 |  |  | 1034.2929 |  |  | 1385.4937 |  |  | 1787.2894
[13 empty] | Delta P at this iteration flow rate |  |  | 24.6099 |  |  | 16.1612 |  |  | -66.2023 |  |  | -341.2758 |  |  | -1019.1076 |  |  | -2252.4001 |  |  | -4036.4921 |  |  | -6025.5572 |  |  | -8132.7621 |  |  | -10543.5362
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.2665 |  |  | 36.9265 |  |  | -21.2761 |  |  | -202.7135 |  |  | -614.5803 |  |  | -1287.6906 |  |  | -2139.7714 |  |  | -2902.7007 |  |  | -3382.3304 |  |  | -3300.0727
[13 empty] | C Non choked w/ reducers | 7 |  | 87.5884 |  |  | 156.8999 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 65.3076 |  |  | 103.7982 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 87.5884 |  |  | 156.8999 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 82.8584 | 434.4548 |  | 145.2999 | 630.2564 |  | 5500 | 1558.699 |  | 5500 | 3035.9479 |  | 5500 | 5093.3761 |  | 5500 | 7508.2604 |  | 5500 | 10019.8025 |  | 5500 | 12226.0633 |  | 5500 | 14194.0799 |  | 5500 | 16154.187
[13 empty] | Next iteration flow rate |  |  | 443.1439 | Abs Value of | Flow this | 636.5589 | Abs Value of | Flow this | 1574.286 | Abs Value of | Flow this | 3066.3073 | Abs Value of | Flow this | 5144.3099 | Abs Value of | Flow this | 7583.343 | Abs Value of | Flow this | 10120.0006 | Abs Value of | Flow this | 12348.3239 | Abs Value of | Flow this | 14336.0207 | Abs Value of | Flow this | 16315.7288 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 50.284 |  |  | 43.2313 |  |  | -26.7845 |  |  | -260.6198 |  |  | -836.8334 |  |  | -1885.2348 |  |  | -3401.8617 |  |  | -5092.7327 |  |  | -6884.0325 |  |  | -8933.3914
[13 empty] | P2 at this iteration flow rate |  |  | 25.9832 |  |  | 27.3937 |  |  | 41.3969 |  |  | 88.164 |  |  | 203.4067 |  |  | 413.087 |  |  | 716.4123 |  |  | 1054.5865 |  |  | 1412.8465 |  |  | 1822.7183
[13 empty] | Delta P at this iteration flow rate |  |  | 24.3009 |  |  | 15.8376 |  |  | -68.1814 |  |  | -348.7838 |  |  | -1040.2401 |  |  | -2298.3218 |  |  | -4118.274 |  |  | -6147.3193 |  |  | -8296.879 |  |  | -10756.1097
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.039 |  |  | 36.6952 |  |  | -22.6481 |  |  | -207.6912 |  |  | -627.7845 |  |  | -1314.3645 |  |  | -2183.5093 |  |  | -2961.7051 |  |  | -3450.8842 |  |  | -3366.8319
[13 empty] | C Non choked w/ reducers | 7 |  | 89.9065 |  |  | 160.0795 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 66.7856 |  |  | 105.166 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 89.9065 |  |  | 160.0795 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 85.1765 | 443.1439 |  | 148.4795 | 636.5589 |  | 5500 | 1574.286 |  | 5500 | 3066.3073 |  | 5500 | 5144.3099 |  | 5500 | 7583.343 |  | 5500 | 10120.0006 |  | 5500 | 12348.3239 |  | 5500 | 14336.0207 |  | 5500 | 16315.7288
[13 empty] | Next iteration flow rate |  |  | 452.0068 | Abs Value of | Flow this | 642.9245 | Abs Value of | Flow this | 1590.0289 | Abs Value of | Flow this | 3096.9704 | Abs Value of | Flow this | 5195.753 | Abs Value of | Flow this | 7659.1764 | Abs Value of | Flow this | 10221.2006 | Abs Value of | Flow this | 12471.8071 | Abs Value of | Flow this | 14479.3809 | Abs Value of | Flow this | 16478.8861 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 50.0161 |  |  | 42.9563 |  |  | -28.4669 |  |  | -267.0023 |  |  | -854.7978 |  |  | -1924.2721 |  |  | -3471.3831 |  |  | -5196.2407 |  |  | -7023.5456 |  |  | -9114.0966
[13 empty] | P2 at this iteration flow rate |  |  | 26.0368 |  |  | 27.4487 |  |  | 41.7334 |  |  | 89.4405 |  |  | 206.9996 |  |  | 420.8944 |  |  | 730.3166 |  |  | 1075.2881 |  |  | 1440.7491 |  |  | 1858.8593
[13 empty] | Delta P at this iteration flow rate |  |  | 23.9793 |  |  | 15.5075 |  |  | -70.2003 |  |  | -356.4428 |  |  | -1061.7973 |  |  | -2345.1665 |  |  | -4201.6997 |  |  | -6271.5288 |  |  | -8464.2947 |  |  | -10972.9559
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 43.8022 |  |  | 36.4594 |  |  | -24.0477 |  |  | -212.7689 |  |  | -641.2541 |  |  | -1341.5744 |  |  | -2228.1264 |  |  | -3021.8955 |  |  | -3520.816 |  |  | -3434.933
[13 empty] | C Non choked w/ reducers | 7 |  | 92.3173 |  |  | 163.3919 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 68.3052 |  |  | 106.5607 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 92.3173 |  |  | 163.3919 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 87.5873 | 452.0068 |  | 151.7919 | 642.9245 |  | 5500 | 1590.0289 |  | 5500 | 3096.9704 |  | 5500 | 5195.753 |  | 5500 | 7659.1764 |  | 5500 | 10221.2006 |  | 5500 | 12471.8071 |  | 5500 | 14479.3809 |  | 5500 | 16478.8861
[13 empty] | Next iteration flow rate |  |  | 461.0469 | Abs Value of | Flow this | 649.3538 | Abs Value of | Flow this | 1605.9292 | Abs Value of | Flow this | 3127.9401 | Abs Value of | Flow this | 5247.7105 | Abs Value of | Flow this | 7735.7682 | Abs Value of | Flow this | 10323.4126 | Abs Value of | Flow this | 12596.5252 | Abs Value of | Flow this | 14624.1747 | Abs Value of | Flow this | 16643.675 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 49.7373 |  |  | 42.6757 |  |  | -30.1831 |  |  | -273.5131 |  |  | -873.1232 |  |  | -1964.094 |  |  | -3542.3019 |  |  | -5301.8291 |  |  | -7165.8629 |  |  | -9298.434
[13 empty] | P2 at this iteration flow rate |  |  | 26.0925 |  |  | 27.5049 |  |  | 42.0766 |  |  | 90.7426 |  |  | 210.6646 |  |  | 428.8588 |  |  | 744.5004 |  |  | 1096.4058 |  |  | 1469.2126 |  |  | 1895.7268
[13 empty] | Delta P at this iteration flow rate |  |  | 23.6448 |  |  | 15.1708 |  |  | -72.2597 |  |  | -364.2557 |  |  | -1083.7879 |  |  | -2392.9527 |  |  | -4286.8023 |  |  | -6398.235 |  |  | -8635.0754 |  |  | -11194.1608
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 43.5559 |  |  | 36.2187 |  |  | -25.4754 |  |  | -217.9486 |  |  | -654.9945 |  |  | -1369.3313 |  |  | -2273.6403 |  |  | -3083.2957 |  |  | -3592.1534 |  |  | -3504.403
[13 empty] | C Non choked w/ reducers | 7 |  | 94.8274 |  |  | 166.8471 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 69.868 |  |  | 107.9832 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 94.8274 |  |  | 166.8471 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 90.0974 | 461.0469 |  | 155.2471 | 649.3538 |  | 5500 | 1605.9292 |  | 5500 | 3127.9401 |  | 5500 | 5247.7105 |  | 5500 | 7735.7682 |  | 5500 | 10323.4126 |  | 5500 | 12596.5252 |  | 5500 | 14624.1747 |  | 5500 | 16643.675
[13 empty] | Next iteration flow rate |  |  | 470.2679 | Abs Value of | Flow this | 655.8473 | Abs Value of | Flow this | 1621.9885 | Abs Value of | Flow this | 3159.2195 | Abs Value of | Flow this | 5300.1876 | Abs Value of | Flow this | 7813.1258 | Abs Value of | Flow this | 10426.6467 | Abs Value of | Flow this | 12722.4905 | Abs Value of | Flow this | 14770.4165 | Abs Value of | Flow this | 16810.1117 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 49.4473 |  |  | 42.3894 |  |  | -31.9338 |  |  | -280.1547 |  |  | -891.817 |  |  | -2004.7163 |  |  | -3614.6462 |  |  | -5409.5399 |  |  | -7311.0407 |  |  | -9486.4765
[13 empty] | P2 at this iteration flow rate |  |  | 26.1505 |  |  | 27.5621 |  |  | 42.4268 |  |  | 92.0709 |  |  | 214.4034 |  |  | 436.9833 |  |  | 758.9692 |  |  | 1117.948 |  |  | 1498.2481 |  |  | 1933.3353
[13 empty] | Delta P at this iteration flow rate |  |  | 23.2968 |  |  | 14.8273 |  |  | -74.3606 |  |  | -372.2257 |  |  | -1106.2204 |  |  | -2441.6995 |  |  | -4373.6155 |  |  | -6527.4879 |  |  | -8809.2889 |  |  | -11419.8118
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 43.2997 |  |  | 35.9733 |  |  | -26.9318 |  |  | -223.2325 |  |  | -669.011 |  |  | -1397.6461 |  |  | -2320.069 |  |  | -3145.93 |  |  | -3664.9247 |  |  | -3575.2693
[13 empty] | C Non choked w/ reducers | 7 |  | 97.4438 |  |  | 170.4563 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 71.4759 |  |  | 109.4345 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 97.4438 |  |  | 170.4563 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 92.7138 | 470.2679 |  | 158.8563 | 655.8473 |  | 5500 | 1621.9885 |  | 5500 | 3159.2195 |  | 5500 | 5300.1876 |  | 5500 | 7813.1258 |  | 5500 | 10426.6467 |  | 5500 | 12722.4905 |  | 5500 | 14770.4165 |  | 5500 | 16810.1117
[13 empty] | Next iteration flow rate |  |  | 479.6732 | Abs Value of | Flow this | 662.4058 | Abs Value of | Flow this | 1638.2083 | Abs Value of | Flow this | 3190.8117 | Abs Value of | Flow this | 5353.1895 | Abs Value of | Flow this | 7891.2571 | Abs Value of | Flow this | 10530.9132 | Abs Value of | Flow this | 12849.7154 | Abs Value of | Flow this | 14918.1206 | Abs Value of | Flow this | 16978.2128 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 49.1456 |  |  | 42.0975 |  |  | -33.7197 |  |  | -286.9298 |  |  | -910.8865 |  |  | -2046.1551 |  |  | -3688.4446 |  |  | -5519.4157 |  |  | -7459.1366 |  |  | -9678.2987
[13 empty] | P2 at this iteration flow rate |  |  | 26.2109 |  |  | 27.6205 |  |  | 42.7839 |  |  | 93.426 |  |  | 218.2173 |  |  | 445.271 |  |  | 773.7289 |  |  | 1139.9231 |  |  | 1527.8673 |  |  | 1971.6997
[13 empty] | Delta P at this iteration flow rate |  |  | 22.9347 |  |  | 14.4769 |  |  | -76.5036 |  |  | -380.3558 |  |  | -1129.1039 |  |  | -2491.4261 |  |  | -4462.1736 |  |  | -6659.3388 |  |  | -8987.004 |  |  | -11649.9984
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 43.0331 |  |  | 35.7229 |  |  | -28.4175 |  |  | -228.6226 |  |  | -683.3093 |  |  | -1426.5301 |  |  | -2367.4309 |  |  | -3209.8233 |  |  | -3739.1587 |  |  | -3647.56
[13 empty] | C Non choked w/ reducers | 7 |  | 100.1742 |  |  | 174.2318 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 73.1309 |  |  | 110.9156 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 100.1742 |  |  | 174.2318 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 95.4442 | 479.6732 |  | 162.6318 | 662.4058 |  | 5500 | 1638.2083 |  | 5500 | 3190.8117 |  | 5500 | 5353.1895 |  | 5500 | 7891.2571 |  | 5500 | 10530.9132 |  | 5500 | 12849.7154 |  | 5500 | 14918.1206 |  | 5500 | 16978.2128
[13 empty] | Next iteration flow rate |  |  | 489.2667 | Abs Value of | Flow this | 669.0298 | Abs Value of | Flow this | 1654.5904 | Abs Value of | Flow this | 3222.7198 | Abs Value of | Flow this | 5406.7214 | Abs Value of | Flow this | 7970.1697 | Abs Value of | Flow this | 10636.2223 | Abs Value of | Flow this | 12978.2125 | Abs Value of | Flow this | 15067.3018 | Abs Value of | Flow this | 17147.995 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 48.8316 |  |  | 41.7996 |  |  | -35.5415 |  |  | -293.8411 |  |  | -930.3394 |  |  | -2088.4268 |  |  | -3763.7264 |  |  | -5631.4999 |  |  | -7610.2093 |  |  | -9873.9765
[13 empty] | P2 at this iteration flow rate |  |  | 26.2737 |  |  | 27.6801 |  |  | 43.1483 |  |  | 94.8082 |  |  | 222.1079 |  |  | 453.7254 |  |  | 788.7853 |  |  | 1162.34 |  |  | 1558.0819 |  |  | 2010.8353
[13 empty] | Delta P at this iteration flow rate |  |  | 22.558 |  |  | 14.1195 |  |  | -78.6897 |  |  | -388.6494 |  |  | -1152.4473 |  |  | -2542.1522 |  |  | -4552.5117 |  |  | -6793.8399 |  |  | -9168.2912 |  |  | -11884.8118
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 42.7557 |  |  | 35.4675 |  |  | -29.933 |  |  | -234.121 |  |  | -697.8949 |  |  | -1455.9946 |  |  | -2415.7448 |  |  | -3275.0009 |  |  | -3814.8848 |  |  | -3721.3038
[13 empty] | C Non choked w/ reducers | 7 |  | 103.0273 |  |  | 178.1875 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 74.8351 |  |  | 112.4274 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 103.0273 |  |  | 178.1875 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 98.2973 | 489.2667 |  | 166.5875 | 669.0298 |  | 5500 | 1654.5904 |  | 5500 | 3222.7198 |  | 5500 | 5406.7214 |  | 5500 | 7970.1697 |  | 5500 | 10636.2223 |  | 5500 | 12978.2125 |  | 5500 | 15067.3018 |  | 5500 | 17147.995
[13 empty] | Next iteration flow rate |  |  | 499.052 | Abs Value of | Flow this | 675.7201 | Abs Value of | Flow this | 1671.1363 | Abs Value of | Flow this | 3254.947 | Abs Value of | Flow this | 5460.7886 | Abs Value of | Flow this | 8049.8714 | Abs Value of | Flow this | 10742.5845 | Abs Value of | Flow this | 13107.9946 | Abs Value of | Flow this | 15217.9749 | Abs Value of | Flow this | 17319.4749 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 48.505 |  |  | 41.4958 |  |  | -37.3999 |  |  | -300.8914 |  |  | -950.1832 |  |  | -2131.5482 |  |  | -3840.5213 |  |  | -5745.8371 |  |  | -7764.3185 |  |  | -10073.5875
[13 empty] | P2 at this iteration flow rate |  |  | 26.339 |  |  | 27.7408 |  |  | 43.52 |  |  | 96.2183 |  |  | 226.0766 |  |  | 462.3496 |  |  | 804.1443 |  |  | 1185.2074 |  |  | 1588.9037 |  |  | 2050.7575
[13 empty] | Delta P at this iteration flow rate |  |  | 22.166 |  |  | 13.7549 |  |  | -80.9198 |  |  | -397.1096 |  |  | -1176.2599 |  |  | -2593.8978 |  |  | -4644.6655 |  |  | -6931.0445 |  |  | -9353.2222 |  |  | -12124.345
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 42.4671 |  |  | 35.2069 |  |  | -31.479 |  |  | -239.7299 |  |  | -712.7738 |  |  | -1486.0513 |  |  | -2465.0297 |  |  | -3341.4885 |  |  | -3892.133 |  |  | -3796.5298
[13 empty] | C Non choked w/ reducers | 7 |  | 106.0129 |  |  | 182.3391 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 76.5907 |  |  | 113.9711 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 106.0129 |  |  | 182.3391 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 101.2829 | 499.052 |  | 170.7391 | 675.7201 |  | 5500 | 1671.1363 |  | 5500 | 3254.947 |  | 5500 | 5460.7886 |  | 5500 | 8049.8714 |  | 5500 | 10742.5845 |  | 5500 | 13107.9946 |  | 5500 | 15217.9749 |  | 5500 | 17319.4749
[13 empty] | Next iteration flow rate |  |  | 509.0331 | Abs Value of | Flow this | 682.4773 | Abs Value of | Flow this | 1687.8477 | Abs Value of | Flow this | 3287.4965 | Abs Value of | Flow this | 5515.3965 | Abs Value of | Flow this | 8130.3701 | Abs Value of | Flow this | 10850.0104 | Abs Value of | Flow this | 13239.0746 | Abs Value of | Flow this | 15370.1546 | Abs Value of | Flow this | 17492.6697 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 48.1652 |  |  | 41.1858 |  |  | -39.2956 |  |  | -308.0833 |  |  | -970.4259 |  |  | -2175.5363 |  |  | -3918.8598 |  |  | -5862.4724 |  |  | -7921.5253 |  |  | -10277.2106
[13 empty] | P2 at this iteration flow rate |  |  | 26.407 |  |  | 27.8028 |  |  | 43.8991 |  |  | 97.6567 |  |  | 230.1252 |  |  | 471.1473 |  |  | 819.812 |  |  | 1208.5345 |  |  | 1620.3451 |  |  | 2091.4821
[13 empty] | Delta P at this iteration flow rate |  |  | 21.7583 |  |  | 13.383 |  |  | -83.1947 |  |  | -405.7399 |  |  | -1200.5511 |  |  | -2646.6836 |  |  | -4738.6717 |  |  | -7071.0069 |  |  | -9541.8704 |  |  | -12368.6927
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 42.1669 |  |  | 34.9411 |  |  | -33.0561 |  |  | -245.4516 |  |  | -727.9517 |  |  | -1516.7122 |  |  | -2515.3054 |  |  | -3409.3125 |  |  | -3970.9339 |  |  | -3873.2678
[13 empty] | C Non choked w/ reducers | 7 |  | 109.1417 |  |  | 186.7041 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 78.4002 |  |  | 115.5478 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 109.1417 |  |  | 186.7041 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 104.4117 | 509.0331 |  | 175.1041 | 682.4773 |  | 5500 | 1687.8477 |  | 5500 | 3287.4965 |  | 5500 | 5515.3965 |  | 5500 | 8130.3701 |  | 5500 | 10850.0104 |  | 5500 | 13239.0746 |  | 5500 | 15370.1546 |  | 5500 | 17492.6697
[13 empty] | Next iteration flow rate |  |  | 519.2137 | Abs Value of | Flow this | 689.3021 | Abs Value of | Flow this | 1704.7262 | Abs Value of | Flow this | 3320.3715 | Abs Value of | Flow this | 5570.5504 | Abs Value of | Flow this | 8211.6738 | Abs Value of | Flow this | 10958.5105 | Abs Value of | Flow this | 13371.4653 | Abs Value of | Flow this | 15523.8561 | Abs Value of | Flow this | 17667.5964 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 47.8117 |  |  | 40.8696 |  |  | -41.2295 |  |  | -315.4198 |  |  | -991.0755 |  |  | -2220.4086 |  |  | -3998.7729 |  |  | -5981.4522 |  |  | -8081.892 |  |  | -10484.9265
[13 empty] | P2 at this iteration flow rate |  |  | 26.4777 |  |  | 27.8661 |  |  | 44.2859 |  |  | 99.124 |  |  | 234.2551 |  |  | 480.1217 |  |  | 835.7946 |  |  | 1232.3304 |  |  | 1652.4184 |  |  | 2133.0253
[13 empty] | Delta P at this iteration flow rate |  |  | 21.334 |  |  | 13.0035 |  |  | -85.5154 |  |  | -414.5437 |  |  | -1225.3306 |  |  | -2700.5303 |  |  | -4834.5675 |  |  | -7213.7826 |  |  | -9734.3104 |  |  | -12617.9518
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 41.8545 |  |  | 34.67 |  |  | -34.6649 |  |  | -251.2883 |  |  | -743.4346 |  |  | -1547.9893 |  |  | -2566.5915 |  |  | -3478.4998 |  |  | -4051.3187 |  |  | -3951.5483
[13 empty] | C Non choked w/ reducers | 7 |  | 112.426 |  |  | 191.3024 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 80.266 |  |  | 117.1587 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 112.426 |  |  | 191.3024 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 107.696 | 519.2137 |  | 179.7024 | 689.3021 |  | 5500 | 1704.7262 |  | 5500 | 3320.3715 |  | 5500 | 5570.5504 |  | 5500 | 8211.6738 |  | 5500 | 10958.5105 |  | 5500 | 13371.4653 |  | 5500 | 15523.8561 |  | 5500 | 17667.5964
[13 empty] | Next iteration flow rate |  |  | 529.598 | Abs Value of | Flow this | 696.1951 | Abs Value of | Flow this | 1721.7734 | Abs Value of | Flow this | 3353.5752 | Abs Value of | Flow this | 5626.2559 | Abs Value of | Flow this | 8293.7905 | Abs Value of | Flow this | 11068.0956 | Abs Value of | Flow this | 13505.18 | Abs Value of | Flow this | 15679.0947 | Abs Value of | Flow this | 17844.2723 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 47.4439 |  |  | 40.5471 |  |  | -43.2022 |  |  | -322.9037 |  |  | -1012.1401 |  |  | -2266.1828 |  |  | -4080.2922 |  |  | -6102.8234 |  |  | -8245.4821 |  |  | -10696.8176
[13 empty] | P2 at this iteration flow rate |  |  | 26.5512 |  |  | 27.9306 |  |  | 44.6804 |  |  | 100.6207 |  |  | 238.468 |  |  | 489.2766 |  |  | 852.0984 |  |  | 1256.6047 |  |  | 1685.1364 |  |  | 2175.4035
[13 empty] | Delta P at this iteration flow rate |  |  | 20.8926 |  |  | 12.6165 |  |  | -87.8826 |  |  | -423.5245 |  |  | -1250.6081 |  |  | -2755.4594 |  |  | -4932.3907 |  |  | -7359.428 |  |  | -9930.6185 |  |  | -12872.2211
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 41.5296 |  |  | 34.3934 |  |  | -36.306 |  |  | -257.2423 |  |  | -759.2288 |  |  | -1579.8951 |  |  | -2618.9085 |  |  | -3549.0778 |  |  | -4133.3192 |  |  | -4031.4023
[13 empty] | C Non choked w/ reducers | 7 |  | 115.8795 |  |  | 196.1567 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 82.191 |  |  | 118.8051 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 115.8795 |  |  | 196.1567 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 111.1495 | 529.598 |  | 184.5567 | 696.1951 |  | 5500 | 1721.7734 |  | 5500 | 3353.5752 |  | 5500 | 5626.2559 |  | 5500 | 8293.7905 |  | 5500 | 11068.0956 |  | 5500 | 13505.18 |  | 5500 | 15679.0947 |  | 5500 | 17844.2723
[13 empty] | Next iteration flow rate |  |  | 540.1899 | Abs Value of | Flow this | 703.1571 | Abs Value of | Flow this | 1738.9912 | Abs Value of | Flow this | 3387.1109 | Abs Value of | Flow this | 5682.5185 | Abs Value of | Flow this | 8376.7284 | Abs Value of | Flow this | 11178.7765 | Abs Value of | Flow this | 13640.2318 | Abs Value of | Flow this | 15835.8857 | Abs Value of | Flow this | 18022.7151 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 47.0612 |  |  | 40.2181 |  |  | -45.2146 |  |  | -330.5381 |  |  | -1033.6281 |  |  | -2312.8771 |  |  | -4163.4501 |  |  | -6226.6341 |  |  | -8412.3603 |  |  | -10912.9676
[13 empty] | P2 at this iteration flow rate |  |  | 26.6278 |  |  | 27.9964 |  |  | 45.0829 |  |  | 102.1476 |  |  | 242.7656 |  |  | 498.6154 |  |  | 868.73 |  |  | 1281.3668 |  |  | 1718.5121 |  |  | 2218.6335
[13 empty] | Delta P at this iteration flow rate |  |  | 20.4334 |  |  | 12.2217 |  |  | -90.2975 |  |  | -432.6857 |  |  | -1276.3938 |  |  | -2811.4926 |  |  | -5032.1801 |  |  | -7508.0009 |  |  | -10130.8723 |  |  | -13131.6011
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 41.1915 |  |  | 34.1113 |  |  | -37.9801 |  |  | -263.316 |  |  | -775.3405 |  |  | -1612.4423 |  |  | -2672.2771 |  |  | -3621.0743 |  |  | -4216.9679 |  |  | -4112.8612
[13 empty] | C Non choked w/ reducers | 7 |  | 119.5178 |  |  | 201.2929 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 84.1782 |  |  | 120.4884 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 119.5178 |  |  | 201.2929 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 114.7878 | 540.1899 |  | 189.6929 | 703.1571 |  | 5500 | 1738.9912 |  | 5500 | 3387.1109 |  | 5500 | 5682.5185 |  | 5500 | 8376.7284 |  | 5500 | 11178.7765 |  | 5500 | 13640.2318 |  | 5500 | 15835.8857 |  | 5500 | 18022.7151
[13 empty] | Next iteration flow rate |  |  | 550.9937 | Abs Value of | Flow this | 710.1887 | Abs Value of | Flow this | 1756.3811 | Abs Value of | Flow this | 3420.982 | Abs Value of | Flow this | 5739.3437 | Abs Value of | Flow this | 8460.4957 | Abs Value of | Flow this | 11290.5643 | Abs Value of | Flow this | 13776.6341 | Abs Value of | Flow this | 15994.2445 | Abs Value of | Flow this | 18202.9422 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 46.663 |  |  | 39.8824 |  |  | -47.2674 |  |  | -338.3259 |  |  | -1055.5481 |  |  | -2360.51 |  |  | -4248.2795 |  |  | -6352.9335 |  |  | -8582.5927 |  |  | -11133.4623
[13 empty] | P2 at this iteration flow rate |  |  | 26.7074 |  |  | 28.0635 |  |  | 45.4935 |  |  | 103.7052 |  |  | 247.1496 |  |  | 508.142 |  |  | 885.6959 |  |  | 1306.6267 |  |  | 1752.5585 |  |  | 2262.7325
[13 empty] | Delta P at this iteration flow rate |  |  | 19.9557 |  |  | 11.8189 |  |  | -92.7609 |  |  | -442.0311 |  |  | -1302.6977 |  |  | -2868.652 |  |  | -5133.9754 |  |  | -7659.5602 |  |  | -10335.1513 |  |  | -13396.1947
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 40.8397 |  |  | 33.8234 |  |  | -39.6878 |  |  | -269.5117 |  |  | -791.776 |  |  | -1645.6436 |  |  | -2726.7184 |  |  | -3694.518 |  |  | -4302.298 |  |  | -4195.9576
[13 empty] | C Non choked w/ reducers | 7 |  | 123.3589 |  |  | 206.7409 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 86.2308 |  |  | 122.21 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 123.3589 |  |  | 206.7409 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 118.6289 | 550.9937 |  | 195.1409 | 710.1887 |  | 5500 | 1756.3811 |  | 5500 | 3420.982 |  | 5500 | 5739.3437 |  | 5500 | 8460.4957 |  | 5500 | 11290.5643 |  | 5500 | 13776.6341 |  | 5500 | 15994.2445 |  | 5500 | 18202.9422
[13 empty] | Next iteration flow rate |  |  | 562.0136 | Abs Value of | Flow this | 717.2906 | Abs Value of | Flow this | 1773.9449 | Abs Value of | Flow this | 3455.1919 | Abs Value of | Flow this | 5796.7371 | Abs Value of | Flow this | 8545.1007 | Abs Value of | Flow this | 11403.47 | Abs Value of | Flow this | 13914.4005 | Abs Value of | Flow this | 16154.187 | Abs Value of | Flow this | 18384.9716 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 46.2488 |  |  | 39.5401 |  |  | -49.3615 |  |  | -346.2703 |  |  | -1077.9086 |  |  | -2409.1002 |  |  | -4334.8139 |  |  | -6481.7715 |  |  | -8756.2469 |  |  | -11358.3889
[13 empty] | P2 at this iteration flow rate |  |  | 26.7902 |  |  | 28.132 |  |  | 45.9123 |  |  | 105.2941 |  |  | 251.6217 |  |  | 517.86 |  |  | 903.0028 |  |  | 1332.3943 |  |  | 1787.2894 |  |  | 2307.7178
[13 empty] | Delta P at this iteration flow rate |  |  | 19.4586 |  |  | 11.4081 |  |  | -95.2738 |  |  | -451.5644 |  |  | -1329.5303 |  |  | -2926.9603 |  |  | -5237.8167 |  |  | -7814.1658 |  |  | -10543.5362 |  |  | -13666.1067
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 40.4737 |  |  | 33.5298 |  |  | -41.4299 |  |  | -275.832 |  |  | -808.5418 |  |  | -1679.5123 |  |  | -2782.254 |  |  | -3769.438 |  |  | -4389.3432 |  |  | -4280.7241
[13 empty] | C Non choked w/ reducers | 7 |  | 127.4231 |  |  | 212.5351 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 88.3522 |  |  | 123.9713 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 127.4231 |  |  | 212.5351 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 122.6931 | 562.0136 |  | 200.9351 | 717.2906 |  | 5500 | 1773.9449 |  | 5500 | 3455.1919 |  | 5500 | 5796.7371 |  | 5500 | 8545.1007 |  | 5500 | 11403.47 |  | 5500 | 13914.4005 |  | 5500 | 16154.187 |  | 5500 | 18384.9716
[13 empty] | Next iteration flow rate |  |  | 573.2539 | Abs Value of | Flow this | 724.4635 | Abs Value of | Flow this | 1791.6843 | Abs Value of | Flow this | 3489.7438 | Abs Value of | Flow this | 5854.7045 | Abs Value of | Flow this | 8630.5517 | Abs Value of | Flow this | 11517.5046 | Abs Value of | Flow this | 14053.5445 | Abs Value of | Flow this | 16315.7288 | Abs Value of | Flow this | 18568.8213 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 45.8179 |  |  | 39.1908 |  |  | -51.4977 |  |  | -354.3744 |  |  | -1100.7186 |  |  | -2458.6672 |  |  | -4423.0877 |  |  | -6613.1991 |  |  | -8933.3914 |  |  | -11587.8365
[13 empty] | P2 at this iteration flow rate |  |  | 26.8764 |  |  | 28.2018 |  |  | 46.3395 |  |  | 106.9149 |  |  | 256.1837 |  |  | 527.7734 |  |  | 920.6575 |  |  | 1358.6798 |  |  | 1822.7183 |  |  | 2353.6073
[13 empty] | Delta P at this iteration flow rate |  |  | 18.9414 |  |  | 10.989 |  |  | -97.8372 |  |  | -461.2892 |  |  | -1356.9023 |  |  | -2986.4406 |  |  | -5343.7452 |  |  | -7971.8789 |  |  | -10756.1097 |  |  | -13941.4438
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 40.0929 |  |  | 33.2303 |  |  | -43.207 |  |  | -282.2793 |  |  | -825.6446 |  |  | -1714.0617 |  |  | -2838.9058 |  |  | -3845.8638 |  |  | -4478.138 |  |  | -4367.1945
[13 empty] | C Non choked w/ reducers | 7 |  | 131.7339 |  |  | 218.7156 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 90.5461 |  |  | 125.774 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 131.7339 |  |  | 218.7156 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 127.0039 | 573.2539 |  | 207.1156 | 724.4635 |  | 5500 | 1791.6843 |  | 5500 | 3489.7438 |  | 5500 | 5854.7045 |  | 5500 | 8630.5517 |  | 5500 | 11517.5046 |  | 5500 | 14053.5445 |  | 5500 | 16315.7288 |  | 5500 | 18568.8213
[13 empty] | Next iteration flow rate |  |  | 584.719 | Abs Value of | Flow this | 731.7081 | Abs Value of | Flow this | 1809.6012 | Abs Value of | Flow this | 3524.6412 | Abs Value of | Flow this | 5913.2515 | Abs Value of | Flow this | 8716.8572 | Abs Value of | Flow this | 11632.6797 | Abs Value of | Flow this | 14194.0799 | Abs Value of | Flow this | 16478.8861 | Abs Value of | Flow this | 18754.5096 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 45.3695 |  |  | 38.8345 |  |  | -53.6768 |  |  | -362.6413 |  |  | -1123.9871 |  |  | -2509.2304 |  |  | -4513.1358 |  |  | -6747.2684 |  |  | -9114.0966 |  |  | -11821.896
[13 empty] | P2 at this iteration flow rate |  |  | 26.9661 |  |  | 28.2731 |  |  | 46.7754 |  |  | 108.5683 |  |  | 260.8374 |  |  | 537.8861 |  |  | 938.6672 |  |  | 1385.4937 |  |  | 1858.8593 |  |  | 2400.4192
[13 empty] | Delta P at this iteration flow rate |  |  | 18.4034 |  |  | 10.5614 |  |  | -100.4521 |  |  | -471.2096 |  |  | -1384.8245 |  |  | -3047.1165 |  |  | -5451.8029 |  |  | -8132.7621 |  |  | -10972.9559 |  |  | -14222.3153
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 39.6968 |  |  | 32.9248 |  |  | -45.0198 |  |  | -288.8563 |  |  | -843.0912 |  |  | -1749.3056 |  |  | -2896.6963 |  |  | -3923.8257 |  |  | -4568.7175 |  |  | -4455.4029
[13 empty] | C Non choked w/ reducers | 7 |  | 136.3186 |  |  | 225.3296 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 92.8168 |  |  | 127.6198 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 136.3186 |  |  | 225.3296 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 131.5886 | 584.719 |  | 213.7296 | 731.7081 |  | 5500 | 1809.6012 |  | 5500 | 3524.6412 |  | 5500 | 5913.2515 |  | 5500 | 8716.8572 |  | 5500 | 11632.6797 |  | 5500 | 14194.0799 |  | 5500 | 16478.8861 |  | 5500 | 18754.5096
[13 empty] | Next iteration flow rate |  |  | 596.4133 | Abs Value of | Flow this | 739.0252 | Abs Value of | Flow this | 1827.6972 | Abs Value of | Flow this | 3559.8876 | Abs Value of | Flow this | 5972.384 | Abs Value of | Flow this | 8804.0258 | Abs Value of | Flow this | 11749.0065 | Abs Value of | Flow this | 14336.0207 | Abs Value of | Flow this | 16643.675 | Abs Value of | Flow this | 18942.0547 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 44.903 |  |  | 38.4711 |  |  | -55.8997 |  |  | -371.0744 |  |  | -1147.7232 |  |  | -2560.8099 |  |  | -4604.9938 |  |  | -6884.0325 |  |  | -9298.434 |  |  | -12060.6602
[13 empty] | P2 at this iteration flow rate |  |  | 27.0594 |  |  | 28.3458 |  |  | 47.2199 |  |  | 110.2549 |  |  | 265.5846 |  |  | 548.202 |  |  | 957.0388 |  |  | 1412.8465 |  |  | 1895.7268 |  |  | 2448.172
[13 empty] | Delta P at this iteration flow rate |  |  | 17.8436 |  |  | 10.1253 |  |  | -103.1196 |  |  | -481.3293 |  |  | -1413.3078 |  |  | -3109.0119 |  |  | -5562.0326 |  |  | -8296.879 |  |  | -11194.1608 |  |  | -14508.8322
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 39.2846 |  |  | 32.6131 |  |  | -46.8691 |  |  | -295.5654 |  |  | -860.8885 |  |  | -1785.2579 |  |  | -2955.6485 |  |  | -4003.3547 |  |  | -4661.1178 |  |  | -4545.3843
[13 empty] | C Non choked w/ reducers | 7 |  | 141.2091 |  |  | 232.4326 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 95.1684 |  |  | 129.5104 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 141.2091 |  |  | 232.4326 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 136.4791 | 596.4133 |  | 220.8326 | 739.0252 |  | 5500 | 1827.6972 |  | 5500 | 3559.8876 |  | 5500 | 5972.384 |  | 5500 | 8804.0258 |  | 5500 | 11749.0065 |  | 5500 | 14336.0207 |  | 5500 | 16643.675 |  | 5500 | 18942.0547
[13 empty] | Next iteration flow rate |  |  | 608.3416 | Abs Value of | Flow this | 746.4154 | Abs Value of | Flow this | 1845.9742 | Abs Value of | Flow this | 3595.4865 | Abs Value of | Flow this | 6032.1079 | Abs Value of | Flow this | 8892.066 | Abs Value of | Flow this | 11866.4966 | Abs Value of | Flow this | 14479.3809 | Abs Value of | Flow this | 16810.1117 | Abs Value of | Flow this | 19131.4752 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 44.4177 |  |  | 38.1003 |  |  | -58.1673 |  |  | -379.677 |  |  | -1171.9365 |  |  | -2613.4262 |  |  | -4698.6982 |  |  | -7023.5456 |  |  | -9486.4765 |  |  | -12304.2235
[13 empty] | P2 at this iteration flow rate |  |  | 27.1565 |  |  | 28.4199 |  |  | 47.6735 |  |  | 111.9754 |  |  | 270.4273 |  |  | 558.7252 |  |  | 975.7796 |  |  | 1440.7491 |  |  | 1933.3353 |  |  | 2496.8847
[13 empty] | Delta P at this iteration flow rate |  |  | 17.2612 |  |  | 9.6804 |  |  | -105.8408 |  |  | -491.6524 |  |  | -1442.3638 |  |  | -3172.1515 |  |  | -5674.4778 |  |  | -8464.2947 |  |  | -11419.8118 |  |  | -14801.1081
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 38.8558 |  |  | 32.2952 |  |  | -48.7555 |  |  | -302.4093 |  |  | -879.0435 |  |  | -1821.9328 |  |  | -3015.7855 |  |  | -4084.4823 |  |  | -4755.3753 |  |  | -4637.1743
[13 empty] | C Non choked w/ reducers | 7 |  | 146.443 |  |  | 240.0908 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 97.606 |  |  | 131.4478 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 146.443 |  |  | 240.0908 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 141.713 | 608.3416 |  | 228.4908 | 746.4154 |  | 5500 | 1845.9742 |  | 5500 | 3595.4865 |  | 5500 | 6032.1079 |  | 5500 | 8892.066 |  | 5500 | 11866.4966 |  | 5500 | 14479.3809 |  | 5500 | 16810.1117 |  | 5500 | 19131.4752
[13 empty] | Next iteration flow rate |  |  | 620.5084 | Abs Value of | Flow this | 753.8796 | Abs Value of | Flow this | 1864.4339 | Abs Value of | Flow this | 3631.4414 | Abs Value of | Flow this | 6092.429 | Abs Value of | Flow this | 8980.9867 | Abs Value of | Flow this | 11985.1615 | Abs Value of | Flow this | 14624.1747 | Abs Value of | Flow this | 16978.2128 | Abs Value of | Flow this | 19322.79 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 43.9127 |  |  | 37.7221 |  |  | -60.4805 |  |  | -388.4525 |  |  | -1196.6364 |  |  | -2667.1001 |  |  | -4794.286 |  |  | -7165.8629 |  |  | -9678.2987 |  |  | -12552.6824
[13 empty] | P2 at this iteration flow rate |  |  | 27.2575 |  |  | 28.4956 |  |  | 48.1361 |  |  | 113.7305 |  |  | 275.3673 |  |  | 569.46 |  |  | 994.8972 |  |  | 1469.2126 |  |  | 1971.6997 |  |  | 2546.5765
[13 empty] | Delta P at this iteration flow rate |  |  | 16.6553 |  |  | 9.2266 |  |  | -108.6166 |  |  | -502.183 |  |  | -1472.0037 |  |  | -3236.5601 |  |  | -5789.1833 |  |  | -8635.0754 |  |  | -11649.9984 |  |  | -15099.2588
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 38.4097 |  |  | 31.9709 |  |  | -50.6798 |  |  | -309.3909 |  |  | -897.5635 |  |  | -1859.3449 |  |  | -3077.1313 |  |  | -4167.2405 |  |  | -4851.5273 |  |  | -4730.8093
[13 empty] | C Non choked w/ reducers | 7 |  | 152.0647 |  |  | 248.384 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 100.1346 |  |  | 133.4339 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 152.0647 |  |  | 248.384 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 147.3347 | 620.5084 |  | 236.784 | 753.8796 |  | 5500 | 1864.4339 |  | 5500 | 3631.4414 |  | 5500 | 6092.429 |  | 5500 | 8980.9867 |  | 5500 | 11985.1615 |  | 5500 | 14624.1747 |  | 5500 | 16978.2128 |  | 5500 | 19322.79
[13 empty] | Next iteration flow rate |  |  | 632.9186 | Abs Value of | Flow this | 761.4184 | Abs Value of | Flow this | 1883.0783 | Abs Value of | Flow this | 3667.7558 | Abs Value of | Flow this | 6153.3533 | Abs Value of | Flow this | 9070.7965 | Abs Value of | Flow this | 12105.0131 | Abs Value of | Flow this | 14770.4165 | Abs Value of | Flow this | 17147.995 | Abs Value of | Flow this | 19516.0179 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 43.3874 |  |  | 37.3363 |  |  | -62.8401 |  |  | -397.4044 |  |  | -1221.8328 |  |  | -2721.8528 |  |  | -4891.7952 |  |  | -7311.0407 |  |  | -9873.9765 |  |  | -12806.1353
[13 empty] | P2 at this iteration flow rate |  |  | 27.3625 |  |  | 28.5727 |  |  | 48.608 |  |  | 115.5209 |  |  | 280.4066 |  |  | 580.4106 |  |  | 1014.399 |  |  | 1498.2481 |  |  | 2010.8353 |  |  | 2597.2671
[13 empty] | Delta P at this iteration flow rate |  |  | 16.0249 |  |  | 8.7636 |  |  | -111.4482 |  |  | -512.9253 |  |  | -1502.2394 |  |  | -3302.2634 |  |  | -5906.1942 |  |  | -8809.2889 |  |  | -11884.8118 |  |  | -15403.4023
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 37.9455 |  |  | 31.6401 |  |  | -52.6428 |  |  | -316.5127 |  |  | -916.4556 |  |  | -1897.509 |  |  | -3139.7102 |  |  | -4251.6621 |  |  | -4949.612 |  |  | -4826.3264
[13 empty] | C Non choked w/ reducers | 7 |  | 158.1275 |  |  | 257.4089 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 102.7601 |  |  | 135.471 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 158.1275 |  |  | 257.4089 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 153.3975 | 632.9186 |  | 245.8089 | 761.4184 |  | 5500 | 1883.0783 |  | 5500 | 3667.7558 |  | 5500 | 6153.3533 |  | 5500 | 9070.7965 |  | 5500 | 12105.0131 |  | 5500 | 14770.4165 |  | 5500 | 17147.995 |  | 5500 | 19516.0179
[13 empty] | Next iteration flow rate |  |  | 645.577 | Abs Value of | Flow this | 769.0326 | Abs Value of | Flow this | 1901.909 | Abs Value of | Flow this | 3704.4333 | Abs Value of | Flow this | 6214.8868 | Abs Value of | Flow this | 9161.5045 | Abs Value of | Flow this | 12226.0633 | Abs Value of | Flow this | 14918.1206 | Abs Value of | Flow this | 17319.4749 | Abs Value of | Flow this | 19711.178 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 42.8408 |  |  | 36.9428 |  |  | -65.2472 |  |  | -406.5363 |  |  | -1247.5357 |  |  | -2777.7061 |  |  | -4991.2643 |  |  | -7459.1366 |  |  | -10073.5875 |  |  | -13064.6826
[13 empty] | P2 at this iteration flow rate |  |  | 27.4718 |  |  | 28.6514 |  |  | 49.0894 |  |  | 117.3473 |  |  | 285.5471 |  |  | 591.5812 |  |  | 1034.2929 |  |  | 1527.8673 |  |  | 2050.7575 |  |  | 2648.9765
[13 empty] | Delta P at this iteration flow rate |  |  | 15.369 |  |  | 8.2913 |  |  | -114.3367 |  |  | -523.8835 |  |  | -1533.0828 |  |  | -3369.2873 |  |  | -6025.5572 |  |  | -8987.004 |  |  | -12124.345 |  |  | -15713.6591
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 37.4626 |  |  | 31.3026 |  |  | -54.6453 |  |  | -323.7777 |  |  | -935.7275 |  |  | -1936.4402 |  |  | -3203.5469 |  |  | -4337.7806 |  |  | -5049.6682 |  |  | -4923.7633
[13 empty] | C Non choked w/ reducers | 7 |  | 164.6956 |  |  | 267.2846 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 105.4887 |  |  | 137.5614 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 164.6956 |  |  | 267.2846 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 159.9656 | 645.577 |  | 255.6846 | 769.0326 |  | 5500 | 1901.909 |  | 5500 | 3704.4333 |  | 5500 | 6214.8868 |  | 5500 | 9161.5045 |  | 5500 | 12226.0633 |  | 5500 | 14918.1206 |  | 5500 | 17319.4749 |  | 5500 | 19711.178
[13 empty] | Next iteration flow rate |  |  | 658.4885 | Abs Value of | Flow this | 776.7229 | Abs Value of | Flow this | 1920.9281 | Abs Value of | Flow this | 3741.4777 | Abs Value of | Flow this | 6277.0357 | Abs Value of | Flow this | 9253.1195 | Abs Value of | Flow this | 12348.3239 | Abs Value of | Flow this | 15067.3018 | Abs Value of | Flow this | 17492.6697 | Abs Value of | Flow this | 19908.2898 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 42.2722 |  |  | 36.5413 |  |  | -67.7027 |  |  | -415.8517 |  |  | -1273.7551 |  |  | -2834.682 |  |  | -5092.7327 |  |  | -7610.2093 |  |  | -10277.2106 |  |  | -13328.4268
[13 empty] | P2 at this iteration flow rate |  |  | 27.5856 |  |  | 28.7317 |  |  | 49.5805 |  |  | 119.2103 |  |  | 290.791 |  |  | 602.9764 |  |  | 1054.5865 |  |  | 1558.0819 |  |  | 2091.4821 |  |  | 2701.7254
[13 empty] | Delta P at this iteration flow rate |  |  | 14.6866 |  |  | 7.8096 |  |  | -117.2833 |  |  | -535.062 |  |  | -1564.5462 |  |  | -3437.6584 |  |  | -6147.3193 |  |  | -9168.2912 |  |  | -12368.6927 |  |  | -16030.1521
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 36.9602 |  |  | 30.9583 |  |  | -56.688 |  |  | -331.1888 |  |  | -955.3868 |  |  | -1976.1539 |  |  | -3268.6667 |  |  | -4425.6301 |  |  | -5151.7356 |  |  | -5023.1588
[13 empty] | C Non choked w/ reducers | 7 |  | 171.8477 |  |  | 278.1594 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 108.3273 |  |  | 139.7074 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 171.8477 |  |  | 278.1594 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 167.1177 | 658.4885 |  | 266.5594 | 776.7229 |  | 5500 | 1920.9281 |  | 5500 | 3741.4777 |  | 5500 | 6277.0357 |  | 5500 | 9253.1195 |  | 5500 | 12348.3239 |  | 5500 | 15067.3018 |  | 5500 | 17492.6697 |  | 5500 | 19908.2898
[13 empty] | Next iteration flow rate |  |  | 671.6583 | Abs Value of | Flow this | 784.4901 | Abs Value of | Flow this | 1940.1374 | Abs Value of | Flow this | 3778.8925 | Abs Value of | Flow this | 6339.806 | Abs Value of | Flow this | 9345.6507 | Abs Value of | Flow this | 12471.8071 | Abs Value of | Flow this | 15217.9749 | Abs Value of | Flow this | 17667.5964 | Abs Value of | Flow this | 20107.3727 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 41.6806 |  |  | 36.1318 |  |  | -70.2076 |  |  | -425.3543 |  |  | -1300.5016 |  |  | -2892.8031 |  |  | -5196.2407 |  |  | -7764.3185 |  |  | -10484.9265 |  |  | -13597.4721
[13 empty] | P2 at this iteration flow rate |  |  | 27.7039 |  |  | 28.8136 |  |  | 50.0815 |  |  | 121.1109 |  |  | 296.1403 |  |  | 614.6006 |  |  | 1075.2881 |  |  | 1588.9037 |  |  | 2133.0253 |  |  | 2755.5344
[13 empty] | Delta P at this iteration flow rate |  |  | 13.9767 |  |  | 7.3181 |  |  | -120.2891 |  |  | -546.4652 |  |  | -1596.642 |  |  | -3507.4038 |  |  | -6271.5288 |  |  | -9353.2222 |  |  | -12617.9518 |  |  | -16353.0066
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 36.4375 |  |  | 30.6071 |  |  | -58.7718 |  |  | -338.7488 |  |  | -975.4412 |  |  | -2016.6658 |  |  | -3335.0954 |  |  | -4515.2454 |  |  | -5255.8545 |  |  | -5124.5521
[13 empty] | C Non choked w/ reducers | 7 |  | 179.6813 |  |  | 290.2209 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 111.2836 |  |  | 141.9117 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 179.6813 |  |  | 290.2209 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 174.9513 | 671.6583 |  | 278.6209 | 784.4901 |  | 5500 | 1940.1374 |  | 5500 | 3778.8925 |  | 5500 | 6339.806 |  | 5500 | 9345.6507 |  | 5500 | 12471.8071 |  | 5500 | 15217.9749 |  | 5500 | 17667.5964 |  | 5500 | 20107.3727
[13 empty] | Next iteration flow rate |  |  | 685.0915 | Abs Value of | Flow this | 792.335 | Abs Value of | Flow this | 1959.5388 | Abs Value of | Flow this | 3816.6814 | Abs Value of | Flow this | 6403.2041 | Abs Value of | Flow this | 9439.1072 | Abs Value of | Flow this | 12596.5252 | Abs Value of | Flow this | 15370.1546 | Abs Value of | Flow this | 17844.2723 | Abs Value of | Flow this | 20308.4464 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 41.0651 |  |  | 35.714 |  |  | -72.7628 |  |  | -435.0479 |  |  | -1327.7857 |  |  | -2952.0925 |  |  | -5301.8291 |  |  | -7921.5253 |  |  | -10696.8176 |  |  | -13871.9254
[13 empty] | P2 at this iteration flow rate |  |  | 27.827 |  |  | 28.8972 |  |  | 50.5926 |  |  | 123.0496 |  |  | 301.5971 |  |  | 626.4585 |  |  | 1096.4058 |  |  | 1620.3451 |  |  | 2175.4035 |  |  | 2810.4251
[13 empty] | Delta P at this iteration flow rate |  |  | 13.2381 |  |  | 6.8168 |  |  | -123.3553 |  |  | -558.0975 |  |  | -1629.3829 |  |  | -3578.551 |  |  | -6398.235 |  |  | -9541.8704 |  |  | -12872.2211 |  |  | -16682.3504
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 35.8937 |  |  | 30.2489 |  |  | -60.8974 |  |  | -346.4607 |  |  | -995.8987 |  |  | -2057.992 |  |  | -3402.8594 |  |  | -4606.6619 |  |  | -5362.0662 |  |  | -5227.9834
[13 empty] | C Non choked w/ reducers | 7 |  | 188.3185 |  |  | 303.7102 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 114.3659 |  |  | 144.177 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 188.3185 |  |  | 303.7102 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 183.5885 | 685.0915 |  | 292.1102 | 792.335 |  | 5500 | 1959.5388 |  | 5500 | 3816.6814 |  | 5500 | 6403.2041 |  | 5500 | 9439.1072 |  | 5500 | 12596.5252 |  | 5500 | 15370.1546 |  | 5500 | 17844.2723 |  | 5500 | 20308.4464
[13 empty] | Next iteration flow rate |  |  | 698.7933 | Abs Value of | Flow this | 800.2584 | Abs Value of | Flow this | 1979.1342 | Abs Value of | Flow this | 3854.8482 | Abs Value of | Flow this | 6467.2361 | Abs Value of | Flow this | 9533.4983 | Abs Value of | Flow this | 12722.4905 | Abs Value of | Flow this | 15523.8561 | Abs Value of | Flow this | 18022.7151 | Abs Value of | Flow this | 20511.5309 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 40.4247 |  |  | 35.2879 |  |  | -75.3693 |  |  | -444.9364 |  |  | -1355.6182 |  |  | -3012.5736 |  |  | -5409.5399 |  |  | -8081.892 |  |  | -10912.9676 |  |  | -14151.8951
[13 empty] | P2 at this iteration flow rate |  |  | 27.9551 |  |  | 28.9824 |  |  | 51.1139 |  |  | 125.0273 |  |  | 307.1636 |  |  | 638.5547 |  |  | 1117.948 |  |  | 1652.4184 |  |  | 2218.6335 |  |  | 2866.419
[13 empty] | Delta P at this iteration flow rate |  |  | 12.4696 |  |  | 6.3054 |  |  | -126.4832 |  |  | -569.9637 |  |  | -1662.7819 |  |  | -3651.1283 |  |  | -6527.4879 |  |  | -9734.3104 |  |  | -13131.6011 |  |  | -17018.3141
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 35.3279 |  |  | 29.8834 |  |  | -63.0658 |  |  | -354.3277 |  |  | -1016.7674 |  |  | -2100.1489 |  |  | -3471.9854 |  |  | -4699.916 |  |  | -5470.4127 |  |  | -5333.4937
[13 empty] | C Non choked w/ reducers | 7 |  | 197.9151 |  |  | 318.944 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 117.5836 |  |  | 146.5065 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 197.9151 |  |  | 318.944 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 193.1851 | 698.7933 |  | 307.344 | 800.2584 |  | 5500 | 1979.1342 |  | 5500 | 3854.8482 |  | 5500 | 6467.2361 |  | 5500 | 9533.4983 |  | 5500 | 12722.4905 |  | 5500 | 15523.8561 |  | 5500 | 18022.7151 |  | 5500 | 20511.5309
[13 empty] | Next iteration flow rate |  |  | 712.7692 | Abs Value of | Flow this | 808.2609 | Abs Value of | Flow this | 1998.9255 | Abs Value of | Flow this | 3893.3967 | Abs Value of | Flow this | 6531.9085 | Abs Value of | Flow this | 9628.8333 | Abs Value of | Flow this | 12849.7154 | Abs Value of | Flow this | 15679.0947 | Abs Value of | Flow this | 18202.9422 | Abs Value of | Flow this | 20716.6462 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 39.7584 |  |  | 34.8531 |  |  | -78.0282 |  |  | -455.0237 |  |  | -1384.0102 |  |  | -3074.2703 |  |  | -5519.4157 |  |  | -8245.4821 |  |  | -11133.4623 |  |  | -14437.4922
[13 empty] | P2 at this iteration flow rate |  |  | 28.0883 |  |  | 29.0694 |  |  | 51.6456 |  |  | 127.0447 |  |  | 312.842 |  |  | 650.8941 |  |  | 1139.9231 |  |  | 1685.1364 |  |  | 2262.7325 |  |  | 2923.5384
[13 empty] | Delta P at this iteration flow rate |  |  | 11.6701 |  |  | 5.7838 |  |  | -129.6739 |  |  | -582.0684 |  |  | -1696.8522 |  |  | -3725.1644 |  |  | -6659.3388 |  |  | -9930.6185 |  |  | -13396.1947 |  |  | -17361.0306
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 34.7392 |  |  | 29.5106 |  |  | -65.2778 |  |  | -362.3528 |  |  | -1038.0556 |  |  | -2143.1531 |  |  | -3542.5008 |  |  | -4795.0444 |  |  | -5580.937 |  |  | -5441.1247
[13 empty] | C Non choked w/ reducers | 7 |  | 208.6739 |  |  | 336.3475 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 120.9472 |  |  | 148.9033 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 208.6739 |  |  | 336.3475 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 203.9439 | 712.7692 |  | 324.7475 | 808.2609 |  | 5500 | 1998.9255 |  | 5500 | 3893.3967 |  | 5500 | 6531.9085 |  | 5500 | 9628.8333 |  | 5500 | 12849.7154 |  | 5500 | 15679.0947 |  | 5500 | 18202.9422 |  | 5500 | 20716.6462
[13 empty] | Next iteration flow rate |  |  | 727.0245 | Abs Value of | Flow this | 816.3436 | Abs Value of | Flow this | 2018.9148 | Abs Value of | Flow this | 3932.3306 | Abs Value of | Flow this | 6597.2276 | Abs Value of | Flow this | 9725.1216 | Abs Value of | Flow this | 12978.2125 | Abs Value of | Flow this | 15835.8857 | Abs Value of | Flow this | 18384.9716 | Abs Value of | Flow this | 20923.8127 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 39.0653 |  |  | 34.4097 |  |  | -80.7406 |  |  | -465.3137 |  |  | -1412.9728 |  |  | -3137.2072 |  |  | -5631.4999 |  |  | -8412.3603 |  |  | -11358.3889 |  |  | -14728.8298
[13 empty] | P2 at this iteration flow rate |  |  | 28.2269 |  |  | 29.1581 |  |  | 52.1881 |  |  | 129.1027 |  |  | 318.6346 |  |  | 663.4814 |  |  | 1162.34 |  |  | 1718.5121 |  |  | 2307.7178 |  |  | 2981.806
[13 empty] | Delta P at this iteration flow rate |  |  | 10.8383 |  |  | 5.2516 |  |  | -132.9287 |  |  | -594.4164 |  |  | -1731.6074 |  |  | -3800.6886 |  |  | -6793.8399 |  |  | -10130.8723 |  |  | -13666.1067 |  |  | -17710.6357
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 34.1268 |  |  | 29.1303 |  |  | -67.5342 |  |  | -370.5392 |  |  | -1059.7717 |  |  | -2187.0218 |  |  | -3614.4336 |  |  | -4892.0849 |  |  | -5693.6828 |  |  | -5550.9191
[13 empty] | C Non choked w/ reducers | 7 |  | 220.8641 |  |  | 356.5077 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 124.4682 |  |  | 151.3708 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 220.8641 |  |  | 356.5077 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 216.1341 | 727.0245 |  | 344.9077 | 816.3436 |  | 5500 | 2018.9148 |  | 5500 | 3932.3306 |  | 5500 | 6597.2276 |  | 5500 | 9725.1216 |  | 5500 | 12978.2125 |  | 5500 | 15835.8857 |  | 5500 | 18384.9716 |  | 5500 | 20923.8127
[13 empty] | Next iteration flow rate |  |  | 741.565 | Abs Value of | Flow this | 824.507 | Abs Value of | Flow this | 2039.1039 | Abs Value of | Flow this | 3971.654 | Abs Value of | Flow this | 6663.1998 | Abs Value of | Flow this | 9822.3729 | Abs Value of | Flow this | 13107.9946 | Abs Value of | Flow this | 15994.2445 | Abs Value of | Flow this | 18568.8213 | Abs Value of | Flow this | 21133.0508 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 38.3441 |  |  | 33.9573 |  |  | -83.5075 |  |  | -475.8105 |  |  | -1442.5176 |  |  | -3201.409 |  |  | -5745.8371 |  |  | -8582.5927 |  |  | -11587.8365 |  |  | -15026.0233
[13 empty] | P2 at this iteration flow rate |  |  | 28.3712 |  |  | 29.2485 |  |  | 52.7415 |  |  | 131.2021 |  |  | 324.5435 |  |  | 676.3218 |  |  | 1185.2074 |  |  | 1752.5585 |  |  | 2353.6073 |  |  | 3041.2447
[13 empty] | Delta P at this iteration flow rate |  |  | 9.9729 |  |  | 4.7087 |  |  | -136.249 |  |  | -607.0126 |  |  | -1767.0611 |  |  | -3877.7308 |  |  | -6931.0445 |  |  | -10335.1513 |  |  | -13941.4438 |  |  | -18067.2679
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 33.4896 |  |  | 28.7424 |  |  | -69.836 |  |  | -378.8901 |  |  | -1081.9242 |  |  | -2231.7721 |  |  | -3687.8122 |  |  | -4991.0759 |  |  | -5808.6949 |  |  | -5662.9204
[13 empty] | C Non choked w/ reducers | 7 |  | 234.8526 |  |  | 380.2626 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 128.1596 |  |  | 153.9128 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 234.8526 |  |  | 380.2626 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 230.1226 | 741.565 |  | 368.6626 | 824.507 |  | 5500 | 2039.1039 |  | 5500 | 3971.654 |  | 5500 | 6663.1998 |  | 5500 | 9822.3729 |  | 5500 | 13107.9946 |  | 5500 | 15994.2445 |  | 5500 | 18568.8213 |  | 5500 | 21133.0508
[13 empty] | Next iteration flow rate |  |  | 756.3963 | Abs Value of | Flow this | 832.7521 | Abs Value of | Flow this | 2059.495 | Abs Value of | Flow this | 4011.3705 | Abs Value of | Flow this | 6729.8318 | Abs Value of | Flow this | 9920.5966 | Abs Value of | Flow this | 13239.0746 | Abs Value of | Flow this | 16154.187 | Abs Value of | Flow this | 18754.5096 | Abs Value of | Flow this | 21344.3813 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 37.5938 |  |  | 33.4958 |  |  | -86.33 |  |  | -486.5183 |  |  | -1472.6562 |  |  | -3266.9014 |  |  | -5862.4724 |  |  | -8756.2469 |  |  | -11821.896 |  |  | -15329.1904
[13 empty] | P2 at this iteration flow rate |  |  | 28.5212 |  |  | 29.3408 |  |  | 53.306 |  |  | 133.3437 |  |  | 330.5712 |  |  | 689.4203 |  |  | 1208.5345 |  |  | 1787.2894 |  |  | 2400.4192 |  |  | 3101.8781
[13 empty] | Delta P at this iteration flow rate |  |  | 9.0725 |  |  | 4.155 |  |  | -139.636 |  |  | -619.8619 |  |  | -1803.2274 |  |  | -3956.3216 |  |  | -7071.0069 |  |  | -10543.5362 |  |  | -14222.3153 |  |  | -18431.0684
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 32.8266 |  |  | 28.3466 |  |  | -72.1841 |  |  | -387.4089 |  |  | -1104.5221 |  |  | -2277.422 |  |  | -3762.6658 |  |  | -5092.0566 |  |  | -5926.0187 |  |  | -5777.1729
[13 empty] | C Non choked w/ reducers | 7 |  | 251.1552 |  |  | 408.8587 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 132.0362 |  |  | 156.5332 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 251.1552 |  |  | 408.8587 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 246.4252 | 756.3963 |  | 397.2587 | 832.7521 |  | 5500 | 2059.495 |  | 5500 | 4011.3705 |  | 5500 | 6729.8318 |  | 5500 | 9920.5966 |  | 5500 | 13239.0746 |  | 5500 | 16154.187 |  | 5500 | 18754.5096 |  | 5500 | 21344.3813
[13 empty] | Next iteration flow rate |  |  | 771.5243 | Abs Value of | Flow this | 841.0796 | Abs Value of | Flow this | 2080.0899 | Abs Value of | Flow this | 4051.4842 | Abs Value of | Flow this | 6797.1302 | Abs Value of | Flow this | 10019.8025 | Abs Value of | Flow this | 13371.4653 | Abs Value of | Flow this | 16315.7288 | Abs Value of | Flow this | 18942.0547 | Abs Value of | Flow this | 21557.8251 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 36.8131 |  |  | 33.0251 |  |  | -89.2093 |  |  | -497.4413 |  |  | -1503.4006 |  |  | -3333.7101 |  |  | -5981.4522 |  |  | -8933.3914 |  |  | -12060.6602 |  |  | -15638.4511
[13 empty] | P2 at this iteration flow rate |  |  | 28.6774 |  |  | 29.435 |  |  | 53.8819 |  |  | 135.5283 |  |  | 336.7201 |  |  | 702.782 |  |  | 1232.3304 |  |  | 1822.7183 |  |  | 2448.172 |  |  | 3163.7302
[13 empty] | Delta P at this iteration flow rate |  |  | 8.1358 |  |  | 3.5901 |  |  | -143.0911 |  |  | -632.9696 |  |  | -1840.1207 |  |  | -4036.4921 |  |  | -7213.7826 |  |  | -10756.1097 |  |  | -14508.8322 |  |  | -18802.1813
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 32.1369 |  |  | 27.943 |  |  | -74.5793 |  |  | -396.099 |  |  | -1127.5741 |  |  | -2323.9894 |  |  | -3839.0239 |  |  | -5195.0671 |  |  | -6045.7006 |  |  | -5893.7219
[13 empty] | C Non choked w/ reducers | 7 |  | 270.5247 |  |  | 444.2495 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 136.1144 |  |  | 159.2365 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 270.5247 |  |  | 444.2495 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 265.7947 | 771.5243 |  | 432.6495 | 841.0796 |  | 5500 | 2080.0899 |  | 5500 | 4051.4842 |  | 5500 | 6797.1302 |  | 5500 | 10019.8025 |  | 5500 | 13371.4653 |  | 5500 | 16315.7288 |  | 5500 | 18942.0547 |  | 5500 | 21557.8251
[13 empty] | Next iteration flow rate |  |  | 786.9547 | Abs Value of | Flow this | 849.4904 | Abs Value of | Flow this | 2100.8908 | Abs Value of | Flow this | 4091.999 | Abs Value of | Flow this | 6865.1015 | Abs Value of | Flow this | 10120.0006 | Abs Value of | Flow this | 13505.18 | Abs Value of | Flow this | 16478.8861 | Abs Value of | Flow this | 19131.4752 | Abs Value of | Flow this | 21773.4034 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 36.001 |  |  | 32.5449 |  |  | -92.1464 |  |  | -508.5839 |  |  | -1534.7629 |  |  | -3401.8617 |  |  | -6102.8234 |  |  | -9114.0966 |  |  | -12304.2235 |  |  | -15953.928
[13 empty] | P2 at this iteration flow rate |  |  | 28.8398 |  |  | 29.531 |  |  | 54.4693 |  |  | 137.7568 |  |  | 342.9926 |  |  | 716.4123 |  |  | 1256.6047 |  |  | 1858.8593 |  |  | 2496.8847 |  |  | 3226.8256
[13 empty] | Delta P at this iteration flow rate |  |  | 7.1612 |  |  | 3.0138 |  |  | -146.6157 |  |  | -646.3407 |  |  | -1877.7555 |  |  | -4118.274 |  |  | -7359.428 |  |  | -10972.9559 |  |  | -14801.1081 |  |  | -19180.7536
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 31.4194 |  |  | 27.5312 |  |  | -77.0227 |  |  | -404.9637 |  |  | -1151.0895 |  |  | -2371.4929 |  |  | -3916.9168 |  |  | -5300.148 |  |  | -6167.7882 |  |  | -6012.6135
[13 empty] | C Non choked w/ reducers | 7 |  | 294.113 |  |  | 489.7126 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 140.4132 |  |  | 162.0272 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 294.113 |  |  | 489.7126 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 289.383 | 786.9547 |  | 478.1126 | 849.4904 |  | 5500 | 2100.8908 |  | 5500 | 4091.999 |  | 5500 | 6865.1015 |  | 5500 | 10120.0006 |  | 5500 | 13505.18 |  | 5500 | 16478.8861 |  | 5500 | 19131.4752 |  | 5500 | 21773.4034
[13 empty] | Next iteration flow rate |  |  | 802.6938 | Abs Value of | Flow this | 857.9853 | Abs Value of | Flow this | 2121.8997 | Abs Value of | Flow this | 4132.919 | Abs Value of | Flow this | 6933.7525 | Abs Value of | Flow this | 10221.2006 | Abs Value of | Flow this | 13640.2318 | Abs Value of | Flow this | 16643.675 | Abs Value of | Flow this | 19322.79 | Abs Value of | Flow this | 21991.1374 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 35.156 |  |  | 32.055 |  |  | -95.1426 |  |  | -519.9504 |  |  | -1566.7557 |  |  | -3471.3831 |  |  | -6226.6341 |  |  | -9298.434 |  |  | -12552.6824 |  |  | -16275.7459
[13 empty] | P2 at this iteration flow rate |  |  | 29.0088 |  |  | 29.629 |  |  | 55.0685 |  |  | 140.0301 |  |  | 349.3911 |  |  | 730.3166 |  |  | 1281.3668 |  |  | 1895.7268 |  |  | 2546.5765 |  |  | 3291.1892
[13 empty] | Delta P at this iteration flow rate |  |  | 6.1472 |  |  | 2.426 |  |  | -150.2111 |  |  | -659.9805 |  |  | -1916.1468 |  |  | -4201.6997 |  |  | -7508.0009 |  |  | -11194.1608 |  |  | -15099.2588 |  |  | -19566.9351
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 30.6728 |  |  | 27.1111 |  |  | -79.5152 |  |  | -414.0065 |  |  | -1175.0775 |  |  | -2419.9511 |  |  | -3996.3753 |  |  | -5407.3411 |  |  | -6292.3298 |  |  | -6133.8948
[13 empty] | C Non choked w/ reducers | 7 |  | 323.793 |  |  | 551.2863 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 144.954 |  |  | 164.9104 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 323.793 |  |  | 551.2863 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 319.063 | 802.6938 |  | 539.6863 | 857.9853 |  | 5500 | 2121.8997 |  | 5500 | 4132.919 |  | 5500 | 6933.7525 |  | 5500 | 10221.2006 |  | 5500 | 13640.2318 |  | 5500 | 16643.675 |  | 5500 | 19322.79 |  | 5500 | 21991.1374
[13 empty] | Next iteration flow rate |  |  | 818.7477 | Abs Value of | Flow this | 866.5651 | Abs Value of | Flow this | 2143.1187 | Abs Value of | Flow this | 4174.2482 | Abs Value of | Flow this | 7003.09 | Abs Value of | Flow this | 10323.4126 | Abs Value of | Flow this | 13776.6341 | Abs Value of | Flow this | 16810.1117 | Abs Value of | Flow this | 19516.0179 | Abs Value of | Flow this | 22211.0488 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 34.2769 |  |  | 31.5553 |  |  | -98.1989 |  |  | -531.5455 |  |  | -1599.3915 |  |  | -3542.3019 |  |  | -6352.9335 |  |  | -9486.4765 |  |  | -12806.1353 |  |  | -16604.0325
[13 empty] | P2 at this iteration flow rate |  |  | 29.1846 |  |  | 29.7289 |  |  | 55.6798 |  |  | 142.3491 |  |  | 355.9183 |  |  | 744.5004 |  |  | 1306.6267 |  |  | 1933.3353 |  |  | 2597.2671 |  |  | 3356.8465
[13 empty] | Delta P at this iteration flow rate |  |  | 5.0923 |  |  | 1.8263 |  |  | -153.8787 |  |  | -673.8946 |  |  | -1955.3098 |  |  | -4286.8023 |  |  | -7659.5602 |  |  | -11419.8118 |  |  | -15403.4023 |  |  | -19960.8789
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 29.8961 |  |  | 26.6826 |  |  | -82.0578 |  |  | -423.2312 |  |  | -1199.5477 |  |  | -2469.3834 |  |  | -4077.431 |  |  | -5516.6888 |  |  | -6419.3746 |  |  | -6257.6139
[13 empty] | C Non choked w/ reducers | 7 |  | 362.8696 |  |  | 641.7302 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 149.7614 |  |  | 167.8917 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 362.8696 |  |  | 641.7302 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 358.1396 | 818.7477 |  | 630.1302 | 866.5651 |  | 5500 | 2143.1187 |  | 5500 | 4174.2482 |  | 5500 | 7003.09 |  | 5500 | 10323.4126 |  | 5500 | 13776.6341 |  | 5500 | 16810.1117 |  | 5500 | 19516.0179 |  | 5500 | 22211.0488
[13 empty] | Next iteration flow rate |  |  | 835.1227 | Abs Value of | Flow this | 875.2308 | Abs Value of | Flow this | 2164.5499 | Abs Value of | Flow this | 4215.9907 | Abs Value of | Flow this | 7073.1209 | Abs Value of | Flow this | 10426.6467 | Abs Value of | Flow this | 13914.4005 | Abs Value of | Flow this | 16978.2128 | Abs Value of | Flow this | 19711.178 | Abs Value of | Flow this | 22433.1593 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 33.3623 |  |  | 31.0455 |  |  | -101.3168 |  |  | -543.3735 |  |  | -1632.6833 |  |  | -3614.6462 |  |  | -6481.7715 |  |  | -9678.2987 |  |  | -13064.6826 |  |  | -16938.9175
[13 empty] | P2 at this iteration flow rate |  |  | 29.3675 |  |  | 29.8309 |  |  | 56.3034 |  |  | 144.7147 |  |  | 362.5767 |  |  | 758.9692 |  |  | 1332.3943 |  |  | 1971.6997 |  |  | 2648.9765 |  |  | 3423.8235
[13 empty] | Delta P at this iteration flow rate |  |  | 3.9947 |  |  | 1.2146 |  |  | -157.6201 |  |  | -688.0883 |  |  | -1995.2599 |  |  | -4373.6155 |  |  | -7814.1658 |  |  | -11649.9984 |  |  | -15713.6591 |  |  | -20362.741
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 29.088 |  |  | 26.2454 |  |  | -84.6515 |  |  | -432.6412 |  |  | -1224.5098 |  |  | -2519.8092 |  |  | -4160.1159 |  |  | -5628.2343 |  |  | -6548.9731 |  |  | -6383.8197
[13 empty] | C Non choked w/ reducers | 7 |  | 417.8911 |  |  | 794.7706 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 154.864 |  |  | 170.9769 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 417.8911 |  |  | 794.7706 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 413.1611 | 835.1227 |  | 783.1706 | 875.2308 |  | 5500 | 2164.5499 |  | 5500 | 4215.9907 |  | 5500 | 7073.1209 |  | 5500 | 10426.6467 |  | 5500 | 13914.4005 |  | 5500 | 16978.2128 |  | 5500 | 19711.178 |  | 5500 | 22433.1593
[13 empty] | Next iteration flow rate |  |  | 851.8251 | Abs Value of | Flow this | 883.9831 | Abs Value of | Flow this | 2186.1954 | Abs Value of | Flow this | 4258.1506 | Abs Value of | Flow this | 7143.8521 | Abs Value of | Flow this | 10530.9132 | Abs Value of | Flow this | 14053.5445 | Abs Value of | Flow this | 17147.995 | Abs Value of | Flow this | 19908.2898 | Abs Value of | Flow this | 22657.4909 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 32.4107 |  |  | 30.5255 |  |  | -104.4972 |  |  | -555.4394 |  |  | -1666.6442 |  |  | -3688.4446 |  |  | -6613.1991 |  |  | -9873.9765 |  |  | -13328.4268 |  |  | -17280.5338
[13 empty] | P2 at this iteration flow rate |  |  | 29.5579 |  |  | 29.9349 |  |  | 56.9394 |  |  | 147.1279 |  |  | 369.3688 |  |  | 773.7289 |  |  | 1358.6798 |  |  | 2010.8353 |  |  | 2701.7254 |  |  | 3492.1468
[13 empty] | Delta P at this iteration flow rate |  |  | 2.8528 |  |  | 0.59063 |  |  | -161.4367 |  |  | -702.5672 |  |  | -2036.0131 |  |  | -4462.1736 |  |  | -7971.8789 |  |  | -11884.8118 |  |  | -16030.1521 |  |  | -20772.6805
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 28.2472 |  |  | 25.7995 |  |  | -87.2974 |  |  | -442.2404 |  |  | -1249.9736 |  |  | -2571.2486 |  |  | -4244.4627 |  |  | -5742.0219 |  |  | -6681.1764 |  |  | -6512.5623
[13 empty] | C Non choked w/ reducers | 7 |  | 504.392 |  |  | 1151.1358 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 160.2948 |  |  | 174.1727 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 504.392 |  |  | 1151.1358 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 499.662 | 851.8251 |  | 1139.5358 | 883.9831 |  | 5500 | 2186.1954 |  | 5500 | 4258.1506 |  | 5500 | 7143.8521 |  | 5500 | 10530.9132 |  | 5500 | 14053.5445 |  | 5500 | 17147.995 |  | 5500 | 19908.2898 |  | 5500 | 22657.4909
[13 empty] | Next iteration flow rate |  |  | 868.8616 | Abs Value of | Flow this | 892.8229 | Abs Value of | Flow this | 2208.0573 | Abs Value of | Flow this | 4300.7321 | Abs Value of | Flow this | 7215.2906 | Abs Value of | Flow this | 10636.2223 | Abs Value of | Flow this | 14194.0799 | Abs Value of | Flow this | 17319.4749 | Abs Value of | Flow this | 20107.3727 | Abs Value of | Flow this | 22884.0658 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 31.4207 |  |  | 29.9951 |  |  | -107.7416 |  |  | -567.7477 |  |  | -1701.2878 |  |  | -3763.7264 |  |  | -6747.2684 |  |  | -10073.5875 |  |  | -13597.4721 |  |  | -17629.0165
[13 empty] | P2 at this iteration flow rate |  |  | 29.7559 |  |  | 30.041 |  |  | 57.5883 |  |  | 149.5895 |  |  | 376.2976 |  |  | 788.7853 |  |  | 1385.4937 |  |  | 2050.7575 |  |  | 2755.5344 |  |  | 3561.8433
[13 empty] | Delta P at this iteration flow rate |  |  | 1.6648 |  |  | -0.045908 |  |  | -165.33 |  |  | -717.3373 |  |  | -2077.5854 |  |  | -4552.5117 |  |  | -8132.7621 |  |  | -12124.345 |  |  | -16353.0066 |  |  | -21190.8598
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 27.3725 |  |  | 25.3446 |  |  | -89.9964 |  |  | -452.0326 |  |  | -1275.9492 |  |  | -2623.722 |  |  | -4330.5049 |  |  | -5858.0967 |  |  | -6816.0371 |  |  | -6643.8926
[13 empty] | C Non choked w/ reducers | 7 |  | 673.4784 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 166.0926 |  |  | 177.486 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 673.4784 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 668.7484 | 868.8616 |  | 5500 | 892.8229 |  | 5500 | 2208.0573 |  | 5500 | 4300.7321 |  | 5500 | 7215.2906 |  | 5500 | 10636.2223 |  | 5500 | 14194.0799 |  | 5500 | 17319.4749 |  | 5500 | 20107.3727 |  | 5500 | 22884.0658
[13 empty] | Next iteration flow rate |  |  | 886.2389 | Abs Value of | Flow this | 901.7512 | Abs Value of | Flow this | 2230.1379 | Abs Value of | Flow this | 4343.7394 | Abs Value of | Flow this | 7287.4435 | Abs Value of | Flow this | 10742.5845 | Abs Value of | Flow this | 14336.0207 | Abs Value of | Flow this | 17492.6697 | Abs Value of | Flow this | 20308.4464 | Abs Value of | Flow this | 23112.9064 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 30.3907 |  |  | 29.454 |  |  | -111.0513 |  |  | -580.3035 |  |  | -1736.6277 |  |  | -3840.5213 |  |  | -6884.0325 |  |  | -10277.2106 |  |  | -13871.9254 |  |  | -17984.5038
[13 empty] | P2 at this iteration flow rate |  |  | 29.9619 |  |  | 30.1492 |  |  | 58.2503 |  |  | 152.1007 |  |  | 383.3655 |  |  | 804.1443 |  |  | 1412.8465 |  |  | 2091.4821 |  |  | 2810.4251 |  |  | 3632.9408
[13 empty] | Delta P at this iteration flow rate |  |  | 0.4288 |  |  | -0.69524 |  |  | -169.3015 |  |  | -732.4041 |  |  | -2119.9932 |  |  | -4644.6655 |  |  | -8296.879 |  |  | -12368.6927 |  |  | -16682.3504 |  |  | -21617.4445
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 26.4624 |  |  | 24.8806 |  |  | -92.7497 |  |  | -462.0215 |  |  | -1302.4469 |  |  | -2677.25 |  |  | -4418.2766 |  |  | -5976.5045 |  |  | -6953.6085 |  |  | -6777.8627
[13 empty] | C Non choked w/ reducers | 7 |  | 1353.5662 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 172.3029 |  |  | 180.9248 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1353.5662 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1348.8362 | 886.2389 |  | 5500 | 901.7512 |  | 5500 | 2230.1379 |  | 5500 | 4343.7394 |  | 5500 | 7287.4435 |  | 5500 | 10742.5845 |  | 5500 | 14336.0207 |  | 5500 | 17492.6697 |  | 5500 | 20308.4464 |  | 5500 | 23112.9064
[13 empty] | Next iteration flow rate |  |  | 903.9636 | Abs Value of | Flow this | 910.7687 | Abs Value of | Flow this | 2252.4393 | Abs Value of | Flow this | 4387.1768 | Abs Value of | Flow this | 7360.318 | Abs Value of | Flow this | 10850.0104 | Abs Value of | Flow this | 14479.3809 | Abs Value of | Flow this | 17667.5964 | Abs Value of | Flow this | 20511.5309 | Abs Value of | Flow this | 23344.0355 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 29.319 |  |  | 28.902 |  |  | -114.4274 |  |  | -593.1116 |  |  | -1772.6779 |  |  | -3918.8598 |  |  | -7023.5456 |  |  | -10484.9265 |  |  | -14151.8951 |  |  | -18347.1363
[13 empty] | P2 at this iteration flow rate |  |  | 30.1762 |  |  | 30.2596 |  |  | 58.9255 |  |  | 154.6623 |  |  | 390.5756 |  |  | 819.812 |  |  | 1440.7491 |  |  | 2133.0253 |  |  | 2866.419 |  |  | 3705.4673
[13 empty] | Delta P at this iteration flow rate |  |  | -0.85715 |  |  | -1.3576 |  |  | -173.3529 |  |  | -747.7739 |  |  | -2163.2535 |  |  | -4738.6717 |  |  | -8464.2947 |  |  | -12617.9518 |  |  | -17018.3141 |  |  | -22052.6036
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 25.5156 |  |  | 24.4072 |  |  | -95.5583 |  |  | -472.2113 |  |  | -1329.4772 |  |  | -2731.854 |  |  | -4507.8125 |  |  | -6097.2924 |  |  | -7093.945 |  |  | -6914.5255
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 178.9801 |  |  | 184.4975 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 903.9636 |  | 5500 | 910.7687 |  | 5500 | 2252.4393 |  | 5500 | 4387.1768 |  | 5500 | 7360.318 |  | 5500 | 10850.0104 |  | 5500 | 14479.3809 |  | 5500 | 17667.5964 |  | 5500 | 20511.5309 |  | 5500 | 23344.0355
[13 empty] | Next iteration flow rate |  |  | 922.0429 | Abs Value of | Flow this | 919.8764 | Abs Value of | Flow this | 2274.9637 | Abs Value of | Flow this | 4431.0486 | Abs Value of | Flow this | 7433.9211 | Abs Value of | Flow this | 10958.5105 | Abs Value of | Flow this | 14624.1747 | Abs Value of | Flow this | 17844.2723 | Abs Value of | Flow this | 20716.6462 | Abs Value of | Flow this | 23577.4758 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 28.2041 |  |  | 28.3389 |  |  | -117.8714 |  |  | -606.1771 |  |  | -1809.4528 |  |  | -3998.7729 |  |  | -7165.8629 |  |  | -10696.8176 |  |  | -14437.4922 |  |  | -18717.0578
[13 empty] | P2 at this iteration flow rate |  |  | 30.3992 |  |  | 30.3722 |  |  | 59.6143 |  |  | 157.2754 |  |  | 397.9306 |  |  | 835.7946 |  |  | 1469.2126 |  |  | 2175.4035 |  |  | 2923.5384 |  |  | 3779.4516
[13 empty] | Delta P at this iteration flow rate |  |  | -2.1951 |  |  | -2.0333 |  |  | -177.4857 |  |  | -763.4525 |  |  | -2207.3833 |  |  | -4834.5675 |  |  | -8635.0754 |  |  | -12872.2211 |  |  | -17361.0306 |  |  | -22496.5093
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 24.5305 |  |  | 23.9244 |  |  | -98.4234 |  |  | -482.6058 |  |  | -1357.0509 |  |  | -2787.5555 |  |  | -4599.148 |  |  | -6220.5081 |  |  | -7237.1023 |  |  | -7053.9353
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 186.1891 |  |  | 188.2135 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 922.0429 |  | 5500 | 919.8764 |  | 5500 | 2274.9637 |  | 5500 | 4431.0486 |  | 5500 | 7433.9211 |  | 5500 | 10958.5105 |  | 5500 | 14624.1747 |  | 5500 | 17844.2723 |  | 5500 | 20716.6462 |  | 5500 | 23577.4758
[13 empty] | Next iteration flow rate |  |  | 940.4838 | Abs Value of | Flow this | 929.0751 | Abs Value of | Flow this | 2297.7133 | Abs Value of | Flow this | 4475.3591 | Abs Value of | Flow this | 7508.2604 | Abs Value of | Flow this | 11068.0956 | Abs Value of | Flow this | 14770.4165 | Abs Value of | Flow this | 18022.7151 | Abs Value of | Flow this | 20923.8127 | Abs Value of | Flow this | 23813.2506 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 27.0441 |  |  | 27.7645 |  |  | -121.3847 |  |  | -619.5053 |  |  | -1846.9668 |  |  | -4080.2922 |  |  | -7311.0407 |  |  | -10912.9676 |  |  | -14728.8298 |  |  | -19094.4146
[13 empty] | P2 at this iteration flow rate |  |  | 30.6312 |  |  | 30.4871 |  |  | 60.3169 |  |  | 159.9411 |  |  | 405.4334 |  |  | 852.0984 |  |  | 1498.2481 |  |  | 2218.6335 |  |  | 2981.806 |  |  | 3854.9229
[13 empty] | Delta P at this iteration flow rate |  |  | -3.587 |  |  | -2.7226 |  |  | -181.7016 |  |  | -779.4464 |  |  | -2252.4001 |  |  | -4932.3907 |  |  | -8809.2889 |  |  | -13131.6011 |  |  | -17710.6357 |  |  | -22949.3376
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 23.5057 |  |  | 23.4318 |  |  | -101.346 |  |  | -493.2093 |  |  | -1385.1787 |  |  | -2844.3766 |  |  | -4692.3194 |  |  | -6346.2004 |  |  | -7383.1371 |  |  | -7196.1472
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 194.009 |  |  | 192.0833 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 940.4838 |  | 5500 | 929.0751 |  | 5500 | 2297.7133 |  | 5500 | 4475.3591 |  | 5500 | 7508.2604 |  | 5500 | 11068.0956 |  | 5500 | 14770.4165 |  | 5500 | 18022.7151 |  | 5500 | 20923.8127 |  | 5500 | 23813.2506
[13 empty] | Next iteration flow rate |  |  | 959.2934 | Abs Value of | Flow this | 938.3659 | Abs Value of | Flow this | 2320.6905 | Abs Value of | Flow this | 4520.1127 | Abs Value of | Flow this | 7583.343 | Abs Value of | Flow this | 11178.7765 | Abs Value of | Flow this | 14918.1206 | Abs Value of | Flow this | 18202.9422 | Abs Value of | Flow this | 21133.0508 | Abs Value of | Flow this | 24051.3831 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 25.8373 |  |  | 27.1785 |  |  | -124.9685 |  |  | -633.1014 |  |  | -1885.2348 |  |  | -4163.4501 |  |  | -7459.1366 |  |  | -11133.4623 |  |  | -15026.0233 |  |  | -19479.3564
[13 empty] | P2 at this iteration flow rate |  |  | 30.8725 |  |  | 30.6043 |  |  | 61.0337 |  |  | 162.6603 |  |  | 413.087 |  |  | 868.73 |  |  | 1527.8673 |  |  | 2262.7325 |  |  | 3041.2447 |  |  | 3931.9113
[13 empty] | Delta P at this iteration flow rate |  |  | -5.0352 |  |  | -3.4258 |  |  | -186.0022 |  |  | -795.7616 |  |  | -2298.3218 |  |  | -5032.1801 |  |  | -8987.004 |  |  | -13396.1947 |  |  | -18067.2679 |  |  | -23411.2677
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 22.4394 |  |  | 22.9293 |  |  | -104.3274 |  |  | -504.0259 |  |  | -1413.872 |  |  | -2902.3398 |  |  | -4787.3636 |  |  | -6474.4191 |  |  | -7532.1071 |  |  | -7341.2175
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 202.5362 |  |  | 196.1184 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 959.2934 |  | 5500 | 938.3659 |  | 5500 | 2320.6905 |  | 5500 | 4520.1127 |  | 5500 | 7583.343 |  | 5500 | 11178.7765 |  | 5500 | 14918.1206 |  | 5500 | 18202.9422 |  | 5500 | 21133.0508 |  | 5500 | 24051.3831
[13 empty] | Next iteration flow rate |  |  | 978.4793 | Abs Value of | Flow this | 947.7495 | Abs Value of | Flow this | 2343.8974 | Abs Value of | Flow this | 4565.3138 | Abs Value of | Flow this | 7659.1764 | Abs Value of | Flow this | 11290.5643 | Abs Value of | Flow this | 15067.3018 | Abs Value of | Flow this | 18384.9716 | Abs Value of | Flow this | 21344.3813 | Abs Value of | Flow this | 24291.8969 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 24.5817 |  |  | 26.5808 |  |  | -128.6244 |  |  | -646.9707 |  |  | -1924.2721 |  |  | -4248.2795 |  |  | -7610.2093 |  |  | -11358.3889 |  |  | -15329.1904 |  |  | -19872.0355
[13 empty] | P2 at this iteration flow rate |  |  | 31.1237 |  |  | 30.7238 |  |  | 61.7649 |  |  | 165.4341 |  |  | 420.8944 |  |  | 885.6959 |  |  | 1558.0819 |  |  | 2307.7178 |  |  | 3101.8781 |  |  | 4010.4471
[13 empty] | Delta P at this iteration flow rate |  |  | -6.5419 |  |  | -4.143 |  |  | -190.3893 |  |  | -812.4049 |  |  | -2345.1665 |  |  | -5133.9754 |  |  | -9168.2912 |  |  | -13666.1067 |  |  | -18431.0684 |  |  | -23882.4826
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 21.33 |  |  | 22.4168 |  |  | -107.3687 |  |  | -515.0599 |  |  | -1443.142 |  |  | -2961.4681 |  |  | -4884.3181 |  |  | -6605.215 |  |  | -7684.0715 |  |  | -7489.2038
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 211.8911 |  |  | 200.3314 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 978.4793 |  | 5500 | 947.7495 |  | 5500 | 2343.8974 |  | 5500 | 4565.3138 |  | 5500 | 7659.1764 |  | 5500 | 11290.5643 |  | 5500 | 15067.3018 |  | 5500 | 18384.9716 |  | 5500 | 21344.3813 |  | 5500 | 24291.8969
[13 empty] | Next iteration flow rate |  |  | 998.0489 | Abs Value of | Flow this | 957.227 | Abs Value of | Flow this | 2367.3363 | Abs Value of | Flow this | 4610.9669 | Abs Value of | Flow this | 7735.7682 | Abs Value of | Flow this | 11403.47 | Abs Value of | Flow this | 15217.9749 | Abs Value of | Flow this | 18568.8213 | Abs Value of | Flow this | 21557.8251 | Abs Value of | Flow this | 24534.8159 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 23.2754 |  |  | 25.9711 |  |  | -132.3537 |  |  | -661.1188 |  |  | -1964.094 |  |  | -4334.8139 |  |  | -7764.3185 |  |  | -11587.8365 |  |  | -15638.4511 |  |  | -20272.6074
[13 empty] | P2 at this iteration flow rate |  |  | 31.3849 |  |  | 30.8458 |  |  | 62.5107 |  |  | 168.2638 |  |  | 428.8588 |  |  | 903.0028 |  |  | 1588.9037 |  |  | 2353.6073 |  |  | 3163.7302 |  |  | 4090.5615
[13 empty] | Delta P at this iteration flow rate |  |  | -8.1095 |  |  | -4.8747 |  |  | -194.8645 |  |  | -829.3826 |  |  | -2392.9527 |  |  | -5237.8167 |  |  | -9353.2222 |  |  | -13941.4438 |  |  | -18802.1813 |  |  | -24363.1689
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 20.1759 |  |  | 21.8939 |  |  | -110.4712 |  |  | -526.3157 |  |  | -1473.0003 |  |  | -3021.7848 |  |  | -4983.2214 |  |  | -6738.64 |  |  | -7839.0904 |  |  | -7640.1646
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 222.2248 |  |  | 204.7365 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 998.0489 |  | 5500 | 957.227 |  | 5500 | 2367.3363 |  | 5500 | 4610.9669 |  | 5500 | 7735.7682 |  | 5500 | 11403.47 |  | 5500 | 15217.9749 |  | 5500 | 18568.8213 |  | 5500 | 21557.8251 |  | 5500 | 24534.8159
[13 empty] | Next iteration flow rate |  |  | 1018.0099 | Abs Value of | Flow this | 966.7993 | Abs Value of | Flow this | 2391.0097 | Abs Value of | Flow this | 4657.0766 | Abs Value of | Flow this | 7813.1258 | Abs Value of | Flow this | 11517.5046 | Abs Value of | Flow this | 15370.1546 | Abs Value of | Flow this | 18754.5096 | Abs Value of | Flow this | 21773.4034 | Abs Value of | Flow this | 24780.1641 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 21.9163 |  |  | 25.3491 |  |  | -136.1581 |  |  | -675.5514 |  |  | -2004.7163 |  |  | -4423.0877 |  |  | -7921.5253 |  |  | -11821.896 |  |  | -15953.928 |  |  | -20681.2308
[13 empty] | P2 at this iteration flow rate |  |  | 31.6567 |  |  | 30.9702 |  |  | 63.2716 |  |  | 171.1503 |  |  | 436.9833 |  |  | 920.6575 |  |  | 1620.3451 |  |  | 2400.4192 |  |  | 3226.8256 |  |  | 4172.2862
[13 empty] | Delta P at this iteration flow rate |  |  | -9.7404 |  |  | -5.6211 |  |  | -199.4297 |  |  | -846.7016 |  |  | -2441.6995 |  |  | -5343.7452 |  |  | -9541.8704 |  |  | -14222.3153 |  |  | -19180.7536 |  |  | -24853.517
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 18.9751 |  |  | 21.3605 |  |  | -113.636 |  |  | -537.7978 |  |  | -1503.4587 |  |  | -3083.314 |  |  | -5084.1127 |  |  | -6874.7467 |  |  | -7997.2251 |  |  | -7794.1597
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 233.7314 |  |  | 209.3497 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1018.0099 |  | 5500 | 966.7993 |  | 5500 | 2391.0097 |  | 5500 | 4657.0766 |  | 5500 | 7813.1258 |  | 5500 | 11517.5046 |  | 5500 | 15370.1546 |  | 5500 | 18754.5096 |  | 5500 | 21773.4034 |  | 5500 | 24780.1641
[13 empty] | Next iteration flow rate |  |  | 1038.3701 | Abs Value of | Flow this | 976.4673 | Abs Value of | Flow this | 2414.9198 | Abs Value of | Flow this | 4703.6474 | Abs Value of | Flow this | 7891.2571 | Abs Value of | Flow this | 11632.6797 | Abs Value of | Flow this | 15523.8561 | Abs Value of | Flow this | 18942.0547 | Abs Value of | Flow this | 21991.1374 | Abs Value of | Flow this | 25027.9657 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 20.5023 |  |  | 24.7146 |  |  | -140.0389 |  |  | -690.2739 |  |  | -2046.1551 |  |  | -4513.1358 |  |  | -8081.892 |  |  | -12060.6602 |  |  | -16275.7459 |  |  | -21098.0676
[13 empty] | P2 at this iteration flow rate |  |  | 31.9395 |  |  | 31.0971 |  |  | 64.0478 |  |  | 174.0948 |  |  | 445.271 |  |  | 938.6672 |  |  | 1652.4184 |  |  | 2448.172 |  |  | 3291.1892 |  |  | 4255.6535
[13 empty] | Delta P at this iteration flow rate |  |  | -11.4372 |  |  | -6.3825 |  |  | -204.0866 |  |  | -864.3687 |  |  | -2491.4261 |  |  | -5451.8029 |  |  | -9734.3104 |  |  | -14508.8322 |  |  | -19566.9351 |  |  | -25353.7211
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 17.7258 |  |  | 20.8164 |  |  | -116.8645 |  |  | -549.5106 |  |  | -1534.5294 |  |  | -3146.0798 |  |  | -5187.0319 |  |  | -7013.5893 |  |  | -8158.5383 |  |  | -7951.2501
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 246.6645 |  |  | 214.1888 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1038.3701 |  | 5500 | 976.4673 |  | 5500 | 2414.9198 |  | 5500 | 4703.6474 |  | 5500 | 7891.2571 |  | 5500 | 11632.6797 |  | 5500 | 15523.8561 |  | 5500 | 18942.0547 |  | 5500 | 21991.1374 |  | 5500 | 25027.9657
[13 empty] | Next iteration flow rate |  |  | 1059.1375 | Abs Value of | Flow this | 986.232 | Abs Value of | Flow this | 2439.069 | Abs Value of | Flow this | 4750.6838 | Abs Value of | Flow this | 7970.1697 | Abs Value of | Flow this | 11749.0065 | Abs Value of | Flow this | 15679.0947 | Abs Value of | Flow this | 19131.4752 | Abs Value of | Flow this | 22211.0488 | Abs Value of | Flow this | 25278.2454 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 19.0312 |  |  | 24.0673 |  |  | -143.9977 |  |  | -705.2925 |  |  | -2088.4268 |  |  | -4604.9938 |  |  | -8245.4821 |  |  | -12304.2235 |  |  | -16604.0325 |  |  | -21523.2827
[13 empty] | P2 at this iteration flow rate |  |  | 32.2338 |  |  | 31.2265 |  |  | 64.8395 |  |  | 177.0985 |  |  | 453.7254 |  |  | 957.0388 |  |  | 1685.1364 |  |  | 2496.8847 |  |  | 3356.8465 |  |  | 4340.6965
[13 empty] | Delta P at this iteration flow rate |  |  | -13.2025 |  |  | -7.1592 |  |  | -208.8372 |  |  | -882.391 |  |  | -2542.1522 |  |  | -5562.0326 |  |  | -9930.6185 |  |  | -14801.1081 |  |  | -19960.8789 |  |  | -25863.9793
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 16.426 |  |  | 20.2613 |  |  | -120.1578 |  |  | -561.4589 |  |  | -1566.2246 |  |  | -3210.1073 |  |  | -5292.0197 |  |  | -7155.2225 |  |  | -8323.0939 |  |  | -8111.4981
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 261.3627 |  |  | 219.2738 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1059.1375 |  | 5500 | 986.232 |  | 5500 | 2439.069 |  | 5500 | 4750.6838 |  | 5500 | 7970.1697 |  | 5500 | 11749.0065 |  | 5500 | 15679.0947 |  | 5500 | 19131.4752 |  | 5500 | 22211.0488 |  | 5500 | 25278.2454
[13 empty] | Next iteration flow rate |  |  | 1080.3202 | Abs Value of | Flow this | 996.0943 | Abs Value of | Flow this | 2463.4597 | Abs Value of | Flow this | 4798.1907 | Abs Value of | Flow this | 8049.8714 | Abs Value of | Flow this | 11866.4966 | Abs Value of | Flow this | 15835.8857 | Abs Value of | Flow this | 19322.79 | Abs Value of | Flow this | 22433.1593 | Abs Value of | Flow this | 25531.0278 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 17.5007 |  |  | 23.4071 |  |  | -148.036 |  |  | -720.6129 |  |  | -2131.5482 |  |  | -4698.6982 |  |  | -8412.3603 |  |  | -12552.6824 |  |  | -16938.9175 |  |  | -21957.0447
[13 empty] | P2 at this iteration flow rate |  |  | 32.5399 |  |  | 31.3586 |  |  | 65.6472 |  |  | 180.1626 |  |  | 462.3496 |  |  | 975.7796 |  |  | 1718.5121 |  |  | 2546.5765 |  |  | 3423.8235 |  |  | 4427.4489
[13 empty] | Delta P at this iteration flow rate |  |  | -15.0392 |  |  | -7.9515 |  |  | -213.6832 |  |  | -900.7754 |  |  | -2593.8978 |  |  | -5674.4778 |  |  | -10130.8723 |  |  | -15099.2588 |  |  | -20362.741 |  |  | -26384.4937
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 15.0737 |  |  | 19.6951 |  |  | -123.5173 |  |  | -573.6473 |  |  | -1598.5568 |  |  | -3275.4216 |  |  | -5399.1179 |  |  | -7299.7026 |  |  | -8490.9571 |  |  | -8274.967
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 278.2914 |  |  | 224.6274 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1080.3202 |  | 5500 | 996.0943 |  | 5500 | 2463.4597 |  | 5500 | 4798.1907 |  | 5500 | 8049.8714 |  | 5500 | 11866.4966 |  | 5500 | 15835.8857 |  | 5500 | 19322.79 |  | 5500 | 22433.1593 |  | 5500 | 25531.0278
[13 empty] | Next iteration flow rate |  |  | 1101.9266 | Abs Value of | Flow this | 1006.0552 | Abs Value of | Flow this | 2488.0943 | Abs Value of | Flow this | 4846.1726 | Abs Value of | Flow this | 8130.3701 | Abs Value of | Flow this | 11985.1615 | Abs Value of | Flow this | 15994.2445 | Abs Value of | Flow this | 19516.0179 | Abs Value of | Flow this | 22657.4909 | Abs Value of | Flow this | 25786.3381 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 15.9083 |  |  | 22.7335 |  |  | -152.1556 |  |  | -736.2412 |  |  | -2175.5363 |  |  | -4794.286 |  |  | -8582.5927 |  |  | -12806.1353 |  |  | -17280.5338 |  |  | -22399.5253
[13 empty] | P2 at this iteration flow rate |  |  | 32.8583 |  |  | 31.4933 |  |  | 66.4711 |  |  | 183.2882 |  |  | 471.1473 |  |  | 994.8972 |  |  | 1752.5585 |  |  | 2597.2671 |  |  | 3492.1468 |  |  | 4515.9451
[13 empty] | Delta P at this iteration flow rate |  |  | -16.95 |  |  | -8.7598 |  |  | -218.6267 |  |  | -919.5294 |  |  | -2646.6836 |  |  | -5789.1833 |  |  | -10335.1513 |  |  | -15403.4023 |  |  | -20772.6805 |  |  | -26915.4704
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 13.6667 |  |  | 19.1176 |  |  | -126.9443 |  |  | -586.0807 |  |  | -1631.539 |  |  | -3342.0489 |  |  | -5508.3687 |  |  | -7447.0867 |  |  | -8662.1944 |  |  | -8441.7216
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 298.1103 |  |  | 230.2753 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1101.9266 |  | 5500 | 1006.0552 |  | 5500 | 2488.0943 |  | 5500 | 4846.1726 |  | 5500 | 8130.3701 |  | 5500 | 11985.1615 |  | 5500 | 15994.2445 |  | 5500 | 19516.0179 |  | 5500 | 22657.4909 |  | 5500 | 25786.3381
[13 empty] | Next iteration flow rate |  |  | 1123.9652 | Abs Value of | Flow this | 1016.1158 | Abs Value of | Flow this | 2512.9752 | Abs Value of | Flow this | 4894.6343 | Abs Value of | Flow this | 8211.6738 | Abs Value of | Flow this | 12105.0131 | Abs Value of | Flow this | 16154.187 | Abs Value of | Flow this | 19711.178 | Abs Value of | Flow this | 22884.0658 | Abs Value of | Flow this | 26044.2015 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 14.2516 |  |  | 22.0465 |  |  | -156.3579 |  |  | -752.1837 |  |  | -2220.4086 |  |  | -4891.7952 |  |  | -8756.2469 |  |  | -13064.6826 |  |  | -17629.0165 |  |  | -22850.8998
[13 empty] | P2 at this iteration flow rate |  |  | 33.1897 |  |  | 31.6307 |  |  | 67.3116 |  |  | 186.4767 |  |  | 480.1217 |  |  | 1014.399 |  |  | 1787.2894 |  |  | 2648.9765 |  |  | 3561.8433 |  |  | 4606.22
[13 empty] | Delta P at this iteration flow rate |  |  | -18.9381 |  |  | -9.5842 |  |  | -223.6695 |  |  | -938.6604 |  |  | -2700.5303 |  |  | -5906.1942 |  |  | -10543.5362 |  |  | -15713.6591 |  |  | -21190.8598 |  |  | -27457.1198
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 12.203 |  |  | 18.5284 |  |  | -130.4403 |  |  | -598.7641 |  |  | -1665.184 |  |  | -3410.0153 |  |  | -5619.8154 |  |  | -7597.4333 |  |  | -8836.8735 |  |  | -8611.828
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 321.7931 |  |  | 236.247 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1123.9652 |  | 5500 | 1016.1158 |  | 5500 | 2512.9752 |  | 5500 | 4894.6343 |  | 5500 | 8211.6738 |  | 5500 | 12105.0131 |  | 5500 | 16154.187 |  | 5500 | 19711.178 |  | 5500 | 22884.0658 |  | 5500 | 26044.2015
[13 empty] | Next iteration flow rate |  |  | 1146.4445 | Abs Value of | Flow this | 1026.2769 | Abs Value of | Flow this | 2538.105 | Abs Value of | Flow this | 4943.5807 | Abs Value of | Flow this | 8293.7905 | Abs Value of | Flow this | 12226.0633 | Abs Value of | Flow this | 16315.7288 | Abs Value of | Flow this | 19908.2898 | Abs Value of | Flow this | 23112.9064 | Abs Value of | Flow this | 26304.6435 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 12.5279 |  |  | 21.3456 |  |  | -160.6447 |  |  | -768.4466 |  |  | -2266.1828 |  |  | -4991.2643 |  |  | -8933.3914 |  |  | -13328.4268 |  |  | -17984.5038 |  |  | -23311.3469
[13 empty] | P2 at this iteration flow rate |  |  | 33.5344 |  |  | 31.7709 |  |  | 68.1689 |  |  | 189.7293 |  |  | 489.2766 |  |  | 1034.2929 |  |  | 1822.7183 |  |  | 2701.7254 |  |  | 3632.9408 |  |  | 4698.3094
[13 empty] | Delta P at this iteration flow rate |  |  | -21.0065 |  |  | -10.4253 |  |  | -228.8137 |  |  | -958.1759 |  |  | -2755.4594 |  |  | -6025.5572 |  |  | -10756.1097 |  |  | -16030.1521 |  |  | -21617.4445 |  |  | -28009.6563
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 10.6801 |  |  | 17.9273 |  |  | -134.0065 |  |  | -611.7023 |  |  | -1699.5054 |  |  | -3479.3478 |  |  | -5733.5022 |  |  | -7750.8018 |  |  | -9015.0637 |  |  | -8785.3536
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 350.851 |  |  | 242.5763 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1146.4445 |  | 5500 | 1026.2769 |  | 5500 | 2538.105 |  | 5500 | 4943.5807 |  | 5500 | 8293.7905 |  | 5500 | 12226.0633 |  | 5500 | 16315.7288 |  | 5500 | 19908.2898 |  | 5500 | 23112.9064 |  | 5500 | 26304.6435
[13 empty] | Next iteration flow rate |  |  | 1169.3734 | Abs Value of | Flow this | 1036.5397 | Abs Value of | Flow this | 2563.486 | Abs Value of | Flow this | 4993.0165 | Abs Value of | Flow this | 8376.7284 | Abs Value of | Flow this | 12348.3239 | Abs Value of | Flow this | 16478.8861 | Abs Value of | Flow this | 20107.3727 | Abs Value of | Flow this | 23344.0355 | Abs Value of | Flow this | 26567.6899 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 10.7346 |  |  | 20.6306 |  |  | -165.0177 |  |  | -785.0364 |  |  | -2312.8771 |  |  | -5092.7327 |  |  | -9114.0966 |  |  | -13597.4721 |  |  | -18347.1363 |  |  | -23781.049
[13 empty] | P2 at this iteration flow rate |  |  | 33.8931 |  |  | 31.9139 |  |  | 69.0435 |  |  | 193.0473 |  |  | 498.6154 |  |  | 1054.5865 |  |  | 1858.8593 |  |  | 2755.5344 |  |  | 3705.4673 |  |  | 4792.2498
[13 empty] | Delta P at this iteration flow rate |  |  | -23.1584 |  |  | -11.2833 |  |  | -234.0612 |  |  | -978.0836 |  |  | -2811.4926 |  |  | -6147.3193 |  |  | -10972.9559 |  |  | -16353.0066 |  |  | -22052.6036 |  |  | -28573.2988
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 9.0956 |  |  | 17.3142 |  |  | -137.6443 |  |  | -624.9007 |  |  | -1734.5166 |  |  | -3550.074 |  |  | -5849.4741 |  |  | -7907.253 |  |  | -9196.8355 |  |  | -8962.367
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 387.7871 |  |  | 249.3023 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1169.3734 |  | 5500 | 1036.5397 |  | 5500 | 2563.486 |  | 5500 | 4993.0165 |  | 5500 | 8376.7284 |  | 5500 | 12348.3239 |  | 5500 | 16478.8861 |  | 5500 | 20107.3727 |  | 5500 | 23344.0355 |  | 5500 | 26567.6899
[13 empty] | Next iteration flow rate |  |  | 1192.7608 | Abs Value of | Flow this | 1046.9051 | Abs Value of | Flow this | 2589.1209 | Abs Value of | Flow this | 5042.9466 | Abs Value of | Flow this | 8460.4957 | Abs Value of | Flow this | 12471.8071 | Abs Value of | Flow this | 16643.675 | Abs Value of | Flow this | 20308.4464 | Abs Value of | Flow this | 23577.4758 | Abs Value of | Flow this | 26833.3668 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 8.8689 |  |  | 19.9013 |  |  | -169.4786 |  |  | -801.9596 |  |  | -2360.51 |  |  | -5196.2407 |  |  | -9298.434 |  |  | -13871.9254 |  |  | -18717.0578 |  |  | -24260.1921
[13 empty] | P2 at this iteration flow rate |  |  | 34.2662 |  |  | 32.0597 |  |  | 69.9357 |  |  | 196.4319 |  |  | 508.142 |  |  | 1075.2881 |  |  | 1895.7268 |  |  | 2810.4251 |  |  | 3779.4516 |  |  | 4888.0784
[13 empty] | Delta P at this iteration flow rate |  |  | -25.3973 |  |  | -12.1585 |  |  | -239.4143 |  |  | -998.3915 |  |  | -2868.652 |  |  | -6271.5288 |  |  | -11194.1608 |  |  | -16682.3504 |  |  | -22496.5093 |  |  | -29148.2705
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 7.4472 |  |  | 16.6888 |  |  | -141.3553 |  |  | -638.3643 |  |  | -1770.2315 |  |  | -3622.2217 |  |  | -5967.7771 |  |  | -8066.8489 |  |  | -9382.2609 |  |  | -9142.9384
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 437.1331 |  |  | 256.4701 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1192.7608 |  | 5500 | 1046.9051 |  | 5500 | 2589.1209 |  | 5500 | 5042.9466 |  | 5500 | 8460.4957 |  | 5500 | 12471.8071 |  | 5500 | 16643.675 |  | 5500 | 20308.4464 |  | 5500 | 23577.4758 |  | 5500 | 26833.3668
[13 empty] | Next iteration flow rate |  |  | 1216.616 | Abs Value of | Flow this | 1057.3741 | Abs Value of | Flow this | 2615.0121 | Abs Value of | Flow this | 5093.3761 | Abs Value of | Flow this | 8545.1007 | Abs Value of | Flow this | 12596.5252 | Abs Value of | Flow this | 16810.1117 | Abs Value of | Flow this | 20511.5309 | Abs Value of | Flow this | 23813.2506 | Abs Value of | Flow this | 27101.7005 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 6.9278 |  |  | 19.1573 |  |  | -174.0291 |  |  | -819.223 |  |  | -2409.1002 |  |  | -5301.8291 |  |  | -9486.4765 |  |  | -14151.8951 |  |  | -19094.4146 |  |  | -24748.966
[13 empty] | P2 at this iteration flow rate |  |  | 34.6544 |  |  | 32.2085 |  |  | 70.8458 |  |  | 199.8846 |  |  | 517.86 |  |  | 1096.4058 |  |  | 1933.3353 |  |  | 2866.419 |  |  | 3854.9229 |  |  | 4985.8332
[13 empty] | Delta P at this iteration flow rate |  |  | -27.7266 |  |  | -13.0513 |  |  | -244.8749 |  |  | -1019.1076 |  |  | -2926.9603 |  |  | -6398.235 |  |  | -11419.8118 |  |  | -17018.3141 |  |  | -22949.3376 |  |  | -29734.7992
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 5.7322 |  |  | 16.0508 |  |  | -145.1409 |  |  | -652.0985 |  |  | -1806.6643 |  |  | -3695.8196 |  |  | -6088.4579 |  |  | -8229.6527 |  |  | -9571.4133 |  |  | -9327.1392
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 508.2193 |  |  | 264.1329 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1216.616 |  | 5500 | 1057.3741 |  | 5500 | 2615.0121 |  | 5500 | 5093.3761 |  | 5500 | 8545.1007 |  | 5500 | 12596.5252 |  | 5500 | 16810.1117 |  | 5500 | 20511.5309 |  | 5500 | 23813.2506 |  | 5500 | 27101.7005
[13 empty] | Next iteration flow rate |  |  | 1240.9484 | Abs Value of | Flow this | 1067.9479 | Abs Value of | Flow this | 2641.1622 | Abs Value of | Flow this | 5144.3099 | Abs Value of | Flow this | 8630.5517 | Abs Value of | Flow this | 12722.4905 | Abs Value of | Flow this | 16978.2128 | Abs Value of | Flow this | 20716.6462 | Abs Value of | Flow this | 24051.3831 | Abs Value of | Flow this | 27372.7175 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 4.9083 |  |  | 18.3983 |  |  | -178.6711 |  |  | -836.8334 |  |  | -2458.6672 |  |  | -5409.5399 |  |  | -9678.2987 |  |  | -14437.4922 |  |  | -19479.3564 |  |  | -25247.5642
[13 empty] | P2 at this iteration flow rate |  |  | 35.0583 |  |  | 32.3603 |  |  | 71.7742 |  |  | 203.4067 |  |  | 527.7734 |  |  | 1117.948 |  |  | 1971.6997 |  |  | 2923.5384 |  |  | 3931.9113 |  |  | 5085.5528
[13 empty] | Delta P at this iteration flow rate |  |  | -30.1501 |  |  | -13.962 |  |  | -250.4453 |  |  | -1040.2401 |  |  | -2986.4406 |  |  | -6527.4879 |  |  | -11649.9984 |  |  | -17361.0306 |  |  | -23411.2677 |  |  | -30333.1171
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 3.9478 |  |  | 15.3999 |  |  | -149.0026 |  |  | -666.1088 |  |  | -1843.8294 |  |  | -3770.8968 |  |  | -6211.5644 |  |  | -8395.7288 |  |  | -9764.3677 |  |  | -9515.0425
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 624.6418 |  |  | 272.3531 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1240.9484 |  | 5500 | 1067.9479 |  | 5500 | 2641.1622 |  | 5500 | 5144.3099 |  | 5500 | 8630.5517 |  | 5500 | 12722.4905 |  | 5500 | 16978.2128 |  | 5500 | 20716.6462 |  | 5500 | 24051.3831 |  | 5500 | 27372.7175
[13 empty] | Next iteration flow rate |  |  | 1265.7673 | Abs Value of | Flow this | 1078.6274 | Abs Value of | Flow this | 2667.5738 | Abs Value of | Flow this | 5195.753 | Abs Value of | Flow this | 8716.8572 | Abs Value of | Flow this | 12849.7154 | Abs Value of | Flow this | 17147.995 | Abs Value of | Flow this | 20923.8127 | Abs Value of | Flow this | 24291.8969 | Abs Value of | Flow this | 27646.4447 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 2.8072 |  |  | 17.6241 |  |  | -183.4064 |  |  | -854.7978 |  |  | -2509.2304 |  |  | -5519.4157 |  |  | -9873.9765 |  |  | -14728.8298 |  |  | -19872.0355 |  |  | -25756.1843
[13 empty] | P2 at this iteration flow rate |  |  | 35.4786 |  |  | 32.5152 |  |  | 72.7213 |  |  | 206.9996 |  |  | 537.8861 |  |  | 1139.9231 |  |  | 2010.8353 |  |  | 2981.806 |  |  | 4010.4471 |  |  | 5187.2769
[13 empty] | Delta P at this iteration flow rate |  |  | -32.6714 |  |  | -14.8911 |  |  | -256.1277 |  |  | -1061.7973 |  |  | -3047.1165 |  |  | -6659.3388 |  |  | -11884.8118 |  |  | -17710.6357 |  |  | -23882.4826 |  |  | -30943.4611
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 2.0914 |  |  | 14.736 |  |  | -152.9419 |  |  | -680.4007 |  |  | -1881.7415 |  |  | -3847.4831 |  |  | -6337.1454 |  |  | -8565.143 |  |  | -9961.2005 |  |  | -9706.7227
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 875.3664 |  |  | 281.205 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1265.7673 |  | 5500 | 1078.6274 |  | 5500 | 2667.5738 |  | 5500 | 5195.753 |  | 5500 | 8716.8572 |  | 5500 | 12849.7154 |  | 5500 | 17147.995 |  | 5500 | 20923.8127 |  | 5500 | 24291.8969 |  | 5500 | 27646.4447
[13 empty] | Next iteration flow rate |  |  | 1291.0827 | Abs Value of | Flow this | 1089.4136 | Abs Value of | Flow this | 2694.2496 | Abs Value of | Flow this | 5247.7105 | Abs Value of | Flow this | 8804.0258 | Abs Value of | Flow this | 12978.2125 | Abs Value of | Flow this | 17319.4749 | Abs Value of | Flow this | 21133.0508 | Abs Value of | Flow this | 24534.8159 | Abs Value of | Flow this | 27922.9091 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 0.62116 |  |  | 16.8343 |  |  | -188.2369 |  |  | -873.1232 |  |  | -2560.8099 |  |  | -5631.4999 |  |  | -10073.5875 |  |  | -15026.0233 |  |  | -20272.6074 |  |  | -26275.0276
[13 empty] | P2 at this iteration flow rate |  |  | 35.9158 |  |  | 32.6731 |  |  | 73.6874 |  |  | 210.6646 |  |  | 548.202 |  |  | 1162.34 |  |  | 2050.7575 |  |  | 3041.2447 |  |  | 4090.5615 |  |  | 5291.0455
[13 empty] | Delta P at this iteration flow rate |  |  | -35.2946 |  |  | -15.8388 |  |  | -261.9242 |  |  | -1083.7879 |  |  | -3109.0119 |  |  | -6793.8399 |  |  | -12124.345 |  |  | -18067.2679 |  |  | -24363.1689 |  |  | -31566.0731
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 0.16001 |  |  | 14.0588 |  |  | -156.9604 |  |  | -694.9798 |  |  | -1920.4157 |  |  | -3925.6087 |  |  | -6465.2506 |  |  | -8737.9625 |  |  | -10161.9897 |  |  | -9902.2556
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3228.0322 |  |  | 290.7776 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1291.0827 |  | 5500 | 1089.4136 |  | 5500 | 2694.2496 |  | 5500 | 5247.7105 |  | 5500 | 8804.0258 |  | 5500 | 12978.2125 |  | 5500 | 17319.4749 |  | 5500 | 21133.0508 |  | 5500 | 24534.8159 |  | 5500 | 27922.9091
[13 empty] | Next iteration flow rate |  |  | 1316.9043 | Abs Value of | Flow this | 1100.3078 | Abs Value of | Flow this | 2721.1921 | Abs Value of | Flow this | 5300.1876 | Abs Value of | Flow this | 8892.066 | Abs Value of | Flow this | 13107.9946 | Abs Value of | Flow this | 17492.6697 | Abs Value of | Flow this | 21344.3813 | Abs Value of | Flow this | 24780.1641 | Abs Value of | Flow this | 28202.1382 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -1.6532 |  |  | 16.0287 |  |  | -193.1644 |  |  | -891.817 |  |  | -2613.4262 |  |  | -5745.8371 |  |  | -10277.2106 |  |  | -15329.1904 |  |  | -20681.2308 |  |  | -26804.2997
[13 empty] | P2 at this iteration flow rate |  |  | 36.3706 |  |  | 32.8343 |  |  | 74.6729 |  |  | 214.4034 |  |  | 558.7252 |  |  | 1185.2074 |  |  | 2091.4821 |  |  | 3101.8781 |  |  | 4172.2862 |  |  | 5396.8999
[13 empty] | Delta P at this iteration flow rate |  |  | -38.0238 |  |  | -16.8056 |  |  | -267.8373 |  |  | -1106.2204 |  |  | -3172.1515 |  |  | -6931.0445 |  |  | -12368.6927 |  |  | -18431.0684 |  |  | -24853.517 |  |  | -32201.1996
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -1.8494 |  |  | 13.3679 |  |  | -161.0596 |  |  | -709.852 |  |  | -1959.8672 |  |  | -4005.3047 |  |  | -6595.9306 |  |  | -8914.2557 |  |  | -10366.8147 |  |  | -10101.7188
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 301.1788 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1316.9043 |  | 5500 | 1100.3078 |  | 5500 | 2721.1921 |  | 5500 | 5300.1876 |  | 5500 | 8892.066 |  | 5500 | 13107.9946 |  | 5500 | 17492.6697 |  | 5500 | 21344.3813 |  | 5500 | 24780.1641 |  | 5500 | 28202.1382
[13 empty] | Next iteration flow rate |  |  | 1343.2424 | Abs Value of | Flow this | 1111.3109 | Abs Value of | Flow this | 2748.404 | Abs Value of | Flow this | 5353.1895 | Abs Value of | Flow this | 8980.9867 | Abs Value of | Flow this | 13239.0746 | Abs Value of | Flow this | 17667.5964 | Abs Value of | Flow this | 21557.8251 | Abs Value of | Flow this | 25027.9657 | Abs Value of | Flow this | 28484.1596 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -4.0194 |  |  | 15.2069 |  |  | -198.1911 |  |  | -910.8865 |  |  | -2667.1001 |  |  | -5862.4724 |  |  | -10484.9265 |  |  | -15638.4511 |  |  | -21098.0676 |  |  | -27344.2101
[13 empty] | P2 at this iteration flow rate |  |  | 36.8439 |  |  | 32.9986 |  |  | 75.6782 |  |  | 218.2173 |  |  | 569.46 |  |  | 1208.5345 |  |  | 2133.0253 |  |  | 3163.7302 |  |  | 4255.6535 |  |  | 5504.882
[13 empty] | Delta P at this iteration flow rate |  |  | -40.8632 |  |  | -17.7918 |  |  | -273.8693 |  |  | -1129.1039 |  |  | -3236.5601 |  |  | -7071.0069 |  |  | -12617.9518 |  |  | -18802.1813 |  |  | -25353.7211 |  |  | -32849.0921
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -3.9401 |  |  | 12.6631 |  |  | -165.2413 |  |  | -725.0232 |  |  | -2000.1117 |  |  | -4086.6026 |  |  | -6729.2373 |  |  | -9094.0923 |  |  | -10575.7567 |  |  | -10305.1911
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 312.5408 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1343.2424 |  | 5500 | 1111.3109 |  | 5500 | 2748.404 |  | 5500 | 5353.1895 |  | 5500 | 8980.9867 |  | 5500 | 13239.0746 |  | 5500 | 17667.5964 |  | 5500 | 21557.8251 |  | 5500 | 25027.9657 |  | 5500 | 28484.1596
[13 empty] | Next iteration flow rate |  |  | 1370.1073 | Abs Value of | Flow this | 1122.424 | Abs Value of | Flow this | 2775.888 | Abs Value of | Flow this | 5406.7214 | Abs Value of | Flow this | 9070.7965 | Abs Value of | Flow this | 13371.4653 | Abs Value of | Flow this | 17844.2723 | Abs Value of | Flow this | 21773.4034 | Abs Value of | Flow this | 25278.2454 | Abs Value of | Flow this | 28769.0012 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -6.4812 |  |  | 14.3685 |  |  | -203.3187 |  |  | -930.3394 |  |  | -2721.8528 |  |  | -5981.4522 |  |  | -10696.8176 |  |  | -15953.928 |  |  | -21523.2827 |  |  | -27894.9727
[13 empty] | P2 at this iteration flow rate |  |  | 37.3362 |  |  | 33.1663 |  |  | 76.7037 |  |  | 222.1079 |  |  | 580.4106 |  |  | 1232.3304 |  |  | 2175.4035 |  |  | 3226.8256 |  |  | 4340.6965 |  |  | 5615.0345
[13 empty] | Delta P at this iteration flow rate |  |  | -43.8174 |  |  | -18.7978 |  |  | -280.0225 |  |  | -1152.4473 |  |  | -3302.2634 |  |  | -7213.7826 |  |  | -12872.2211 |  |  | -19180.7536 |  |  | -25863.9793 |  |  | -33510.0073
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -6.1151 |  |  | 11.9442 |  |  | -169.507 |  |  | -740.4992 |  |  | -2041.165 |  |  | -4169.5345 |  |  | -6865.2235 |  |  | -9277.5437 |  |  | -10788.8984 |  |  | -10512.7533
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 325.0274 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1370.1073 |  | 5500 | 1122.424 |  | 5500 | 2775.888 |  | 5500 | 5406.7214 |  | 5500 | 9070.7965 |  | 5500 | 13371.4653 |  | 5500 | 17844.2723 |  | 5500 | 21773.4034 |  | 5500 | 25278.2454 |  | 5500 | 28769.0012
[13 empty] | Next iteration flow rate |  |  | 1397.5094 | Abs Value of | Flow this | 1133.6482 | Abs Value of | Flow this | 2803.6469 | Abs Value of | Flow this | 5460.7886 | Abs Value of | Flow this | 9161.5045 | Abs Value of | Flow this | 13505.18 | Abs Value of | Flow this | 18022.7151 | Abs Value of | Flow this | 21991.1374 | Abs Value of | Flow this | 25531.0278 | Abs Value of | Flow this | 29056.6912 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -9.0424 |  |  | 13.5133 |  |  | -208.5494 |  |  | -950.1832 |  |  | -2777.7061 |  |  | -6102.8234 |  |  | -10912.9676 |  |  | -16275.7459 |  |  | -21957.0447 |  |  | -28456.8057
[13 empty] | P2 at this iteration flow rate |  |  | 37.8485 |  |  | 33.3373 |  |  | 77.7499 |  |  | 226.0766 |  |  | 591.5812 |  |  | 1256.6047 |  |  | 2218.6335 |  |  | 3291.1892 |  |  | 4427.4489 |  |  | 5727.4011
[13 empty] | Delta P at this iteration flow rate |  |  | -46.8909 |  |  | -19.824 |  |  | -286.2993 |  |  | -1176.2599 |  |  | -3369.2873 |  |  | -7359.428 |  |  | -13131.6011 |  |  | -19566.9351 |  |  | -26384.4937 |  |  | -34184.2068
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -8.3781 |  |  | 11.2108 |  |  | -173.8584 |  |  | -756.2864 |  |  | -2083.0436 |  |  | -4254.1334 |  |  | -7003.943 |  |  | -9464.6824 |  |  | -11006.3243 |  |  | -10724.4874
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 338.845 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1397.5094 |  | 5500 | 1133.6482 |  | 5500 | 2803.6469 |  | 5500 | 5460.7886 |  | 5500 | 9161.5045 |  | 5500 | 13505.18 |  | 5500 | 18022.7151 |  | 5500 | 21991.1374 |  | 5500 | 25531.0278 |  | 5500 | 29056.6912
[13 empty] | Next iteration flow rate |  |  | 1425.4596 | Abs Value of | Flow this | 1144.9847 | Abs Value of | Flow this | 2831.6834 | Abs Value of | Flow this | 5515.3965 | Abs Value of | Flow this | 9253.1195 | Abs Value of | Flow this | 13640.2318 | Abs Value of | Flow this | 18202.9422 | Abs Value of | Flow this | 22211.0488 | Abs Value of | Flow this | 25786.3381 | Abs Value of | Flow this | 29347.2581 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -11.7071 |  |  | 12.6409 |  |  | -213.8853 |  |  | -970.4259 |  |  | -2834.682 |  |  | -6226.6341 |  |  | -11133.4623 |  |  | -16604.0325 |  |  | -22399.5253 |  |  | -29029.9315
[13 empty] | P2 at this iteration flow rate |  |  | 38.3814 |  |  | 33.5118 |  |  | 78.8171 |  |  | 230.1252 |  |  | 602.9764 |  |  | 1281.3668 |  |  | 2262.7325 |  |  | 3356.8465 |  |  | 4515.9451 |  |  | 5842.0263
[13 empty] | Delta P at this iteration flow rate |  |  | -50.0886 |  |  | -20.8709 |  |  | -292.7024 |  |  | -1200.5511 |  |  | -3437.6584 |  |  | -7508.0009 |  |  | -13396.1947 |  |  | -19960.8789 |  |  | -26915.4704 |  |  | -34871.9578
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -10.7325 |  |  | 10.4627 |  |  | -178.2973 |  |  | -772.3908 |  |  | -2125.7639 |  |  | -4340.4328 |  |  | -7145.4508 |  |  | -9655.5826 |  |  | -11228.1204 |  |  | -10940.4774
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 354.2576 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1425.4596 |  | 5500 | 1144.9847 |  | 5500 | 2831.6834 |  | 5500 | 5515.3965 |  | 5500 | 9253.1195 |  | 5500 | 13640.2318 |  | 5500 | 18202.9422 |  | 5500 | 22211.0488 |  | 5500 | 25786.3381 |  | 5500 | 29347.2581
[13 empty] | Next iteration flow rate |  |  | 1453.9688 | Abs Value of | Flow this | 1156.4345 | Abs Value of | Flow this | 2860.0002 | Abs Value of | Flow this | 5570.5504 | Abs Value of | Flow this | 9345.6507 | Abs Value of | Flow this | 13776.6341 | Abs Value of | Flow this | 18384.9716 | Abs Value of | Flow this | 22433.1593 | Abs Value of | Flow this | 26044.2015 | Abs Value of | Flow this | 29640.7307 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -14.4795 |  |  | 11.751 |  |  | -219.3284 |  |  | -991.0755 |  |  | -2892.8031 |  |  | -6352.9335 |  |  | -11358.3889 |  |  | -16938.9175 |  |  | -22850.8998 |  |  | -29614.5772
[13 empty] | P2 at this iteration flow rate |  |  | 38.9359 |  |  | 33.6898 |  |  | 79.9057 |  |  | 234.2551 |  |  | 614.6006 |  |  | 1306.6267 |  |  | 2307.7178 |  |  | 3423.8235 |  |  | 4606.22 |  |  | 5958.9554
[13 empty] | Delta P at this iteration flow rate |  |  | -53.4154 |  |  | -21.9388 |  |  | -299.2341 |  |  | -1225.3306 |  |  | -3507.4038 |  |  | -7659.5602 |  |  | -13666.1067 |  |  | -20362.741 |  |  | -27457.1198 |  |  | -35573.5326
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -13.182 |  |  | 9.6996 |  |  | -182.8255 |  |  | -788.819 |  |  | -2169.3429 |  |  | -4428.4667 |  |  | -7289.8029 |  |  | -9850.32 |  |  | -11454.3746 |  |  | -11160.8088
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 371.6094 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1453.9688 |  | 5500 | 1156.4345 |  | 5500 | 2860.0002 |  | 5500 | 5570.5504 |  | 5500 | 9345.6507 |  | 5500 | 13776.6341 |  | 5500 | 18384.9716 |  | 5500 | 22433.1593 |  | 5500 | 26044.2015 |  | 5500 | 29640.7307
[13 empty] | Next iteration flow rate |  |  | 1483.0482 | Abs Value of | Flow this | 1167.9989 | Abs Value of | Flow this | 2888.6002 | Abs Value of | Flow this | 5626.2559 | Abs Value of | Flow this | 9439.1072 | Abs Value of | Flow this | 13914.4005 | Abs Value of | Flow this | 18568.8213 | Abs Value of | Flow this | 22657.4909 | Abs Value of | Flow this | 26304.6435 | Abs Value of | Flow this | 29937.138 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -17.3639 |  |  | 10.8431 |  |  | -224.8809 |  |  | -1012.1401 |  |  | -2952.0925 |  |  | -6481.7715 |  |  | -11587.8365 |  |  | -17280.5338 |  |  | -23311.3469 |  |  | -30210.9742
[13 empty] | P2 at this iteration flow rate |  |  | 39.5128 |  |  | 33.8714 |  |  | 81.0162 |  |  | 238.468 |  |  | 626.4585 |  |  | 1332.3943 |  |  | 2353.6073 |  |  | 3492.1468 |  |  | 4698.3094 |  |  | 6078.2348
[13 empty] | Delta P at this iteration flow rate |  |  | -56.8767 |  |  | -23.0282 |  |  | -305.8971 |  |  | -1250.6081 |  |  | -3578.551 |  |  | -7814.1658 |  |  | -13941.4438 |  |  | -20772.6805 |  |  | -28009.6563 |  |  | -36289.209
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -15.7304 |  |  | 8.9211 |  |  | -187.4446 |  |  | -805.5774 |  |  | -2213.7979 |  |  | -4518.2701 |  |  | -7437.0565 |  |  | -10048.9715 |  |  | -11685.1766 |  |  | -11385.5689
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 391.3593 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1483.0482 |  | 5500 | 1167.9989 |  | 5500 | 2888.6002 |  | 5500 | 5626.2559 |  | 5500 | 9439.1072 |  | 5500 | 13914.4005 |  | 5500 | 18568.8213 |  | 5500 | 22657.4909 |  | 5500 | 26304.6435 |  | 5500 | 29937.138
[13 empty] | Next iteration flow rate |  |  | 1512.7091 | Abs Value of | Flow this | 1179.6789 | Abs Value of | Flow this | 2917.4862 | Abs Value of | Flow this | 5682.5185 | Abs Value of | Flow this | 9533.4983 | Abs Value of | Flow this | 14053.5445 | Abs Value of | Flow this | 18754.5096 | Abs Value of | Flow this | 22884.0658 | Abs Value of | Flow this | 26567.6899 | Abs Value of | Flow this | 30236.5094 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -20.3648 |  |  | 9.9171 |  |  | -230.545 |  |  | -1033.6281 |  |  | -3012.5736 |  |  | -6613.1991 |  |  | -11821.896 |  |  | -17629.0165 |  |  | -23781.049 |  |  | -30819.3588
[13 empty] | P2 at this iteration flow rate |  |  | 40.113 |  |  | 34.0566 |  |  | 82.149 |  |  | 242.7656 |  |  | 638.5547 |  |  | 1358.6798 |  |  | 2400.4192 |  |  | 3561.8433 |  |  | 4792.2498 |  |  | 6199.9118
[13 empty] | Delta P at this iteration flow rate |  |  | -60.4778 |  |  | -24.1395 |  |  | -312.6941 |  |  | -1276.3938 |  |  | -3651.1283 |  |  | -7971.8789 |  |  | -14222.3153 |  |  | -21190.8598 |  |  | -28573.2988 |  |  | -37019.2705
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -18.3818 |  |  | 8.1269 |  |  | -192.1566 |  |  | -822.6726 |  |  | -2259.1464 |  |  | -4609.8786 |  |  | -7587.2698 |  |  | -10251.6159 |  |  | -11920.6176 |  |  | -11614.8466
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 414.1353 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1512.7091 |  | 5500 | 1179.6789 |  | 5500 | 2917.4862 |  | 5500 | 5682.5185 |  | 5500 | 9533.4983 |  | 5500 | 14053.5445 |  | 5500 | 18754.5096 |  | 5500 | 22884.0658 |  | 5500 | 26567.6899 |  | 5500 | 30236.5094
[13 empty] | Next iteration flow rate |  |  | 1542.9633 | Abs Value of | Flow this | 1191.4757 | Abs Value of | Flow this | 2946.6611 | Abs Value of | Flow this | 5739.3437 | Abs Value of | Flow this | 9628.8333 | Abs Value of | Flow this | 14194.0799 | Abs Value of | Flow this | 18942.0547 | Abs Value of | Flow this | 23112.9064 | Abs Value of | Flow this | 26833.3668 | Abs Value of | Flow this | 30538.8745 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -23.487 |  |  | 8.9724 |  |  | -236.323 |  |  | -1055.5481 |  |  | -3074.2703 |  |  | -6747.2684 |  |  | -12060.6602 |  |  | -17984.5038 |  |  | -24260.1921 |  |  | -31439.9719
[13 empty] | P2 at this iteration flow rate |  |  | 40.7374 |  |  | 34.2455 |  |  | 83.3046 |  |  | 247.1496 |  |  | 650.8941 |  |  | 1385.4937 |  |  | 2448.172 |  |  | 3632.9408 |  |  | 4888.0784 |  |  | 6324.0344
[13 empty] | Delta P at this iteration flow rate |  |  | -64.2243 |  |  | -25.2731 |  |  | -319.6276 |  |  | -1302.6977 |  |  | -3725.1644 |  |  | -8132.7621 |  |  | -14508.8322 |  |  | -21617.4445 |  |  | -29148.2705 |  |  | -37764.0063
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -21.1404 |  |  | 7.3168 |  |  | -196.9633 |  |  | -840.1114 |  |  | -2305.4063 |  |  | -4703.3284 |  |  | -7740.5025 |  |  | -10458.3335 |  |  | -12160.791 |  |  | -11848.7328
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 440.8242 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1542.9633 |  | 5500 | 1191.4757 |  | 5500 | 2946.6611 |  | 5500 | 5739.3437 |  | 5500 | 9628.8333 |  | 5500 | 14194.0799 |  | 5500 | 18942.0547 |  | 5500 | 23112.9064 |  | 5500 | 26833.3668 |  | 5500 | 30538.8745
[13 empty] | Next iteration flow rate |  |  | 1573.8226 | Abs Value of | Flow this | 1203.3904 | Abs Value of | Flow this | 2976.1277 | Abs Value of | Flow this | 5796.7371 | Abs Value of | Flow this | 9725.1216 | Abs Value of | Flow this | 14336.0207 | Abs Value of | Flow this | 19131.4752 | Abs Value of | Flow this | 23344.0355 | Abs Value of | Flow this | 27101.7005 | Abs Value of | Flow this | 30844.2632 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -26.7352 |  |  | 8.0087 |  |  | -242.2171 |  |  | -1077.9086 |  |  | -3137.2072 |  |  | -6884.0325 |  |  | -12304.2235 |  |  | -18347.1363 |  |  | -24748.966 |  |  | -32073.0593
[13 empty] | P2 at this iteration flow rate |  |  | 41.387 |  |  | 34.4383 |  |  | 84.4834 |  |  | 251.6217 |  |  | 663.4814 |  |  | 1412.8465 |  |  | 2496.8847 |  |  | 3705.4673 |  |  | 4985.8332 |  |  | 6450.6519
[13 empty] | Delta P at this iteration flow rate |  |  | -68.1223 |  |  | -26.4295 |  |  | -326.7006 |  |  | -1329.5303 |  |  | -3800.6886 |  |  | -8296.879 |  |  | -14801.1081 |  |  | -22052.6036 |  |  | -29734.7992 |  |  | -38523.7112
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -24.0104 |  |  | 6.4904 |  |  | -201.8666 |  |  | -857.9007 |  |  | -2352.5962 |  |  | -4798.6565 |  |  | -7896.8151 |  |  | -10669.2061 |  |  | -12405.792 |  |  | -12087.3202
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 472.7277 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1573.8226 |  | 5500 | 1203.3904 |  | 5500 | 2976.1277 |  | 5500 | 5796.7371 |  | 5500 | 9725.1216 |  | 5500 | 14336.0207 |  | 5500 | 19131.4752 |  | 5500 | 23344.0355 |  | 5500 | 27101.7005 |  | 5500 | 30844.2632
[13 empty] | Next iteration flow rate |  |  | 1605.299 | Abs Value of | Flow this | 1215.4243 | Abs Value of | Flow this | 3005.889 | Abs Value of | Flow this | 5854.7045 | Abs Value of | Flow this | 9822.3729 | Abs Value of | Flow this | 14479.3809 | Abs Value of | Flow this | 19322.79 | Abs Value of | Flow this | 23577.4758 | Abs Value of | Flow this | 27372.7175 | Abs Value of | Flow this | 31152.7059 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -30.1148 |  |  | 7.0257 |  |  | -248.2297 |  |  | -1100.7186 |  |  | -3201.409 |  |  | -7023.5456 |  |  | -12552.6824 |  |  | -18717.0578 |  |  | -25247.5642 |  |  | -32718.8718
[13 empty] | P2 at this iteration flow rate |  |  | 42.063 |  |  | 34.6349 |  |  | 85.6859 |  |  | 256.1837 |  |  | 676.3218 |  |  | 1440.7491 |  |  | 2546.5765 |  |  | 3779.4516 |  |  | 5085.5528 |  |  | 6579.8144
[13 empty] | Delta P at this iteration flow rate |  |  | -72.1777 |  |  | -27.6092 |  |  | -333.9156 |  |  | -1356.9023 |  |  | -3877.7308 |  |  | -8464.2947 |  |  | -15099.2588 |  |  | -22496.5093 |  |  | -30333.1171 |  |  | -39298.6862
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -26.9963 |  |  | 5.6474 |  |  | -206.8685 |  |  | -876.0476 |  |  | -2400.7345 |  |  | -4895.9008 |  |  | -8056.2696 |  |  | -10884.3173 |  |  | -12655.7174 |  |  | -12330.7031
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 511.851 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1605.299 |  | 5500 | 1215.4243 |  | 5500 | 3005.889 |  | 5500 | 5854.7045 |  | 5500 | 9822.3729 |  | 5500 | 14479.3809 |  | 5500 | 19322.79 |  | 5500 | 23577.4758 |  | 5500 | 27372.7175 |  | 5500 | 31152.7059
[13 empty] | Next iteration flow rate |  |  | 1637.405 | Abs Value of | Flow this | 1227.5786 | Abs Value of | Flow this | 3035.9479 | Abs Value of | Flow this | 5913.2515 | Abs Value of | Flow this | 9920.5966 | Abs Value of | Flow this | 14624.1747 | Abs Value of | Flow this | 19516.0179 | Abs Value of | Flow this | 23813.2506 | Abs Value of | Flow this | 27646.4447 | Abs Value of | Flow this | 31464.2329 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -33.6308 |  |  | 6.0229 |  |  | -254.3631 |  |  | -1123.9871 |  |  | -3266.9014 |  |  | -7165.8629 |  |  | -12806.1353 |  |  | -19094.4146 |  |  | -25756.1843 |  |  | -33377.6652
[13 empty] | P2 at this iteration flow rate |  |  | 42.7662 |  |  | 34.8354 |  |  | 86.9126 |  |  | 260.8374 |  |  | 689.4203 |  |  | 1469.2126 |  |  | 2597.2671 |  |  | 3854.9229 |  |  | 5187.2769 |  |  | 6711.573
[13 empty] | Delta P at this iteration flow rate |  |  | -76.397 |  |  | -28.8125 |  |  | -341.2758 |  |  | -1384.8245 |  |  | -3956.3216 |  |  | -8635.0754 |  |  | -15403.4023 |  |  | -22949.3376 |  |  | -30943.4611 |  |  | -40089.2382
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -30.1028 |  |  | 4.7875 |  |  | -211.9709 |  |  | -894.5593 |  |  | -2449.8404 |  |  | -4995.0996 |  |  | -8218.9291 |  |  | -11103.7522 |  |  | -12910.6663 |  |  | -12578.978
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 561.4826 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1637.405 |  | 5500 | 1227.5786 |  | 5500 | 3035.9479 |  | 5500 | 5913.2515 |  | 5500 | 9920.5966 |  | 5500 | 14624.1747 |  | 5500 | 19516.0179 |  | 5500 | 23813.2506 |  | 5500 | 27646.4447 |  | 5500 | 31464.2329
[13 empty] | Next iteration flow rate |  |  | 1670.1531 | Abs Value of | Flow this | 1239.8543 | Abs Value of | Flow this | 3066.3073 | Abs Value of | Flow this | 5972.384 | Abs Value of | Flow this | 10019.8025 | Abs Value of | Flow this | 14770.4165 | Abs Value of | Flow this | 19711.178 | Abs Value of | Flow this | 24051.3831 | Abs Value of | Flow this | 27922.9091 | Abs Value of | Flow this | 31778.8752 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -37.2889 |  |  | 4.9999 |  |  | -260.6198 |  |  | -1147.7232 |  |  | -3333.7101 |  |  | -7311.0407 |  |  | -13064.6826 |  |  | -19479.3564 |  |  | -26275.0276 |  |  | -34049.7003
[13 empty] | P2 at this iteration flow rate |  |  | 43.4978 |  |  | 35.04 |  |  | 88.164 |  |  | 265.5846 |  |  | 702.782 |  |  | 1498.2481 |  |  | 2648.9765 |  |  | 3931.9113 |  |  | 5291.0455 |  |  | 6845.9801
[13 empty] | Delta P at this iteration flow rate |  |  | -80.7867 |  |  | -30.0401 |  |  | -348.7838 |  |  | -1413.3078 |  |  | -4036.4921 |  |  | -8809.2889 |  |  | -15713.6591 |  |  | -23411.2677 |  |  | -31566.0731 |  |  | -40895.6803
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -33.3349 |  |  | 3.9103 |  |  | -217.1758 |  |  | -913.4431 |  |  | -2499.9333 |  |  | -5096.2924 |  |  | -8384.8581 |  |  | -11327.5977 |  |  | -13170.7397 |  |  | -12832.2433
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 627.4922 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1670.1531 |  | 5500 | 1239.8543 |  | 5500 | 3066.3073 |  | 5500 | 5972.384 |  | 5500 | 10019.8025 |  | 5500 | 14770.4165 |  | 5500 | 19711.178 |  | 5500 | 24051.3831 |  | 5500 | 27922.9091 |  | 5500 | 31778.8752
[13 empty] | Next iteration flow rate |  |  | 1703.5562 | Abs Value of | Flow this | 1252.2529 | Abs Value of | Flow this | 3096.9704 | Abs Value of | Flow this | 6032.1079 | Abs Value of | Flow this | 10120.0006 | Abs Value of | Flow this | 14918.1206 | Abs Value of | Flow this | 19908.2898 | Abs Value of | Flow this | 24291.8969 | Abs Value of | Flow this | 28202.1382 | Abs Value of | Flow this | 32096.664 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -41.0948 |  |  | 3.9564 |  |  | -267.0023 |  |  | -1171.9365 |  |  | -3401.8617 |  |  | -7459.1366 |  |  | -13328.4268 |  |  | -19872.0355 |  |  | -26804.2997 |  |  | -34735.2433
[13 empty] | P2 at this iteration flow rate |  |  | 44.259 |  |  | 35.2487 |  |  | 89.4405 |  |  | 270.4273 |  |  | 716.4123 |  |  | 1527.8673 |  |  | 2701.7254 |  |  | 4010.4471 |  |  | 5396.8999 |  |  | 6983.0887
[13 empty] | Delta P at this iteration flow rate |  |  | -85.3537 |  |  | -31.2923 |  |  | -356.4428 |  |  | -1442.3638 |  |  | -4118.274 |  |  | -8987.004 |  |  | -16030.1521 |  |  | -23882.4826 |  |  | -32201.1996 |  |  | -41718.3319
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -36.6975 |  |  | 3.0154 |  |  | -222.4854 |  |  | -932.7064 |  |  | -2551.0331 |  |  | -5199.5191 |  |  | -8554.1223 |  |  | -11555.9425 |  |  | -13436.0406 |  |  | -13090.5992
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 721.7045 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1703.5562 |  | 5500 | 1252.2529 |  | 5500 | 3096.9704 |  | 5500 | 6032.1079 |  | 5500 | 10120.0006 |  | 5500 | 14918.1206 |  | 5500 | 19908.2898 |  | 5500 | 24291.8969 |  | 5500 | 28202.1382 |  | 5500 | 32096.664
[13 empty] | Next iteration flow rate |  |  | 1737.6273 | Abs Value of | Flow this | 1264.7754 | Abs Value of | Flow this | 3127.9401 | Abs Value of | Flow this | 6092.429 | Abs Value of | Flow this | 10221.2006 | Abs Value of | Flow this | 15067.3018 | Abs Value of | Flow this | 20107.3727 | Abs Value of | Flow this | 24534.8159 | Abs Value of | Flow this | 28484.1596 | Abs Value of | Flow this | 32417.6306 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -45.0544 |  |  | 2.8919 |  |  | -273.5131 |  |  | -1196.6364 |  |  | -3471.3831 |  |  | -7610.2093 |  |  | -13597.4721 |  |  | -20272.6074 |  |  | -27344.2101 |  |  | -35434.5657
[13 empty] | P2 at this iteration flow rate |  |  | 45.0509 |  |  | 35.4616 |  |  | 90.7426 |  |  | 275.3673 |  |  | 730.3166 |  |  | 1558.0819 |  |  | 2755.5344 |  |  | 4090.5615 |  |  | 5504.882 |  |  | 7122.9531
[13 empty] | Delta P at this iteration flow rate |  |  | -90.1053 |  |  | -32.5697 |  |  | -364.2557 |  |  | -1472.0037 |  |  | -4201.6997 |  |  | -9168.2912 |  |  | -16353.0066 |  |  | -24363.1689 |  |  | -32849.0921 |  |  | -42557.5188
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -40.196 |  |  | 2.1026 |  |  | -227.9017 |  |  | -952.3569 |  |  | -2603.16 |  |  | -5304.8207 |  |  | -8726.7887 |  |  | -11788.8771 |  |  | -13706.674 |  |  | -13354.148
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 872.9284 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1737.6273 |  | 5500 | 1264.7754 |  | 5500 | 3127.9401 |  | 5500 | 6092.429 |  | 5500 | 10221.2006 |  | 5500 | 15067.3018 |  | 5500 | 20107.3727 |  | 5500 | 24534.8159 |  | 5500 | 28484.1596 |  | 5500 | 32417.6306
[13 empty] | Next iteration flow rate |  |  | 1772.3798 | Abs Value of | Flow this | 1277.4232 | Abs Value of | Flow this | 3159.2195 | Abs Value of | Flow this | 6153.3533 | Abs Value of | Flow this | 10323.4126 | Abs Value of | Flow this | 15217.9749 | Abs Value of | Flow this | 20308.4464 | Abs Value of | Flow this | 24780.1641 | Abs Value of | Flow this | 28769.0012 | Abs Value of | Flow this | 32741.8069 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -49.174 |  |  | 1.806 |  |  | -280.1547 |  |  | -1221.8328 |  |  | -3542.3019 |  |  | -7764.3185 |  |  | -13871.9254 |  |  | -20681.2308 |  |  | -27894.9727 |  |  | -36147.9444
[13 empty] | P2 at this iteration flow rate |  |  | 45.8748 |  |  | 35.6788 |  |  | 92.0709 |  |  | 280.4066 |  |  | 744.5004 |  |  | 1588.9037 |  |  | 2810.4251 |  |  | 4172.2862 |  |  | 5615.0345 |  |  | 7265.6289
[13 empty] | Delta P at this iteration flow rate |  |  | -95.0488 |  |  | -33.8727 |  |  | -372.2257 |  |  | -1502.2394 |  |  | -4286.8023 |  |  | -9353.2222 |  |  | -16682.3504 |  |  | -24853.517 |  |  | -33510.0073 |  |  | -43413.5733
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -43.8358 |  |  | 1.1714 |  |  | -233.4269 |  |  | -972.4024 |  |  | -2656.3347 |  |  | -5412.2388 |  |  | -8902.9257 |  |  | -12026.4936 |  |  | -13982.7472 |  |  | -13622.9942
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 1181.206 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1772.3798 |  | 5500 | 1277.4232 |  | 5500 | 3159.2195 |  | 5500 | 6153.3533 |  | 5500 | 10323.4126 |  | 5500 | 15217.9749 |  | 5500 | 20308.4464 |  | 5500 | 24780.1641 |  | 5500 | 28769.0012 |  | 5500 | 32741.8069
[13 empty] | Next iteration flow rate |  |  | 1807.8274 | Abs Value of | Flow this | 1290.1974 | Abs Value of | Flow this | 3190.8117 | Abs Value of | Flow this | 6214.8868 | Abs Value of | Flow this | 10426.6467 | Abs Value of | Flow this | 15370.1546 | Abs Value of | Flow this | 20511.5309 | Abs Value of | Flow this | 25027.9657 | Abs Value of | Flow this | 29056.6912 | Abs Value of | Flow this | 33069.225 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -53.4601 |  |  | 0.69833 |  |  | -286.9298 |  |  | -1247.5357 |  |  | -3614.6462 |  |  | -7921.5253 |  |  | -14151.8951 |  |  | -21098.0676 |  |  | -28456.8057 |  |  | -36875.6621
[13 empty] | P2 at this iteration flow rate |  |  | 46.732 |  |  | 35.9003 |  |  | 93.426 |  |  | 285.5471 |  |  | 758.9692 |  |  | 1620.3451 |  |  | 2866.419 |  |  | 4255.6535 |  |  | 5727.4011 |  |  | 7411.1724
[13 empty] | Delta P at this iteration flow rate |  |  | -100.1921 |  |  | -35.202 |  |  | -380.3558 |  |  | -1533.0828 |  |  | -4373.6155 |  |  | -9541.8704 |  |  | -17018.3141 |  |  | -25353.7211 |  |  | -34184.2068 |  |  | -44286.8346
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -47.6227 |  |  | 0.22148 |  |  | -239.0631 |  |  | -992.8507 |  |  | -2710.5782 |  |  | -5521.816 |  |  | -9082.603 |  |  | -12268.8862 |  |  | -14264.3694 |  |  | -13897.2442
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 2743.6497 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1807.8274 |  | 5500 | 1290.1974 |  | 5500 | 3190.8117 |  | 5500 | 6214.8868 |  | 5500 | 10426.6467 |  | 5500 | 15370.1546 |  | 5500 | 20511.5309 |  | 5500 | 25027.9657 |  | 5500 | 29056.6912 |  | 5500 | 33069.225
[13 empty] | Next iteration flow rate |  |  | 1843.984 | Abs Value of | Flow this | 1303.0994 | Abs Value of | Flow this | 3222.7198 | Abs Value of | Flow this | 6277.0357 | Abs Value of | Flow this | 10530.9132 | Abs Value of | Flow this | 15523.8561 | Abs Value of | Flow this | 20716.6462 | Abs Value of | Flow this | 25278.2454 | Abs Value of | Flow this | 29347.2581 | Abs Value of | Flow this | 33399.9173 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -57.9193 |  |  | -0.43164 |  |  | -293.8411 |  |  | -1273.7551 |  |  | -3688.4446 |  |  | -8081.892 |  |  | -14437.4922 |  |  | -21523.2827 |  |  | -29029.9315 |  |  | -37618.007
[13 empty] | P2 at this iteration flow rate |  |  | 47.6239 |  |  | 36.1263 |  |  | 94.8082 |  |  | 290.791 |  |  | 773.7289 |  |  | 1652.4184 |  |  | 2923.5384 |  |  | 4340.6965 |  |  | 5842.0263 |  |  | 7559.6414
[13 empty] | Delta P at this iteration flow rate |  |  | -105.5431 |  |  | -36.558 |  |  | -388.6494 |  |  | -1564.5462 |  |  | -4462.1736 |  |  | -9734.3104 |  |  | -17361.0306 |  |  | -25863.9793 |  |  | -34871.9578 |  |  | -45177.6484
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -51.5626 |  |  | -0.74752 |  |  | -244.8126 |  |  | -1013.7102 |  |  | -2765.9119 |  |  | -5633.5958 |  |  | -9265.8918 |  |  | -12516.1509 |  |  | -14551.6523 |  |  | -14177.0066
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1843.984 |  | 5500 | 1303.0994 |  | 5500 | 3222.7198 |  | 5500 | 6277.0357 |  | 5500 | 10530.9132 |  | 5500 | 15523.8561 |  | 5500 | 20716.6462 |  | 5500 | 25278.2454 |  | 5500 | 29347.2581 |  | 5500 | 33399.9173
[13 empty] | Next iteration flow rate |  |  | 1880.8637 | Abs Value of | Flow this | 1316.1304 | Abs Value of | Flow this | 3254.947 | Abs Value of | Flow this | 6339.806 | Abs Value of | Flow this | 10636.2223 | Abs Value of | Flow this | 15679.0947 | Abs Value of | Flow this | 20923.8127 | Abs Value of | Flow this | 25531.0278 | Abs Value of | Flow this | 29640.7307 | Abs Value of | Flow this | 33733.9164 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -62.5586 |  |  | -1.5843 |  |  | -300.8914 |  |  | -1300.5016 |  |  | -3763.7264 |  |  | -8245.4821 |  |  | -14728.8298 |  |  | -21957.0447 |  |  | -29614.5772 |  |  | -38375.2729
[13 empty] | P2 at this iteration flow rate |  |  | 48.5517 |  |  | 36.3569 |  |  | 96.2183 |  |  | 296.1403 |  |  | 788.7853 |  |  | 1685.1364 |  |  | 2981.806 |  |  | 4427.4489 |  |  | 5958.9554 |  |  | 7711.0946
[13 empty] | Delta P at this iteration flow rate |  |  | -111.1104 |  |  | -37.9412 |  |  | -397.1096 |  |  | -1596.642 |  |  | -4552.5117 |  |  | -9930.6185 |  |  | -17710.6357 |  |  | -26384.4937 |  |  | -35573.5326 |  |  | -46086.3675
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -55.6616 |  |  | -1.736 |  |  | -250.6777 |  |  | -1034.9888 |  |  | -2822.3579 |  |  | -5747.6223 |  |  | -9452.8648 |  |  | -12768.3857 |  |  | -14844.7095 |  |  | -14462.3922
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1880.8637 |  | 5500 | 1316.1304 |  | 5500 | 3254.947 |  | 5500 | 6339.806 |  | 5500 | 10636.2223 |  | 5500 | 15679.0947 |  | 5500 | 20923.8127 |  | 5500 | 25531.0278 |  | 5500 | 29640.7307 |  | 5500 | 33733.9164
[13 empty] | Next iteration flow rate |  |  | 1918.4809 | Abs Value of | Flow this | 1329.2917 | Abs Value of | Flow this | 3287.4965 | Abs Value of | Flow this | 6403.2041 | Abs Value of | Flow this | 10742.5845 | Abs Value of | Flow this | 15835.8857 | Abs Value of | Flow this | 21133.0508 | Abs Value of | Flow this | 25786.3381 | Abs Value of | Flow this | 29937.138 | Abs Value of | Flow this | 34071.2556 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -67.3854 |  |  | -2.7602 |  |  | -308.0833 |  |  | -1327.7857 |  |  | -3840.5213 |  |  | -8412.3603 |  |  | -15026.0233 |  |  | -22399.5253 |  |  | -30210.9742 |  |  | -39147.7599
[13 empty] | P2 at this iteration flow rate |  |  | 49.5171 |  |  | 36.592 |  |  | 97.6567 |  |  | 301.5971 |  |  | 804.1443 |  |  | 1718.5121 |  |  | 3041.2447 |  |  | 4515.9451 |  |  | 6078.2348 |  |  | 7865.592
[13 empty] | Delta P at this iteration flow rate |  |  | -116.9025 |  |  | -39.3522 |  |  | -405.7399 |  |  | -1629.3829 |  |  | -4644.6655 |  |  | -10130.8723 |  |  | -18067.2679 |  |  | -26915.4704 |  |  | -36289.209 |  |  | -47013.3519
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -59.9263 |  |  | -2.7443 |  |  | -256.6607 |  |  | -1056.6952 |  |  | -2879.9385 |  |  | -5863.9408 |  |  | -9643.5959 |  |  | -13025.6903 |  |  | -15143.6571 |  |  | -14753.5141
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1918.4809 |  | 5500 | 1329.2917 |  | 5500 | 3287.4965 |  | 5500 | 6403.2041 |  | 5500 | 10742.5845 |  | 5500 | 15835.8857 |  | 5500 | 21133.0508 |  | 5500 | 25786.3381 |  | 5500 | 29937.138 |  | 5500 | 34071.2556
[13 empty] | Next iteration flow rate |  |  | 1956.8506 | Abs Value of | Flow this | 1342.5846 | Abs Value of | Flow this | 3320.3715 | Abs Value of | Flow this | 6467.2361 | Abs Value of | Flow this | 10850.0104 | Abs Value of | Flow this | 15994.2445 | Abs Value of | Flow this | 21344.3813 | Abs Value of | Flow this | 26044.2015 | Abs Value of | Flow this | 30236.5094 | Abs Value of | Flow this | 34411.9682 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -72.4072 |  |  | -3.9597 |  |  | -315.4198 |  |  | -1355.6182 |  |  | -3918.8598 |  |  | -8582.5927 |  |  | -15329.1904 |  |  | -22850.8998 |  |  | -30819.3588 |  |  | -39935.7739
[13 empty] | P2 at this iteration flow rate |  |  | 50.5214 |  |  | 36.8319 |  |  | 99.124 |  |  | 307.1636 |  |  | 819.812 |  |  | 1752.5585 |  |  | 3101.8781 |  |  | 4606.22 |  |  | 6199.9118 |  |  | 8023.1948
[13 empty] | Delta P at this iteration flow rate |  |  | -122.9286 |  |  | -40.7916 |  |  | -414.5437 |  |  | -1662.7819 |  |  | -4738.6717 |  |  | -10335.1513 |  |  | -18431.0684 |  |  | -27457.1198 |  |  | -37019.2705 |  |  | -47958.9687
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -64.3632 |  |  | -3.773 |  |  | -262.7639 |  |  | -1078.8379 |  |  | -2938.6764 |  |  | -5982.5972 |  |  | -9838.1607 |  |  | -13288.1668 |  |  | -15448.6137 |  |  | -15050.4876
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1956.8506 |  | 5500 | 1342.5846 |  | 5500 | 3320.3715 |  | 5500 | 6467.2361 |  | 5500 | 10850.0104 |  | 5500 | 15994.2445 |  | 5500 | 21344.3813 |  | 5500 | 26044.2015 |  | 5500 | 30236.5094 |  | 5500 | 34411.9682
[13 empty] | Next iteration flow rate |  |  | 1995.9876 | Abs Value of | Flow this | 1356.0104 | Abs Value of | Flow this | 3353.5752 | Abs Value of | Flow this | 6531.9085 | Abs Value of | Flow this | 10958.5105 | Abs Value of | Flow this | 16154.187 | Abs Value of | Flow this | 21557.8251 | Abs Value of | Flow this | 26304.6435 | Abs Value of | Flow this | 30538.8745 | Abs Value of | Flow this | 34756.0878 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -77.6319 |  |  | -5.1833 |  |  | -322.9037 |  |  | -1384.0102 |  |  | -3998.7729 |  |  | -8756.2469 |  |  | -15638.4511 |  |  | -23311.3469 |  |  | -31439.9719 |  |  | -40739.627
[13 empty] | P2 at this iteration flow rate |  |  | 51.5664 |  |  | 37.0767 |  |  | 100.6207 |  |  | 312.842 |  |  | 835.7946 |  |  | 1787.2894 |  |  | 3163.7302 |  |  | 4698.3094 |  |  | 6324.0344 |  |  | 8183.9654
[13 empty] | Delta P at this iteration flow rate |  |  | -129.1982 |  |  | -42.26 |  |  | -423.5245 |  |  | -1696.8522 |  |  | -4834.5675 |  |  | -10543.5362 |  |  | -18802.1813 |  |  | -28009.6563 |  |  | -37764.0063 |  |  | -48923.5924
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -68.9794 |  |  | -4.8223 |  |  | -268.9898 |  |  | -1101.4256 |  |  | -2998.5949 |  |  | -6103.6387 |  |  | -10036.6362 |  |  | -13555.9191 |  |  | -15759.6998 |  |  | -15353.4302
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1995.9876 |  | 5500 | 1356.0104 |  | 5500 | 3353.5752 |  | 5500 | 6531.9085 |  | 5500 | 10958.5105 |  | 5500 | 16154.187 |  | 5500 | 21557.8251 |  | 5500 | 26304.6435 |  | 5500 | 30538.8745 |  | 5500 | 34756.0878
[13 empty] | Next iteration flow rate |  |  | 2035.9073 | Abs Value of | Flow this | 1369.5705 | Abs Value of | Flow this | 3387.1109 | Abs Value of | Flow this | 6597.2276 | Abs Value of | Flow this | 11068.0956 | Abs Value of | Flow this | 16315.7288 | Abs Value of | Flow this | 21773.4034 | Abs Value of | Flow this | 26567.6899 | Abs Value of | Flow this | 30844.2632 | Abs Value of | Flow this | 35103.6487 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -83.0676 |  |  | -6.4315 |  |  | -330.5381 |  |  | -1412.9728 |  |  | -4080.2922 |  |  | -8933.3914 |  |  | -15953.928 |  |  | -23781.049 |  |  | -32073.0593 |  |  | -41559.6375
[13 empty] | P2 at this iteration flow rate |  |  | 52.6535 |  |  | 37.3263 |  |  | 102.1476 |  |  | 318.6346 |  |  | 852.0984 |  |  | 1822.7183 |  |  | 3226.8256 |  |  | 4792.2498 |  |  | 6450.6519 |  |  | 8347.9675
[13 empty] | Delta P at this iteration flow rate |  |  | -135.7211 |  |  | -43.7578 |  |  | -432.6857 |  |  | -1731.6074 |  |  | -4932.3907 |  |  | -10756.1097 |  |  | -19180.7536 |  |  | -28573.2988 |  |  | -38523.7112 |  |  | -49907.605
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -73.782 |  |  | -5.8926 |  |  | -275.3408 |  |  | -1124.4674 |  |  | -3059.7178 |  |  | -6227.113 |  |  | -10239.1012 |  |  | -13829.0532 |  |  | -16077.0388 |  |  | -15662.4619
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2035.9073 |  | 5500 | 1369.5705 |  | 5500 | 3387.1109 |  | 5500 | 6597.2276 |  | 5500 | 11068.0956 |  | 5500 | 16315.7288 |  | 5500 | 21773.4034 |  | 5500 | 26567.6899 |  | 5500 | 30844.2632 |  | 5500 | 35103.6487
[13 empty] | Next iteration flow rate |  |  | 2076.6255 | Abs Value of | Flow this | 1383.2662 | Abs Value of | Flow this | 3420.982 | Abs Value of | Flow this | 6663.1998 | Abs Value of | Flow this | 11178.7765 | Abs Value of | Flow this | 16478.8861 | Abs Value of | Flow this | 21991.1374 | Abs Value of | Flow this | 26833.3668 | Abs Value of | Flow this | 31152.7059 | Abs Value of | Flow this | 35454.6852 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -88.7229 |  |  | -7.7048 |  |  | -338.3259 |  |  | -1442.5176 |  |  | -4163.4501 |  |  | -9114.0966 |  |  | -16275.7459 |  |  | -24260.1921 |  |  | -32718.8718 |  |  | -42396.1302
[13 empty] | P2 at this iteration flow rate |  |  | 53.7846 |  |  | 37.581 |  |  | 103.7052 |  |  | 324.5435 |  |  | 868.73 |  |  | 1858.8593 |  |  | 3291.1892 |  |  | 4888.0784 |  |  | 6579.8144 |  |  | 8515.266
[13 empty] | Delta P at this iteration flow rate |  |  | -142.5075 |  |  | -45.2857 |  |  | -442.0311 |  |  | -1767.0611 |  |  | -5032.1801 |  |  | -10972.9559 |  |  | -19566.9351 |  |  | -29148.2705 |  |  | -39298.6862 |  |  | -50911.3963
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -78.7787 |  |  | -6.9845 |  |  | -281.8195 |  |  | -1147.9723 |  |  | -3122.0693 |  |  | -6353.0692 |  |  | -10445.6356 |  |  | -14107.6772 |  |  | -16400.7563 |  |  | -15977.7052
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2076.6255 |  | 5500 | 1383.2662 |  | 5500 | 3420.982 |  | 5500 | 6663.1998 |  | 5500 | 11178.7765 |  | 5500 | 16478.8861 |  | 5500 | 21991.1374 |  | 5500 | 26833.3668 |  | 5500 | 31152.7059 |  | 5500 | 35454.6852
[13 empty] | Next iteration flow rate |  |  | 2118.158 | Abs Value of | Flow this | 1397.0989 | Abs Value of | Flow this | 3455.1919 | Abs Value of | Flow this | 6729.8318 | Abs Value of | Flow this | 11290.5643 | Abs Value of | Flow this | 16643.675 | Abs Value of | Flow this | 22211.0488 | Abs Value of | Flow this | 27101.7005 | Abs Value of | Flow this | 31464.2329 | Abs Value of | Flow this | 35809.2321 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -94.6068 |  |  | -9.0037 |  |  | -346.2703 |  |  | -1472.6562 |  |  | -4248.2795 |  |  | -9298.434 |  |  | -16604.0325 |  |  | -24748.966 |  |  | -33377.6652 |  |  | -43249.4365
[13 empty] | P2 at this iteration flow rate |  |  | 54.9614 |  |  | 37.8407 |  |  | 105.2941 |  |  | 330.5712 |  |  | 885.6959 |  |  | 1895.7268 |  |  | 3356.8465 |  |  | 4985.8332 |  |  | 6711.573 |  |  | 8685.9273
[13 empty] | Delta P at this iteration flow rate |  |  | -149.5681 |  |  | -46.8444 |  |  | -451.5644 |  |  | -1803.2274 |  |  | -5133.9754 |  |  | -11194.1608 |  |  | -19960.8789 |  |  | -29734.7992 |  |  | -40089.2382 |  |  | -51935.3637
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -83.9773 |  |  | -8.0984 |  |  | -288.4285 |  |  | -1171.9496 |  |  | -3185.674 |  |  | -6481.5572 |  |  | -10656.3214 |  |  | -14391.9017 |  |  | -16730.9805 |  |  | -16299.2849
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2118.158 |  | 5500 | 1397.0989 |  | 5500 | 3455.1919 |  | 5500 | 6729.8318 |  | 5500 | 11290.5643 |  | 5500 | 16643.675 |  | 5500 | 22211.0488 |  | 5500 | 27101.7005 |  | 5500 | 31464.2329 |  | 5500 | 35809.2321
[13 empty] | Next iteration flow rate |  |  | 2160.5211 | Abs Value of | Flow this | 1411.0699 | Abs Value of | Flow this | 3489.7438 | Abs Value of | Flow this | 6797.1302 | Abs Value of | Flow this | 11403.47 | Abs Value of | Flow this | 16810.1117 | Abs Value of | Flow this | 22433.1593 | Abs Value of | Flow this | 27372.7175 | Abs Value of | Flow this | 31778.8752 | Abs Value of | Flow this | 36167.3244 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -100.7283 |  |  | -10.3286 |  |  | -354.3744 |  |  | -1503.4006 |  |  | -4334.8139 |  |  | -9486.4765 |  |  | -16938.9175 |  |  | -25247.5642 |  |  | -34049.7003 |  |  | -44119.8941
[13 empty] | P2 at this iteration flow rate |  |  | 56.1857 |  |  | 38.1057 |  |  | 106.9149 |  |  | 336.7201 |  |  | 903.0028 |  |  | 1933.3353 |  |  | 3423.8235 |  |  | 5085.5528 |  |  | 6845.9801 |  |  | 8860.0188
[13 empty] | Delta P at this iteration flow rate |  |  | -156.9139 |  |  | -48.4344 |  |  | -461.2892 |  |  | -1840.1207 |  |  | -5237.8167 |  |  | -11419.8118 |  |  | -20362.741 |  |  | -30333.1171 |  |  | -40895.6803 |  |  | -52979.913
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -89.3859 |  |  | -9.2346 |  |  | -295.1702 |  |  | -1196.4089 |  |  | -3250.5572 |  |  | -6612.6277 |  |  | -10871.242 |  |  | -14681.839 |  |  | -17067.8422 |  |  | -16627.3283
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2160.5211 |  | 5500 | 1411.0699 |  | 5500 | 3489.7438 |  | 5500 | 6797.1302 |  | 5500 | 11403.47 |  | 5500 | 16810.1117 |  | 5500 | 22433.1593 |  | 5500 | 27372.7175 |  | 5500 | 31778.8752 |  | 5500 | 36167.3244
[13 empty] | Next iteration flow rate |  |  | 2203.7316 | Abs Value of | Flow this | 1425.1806 | Abs Value of | Flow this | 3524.6412 | Abs Value of | Flow this | 6865.1015 | Abs Value of | Flow this | 11517.5046 | Abs Value of | Flow this | 16978.2128 | Abs Value of | Flow this | 22657.4909 | Abs Value of | Flow this | 27646.4447 | Abs Value of | Flow this | 32096.664 | Abs Value of | Flow this | 36528.9976 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -107.0971 |  |  | -11.6803 |  |  | -362.6413 |  |  | -1534.7629 |  |  | -4423.0877 |  |  | -9678.2987 |  |  | -17280.5338 |  |  | -25756.1843 |  |  | -34735.2433 |  |  | -45007.848
[13 empty] | P2 at this iteration flow rate |  |  | 57.4594 |  |  | 38.3761 |  |  | 108.5683 |  |  | 342.9926 |  |  | 920.6575 |  |  | 1971.6997 |  |  | 3492.1468 |  |  | 5187.2769 |  |  | 6983.0887 |  |  | 9037.6096
[13 empty] | Delta P at this iteration flow rate |  |  | -164.5565 |  |  | -50.0563 |  |  | -471.2096 |  |  | -1877.7555 |  |  | -5343.7452 |  |  | -11649.9984 |  |  | -20772.6805 |  |  | -30943.4611 |  |  | -41718.3319 |  |  | -54045.4576
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -95.013 |  |  | -10.3937 |  |  | -302.0475 |  |  | -1221.3599 |  |  | -3316.7446 |  |  | -6746.3328 |  |  | -11090.4825 |  |  | -14977.6041 |  |  | -17411.4748 |  |  | -16961.9654
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2203.7316 |  | 5500 | 1425.1806 |  | 5500 | 3524.6412 |  | 5500 | 6865.1015 |  | 5500 | 11517.5046 |  | 5500 | 16978.2128 |  | 5500 | 22657.4909 |  | 5500 | 27646.4447 |  | 5500 | 32096.664 |  | 5500 | 36528.9976
[13 empty] | Next iteration flow rate |  |  | 2247.8062 | Abs Value of | Flow this | 1439.4324 | Abs Value of | Flow this | 3559.8876 | Abs Value of | Flow this | 6933.7525 | Abs Value of | Flow this | 11632.6797 | Abs Value of | Flow this | 17147.995 | Abs Value of | Flow this | 22884.0658 | Abs Value of | Flow this | 27922.9091 | Abs Value of | Flow this | 32417.6306 | Abs Value of | Flow this | 36894.2876 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -113.7233 |  |  | -13.0591 |  |  | -371.0744 |  |  | -1566.7557 |  |  | -4513.1358 |  |  | -9873.9765 |  |  | -17629.0165 |  |  | -26275.0276 |  |  | -35434.5657 |  |  | -45913.6498
[13 empty] | P2 at this iteration flow rate |  |  | 58.7847 |  |  | 38.6518 |  |  | 110.2549 |  |  | 349.3911 |  |  | 938.6672 |  |  | 2010.8353 |  |  | 3561.8433 |  |  | 5291.0455 |  |  | 7122.9531 |  |  | 9218.77
[13 empty] | Delta P at this iteration flow rate |  |  | -172.5079 |  |  | -51.7109 |  |  | -481.3293 |  |  | -1916.1468 |  |  | -5451.8029 |  |  | -11884.8118 |  |  | -21190.8598 |  |  | -31566.0731 |  |  | -42557.5188 |  |  | -55132.4197
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -100.8674 |  |  | -11.576 |  |  | -309.063 |  |  | -1246.8123 |  |  | -3384.2623 |  |  | -6882.7253 |  |  | -11314.1297 |  |  | -15279.314 |  |  | -17762.0145 |  |  | -17303.3287
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2247.8062 |  | 5500 | 1439.4324 |  | 5500 | 3559.8876 |  | 5500 | 6933.7525 |  | 5500 | 11632.6797 |  | 5500 | 17147.995 |  | 5500 | 22884.0658 |  | 5500 | 27922.9091 |  | 5500 | 32417.6306 |  | 5500 | 36894.2876
[13 empty] | Next iteration flow rate |  |  | 2292.7623 | Abs Value of | Flow this | 1453.8267 | Abs Value of | Flow this | 3595.4865 | Abs Value of | Flow this | 7003.09 | Abs Value of | Flow this | 11749.0065 | Abs Value of | Flow this | 17319.4749 | Abs Value of | Flow this | 23112.9064 | Abs Value of | Flow this | 28202.1382 | Abs Value of | Flow this | 32741.8069 | Abs Value of | Flow this | 37263.2305 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -120.6171 |  |  | -14.4656 |  |  | -379.677 |  |  | -1599.3915 |  |  | -4604.9938 |  |  | -10073.5875 |  |  | -17984.5038 |  |  | -26804.2997 |  |  | -36147.9444 |  |  | -46837.6582
[13 empty] | P2 at this iteration flow rate |  |  | 60.1634 |  |  | 38.9331 |  |  | 111.9754 |  |  | 355.9183 |  |  | 957.0388 |  |  | 2050.7575 |  |  | 3632.9408 |  |  | 5396.8999 |  |  | 7265.6289 |  |  | 9403.5716
[13 empty] | Delta P at this iteration flow rate |  |  | -180.7805 |  |  | -53.3987 |  |  | -491.6524 |  |  | -1955.3098 |  |  | -5562.0326 |  |  | -12124.345 |  |  | -21617.4445 |  |  | -32201.1996 |  |  | -43413.5733 |  |  | -56241.2298
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -106.9584 |  |  | -12.7822 |  |  | -316.2195 |  |  | -1272.7763 |  |  | -3453.1371 |  |  | -7021.8593 |  |  | -11542.2722 |  |  | -15587.0883 |  |  | -18119.6 |  |  | -17651.5534
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2292.7623 |  | 5500 | 1453.8267 |  | 5500 | 3595.4865 |  | 5500 | 7003.09 |  | 5500 | 11749.0065 |  | 5500 | 17319.4749 |  | 5500 | 23112.9064 |  | 5500 | 28202.1382 |  | 5500 | 32741.8069 |  | 5500 | 37263.2305
[13 empty] | Next iteration flow rate |  |  | 2338.6176 | Abs Value of | Flow this | 1468.365 | Abs Value of | Flow this | 3631.4414 | Abs Value of | Flow this | 7073.1209 | Abs Value of | Flow this | 11866.4966 | Abs Value of | Flow this | 17492.6697 | Abs Value of | Flow this | 23344.0355 | Abs Value of | Flow this | 28484.1596 | Abs Value of | Flow this | 33069.225 | Abs Value of | Flow this | 37635.8628 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -127.7894 |  |  | -15.9003 |  |  | -388.4525 |  |  | -1632.6833 |  |  | -4698.6982 |  |  | -10277.2106 |  |  | -18347.1363 |  |  | -27344.2101 |  |  | -36875.6621 |  |  | -47780.2391
[13 empty] | P2 at this iteration flow rate |  |  | 61.5979 |  |  | 39.2201 |  |  | 113.7305 |  |  | 362.5767 |  |  | 975.7796 |  |  | 2091.4821 |  |  | 3705.4673 |  |  | 5504.882 |  |  | 7411.1724 |  |  | 9592.0878
[13 empty] | Delta P at this iteration flow rate |  |  | -189.3873 |  |  | -55.1204 |  |  | -502.183 |  |  | -1995.2599 |  |  | -5674.4778 |  |  | -12368.6927 |  |  | -22052.6036 |  |  | -32849.0921 |  |  | -44286.8346 |  |  | -57372.3269
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -113.2954 |  |  | -14.0125 |  |  | -323.5199 |  |  | -1299.2622 |  |  | -3523.3963 |  |  | -7163.79 |  |  | -11775.0004 |  |  | -15901.0489 |  |  | -18484.373 |  |  | -18006.7775
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2338.6176 |  | 5500 | 1468.365 |  | 5500 | 3631.4414 |  | 5500 | 7073.1209 |  | 5500 | 11866.4966 |  | 5500 | 17492.6697 |  | 5500 | 23344.0355 |  | 5500 | 28484.1596 |  | 5500 | 33069.225 |  | 5500 | 37635.8628
[13 empty] | Next iteration flow rate |  |  | 2385.3899 | Abs Value of | Flow this | 1483.0486 | Abs Value of | Flow this | 3667.7558 | Abs Value of | Flow this | 7143.8521 | Abs Value of | Flow this | 11985.1615 | Abs Value of | Flow this | 17667.5964 | Abs Value of | Flow this | 23577.4758 | Abs Value of | Flow this | 28769.0012 | Abs Value of | Flow this | 33399.9173 | Abs Value of | Flow this | 38012.2214 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -135.2515 |  |  | -17.3639 |  |  | -397.4044 |  |  | -1666.6442 |  |  | -4794.286 |  |  | -10484.9265 |  |  | -18717.0578 |  |  | -27894.9727 |  |  | -37618.007 |  |  | -48741.7659
[13 empty] | P2 at this iteration flow rate |  |  | 63.0903 |  |  | 39.5128 |  |  | 115.5209 |  |  | 369.3688 |  |  | 994.8972 |  |  | 2133.0253 |  |  | 3779.4516 |  |  | 5615.0345 |  |  | 7559.6414 |  |  | 9784.3932
[13 empty] | Delta P at this iteration flow rate |  |  | -198.3418 |  |  | -56.8767 |  |  | -512.9253 |  |  | -2036.0131 |  |  | -5789.1833 |  |  | -12617.9518 |  |  | -22496.5093 |  |  | -33510.0073 |  |  | -45177.6484 |  |  | -58526.1591
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -119.8884 |  |  | -15.2676 |  |  | -330.967 |  |  | -1326.2805 |  |  | -3595.0677 |  |  | -7308.5734 |  |  | -12012.4065 |  |  | -16221.3201 |  |  | -18856.4779 |  |  | -18369.1415
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2385.3899 |  | 5500 | 1483.0486 |  | 5500 | 3667.7558 |  | 5500 | 7143.8521 |  | 5500 | 11985.1615 |  | 5500 | 17667.5964 |  | 5500 | 23577.4758 |  | 5500 | 28769.0012 |  | 5500 | 33399.9173 |  | 5500 | 38012.2214
[13 empty] | Next iteration flow rate |  |  | 2433.0977 | Abs Value of | Flow this | 1497.8791 | Abs Value of | Flow this | 3704.4333 | Abs Value of | Flow this | 7215.2906 | Abs Value of | Flow this | 12105.0131 | Abs Value of | Flow this | 17844.2723 | Abs Value of | Flow this | 23813.2506 | Abs Value of | Flow this | 29056.6912 | Abs Value of | Flow this | 33733.9164 | Abs Value of | Flow this | 38392.3436 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -143.0151 |  |  | -18.857 |  |  | -406.5363 |  |  | -1701.2878 |  |  | -4891.7952 |  |  | -10696.8176 |  |  | -19094.4146 |  |  | -28456.8057 |  |  | -38375.2729 |  |  | -49722.6194
[13 empty] | P2 at this iteration flow rate |  |  | 64.643 |  |  | 39.8114 |  |  | 117.3473 |  |  | 376.2976 |  |  | 1014.399 |  |  | 2175.4035 |  |  | 3854.9229 |  |  | 5727.4011 |  |  | 7711.0946 |  |  | 9980.5639
[13 empty] | Delta P at this iteration flow rate |  |  | -207.6581 |  |  | -58.6684 |  |  | -523.8835 |  |  | -2077.5854 |  |  | -5906.1942 |  |  | -12872.2211 |  |  | -22949.3376 |  |  | -34184.2068 |  |  | -46086.3675 |  |  | -59703.1833
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -126.7478 |  |  | -16.548 |  |  | -338.5637 |  |  | -1353.8419 |  |  | -3668.1797 |  |  | -7456.2669 |  |  | -12254.5843 |  |  | -16548.0287 |  |  | -19236.0621 |  |  | -18738.7891
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2433.0977 |  | 5500 | 1497.8791 |  | 5500 | 3704.4333 |  | 5500 | 7215.2906 |  | 5500 | 12105.0131 |  | 5500 | 17844.2723 |  | 5500 | 23813.2506 |  | 5500 | 29056.6912 |  | 5500 | 33733.9164 |  | 5500 | 38392.3436
[13 empty] | Next iteration flow rate |  |  | 2481.7597 | Abs Value of | Flow this | 1512.8579 | Abs Value of | Flow this | 3741.4777 | Abs Value of | Flow this | 7287.4435 | Abs Value of | Flow this | 12226.0633 | Abs Value of | Flow this | 18022.7151 | Abs Value of | Flow this | 24051.3831 | Abs Value of | Flow this | 29347.2581 | Abs Value of | Flow this | 34071.2556 | Abs Value of | Flow this | 38776.2671 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -151.0923 |  |  | -20.38 |  |  | -415.8517 |  |  | -1736.6277 |  |  | -4991.2643 |  |  | -10912.9676 |  |  | -19479.3564 |  |  | -29029.9315 |  |  | -39147.7599 |  |  | -50723.1881
[13 empty] | P2 at this iteration flow rate |  |  | 66.2585 |  |  | 40.116 |  |  | 119.2103 |  |  | 383.3655 |  |  | 1034.2929 |  |  | 2218.6335 |  |  | 3931.9113 |  |  | 5842.0263 |  |  | 7865.592 |  |  | 10180.6776
[13 empty] | Delta P at this iteration flow rate |  |  | -217.3508 |  |  | -60.496 |  |  | -535.062 |  |  | -2119.9932 |  |  | -6025.5572 |  |  | -13131.6011 |  |  | -23411.2677 |  |  | -34871.9578 |  |  | -47013.3519 |  |  | -60903.8657
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -133.8843 |  |  | -17.8541 |  |  | -346.3132 |  |  | -1381.9572 |  |  | -3742.7613 |  |  | -7606.9291 |  |  | -12501.63 |  |  | -16881.3042 |  |  | -19623.276 |  |  | -19115.8665
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2481.7597 |  | 5500 | 1512.8579 |  | 5500 | 3741.4777 |  | 5500 | 7287.4435 |  | 5500 | 12226.0633 |  | 5500 | 18022.7151 |  | 5500 | 24051.3831 |  | 5500 | 29347.2581 |  | 5500 | 34071.2556 |  | 5500 | 38776.2671
[13 empty] | Next iteration flow rate |  |  | 2531.3949 | Abs Value of | Flow this | 1527.9865 | Abs Value of | Flow this | 3778.8925 | Abs Value of | Flow this | 7360.318 | Abs Value of | Flow this | 12348.3239 | Abs Value of | Flow this | 18202.9422 | Abs Value of | Flow this | 24291.8969 | Abs Value of | Flow this | 29640.7307 | Abs Value of | Flow this | 34411.9682 | Abs Value of | Flow this | 39164.0297 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -159.4959 |  |  | -21.9337 |  |  | -425.3543 |  |  | -1772.6779 |  |  | -5092.7327 |  |  | -11133.4623 |  |  | -19872.0355 |  |  | -29614.5772 |  |  | -39935.7739 |  |  | -51743.8682
[13 empty] | P2 at this iteration flow rate |  |  | 67.9392 |  |  | 40.4267 |  |  | 121.1109 |  |  | 390.5756 |  |  | 1054.5865 |  |  | 2262.7325 |  |  | 4010.4471 |  |  | 5958.9554 |  |  | 8023.1948 |  |  | 10384.8136
[13 empty] | Delta P at this iteration flow rate |  |  | -227.4351 |  |  | -62.3604 |  |  | -546.4652 |  |  | -2163.2535 |  |  | -6147.3193 |  |  | -13396.1947 |  |  | -23882.4826 |  |  | -35573.5326 |  |  | -47958.9687 |  |  | -62128.6818
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -141.3092 |  |  | -19.1864 |  |  | -354.2185 |  |  | -1410.6376 |  |  | -3818.8419 |  |  | -7760.6197 |  |  | -12753.6413 |  |  | -17221.2785 |  |  | -20018.2728 |  |  | -19500.5232
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2531.3949 |  | 5500 | 1527.9865 |  | 5500 | 3778.8925 |  | 5500 | 7360.318 |  | 5500 | 12348.3239 |  | 5500 | 18202.9422 |  | 5500 | 24291.8969 |  | 5500 | 29640.7307 |  | 5500 | 34411.9682 |  | 5500 | 39164.0297
[13 empty] | Next iteration flow rate |  |  | 2582.0228 | Abs Value of | Flow this | 1543.2664 | Abs Value of | Flow this | 3816.6814 | Abs Value of | Flow this | 7433.9211 | Abs Value of | Flow this | 12471.8071 | Abs Value of | Flow this | 18384.9716 | Abs Value of | Flow this | 24534.8159 | Abs Value of | Flow this | 29937.138 | Abs Value of | Flow this | 34756.0878 | Abs Value of | Flow this | 39555.67 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -168.2389 |  |  | -23.5185 |  |  | -435.0479 |  |  | -1809.4528 |  |  | -5196.2407 |  |  | -11358.3889 |  |  | -20272.6074 |  |  | -30210.9742 |  |  | -40739.627 |  |  | -52785.064
[13 empty] | P2 at this iteration flow rate |  |  | 69.6878 |  |  | 40.7437 |  |  | 123.0496 |  |  | 397.9306 |  |  | 1075.2881 |  |  | 2307.7178 |  |  | 4090.5615 |  |  | 6078.2348 |  |  | 8183.9654 |  |  | 10593.0528
[13 empty] | Delta P at this iteration flow rate |  |  | -237.9267 |  |  | -64.2623 |  |  | -558.0975 |  |  | -2207.3833 |  |  | -6271.5288 |  |  | -13666.1067 |  |  | -24363.1689 |  |  | -36289.209 |  |  | -48923.5924 |  |  | -63378.1168
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -149.034 |  |  | -20.5455 |  |  | -362.2826 |  |  | -1439.8946 |  |  | -3896.4518 |  |  | -7917.3994 |  |  | -13010.718 |  |  | -17568.0863 |  |  | -20421.2091 |  |  | -19892.9116
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2582.0228 |  | 5500 | 1543.2664 |  | 5500 | 3816.6814 |  | 5500 | 7433.9211 |  | 5500 | 12471.8071 |  | 5500 | 18384.9716 |  | 5500 | 24534.8159 |  | 5500 | 29937.138 |  | 5500 | 34756.0878 |  | 5500 | 39555.67
[13 empty] | Next iteration flow rate |  |  | 2633.6632 | Abs Value of | Flow this | 1558.699 | Abs Value of | Flow this | 3854.8482 | Abs Value of | Flow this | 7508.2604 | Abs Value of | Flow this | 12596.5252 | Abs Value of | Flow this | 18568.8213 | Abs Value of | Flow this | 24780.1641 | Abs Value of | Flow this | 30236.5094 | Abs Value of | Flow this | 35103.6487 | Abs Value of | Flow this | 39951.2267 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -177.3352 |  |  | -25.1353 |  |  | -444.9364 |  |  | -1846.9668 |  |  | -5301.8291 |  |  | -11587.8365 |  |  | -20681.2308 |  |  | -30819.3588 |  |  | -41559.6375 |  |  | -53847.1878
[13 empty] | P2 at this iteration flow rate |  |  | 71.507 |  |  | 41.0671 |  |  | 125.0273 |  |  | 405.4334 |  |  | 1096.4058 |  |  | 2353.6073 |  |  | 4172.2862 |  |  | 6199.9118 |  |  | 8347.9675 |  |  | 10805.4776
[13 empty] | Delta P at this iteration flow rate |  |  | -248.8422 |  |  | -66.2023 |  |  | -569.9637 |  |  | -2252.4001 |  |  | -6398.235 |  |  | -13941.4438 |  |  | -24853.517 |  |  | -37019.2705 |  |  | -49907.605 |  |  | -64652.6653
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -157.0708 |  |  | -21.9319 |  |  | -370.5088 |  |  | -1469.7395 |  |  | -3975.6216 |  |  | -8077.3303 |  |  | -13272.962 |  |  | -17921.865 |  |  | -20832.2444 |  |  | -20293.1869
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2633.6632 |  | 5500 | 1558.699 |  | 5500 | 3854.8482 |  | 5500 | 7508.2604 |  | 5500 | 12596.5252 |  | 5500 | 18568.8213 |  | 5500 | 24780.1641 |  | 5500 | 30236.5094 |  | 5500 | 35103.6487 |  | 5500 | 39951.2267
[13 empty] | Next iteration flow rate |  |  | 2686.3365 | Abs Value of | Flow this | 1574.286 | Abs Value of | Flow this | 3893.3967 | Abs Value of | Flow this | 7583.343 | Abs Value of | Flow this | 12722.4905 | Abs Value of | Flow this | 18754.5096 | Abs Value of | Flow this | 25027.9657 | Abs Value of | Flow this | 30538.8745 | Abs Value of | Flow this | 35454.6852 | Abs Value of | Flow this | 40350.739 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -186.7989 |  |  | -26.7845 |  |  | -455.0237 |  |  | -1885.2348 |  |  | -5409.5399 |  |  | -11821.896 |  |  | -21098.0676 |  |  | -31439.9719 |  |  | -42396.1302 |  |  | -54930.6603
[13 empty] | P2 at this iteration flow rate |  |  | 73.3998 |  |  | 41.3969 |  |  | 127.0447 |  |  | 413.087 |  |  | 1117.948 |  |  | 2400.4192 |  |  | 4255.6535 |  |  | 6324.0344 |  |  | 8515.266 |  |  | 11022.1721
[13 empty] | Delta P at this iteration flow rate |  |  | -260.1987 |  |  | -68.1814 |  |  | -582.0684 |  |  | -2298.3218 |  |  | -6527.4879 |  |  | -14222.3153 |  |  | -25353.7211 |  |  | -37764.0063 |  |  | -50911.3963 |  |  | -65952.8323
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -165.4324 |  |  | -23.3462 |  |  | -378.9004 |  |  | -1500.1844 |  |  | -4056.3828 |  |  | -8240.4759 |  |  | -13540.477 |  |  | -18282.7546 |  |  | -21251.5415 |  |  | -20701.5077
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2686.3365 |  | 5500 | 1574.286 |  | 5500 | 3893.3967 |  | 5500 | 7583.343 |  | 5500 | 12722.4905 |  | 5500 | 18754.5096 |  | 5500 | 25027.9657 |  | 5500 | 30538.8745 |  | 5500 | 35454.6852 |  | 5500 | 40350.739
[13 empty] | Next iteration flow rate |  |  | 2740.0632 | Abs Value of | Flow this | 1590.0289 | Abs Value of | Flow this | 3932.3306 | Abs Value of | Flow this | 7659.1764 | Abs Value of | Flow this | 12849.7154 | Abs Value of | Flow this | 18942.0547 | Abs Value of | Flow this | 25278.2454 | Abs Value of | Flow this | 30844.2632 | Abs Value of | Flow this | 35809.2321 | Abs Value of | Flow this | 40754.2464 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -196.645 |  |  | -28.4669 |  |  | -465.3137 |  |  | -1924.2721 |  |  | -5519.4157 |  |  | -12060.6602 |  |  | -21523.2827 |  |  | -32073.0593 |  |  | -43249.4365 |  |  | -56035.9105
[13 empty] | P2 at this iteration flow rate |  |  | 75.369 |  |  | 41.7334 |  |  | 129.1027 |  |  | 420.8944 |  |  | 1139.9231 |  |  | 2448.172 |  |  | 4340.6965 |  |  | 6450.6519 |  |  | 8685.9273 |  |  | 11243.2221
[13 empty] | Delta P at this iteration flow rate |  |  | -272.014 |  |  | -70.2003 |  |  | -594.4164 |  |  | -2345.1665 |  |  | -6659.3388 |  |  | -14508.8322 |  |  | -25863.9793 |  |  | -38523.7112 |  |  | -51935.3637 |  |  | -67279.1326
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -174.1318 |  |  | -24.7889 |  |  | -387.4607 |  |  | -1531.2412 |  |  | -4138.7672 |  |  | -8406.9007 |  |  | -13813.3691 |  |  | -18650.8981 |  |  | -21679.2665 |  |  | -21118.0359
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2740.0632 |  | 5500 | 1590.0289 |  | 5500 | 3932.3306 |  | 5500 | 7659.1764 |  | 5500 | 12849.7154 |  | 5500 | 18942.0547 |  | 5500 | 25278.2454 |  | 5500 | 30844.2632 |  | 5500 | 35809.2321 |  | 5500 | 40754.2464
[13 empty] | Next iteration flow rate |  |  | 2794.8645 | Abs Value of | Flow this | 1605.9292 | Abs Value of | Flow this | 3971.654 | Abs Value of | Flow this | 7735.7682 | Abs Value of | Flow this | 12978.2125 | Abs Value of | Flow this | 19131.4752 | Abs Value of | Flow this | 25531.0278 | Abs Value of | Flow this | 31152.7059 | Abs Value of | Flow this | 36167.3244 | Abs Value of | Flow this | 41161.7888 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -206.8889 |  |  | -30.1831 |  |  | -475.8105 |  |  | -1964.094 |  |  | -5631.4999 |  |  | -12304.2235 |  |  | -21957.0447 |  |  | -32718.8718 |  |  | -44119.8941 |  |  | -57163.3764
[13 empty] | P2 at this iteration flow rate |  |  | 77.4178 |  |  | 42.0766 |  |  | 131.2021 |  |  | 428.8588 |  |  | 1162.34 |  |  | 2496.8847 |  |  | 4427.4489 |  |  | 6579.8144 |  |  | 8860.0188 |  |  | 11468.7153
[13 empty] | Delta P at this iteration flow rate |  |  | -284.3067 |  |  | -72.2597 |  |  | -607.0126 |  |  | -2392.9527 |  |  | -6793.8399 |  |  | -14801.1081 |  |  | -26384.4937 |  |  | -39298.6862 |  |  | -52979.913 |  |  | -68632.0916
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -183.1826 |  |  | -26.2606 |  |  | -396.193 |  |  | -1562.9223 |  |  | -4222.8076 |  |  | -8576.6707 |  |  | -14091.7464 |  |  | -19026.4412 |  |  | -22115.5888 |  |  | -21542.9362
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2794.8645 |  | 5500 | 1605.9292 |  | 5500 | 3971.654 |  | 5500 | 7735.7682 |  | 5500 | 12978.2125 |  | 5500 | 19131.4752 |  | 5500 | 25531.0278 |  | 5500 | 31152.7059 |  | 5500 | 36167.3244 |  | 5500 | 41161.7888
[13 empty] | Next iteration flow rate |  |  | 2850.7618 | Abs Value of | Flow this | 1621.9885 | Abs Value of | Flow this | 4011.3705 | Abs Value of | Flow this | 7813.1258 | Abs Value of | Flow this | 13107.9946 | Abs Value of | Flow this | 19322.79 | Abs Value of | Flow this | 25786.3381 | Abs Value of | Flow this | 31464.2329 | Abs Value of | Flow this | 36528.9976 | Abs Value of | Flow this | 41573.4067 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -217.5466 |  |  | -31.9338 |  |  | -486.5183 |  |  | -2004.7163 |  |  | -5745.8371 |  |  | -12552.6824 |  |  | -22399.5253 |  |  | -33377.6652 |  |  | -45007.848 |  |  | -58313.5042
[13 empty] | P2 at this iteration flow rate |  |  | 79.5493 |  |  | 42.4268 |  |  | 133.3437 |  |  | 436.9833 |  |  | 1185.2074 |  |  | 2546.5765 |  |  | 4515.9451 |  |  | 6711.573 |  |  | 9037.6096 |  |  | 11698.7408
[13 empty] | Delta P at this iteration flow rate |  |  | -297.096 |  |  | -74.3606 |  |  | -619.8619 |  |  | -2441.6995 |  |  | -6931.0445 |  |  | -15099.2588 |  |  | -26915.4704 |  |  | -40089.2382 |  |  | -54045.4576 |  |  | -70012.2451
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -192.5991 |  |  | -27.7619 |  |  | -405.1008 |  |  | -1595.2401 |  |  | -4308.5371 |  |  | -8749.853 |  |  | -14375.719 |  |  | -19409.5328 |  |  | -22560.6812 |  |  | -21976.377
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2850.7618 |  | 5500 | 1621.9885 |  | 5500 | 4011.3705 |  | 5500 | 7813.1258 |  | 5500 | 13107.9946 |  | 5500 | 19322.79 |  | 5500 | 25786.3381 |  | 5500 | 31464.2329 |  | 5500 | 36528.9976 |  | 5500 | 41573.4067
[13 empty] | Next iteration flow rate |  |  | 2907.777 | Abs Value of | Flow this | 1638.2083 | Abs Value of | Flow this | 4051.4842 | Abs Value of | Flow this | 7891.2571 | Abs Value of | Flow this | 13239.0746 | Abs Value of | Flow this | 19516.0179 | Abs Value of | Flow this | 26044.2015 | Abs Value of | Flow this | 31778.8752 | Abs Value of | Flow this | 36894.2876 | Abs Value of | Flow this | 41989.1408 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -228.6349 |  |  | -33.7197 |  |  | -497.4413 |  |  | -2046.1551 |  |  | -5862.4724 |  |  | -12806.1353 |  |  | -22850.8998 |  |  | -34049.7003 |  |  | -45913.6498 |  |  | -59486.7497
[13 empty] | P2 at this iteration flow rate |  |  | 81.767 |  |  | 42.7839 |  |  | 135.5283 |  |  | 445.271 |  |  | 1208.5345 |  |  | 2597.2671 |  |  | 4606.22 |  |  | 6845.9801 |  |  | 9218.77 |  |  | 11933.3899
[13 empty] | Delta P at this iteration flow rate |  |  | -310.4019 |  |  | -76.5036 |  |  | -632.9696 |  |  | -2491.4261 |  |  | -7071.0069 |  |  | -15403.4023 |  |  | -27457.1198 |  |  | -40895.6803 |  |  | -55132.4197 |  |  | -71420.1396
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -202.396 |  |  | -29.2934 |  |  | -414.1877 |  |  | -1628.2076 |  |  | -4395.9899 |  |  | -8926.5163 |  |  | -14665.3995 |  |  | -19800.3245 |  |  | -23014.7199 |  |  | -22418.53
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2907.777 |  | 5500 | 1638.2083 |  | 5500 | 4051.4842 |  | 5500 | 7891.2571 |  | 5500 | 13239.0746 |  | 5500 | 19516.0179 |  | 5500 | 26044.2015 |  | 5500 | 31778.8752 |  | 5500 | 36894.2876 |  | 5500 | 41989.1408
[13 empty] | Next iteration flow rate |  |  | 2965.9325 | Abs Value of | Flow this | 1654.5904 | Abs Value of | Flow this | 4091.999 | Abs Value of | Flow this | 7970.1697 | Abs Value of | Flow this | 13371.4653 | Abs Value of | Flow this | 19711.178 | Abs Value of | Flow this | 26304.6435 | Abs Value of | Flow this | 32096.664 | Abs Value of | Flow this | 37263.2305 | Abs Value of | Flow this | 42409.0322 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -240.1712 |  |  | -35.5415 |  |  | -508.5839 |  |  | -2088.4268 |  |  | -5981.4522 |  |  | -13064.6826 |  |  | -23311.3469 |  |  | -34735.2433 |  |  | -46837.6582 |  |  | -60683.5774
[13 empty] | P2 at this iteration flow rate |  |  | 84.0742 |  |  | 43.1483 |  |  | 137.7568 |  |  | 453.7254 |  |  | 1232.3304 |  |  | 2648.9765 |  |  | 4698.3094 |  |  | 6983.0887 |  |  | 9403.5716 |  |  | 12172.7555
[13 empty] | Delta P at this iteration flow rate |  |  | -324.2454 |  |  | -78.6897 |  |  | -646.3407 |  |  | -2542.1522 |  |  | -7213.7826 |  |  | -15713.6591 |  |  | -28009.6563 |  |  | -41718.3319 |  |  | -56241.2298 |  |  | -72856.3328
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -212.5887 |  |  | -30.8556 |  |  | -423.4572 |  |  | -1661.8376 |  |  | -4485.2004 |  |  | -9106.7305 |  |  | -14960.9025 |  |  | -20198.9711 |  |  | -23477.8847 |  |  | -22869.5702
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2965.9325 |  | 5500 | 1654.5904 |  | 5500 | 4091.999 |  | 5500 | 7970.1697 |  | 5500 | 13371.4653 |  | 5500 | 19711.178 |  | 5500 | 26304.6435 |  | 5500 | 32096.664 |  | 5500 | 37263.2305 |  | 5500 | 42409.0322
[13 empty] | Next iteration flow rate |  |  | 3025.2512 | Abs Value of | Flow this | 1671.1363 | Abs Value of | Flow this | 4132.919 | Abs Value of | Flow this | 8049.8714 | Abs Value of | Flow this | 13505.18 | Abs Value of | Flow this | 19908.2898 | Abs Value of | Flow this | 26567.6899 | Abs Value of | Flow this | 32417.6306 | Abs Value of | Flow this | 37635.8628 | Abs Value of | Flow this | 42833.1225 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -252.1735 |  |  | -37.3999 |  |  | -519.9504 |  |  | -2131.5482 |  |  | -6102.8234 |  |  | -13328.4268 |  |  | -23781.049 |  |  | -35434.5657 |  |  | -47780.2391 |  |  | -61904.4613
[13 empty] | P2 at this iteration flow rate |  |  | 86.4747 |  |  | 43.52 |  |  | 140.0301 |  |  | 462.3496 |  |  | 1256.6047 |  |  | 2701.7254 |  |  | 4792.2498 |  |  | 7122.9531 |  |  | 9592.0878 |  |  | 12416.9323
[13 empty] | Delta P at this iteration flow rate |  |  | -338.6482 |  |  | -80.9198 |  |  | -659.9805 |  |  | -2593.8978 |  |  | -7359.428 |  |  | -16030.1521 |  |  | -28573.2988 |  |  | -42557.5188 |  |  | -57372.3269 |  |  | -74321.3935
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -223.1932 |  |  | -32.4493 |  |  | -432.913 |  |  | -1696.1437 |  |  | -4576.2041 |  |  | -9290.567 |  |  | -15262.3452 |  |  | -20605.6306 |  |  | -23950.3592 |  |  | -23329.6764
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 3025.2512 |  | 5500 | 1671.1363 |  | 5500 | 4132.919 |  | 5500 | 8049.8714 |  | 5500 | 13505.18 |  | 5500 | 19908.2898 |  | 5500 | 26567.6899 |  | 5500 | 32417.6306 |  | 5500 | 37635.8628 |  | 5500 | 42833.1225
[13 empty] | Next iteration flow rate |  |  | 3085.7562 | Abs Value of | Flow this | 1687.8477 | Abs Value of | Flow this | 4174.2482 | Abs Value of | Flow this | 8130.3701 | Abs Value of | Flow this | 13640.2318 | Abs Value of | Flow this | 20107.3727 | Abs Value of | Flow this | 26833.3668 | Abs Value of | Flow this | 32741.8069 | Abs Value of | Flow this | 38012.2214 | Abs Value of | Flow this | 43261.4538 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -264.6607 |  |  | -39.2956 |  |  | -531.5455 |  |  | -2175.5363 |  |  | -6226.6341 |  |  | -13597.4721 |  |  | -24260.1921 |  |  | -36147.9444 |  |  | -48741.7659 |  |  | -63149.885
[13 empty] | P2 at this iteration flow rate |  |  | 88.9721 |  |  | 43.8991 |  |  | 142.3491 |  |  | 471.1473 |  |  | 1281.3668 |  |  | 2755.5344 |  |  | 4888.0784 |  |  | 7265.6289 |  |  | 9784.3932 |  |  | 12666.017
[13 empty] | Delta P at this iteration flow rate |  |  | -353.6329 |  |  | -83.1947 |  |  | -673.8946 |  |  | -2646.6836 |  |  | -7508.0009 |  |  | -16353.0066 |  |  | -29148.2705 |  |  | -43413.5733 |  |  | -58526.1591 |  |  | -75815.902
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -234.2261 |  |  | -34.0749 |  |  | -442.5589 |  |  | -1731.1393 |  |  | -4669.037 |  |  | -9478.0987 |  |  | -15569.8468 |  |  | -21020.4638 |  |  | -24432.3305 |  |  | -23799.0307
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 3085.7562 |  | 5500 | 1687.8477 |  | 5500 | 4174.2482 |  | 5500 | 8130.3701 |  | 5500 | 13640.2318 |  | 5500 | 20107.3727 |  | 5500 | 26833.3668 |  | 5500 | 32741.8069 |  | 5500 | 38012.2214 |  | 5500 | 43261.4538
[13 empty] | Next iteration flow rate |  |  | 3147.4713 | Abs Value of | Flow this | 1704.7262 | Abs Value of | Flow this | 4215.9907 | Abs Value of | Flow this | 8211.6738 | Abs Value of | Flow this | 13776.6341 | Abs Value of | Flow this | 20308.4464 | Abs Value of | Flow this | 27101.7005 | Abs Value of | Flow this | 33069.225 | Abs Value of | Flow this | 38392.3436 | Abs Value of | Flow this | 43694.0683 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -277.6524 |  |  | -41.2295 |  |  | -543.3735 |  |  | -2220.4086 |  |  | -6352.9335 |  |  | -13871.9254 |  |  | -24748.966 |  |  | -36875.6621 |  |  | -49722.6194 |  |  | -64420.3417
[13 empty] | P2 at this iteration flow rate |  |  | 91.5705 |  |  | 44.2859 |  |  | 144.7147 |  |  | 480.1217 |  |  | 1306.6267 |  |  | 2810.4251 |  |  | 4985.8332 |  |  | 7411.1724 |  |  | 9980.5639 |  |  | 12920.1083
[13 empty] | Delta P at this iteration flow rate |  |  | -369.2229 |  |  | -85.5154 |  |  | -688.0883 |  |  | -2700.5303 |  |  | -7659.5602 |  |  | -16682.3504 |  |  | -29734.7992 |  |  | -44286.8346 |  |  | -59703.1833 |  |  | -77340.45
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -245.7048 |  |  | -35.7333 |  |  | -452.3987 |  |  | -1766.8383 |  |  | -4763.7357 |  |  | -9669.3997 |  |  | -15883.5293 |  |  | -21443.6353 |  |  | -24923.9893 |  |  | -24277.819
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 3147.4713 |  | 5500 | 1704.7262 |  | 5500 | 4215.9907 |  | 5500 | 8211.6738 |  | 5500 | 13776.6341 |  | 5500 | 20308.4464 |  | 5500 | 27101.7005 |  | 5500 | 33069.225 |  | 5500 | 38392.3436 |  | 5500 | 43694.0683
[13 empty] | Next iteration flow rate |  |  | 3210.4208 | Abs Value of | Flow this | 1721.7734 | Abs Value of | Flow this | 4258.1506 | Abs Value of | Flow this | 8293.7905 | Abs Value of | Flow this | 13914.4005 | Abs Value of | Flow this | 20511.5309 | Abs Value of | Flow this | 27372.7175 | Abs Value of | Flow this | 33399.9173 | Abs Value of | Flow this | 38776.2671 | Abs Value of | Flow this | 44131.009 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -291.169 |  |  | -43.2022 |  |  | -555.4394 |  |  | -2266.1828 |  |  | -6481.7715 |  |  | -14151.8951 |  |  | -25247.5642 |  |  | -37618.007 |  |  | -50723.1881 |  |  | -65716.3346
[13 empty] | P2 at this iteration flow rate |  |  | 94.2738 |  |  | 44.6804 |  |  | 147.1279 |  |  | 489.2766 |  |  | 1332.3943 |  |  | 2866.419 |  |  | 5085.5528 |  |  | 7559.6414 |  |  | 10180.6776 |  |  | 13179.3069
[13 empty] | Delta P at this iteration flow rate |  |  | -385.4428 |  |  | -87.8826 |  |  | -702.5672 |  |  | -2755.4594 |  |  | -7814.1658 |  |  | -17018.3141 |  |  | -30333.1171 |  |  | -45177.6484 |  |  | -60903.8657 |  |  | -78895.6415
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -257.6471 |  |  | -37.425 |  |  | -462.4363 |  |  | -1803.2548 |  |  | -4860.338 |  |  | -9864.5459 |  |  | -16203.5168 |  |  | -21875.3124 |  |  | -25425.5305 |  |  | -24766.231
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 3210.4208 |  | 5500 | 1721.7734 |  | 5500 | 4258.1506 |  | 5500 | 8293.7905 |  | 5500 | 13914.4005 |  | 5500 | 20511.5309 |  | 5500 | 27372.7175 |  | 5500 | 33399.9173 |  | 5500 | 38776.2671 |  | 5500 | 44131.009
[13 empty] | Next iteration flow rate |  |  | 3274.6292 | Abs Value of | Flow this | 1738.9912 | Abs Value of | Flow this | 4300.7321 | Abs Value of | Flow this | 8376.7284 | Abs Value of | Flow this | 14053.5445 | Abs Value of | Flow this | 20716.6462 | Abs Value of | Flow this | 27646.4447 | Abs Value of | Flow this | 33733.9164 | Abs Value of | Flow this | 39164.0297 | Abs Value of | Flow this | 44572.3191 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -305.2317 |  |  | -45.2146 |  |  | -567.7477 |  |  | -2312.8771 |  |  | -6613.1991 |  |  | -14437.4922 |  |  | -25756.1843 |  |  | -38375.2729 |  |  | -51743.8682 |  |  | -67038.3769
[13 empty] | P2 at this iteration flow rate |  |  | 97.0863 |  |  | 45.0829 |  |  | 149.5895 |  |  | 498.6154 |  |  | 1358.6798 |  |  | 2923.5384 |  |  | 5187.2769 |  |  | 7711.0946 |  |  | 10384.8136 |  |  | 13443.7154
[13 empty] | Delta P at this iteration flow rate |  |  | -402.318 |  |  | -90.2975 |  |  | -717.3373 |  |  | -2811.4926 |  |  | -7971.8789 |  |  | -17361.0306 |  |  | -30943.4611 |  |  | -46086.3675 |  |  | -62128.6818 |  |  | -80482.0923
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -270.072 |  |  | -39.1507 |  |  | -472.6756 |  |  | -1840.4034 |  |  | -4958.8819 |  |  | -10063.6145 |  |  | -16529.936 |  |  | -22315.6663 |  |  | -25937.1527 |  |  | -25264.46
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 3274.6292 |  | 5500 | 1738.9912 |  | 5500 | 4300.7321 |  | 5500 | 8376.7284 |  | 5500 | 14053.5445 |  | 5500 | 20716.6462 |  | 5500 | 27646.4447 |  | 5500 | 33733.9164 |  | 5500 | 39164.0297 |  | 5500 | 44572.3191

## Installed Gain
BALL_SEG
3
PV123
Qmax = maximum
[8 empty] | design flow = | 550
Qmin = minimum
[8 empty] | design flow = | 80
[8 empty] | Flow units are | gpm
Installed gain is based on installed flow as graphed above.
1.0 on the relative flow axis represents the maximum specified
design flow, Qmax, for the system being evaluated.
This makes it possible to compare valves of different sizes
and types when they are installed in the same system.
Graph Data
Valve relative travel, h | 0 | 0.05 | 0.1 | 0.15 | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.55 | 0.6 | 0.65 | 0.7 | 0.75 | 0.8 | 0.85 | 0.9 | 0.95 | 1
Relative flow Q/Qmax | 0 | 0.024206 | 0.048413 | 0.084071 | 0.11973 | 0.17647 | 0.2332 | 0.31222 | 0.39124 | 0.48399 | 0.57674 | 0.6732 | 0.76966 | 0.8544 | 0.93913 | 1.0147 | 1.0903 | 1.1656 | 1.2409 | 1.299 | 1.3571 | 0.14545 | 0.14545 | 1 | 1
Gain = Delta Q / Delta h |  | 0.48413 | 0.59865 | 0.71317 | 0.92395 | 1.1347 | 1.3576 | 1.5804 | 1.7177 | 1.855 | 1.8921 | 1.9292 | 1.812 | 1.6947 | 1.6032 | 1.5117 | 1.5087 | 1.5056 | 1.3341 | 1.1625
Qmin vertical line | [21 empty] | 0 | 4
Qmax vertical line | [23 empty] | 0 | 4
Delta Q |  | 0.048413 | 0.059865 | 0.071317 | 0.092395 | 0.11347 | 0.13576 | 0.15804 | 0.17177 | 0.1855 | 0.18921 | 0.19292 | 0.1812 | 0.16947 | 0.16032 | 0.15117 | 0.15087 | 0.15056 | 0.13341 | 0.11625
Delta h |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
`
Qmax

## Typical FL, Fd, XfZ, AEta
Only the values in the Typical FL values table are available for the user to copy and transfer | [9 empty] | Intermediate calculations
to the Valve Sizing tab. The other tables for Fd, xFz and Aη are automatially transferred to the Valve Sizing
and no user action is required. | [8 empty] | DESCRIPTION OF VARIABLE | NAME OF VARIABLE | FORMULA
Typical FL values based on the Cv reported on the Valve Sizing tab | [5 empty] | For initial calculations (before |  |  | CALCULATED IN COLUMN "O" | CALCULATED IN COLUMN "O"
and the valve size entered on the Valve Sizing tab. | [5 empty] | the Cv is known), consider using |  |  | Valv size in inch | VS_INCH | 3
the FL values listed below.
| Flow | 80 | 213 | 423 | 550 | Minimum | Maximum
| Valve type | Liquid pressure recovery factor. FL |  |  |  | Flow | Flow | INSTRUCTIONS FOR FL CALCULATIONS
[8 empty] | Perform initial valve sizing useing the suggested FL values in Columns H & I. |  | VCAP_Cv_T | 14.1587 | 38.9735 | 88.5763 | 135.5671
| Globe, 4 port cage | 0.83983 | 0.84973 | 0.83114 | 0.8185 | 0.84 | 0.82 | Fine tune FL values on Valve sizing tab as follows:
[10 empty] | Cv_over_d_Sq_T | 1.5732 | 4.3304 | 9.8418 | 15.063
| Globe, Parabolic plug | 0.91014 | 0.87907 | 0.84833 | 0.82421 | 0.93 | 0.88 | 1. Copy FL values: Highlight all 4 columns in the row for the valve type | The value of "Cv_over_d_Sq_T" is calculated from the flow coef. on
[8 empty] | you are sizing. | the Valve Sizing tab converted to Cv if the worksheet has been configured
| Rotary eccentric plug | 0.90136 | 0.85373 | 0.7946 | 0.76 | 0.89 | 0.78 | 2. Press Ctrl + C | for Kv and Valve size on the Valve Sizing tab is converted to inch
[8 empty] | 3. Go to the Valve Sizing tab | if the worksheet has been configured for valve size in mm.
| Segment ball | 0.92317 | 0.89366 | 0.83469 | 0.77883 | 0.93 | 0.72 | 4. Right Click on D9.
5. From "Paste Options" Select "Values"
| Butterfly | 0.85651 | 0.82772 | 0.77063 | 0.71711 | 0.85 | 0.58
You may need to repeat Steps 1 through 5 one or two more times until
| Full ball | 0.89869 | 0.87666 | 0.83424 | 0.79594 | 0.91 | 0.67 | the FL values on this tab agree closely with what are on the Valve Sizing tab.
| Name of current Valve Cv Table | BALL_SEG
Typical Fd values based on the Relative Travel on the Valve Sizing tab.
| on the Valve Sizing tab. Fd is only used in the IEC noise calculation. | [8 empty] | Fd calculations
| This data is automaically copied to the Valve Sizing tab. | [8 empty] | Valve travel from Valve Travel tab | 22.2445 | 39.7399 | 60.1147 | 73.3107
| Valve type | Valve style modifier, Fd | [7 empty] | Relative travel | 0.22244 | 0.3974 | 0.60115 | 0.73311
| Globe, 4 port cage =% | 0.42853 | 0.33073 | 0.3128 | 0.33191
[11 empty] | Case 1 | Case 2 | Case 3 | Case 4
| Globe, 4 port cage Linear | 0.38256 | 0.34639 | 0.34584 | 0.3741
Globe, 4 port cage =%
| Globe, Parabolic plug =% | 0.067837 | 0.12869 | 0.24239 | 0.32787
[10 empty] | Relatve travel | 0.22244 | 0.3974 | 0.60115 | 0.73311
| Globe, Parabolic plug Linear | 0.17945 | 0.25626 | 0.3457 | 0.40363 |  |  |  |  | Fd_GCE | 0.42853 | 0.33073 | 0.3128 | 0.33191
| Rotary eccentric plug | 0.12256 | 0.12951 | 0.16352 | 0.18951 |  |  |  |  | Globe, 4 port cage Linear
| Segment ball | 0.77929 | 0.84725 | 0.91936 | 0.95531 |  |  |  |  | Relatve travel | 0.22244 | 0.3974 | 0.60115 | 0.73311
[10 empty] | Fd_GCL | 0.38256 | 0.34639 | 0.34584 | 0.3741
| Butterfly | 0.15426 | 0.20008 | 0.26411 | 0.29901
Globe Parabolic plug =%
| Full ball (Standard port) | 0.69965 | 0.85867 | 0.95091 | 0.98291
[10 empty] | Relatve travel | 0.22244 | 0.3974 | 0.60115 | 0.73311
| Full ball (Full port) | 0.69965 | 0.85867 | 0.95091 | 0.98291 |  |  |  |  | Fd_GPE | 0.067837 | 0.12869 | 0.24239 | 0.32787
Globe Parabolic plug LIN
| Values automatically copied to the | 0.77929 | 0.84725 | 0.91936 | 0.95531
| Vlalve Sizing tab | [8 empty] | Relatve travel | 0.22244 | 0.3974 | 0.60115 | 0.73311
[10 empty] | Fd_GPL | 0.17945 | 0.25626 | 0.3457 | 0.40363
| Typical xFz values based on the Cv reported on Line 19 of the Valve Sizing tab | [8 empty] | Rotary eccentric plug
and the valve size entered in D15 of the Valve Sizing tab.
| This data is automaically copied to the Valve Sizing tab. | [8 empty] | Relatve travel
|  | Differential pressure ratio of incipient | [7 empty] | Relatve travel | 0.22244 | 0.3974 | 0.60115 | 0.73311
| Valve type | cavitation, xFz | [7 empty] | Fd_RP | 0.12256 | 0.12951 | 0.16352 | 0.18951
| Globe, 4 port cage | 0.32213 | 0.22698 | 0.21782 | 0.20606 |  |  |  |  | Segment ball
| Globe, Parabolic plug | 0.65 | 0.62791 | 0.55265 | 0.45841 |  |  |  |  | Relatve travel | 0.22244 | 0.3974 | 0.60115 | 0.73311
[10 empty] | Fd_SEG | 0.77929 | 0.84725 | 0.91936 | 0.95531
| Rotary eccentric plug | 0.47991 | 0.37994 | 0.33972 | 0.24
Butterfly
| Segment ball | 0.42716 | 0.38738 | 0.32461 | 0.28157
[10 empty] | Relatve travel | 0.22244 | 0.3974 | 0.60115 | 0.73311
| Butterfly | 0.36511 | 0.31158 | 0.25683 | 0.23212 |  |  |  |  | Fd_BF | 0.15426 | 0.20008 | 0.26411 | 0.29901
| Full ball | 0.50443 | 0.43866 | 0.33451 | 0.26445 |  |  |  |  | Full ball reduced Port
[10 empty] | Relatve travel | 0.22244 | 0.3974 | 0.60115 | 0.73311
| Values automatically copied to the | 0.42716 | 0.38738 | 0.32461 | 0.28157 |  |  |  |  | Fd_FB | 0.69965 | 0.85867 | 0.95091 | 0.98291
Vlalve Sizing tab
Full ball full Port
[10 empty] | Relatve travel | 0.22244 | 0.3974 | 0.60115 | 0.73311
| Typical values of Valve correction factor for acoustic efficiency, Aη | [8 empty] | Fd_FB_FP | 0.69965 | 0.85867 | 0.95091 | 0.98291
This data is automaically copied to the Valve Sizing tab.
Aη
| Globe | -4.6
| Eccendtric rotary plug | -4.6
| Ball, Segment ball | -4.6
| Butterfly | -4.3
| Values automatically copied to the | -4.6
Vlalve Sizing tab

## Mass to Volumetric Flow
This tab calculates Volumetric Flow for use on the Valve Sizing tab from the Mass flow entered in the blue fields on this tab and the specific gravity entered on the Valve Sizing tab.
Intermediate Calculations
Conversion from Pounds per hour to Gallons per minute (gpm) |  |  | Case 1 | Case 2 | Case 3 | Case 4
Density based on Specific Gravity on the Valve Sizing Tab
| Pounds per hour (lbm/h) | lb_h | 40015 | 106540 | 211575 | 275099 | lbm/ft3 | RHO_lb | 62.3693 | 62.3693 | 62.3693 | 62.3693
| Gallons per minutte (gpm) |  | 80.0052 | 213.0141 | 423.0191 | 550.0277 | kg/m3 | RHO_kg | 999.06 | 999.06 | 999.06 | 999.06
Conversion from Kilograms per hour to cubic meters per hour (m3/h)
| Kilograms per hour (kg/h) | kg_h | 18152 | 48329 | 95977 | 124793
| Cubic meters per hour (m3/h) |  | 18.1691 | 48.3745 | 96.0673 | 124.9104
Data input
Final results

## SPL Conv
Hydrodynamic Noise - IEC 60534-8-4: 2015 | [6 empty] | Scroll to the right to view the conversion from user interface units to units required by the IEC Standard. | Conversion from user interface units to
Volumetric Flow | [7 empty] | Units required by the IEC Standard.
Process Parameters |  |  | Case 1 | Case 2 | Case 3 | Case 4 |  | (kg/s, Pa, kg/m3, m/s, m) | Units | Name | Case 1 | Case 2 | Case 3 | Case 4
Volumetric flow | gpm | Q_..1 | 80 | 213 | 423 | 550 |  | Flow | kg/s | m_dot..S | 5.0427 | 13.4261 | 26.6631 | 34.6683
Inlet pressure (absolute) | psiA | P_1..1 | 56.7 | 55.4 | 50.7 | 46.7 |  | Inlet pressure | Pa | P_1..S | 390932.7389 | 381969.5544 | 349564.1951 | 321985.1659
Pressure drop | psi | DELTA_P..1 | 32 | 30.4 | 24.9 | 20 | No user input is required for the tab. | Pressure drop | Pa | DELTA_P..S | 220632.2336 | 209600.6219 | 171679.4568 | 137895.146
Specific gravity (r1/r0) |  | G..1 | 1 | 1 | 1 | 1 |  | Density of liquid | kg/m3 | RHO_1..S | 999.1 | 999.1 | 999.1 | 999.1
Vapor pressure (absolute) | psiA | P_V..1 | 0.46 | 0.46 | 0.46 | 0.46 | Data at the left is imported fromt the | Vapor Pressure | Pa | P_V..S | 3171.5884 | 3171.5884 | 3171.5884 | 3171.5884
Speed of sound in liquid | ft/s | c_1..1 | 4000 | =========> | =========> | =========> | Valve Sizing tab. | Speed of sound in liquid | m/s | c_1..S | 1219.2 | 1219.2 | 1219.2 | 1219.2
Pipe/Valve Parameters
Flow coefficient (Kv or Cv) | Cv | C_..1 | 14.1587 | 38.9735 | 88.5763 | 135.5671 |  | Flow coefficient (Kv or Cv) | Cv | C_..S | 14.1587 | 38.9735 | 88.5763 | 135.5671
Liquid pressure recovery factor |  | F_L..1 | 0.93 | 0.9 | 0.8 | 0.72 |  | Liquid pressure recovery factor |  | F_L..S | 0.93 | 0.9 | 0.8 | 0.72
Valve style modifier |  | F_D..1 | 0.77929 | 0.84725 | 0.91936 | 0.95531 |  | Valve style modifier |  | F_D..S | 0.77929 | 0.84725 | 0.91936 | 0.95531
Differential pressure ratio of incipient cavitation |  | x_Fz..1 | 0.42716 | 0.38738 | 0.32461 | 0.28157 |  | Differential pressure ratio of incipient cavitation |  | x_Fz..S | 0.42716 | 0.38738 | 0.32461 | 0.28157
Valve correction - accoustic efficiency, Ah |  | A_ETA..1 | -4.6 | =========> | =========> | =========> |  | Valve correction - accoustic efficiency, Ah |  | A_ETA..S | -4.6 | -4.6 | -4.6 | -4.6
Valve Size | inch | D_..1 | 3 | =========> | =========> | =========> |  | Valve size | m | D_..S | 0.0762 | 0.0762 | 0.0762 | 0.0762
Seat or Orifice Diameter | inch | d_o..1 | 3 | =========> | =========> | =========> |  | Seat or orifice diameter | m | d_o..S | 0.0762 | 0.0762 | 0.0762 | 0.0762
Outlet pipe internal diameter | inch | D_i..1 | 6 | =========> | =========> | =========> |  | Outlet pipe internal diameter | m | D_i..S | 0.1524 | 0.1524 | 0.1524 | 0.1524
Outlet pipe wall thickness | inch | t_s..1 | 0.23 | =========> | =========> | =========> |  | Outlet pipe wall thickness | m | T_S..S | 0.005842 | 0.005842 | 0.005842 | 0.005842
[8 empty] | Speed of sound in pipe | m/s | C_S..S | 5000 | 5000 | 5000 | 5000
[8 empty] | Density of pipe material | kg/m3 | RHO_S..S | 7800 | 7800 | 7800 | 7800
Auto filled based on Flag #
Unit Selection for user interface | Flag # | Flag Value | Options
Volumetric flow | IEC_1 | 3 | 1 = m3/s 2 = m3/h, 3 = gpm
Pressure (absolute) | IEC_2 | 4 | 1 = Pa, 2 = kPa, 3 = bar, 4 = psiA
Density | IEC_4 | 2 | 1 = kg/m3, 2 = lbm/ft3
Length | IEC_5 | 3 | 1 = m, 2 = mm, 3 = in
Flow coefficient | IEC_6 | 1 | 1 = Cv, 2 = Kv
Velocity | IEC_7 | 2 | 1 = m/s, 2 = ft/s
Numerical Constants (Auto filled in based on Flag IEC_6)
N_14 | N_14 | 0.0046
N_34 | N_34 | 1.17

## SPL CALCS
No user input is required for this tab.
Calculations based on IEC 60534-8-4: 2015
Lines 6 through 25, Columns D through G are automatically flled trom Columns S through V of the SPL Conv tab | [13 empty] | Table 3 – Indexed third octave center frequencies and “A” weighting factors
[7 empty] | DESCRIPTION OF VARIABLE |  | NAME OF VARIABLE
Process and valve parameters | Units | Name | Case 1 | Case 2 | Case 3 | Case 4 | CALCULATED IN COLUMN "K" | Eqn. # | CALCULATED IN COLUMN "K" | Case 1 | Case 2 | Case 3 | Case 4 | Index, i | Third octave center freq. | “A” weighting factor
Mass Flow Rate | kg/s | m_dot..D | 5.0427 | 13.4261 | 26.6631 | 34.6683 | [8 empty] | f_i (Hz) | ΔLA(fi)
Inlet pressure | Pa | P_1..D | 390932.7389 | 381969.5544 | 349564.1951 | 321985.1659 | [8 empty] | (Hz) | (dB)
Pressure drop | Pa | DELTA_P..D | 220632.2336 | 209600.6219 | 171679.4568 | 137895.146 | Differential Pressure Ratio x_F | 1 | x_F..K | 0.56899 | 0.55333 | 0.49562 | 0.43253 | 1 | 12.5 | -63.4
Outlet pressure | Pa | P_2..D | 170300.5053 | 172368.9325 | 177884.7383 | 184090.0199 | Differential Pressure for Beginning Choked Flow | 2 | Δp_c..K | 220632.2336 | 209600.6219 | 171679.4568 | 137895.146 | 2 | 16 | -56.7
Density of liquid | kg/m^3 | RHO_1..D | 999.1 | 999.1 | 999.1 | 999.1 | Characteristic Pressure Ratio for ALL valves Except multihole trims | 3 | x_F_z..K | 0.42716 | 0.38738 | 0.32461 | 0.28157 | 3 | 20 | -50.5
Vapor pressure | Pa | P_V..D | 3171.5884 | 3171.5884 | 3171.5884 | 3171.5884 | Characteristic Pressure Ratio for Multihole trims (Reserved for future use) | 4 | x_F_z_multi..K |  |  |  |  | 4 | 25 | -44.7
speed of Sound in Liquid | m/s | c_1..D | 1219.2 | 1219.2 | 1219.2 | 1219.2 | Differential Pressure Ratio corrected for inlet pressure - using (3) for x_F_z | 5 | x_F_zp1..K | 0.45066 | 0.40987 | 0.34728 | 0.30435 | 5 | 31.5 | -39.4
[7 empty] | Jet Diameter | 6 | D_j..K | 0.013008 | 0.023082 | 0.0356 | 0.043416 | 6 | 40 | -34.6
[7 empty] | Jet Velocity | 7 | U_vc..K | 22.5976 | 22.7596 | 23.1729 | 23.0756 | 7 | 50 | -30.2
Valve Flow Coefficient |  | C_..D | 14.1587 | 38.9735 | 88.5763 | 135.5671 | Mechanical Power | 8 | W_m..K | 1113.575 | 2816.6488 | 4581.6217 | 4784.8926 | 8 | 63 | -26.2
Liquid pressure recovery factor |  | F_L..D | 0.93 | 0.9 | 0.8 | 0.72 | Flow Conditions |  | Condition..K | Cavitating | Cavitating | Cavitating | Cavitating | 9 | 80 | -22.5
Valve Style Modifier |  | F_d..D | 0.77929 | 0.84725 | 0.91936 | 0.95531 | Acoustic Efficiency Factor (turbulent) | 11 | ETA_turb..K | 4.6557e-07 | 4.6891e-07 | 4.7742e-07 | 4.7542e-07 | 10 | 100 | -19.1
Differential pressure ratio of incipient cavitation |  | x_Fz..D | 0.42716 | 0.38738 | 0.32461 | 0.28157 | Acoustic Efficiency Factor (cavitating) | 12 | ETA_cav..K | 3.1146e-07 | 5.0953e-07 | 5.6626e-07 | 3.7197e-07 | 11 | 125 | -16.1
Valve correction factor for acoustic efficiency, Ah | no dim | A_ETA..D | -4.6 | -4.6 | -4.6 | -4.6 | Internal Sound Pressure Calculation for Turbulent conditions | 9 | W_a_turb..K | N/A Cav | N/A Cav | N/A Cav | N/A Cav | 12 | 160 | -13.4
Nominal Valve size | m | D_..D | 0.0762 | 0.0762 | 0.0762 | 0.0762 | Internal Sound Pressure Calculation for Cavitating conditions | 10 | W_a_cav..K | 0.00086528 | 0.0027559 | 0.0047818 | 0.0040547 | 13 | 200 | -10.9
Seat or Orifice Diameter | m | d_o..D | 0.0762 | 0.0762 | 0.0762 | 0.0762 | Internal Sound Pressure Level at pipe wall | 13 | L_pi..K | 141.6202 | 146.6513 | 149.0445 | 148.3282 | 14 | 250 | -8.6
Internal Pipe Diameter | m | D_i..D | 0.1524 | 0.1524 | 0.1524 | 0.1524 | Strouhal number of jet | 19 | St_p..K | 0.11607 | 0.37222 | 0.95882 | 1.5633 | 15 | 315 | -6.6
Pipe wall thickness | m | t_s..D | 0.005842 | 0.005842 | 0.005842 | 0.005842 | Peak sound frequency (Turbulent) | 18 | f_p_turb..K | 201.6358 | 367.0203 | 624.1241 | 830.9144 | 16 | 400 | -4.8
Speed of Sound in Pipe | m/s | C_s..D | 5000 | 5000 | 5000 | 5000 | Peak sound frequency (Cavitating) | 20 | f_p_cav..K | 415.7891 | 595.7857 | 919.0175 | 1377.9734 | 17 | 500 | -3.2
Density of pipe material | kg/m^3 | RHO_s..D | 7800 | 7800 | 7800 | 7800 | Ring frequency | 21 | f_r..K | 10443.2377 | 10443.2377 | 10443.2377 | 10443.2377 | 18 | 630 | -1.9
[7 empty] | Transmission loss at ring frequency | 22 | TL_fr..K | -45.2775 | -45.2775 | -45.2775 | -45.2775 | 19 | 800 | -0.8
Constant values from the Standard | [13 empty] | 20 | 1000 | 0
Speed of sound in air at standard conditions | m/s | c_a..D | 343 | 343 | 343 | 343 | Frequency distribution function (Turbulent) | 16 | F_turb(f_i) |  |  |  |  | 21 | 1250 | 0.6
Density of air | kg/m^3 | RHO_a..D | 1.293 | 1.293 | 1.293 | 1.293 |  |  | 1 | -20.0766 | -22.6778 | -24.9836 | -26.2265 | 22 | 1600 | 1
[9 empty] | 2 | -19.0045 | -21.6057 | -23.9115 | -25.1544 | 23 | 2000 | 1.2
Canculation of valve outlet velocity | [8 empty] | 3 | -18.0355 | -20.6366 | -22.9424 | -24.1853 | 24 | 2500 | 1.3
Vavle outlet velocity | m/s | U_valve | 1.1068 | 2.9469 | 5.8523 | 7.6094 |  |  | 4 | -17.0665 | -19.6675 | -21.9733 | -23.2162 | 25 | 3150 | 1.2
[9 empty] | 5 | -16.0632 | -18.6639 | -20.9696 | -22.2125 | 26 | 4000 | 1
[9 empty] | 6 | -15.0268 | -17.6265 | -19.9321 | -21.175 | 27 | 5000 | 0.5
|  |  | 64.5875 | 72.8683 | 77.812 | 78.2066 |  |  | 7 | -14.0601 | -16.6576 | -18.9631 | -20.2059 | 28 | 6300 | -0.1
[9 empty] | 8 | -13.0626 | -15.6544 | -17.9594 | -19.2022 | 29 | 8000 | -1.1
[9 empty] | 9 | -12.0416 | -14.6185 | -16.9221 | -18.1648 | 30 | 10000 | -2.5
[9 empty] | 10 | -11.1109 | -13.6529 | -15.9534 | -17.1958 | 31 | 12500 | -4.3
[9 empty] | 11 | -10.234 | -12.6924 | -14.9854 | -16.227 | 32 | 16000 | -6.6
[9 empty] | 12 | -9.4149 | -11.6447 | -13.9162 | -15.1559 | 33 | 20000 | -9.3
[9 empty] | 13 | -8.9765 | -10.7313 | -12.9538 | -14.1889
[9 empty] | 14 | -9.0824 | -9.8952 | -12.0012 | -13.2251
[9 empty] | 15 | -10.0229 | -9.2162 | -11.0395 | -12.2348
[9 empty] | 16 | -11.9019 | -8.9384 | -10.1115 | -11.2329
[9 empty] | 17 | -14.2482 | -9.3549 | -9.3887 | -10.3459
[9 empty] | 18 | -17.0012 | -10.6647 | -8.9615 | -9.5469
[9 empty] | 19 | -20.0046 | -12.8399 | -9.1616 | -9.0098
[9 empty] | 20 | -22.871 | -15.343 | -10.1813 | -9.0267
[9 empty] | 21 | -25.7614 | -18.0732 | -11.9928 | -9.8066
[9 empty] | 22 | -28.9704 | -21.2101 | -14.6295 | -11.6254
[9 empty] | 23 | -31.8751 | -24.0893 | -17.3139 | -13.9126
[9 empty] | 24 | -34.7813 | -26.985 | -20.1264 | -16.5379
[9 empty] | 25 | -37.792 | -29.9912 | -23.0973 | -19.4253
[9 empty] | 26 | -40.9043 | -33.1017 | -26.1934 | -22.4867
[9 empty] | 27 | -43.8115 | -36.0083 | -29.0946 | -25.375
[9 empty] | 28 | -46.8226 | -39.0191 | -32.1032 | -28.3782
[9 empty] | 29 | -49.9351 | -42.1315 | -35.2146 | -31.4874
[9 empty] | 30 | -52.8424 | -45.0387 | -38.1215 | -34.3935
[9 empty] | 31 | -55.7497 | -47.946 | -41.0287 | -37.3004
[9 empty] | 32 | -58.966 | -51.1623 | -44.2449 | -40.5164
[9 empty] | 33 | -61.8733 | -54.0696 | -47.1522 | -43.4237
[7 empty] | Frequency distribution function (Cavitating) | 17 | F_cav(f_i)
[9 empty] | 1 | -31.8295 | -34.1727 | -36.9962 | -39.635
[9 empty] | 2 | -30.2214 | -32.5646 | -35.3881 | -38.0268
[9 empty] | 3 | -28.7678 | -31.1109 | -33.9344 | -36.5732
[9 empty] | 4 | -27.3142 | -29.6573 | -32.4808 | -35.1195
[9 empty] | 5 | -25.8089 | -28.1519 | -30.9752 | -33.614
[9 empty] | 6 | -24.2532 | -26.5958 | -29.419 | -32.0577
[9 empty] | 7 | -22.8004 | -25.1424 | -27.9655 | -30.6041
[9 empty] | 8 | -21.2968 | -23.6375 | -26.4601 | -29.0986
[9 empty] | 9 | -19.7445 | -22.0826 | -24.9042 | -27.5425
[9 empty] | 10 | -18.2982 | -20.6315 | -23.4513 | -26.089
[9 empty] | 11 | -16.8588 | -19.1827 | -21.9989 | -24.6358
[9 empty] | 12 | -15.2827 | -17.5855 | -20.3938 | -23.0285
[9 empty] | 13 | -13.8868 | -16.1518 | -18.9456 | -21.5765
[9 empty] | 14 | -12.5438 | -14.7367 | -17.5026 | -20.126
[9 empty] | 15 | -11.2566 | -13.3093 | -16.0187 | -18.6269
[9 empty] | 16 | -10.125 | -11.9122 | -14.5076 | -17.0842
[9 empty] | 17 | -9.3663 | -10.7403 | -13.1367 | -15.6556
[9 empty] | 18 | -9.0106 | -9.7609 | -11.7961 | -14.201
[9 empty] | 19 | -9.1783 | -9.1354 | -10.5664 | -12.7497
[9 empty] | 20 | -9.7939 | -9.0152 | -9.6624 | -11.4849
[9 empty] | 21 | -10.7464 | -9.3695 | -9.1156 | -10.3781
[9 empty] | 22 | -12.0527 | -10.2302 | -9.0415 | -9.4612
[9 empty] | 23 | -13.3651 | -11.305 | -9.4692 | -9.0391
[9 empty] | 24 | -14.7446 | -12.5511 | -10.2858 | -9.0866
[9 empty] | 25 | -16.2107 | -13.9437 | -11.4155 | -9.6198
[9 empty] | 26 | -17.7467 | -15.441 | -12.7662 | -10.5795
[9 empty] | 27 | -19.1908 | -16.8669 | -14.1206 | -11.7245
[9 empty] | 28 | -20.6914 | -18.3578 | -15.5732 | -13.059
[9 empty] | 29 | -22.2451 | -19.9066 | -17.1021 | -14.525
[9 empty] | 30 | -23.6976 | -21.3567 | -18.543 | -15.936
[9 empty] | 31 | -25.1506 | -22.8086 | -19.9901 | -17.3676
[9 empty] | 32 | -26.7584 | -24.4157 | -21.5946 | -18.9637
[9 empty] | 33 | -28.2119 | -25.869 | -23.0467 | -20.4119
[7 empty] | Internal sound pressure level at each third octave frequency | 14 & 15 | L_pi(f_i)
[7 empty] | Equation 14 is selected under turbulent conditions and Equation 15 |  | 1 | 119.509 | 121.1013 | 120.9768 | 119.744
[7 empty] | is selected under cavitating flow conditions. |  | 2 | 120.6054 | 122.214 | 122.0884 | 120.8357
[9 empty] | 3 | 121.599 | 123.224 | 123.0972 | 121.8247
[9 empty] | 4 | 122.5953 | 124.2383 | 124.1103 | 122.8158
[9 empty] | 5 | 123.6301 | 125.2939 | 125.1644 | 123.845
[9 empty] | 6 | 124.703 | 126.3909 | 126.2599 | 124.912
[9 empty] | 7 | 125.7075 | 127.4214 | 127.2889 | 125.9117
[9 empty] | 8 | 126.7488 | 128.495 | 128.3611 | 126.9507
[9 empty] | 9 | 127.8211 | 129.6115 | 129.4767 | 128.0288
[9 empty] | 10 | 128.8073 | 130.66 | 130.526 | 129.04
[9 empty] | 11 | 129.7517 | 131.712 | 131.5824 | 130.0555
[9 empty] | 12 | 130.6746 | 132.873 | 132.7591 | 131.1842
[9 empty] | 13 | 131.2684 | 133.9046 | 133.8284 | 132.2089
[9 empty] | 14 | 131.4577 | 134.8855 | 134.8988 | 133.2366
[9 empty] | 15 | 131.144 | 135.774 | 135.9973 | 134.3005
[9 empty] | 16 | 130.5196 | 136.4159 | 137.0928 | 135.3893
[9 empty] | 17 | 130.003 | 136.6301 | 138.0212 | 136.3726
[9 empty] | 18 | 129.5645 | 136.4807 | 138.7749 | 137.3022
[9 empty] | 19 | 128.9776 | 136.1192 | 139.1774 | 138.0492
[9 empty] | 20 | 128.1644 | 135.646 | 139.1524 | 138.3878
[9 empty] | 21 | 127.1034 | 134.956 | 138.8409 | 138.2799
[9 empty] | 22 | 125.7272 | 133.8953 | 138.2566 | 137.7869
[9 empty] | 23 | 124.3753 | 132.7182 | 137.4831 | 137.2244
[9 empty] | 24 | 122.9692 | 131.4082 | 136.4674 | 136.5644
[9 empty] | 25 | 121.484 | 129.9722 | 135.2152 | 135.6775
[9 empty] | 26 | 119.9345 | 128.4447 | 133.786 | 134.5168
[9 empty] | 27 | 118.4814 | 126.9992 | 132.3833 | 133.261
[9 empty] | 28 | 116.9743 | 125.4941 | 130.8964 | 131.8536
[9 empty] | 29 | 115.4158 | 123.935 | 129.343 | 130.3377
[9 empty] | 30 | 113.9602 | 122.4781 | 127.8861 | 128.8949
[9 empty] | 31 | 112.5049 | 121.0213 | 126.4276 | 127.4408
[9 empty] | 32 | 110.8954 | 119.4104 | 124.8142 | 125.8274
[9 empty] | 33 | 109.4408 | 117.9548 | 123.3565 | 124.3682
[7 empty] | Change in Transmission loss at given frequencies f_i | 24 | ΔTL(f_i)
[9 empty] | 1 | -58.4385 | -58.4385 | -58.4385 | -58.4385
[9 empty] | 2 | -56.2943 | -56.2943 | -56.2943 | -56.2943
[9 empty] | 3 | -54.3561 | -54.3561 | -54.3561 | -54.3561
[9 empty] | 4 | -52.4179 | -52.4179 | -52.4179 | -52.4179
[9 empty] | 5 | -50.4105 | -50.4105 | -50.4105 | -50.4105
[9 empty] | 6 | -48.3355 | -48.3355 | -48.3355 | -48.3355
[9 empty] | 7 | -46.3973 | -46.3973 | -46.3973 | -46.3973
[9 empty] | 8 | -44.3899 | -44.3899 | -44.3899 | -44.3899
[9 empty] | 9 | -42.3149 | -42.3149 | -42.3149 | -42.3149
[9 empty] | 10 | -40.3768 | -40.3768 | -40.3768 | -40.3768
[9 empty] | 11 | -38.4386 | -38.4386 | -38.4386 | -38.4386
[9 empty] | 12 | -36.2946 | -36.2946 | -36.2946 | -36.2946
[9 empty] | 13 | -34.3565 | -34.3565 | -34.3565 | -34.3565
[9 empty] | 14 | -32.4187 | -32.4187 | -32.4187 | -32.4187
[9 empty] | 15 | -30.4119 | -30.4119 | -30.4119 | -30.4119
[9 empty] | 16 | -28.338 | -28.338 | -28.338 | -28.338
[9 empty] | 17 | -26.4017 | -26.4017 | -26.4017 | -26.4017
[9 empty] | 18 | -24.3977 | -24.3977 | -24.3977 | -24.3977
[9 empty] | 19 | -22.329 | -22.329 | -22.329 | -22.329
[9 empty] | 20 | -20.4013 | -20.4013 | -20.4013 | -20.4013
[9 empty] | 21 | -18.4814 | -18.4814 | -18.4814 | -18.4814
[9 empty] | 22 | -16.3737 | -16.3737 | -16.3737 | -16.3737
[9 empty] | 23 | -14.4944 | -14.4944 | -14.4944 | -14.4944
[9 empty] | 24 | -12.6581 | -12.6581 | -12.6581 | -12.6581
[9 empty] | 25 | -10.834 | -10.834 | -10.834 | -10.834
[9 empty] | 26 | -9.0904 | -9.0904 | -9.0904 | -9.0904
[9 empty] | 27 | -7.6761 | -7.6761 | -7.6761 | -7.6761
[9 empty] | 28 | -6.5521 | -6.5521 | -6.5521 | -6.5521
[9 empty] | 29 | -5.9152 | -5.9152 | -5.9152 | -5.9152
[9 empty] | 30 | -5.9392 | -5.9392 | -5.9392 | -5.9392
[9 empty] | 31 | -6.6285 | -6.6285 | -6.6285 | -6.6285
[9 empty] | 32 | -8.1277 | -8.1277 | -8.1277 | -8.1277
[9 empty] | 33 | -10.0279 | -10.0279 | -10.0279 | -10.0279
[7 empty] | Transmission loss at given frequencies f_i | 23 | TL(f_i)
[9 empty] | 1 | -103.716 | -103.716 | -103.716 | -103.716
[9 empty] | 2 | -101.5718 | -101.5718 | -101.5718 | -101.5718
[9 empty] | 3 | -99.6336 | -99.6336 | -99.6336 | -99.6336
[9 empty] | 4 | -97.6954 | -97.6954 | -97.6954 | -97.6954
[9 empty] | 5 | -95.688 | -95.688 | -95.688 | -95.688
[9 empty] | 6 | -93.613 | -93.613 | -93.613 | -93.613
[9 empty] | 7 | -91.6748 | -91.6748 | -91.6748 | -91.6748
[9 empty] | 8 | -89.6674 | -89.6674 | -89.6674 | -89.6674
[9 empty] | 9 | -87.5924 | -87.5924 | -87.5924 | -87.5924
[9 empty] | 10 | -85.6543 | -85.6543 | -85.6543 | -85.6543
[9 empty] | 11 | -83.7161 | -83.7161 | -83.7161 | -83.7161
[9 empty] | 12 | -81.572 | -81.572 | -81.572 | -81.572
[9 empty] | 13 | -79.634 | -79.634 | -79.634 | -79.634
[9 empty] | 14 | -77.6962 | -77.6962 | -77.6962 | -77.6962
[9 empty] | 15 | -75.6894 | -75.6894 | -75.6894 | -75.6894
[9 empty] | 16 | -73.6155 | -73.6155 | -73.6155 | -73.6155
[9 empty] | 17 | -71.6791 | -71.6791 | -71.6791 | -71.6791
[9 empty] | 18 | -69.6751 | -69.6751 | -69.6751 | -69.6751
[9 empty] | 19 | -67.6065 | -67.6065 | -67.6065 | -67.6065
[9 empty] | 20 | -65.6788 | -65.6788 | -65.6788 | -65.6788
[9 empty] | 21 | -63.7589 | -63.7589 | -63.7589 | -63.7589
[9 empty] | 22 | -61.6512 | -61.6512 | -61.6512 | -61.6512
[9 empty] | 23 | -59.7719 | -59.7719 | -59.7719 | -59.7719
[9 empty] | 24 | -57.9356 | -57.9356 | -57.9356 | -57.9356
[9 empty] | 25 | -56.1115 | -56.1115 | -56.1115 | -56.1115
[9 empty] | 26 | -54.3679 | -54.3679 | -54.3679 | -54.3679
[9 empty] | 27 | -52.9536 | -52.9536 | -52.9536 | -52.9536
[9 empty] | 28 | -51.8296 | -51.8296 | -51.8296 | -51.8296
[9 empty] | 29 | -51.1927 | -51.1927 | -51.1927 | -51.1927
[9 empty] | 30 | -51.2167 | -51.2167 | -51.2167 | -51.2167
[9 empty] | 31 | -51.9059 | -51.9059 | -51.9059 | -51.9059
[9 empty] | 32 | -53.4052 | -53.4052 | -53.4052 | -53.4052
[9 empty] | 33 | -55.3054 | -55.3054 | -55.3054 | -55.3054
[7 empty] | External sound pressure level spectrum at 1m from pipe wall | 25 | L_pe,1m(f_i)
[9 empty] | 1 | 4.5909 | 6.1832 | 6.0587 | 4.8259
[9 empty] | 2 | 7.8315 | 9.4401 | 9.3145 | 8.0618
[9 empty] | 3 | 10.7633 | 12.3883 | 12.2615 | 10.989
[9 empty] | 4 | 13.6978 | 15.3409 | 15.2128 | 13.9184
[9 empty] | 5 | 16.74 | 18.4039 | 18.2744 | 16.955
[9 empty] | 6 | 19.8879 | 21.5759 | 21.4448 | 20.0969
[9 empty] | 7 | 22.8307 | 24.5446 | 24.412 | 23.0348
[9 empty] | 8 | 25.8794 | 27.6255 | 27.4916 | 26.0812
[9 empty] | 9 | 29.0266 | 30.817 | 30.6822 | 29.2343
[9 empty] | 10 | 31.951 | 33.8037 | 33.6696 | 32.1837
[9 empty] | 11 | 34.8335 | 36.7938 | 36.6642 | 35.1373
[9 empty] | 12 | 37.9005 | 40.0989 | 39.985 | 38.4101
[9 empty] | 13 | 40.4323 | 43.0685 | 42.9923 | 41.3728
[9 empty] | 14 | 42.5595 | 45.9873 | 46.0006 | 44.3383
[9 empty] | 15 | 44.2526 | 48.8825 | 49.1059 | 47.4091
[9 empty] | 16 | 45.7021 | 51.5984 | 52.2753 | 50.5717
[9 empty] | 17 | 47.1217 | 53.7489 | 55.14 | 53.4914
[9 empty] | 18 | 48.6873 | 55.6034 | 57.8977 | 56.425
[9 empty] | 19 | 50.1691 | 57.3106 | 60.3688 | 59.2406
[9 empty] | 20 | 51.2835 | 58.7651 | 62.2715 | 61.5069
[9 empty] | 21 | 52.1424 | 59.995 | 63.8799 | 63.3189
[9 empty] | 22 | 52.8739 | 61.042 | 65.4033 | 64.9336
[9 empty] | 23 | 53.4013 | 61.7443 | 66.5091 | 66.2504
[9 empty] | 24 | 53.8315 | 62.2706 | 67.3297 | 67.4267
[9 empty] | 25 | 54.1704 | 62.6586 | 67.9017 | 68.3639
[9 empty] | 26 | 54.3645 | 62.8747 | 68.2161 | 68.9469
[9 empty] | 27 | 54.3257 | 62.8436 | 68.2277 | 69.1054
[9 empty] | 28 | 53.9426 | 62.4624 | 67.8647 | 68.8219
[9 empty] | 29 | 53.021 | 61.5402 | 66.9483 | 67.943
[9 empty] | 30 | 51.5415 | 60.0593 | 65.4674 | 66.4762
[9 empty] | 31 | 49.3969 | 57.9133 | 63.3196 | 64.3328
[9 empty] | 32 | 46.2881 | 54.8031 | 60.2069 | 61.2202
[9 empty] | 33 | 42.9333 | 51.4473 | 56.8491 | 57.8607
[7 empty] | Final overall sound pressure level | 26 | L_pAe,1m
[7 empty] | Summation of L_pe,1m(f_i) and DLA(fi),1m(f_i) and DLA(fi) |  | 1 | 1.3155e-06 | 1.8981e-06 | 1.8445e-06 | 1.3886e-06
[9 empty] | 2 | 1.2976e-05 | 1.8794e-05 | 1.8258e-05 | 1.3683e-05
[7 empty] | Equation (26) has been divided into two parts. |  | 3 | 0.00010625 | 0.00015447 | 0.00015002 | 0.00011192
[7 empty] | This section calculates the portion shown in the red box below. |  | 4 | 0.00079393 | 0.001159 | 0.0011253 | 0.00083529
[7 empty] | In the section below the quantities in this section are added |  | 5 | 0.0054201 | 0.0079504 | 0.0077168 | 0.005695
[7 empty] | logarithmically and converted to dB(A) |  | 6 | 0.03379 | 0.049841 | 0.048359 | 0.035456
[9 empty] | 7 | 0.18326 | 0.27193 | 0.26376 | 0.19208
[9 empty] | 8 | 0.92883 | 1.3885 | 1.3464 | 0.97302
[9 empty] | 9 | 4.4943 | 6.7873 | 6.5799 | 4.7144
[9 empty] | 10 | 19.2796 | 29.5372 | 28.6393 | 20.3408
[9 empty] | 11 | 74.7051 | 117.3224 | 113.8728 | 80.1187
[9 empty] | 12 | 281.8719 | 467.6144 | 455.5116 | 316.9618
[9 empty] | 13 | 897.8985 | 1647.5961 | 1618.9486 | 1115.0022
[9 empty] | 14 | 2488.5631 | 5479.3703 | 5496.1616 | 3748.3056
[9 empty] | 15 | 5824.4533 | 16914.3295 | 17806.9138 | 12047.8753
[9 empty] | 16 | 12308.5867 | 47845.042 | 55914.8622 | 37772.0627
[9 empty] | 17 | 24670.3282 | 113471.4276 | 156315.3704 | 106940.0452
[9 empty] | 18 | 47722.7789 | 234608.5444 | 397893.9002 | 283462.4271
[9 empty] | 19 | 86478.0291 | 447775.0524 | 905487.6859 | 698330.3787
[9 empty] | 20 | 134386.0246 | 752505.0019 | 1687148.8309 | 1414785.2925
[9 empty] | 21 | 188033.9833 | 1146826.6765 | 2805381.6127 | 2465429.8251
[9 empty] | 22 | 243997.9162 | 1600276.5019 | 4368446.296 | 3920696.3544
[9 empty] | 23 | 288491.4472 | 1969817.8947 | 5900813.3902 | 5559561.5315
[9 empty] | 24 | 325950.1728 | 2275389.1665 | 7294077.8329 | 7458825.5098
[9 empty] | 25 | 344384.4932 | 2431429.5359 | 8131408.5864 | 9044712.0263
[9 empty] | 26 | 343916.4007 | 2440474.4823 | 8348528.5707 | 9878394.8933
[9 empty] | 27 | 303790.9995 | 2159536.3089 | 7460475.4618 | 9131470.957
[9 empty] | 28 | 242246.3757 | 1722809.4501 | 5976842.896 | 7450576.0372
[9 empty] | 29 | 155633.8032 | 1106683.0886 | 3844371.0161 | 4833886.0856
[9 empty] | 30 | 80194.8783 | 570074.1048 | 1980340.8491 | 2498138.7574
[9 empty] | 31 | 32336.2637 | 229790.1979 | 797921.9286 | 1007578.5588
[9 empty] | 32 | 9306.9898 | 66116.8952 | 229452.713 | 289745.168
[9 empty] | 33 | 2308.5029 | 16395.8298 | 56873.1087 | 71791.778
[7 empty] | A-weighted overall SPL 1 m from pipe wall | 26 | L_pAe_1m | 64.5875 | 72.8683 | 77.812 | 78.2066

## Valve Travel
VALVE TRAVEL AT GIVEN Cv | [6 empty] | Callculation of Valve capacity in units of Cv and size in units of inch
[9 empty] | Case 1 | Case 2 | Case 3 | Case 4
| Case 1 | Case 2 | Case 3 | Case 4 |  |  | Valve size in Inch | VS_IN | 3 | ===> | ===> | ===>
Valve size (inch) | 3 | [5 empty] | Valve cap. In Cv | VCAP_CV | 14.1587 | 38.9735 | 88.5763 | 135.5671
Calculated Cv | 14.1587 | 38.9735 | 88.5763 | 135.5671 |  |  | Valve Cv Table |  | BALL_SEG
NO USER INPUT IS REQUIRED FOR THIS TAB.
Travel % @ Cv | 22.2445 | 39.7399 | 60.1147 | 73.3107
TheTravel % @ Cv is calculated from the final Cv values on the
|  |  |  | Final results | Valve Sizing tab then copied to Line 24 of the Valve Sizing tab.
Cv table in use | BALL_SEG
[10 empty] | Case 1 | [12 empty] | Case 2 | [12 empty] | Case 3 | [13 empty] | Case 4
[6 empty] | Calc Cv | 14.1587 | [11 empty] | Calc Cv | 38.9735 | [11 empty] | Calc Cv | 88.5763 | [11 empty] | Calc Cv | 135.5671
[5 empty] | Travel, % | Cv @ travel % | 0 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420 | Travel, % | Cv @ travel % | 0 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420 | Travel, % | Cv @ travel % | 0 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420 | Travel, % | Cv @ travel % | 0 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420
[6 empty] | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
[6 empty] | M | 2.1142 | 1.4556 | 0.87719 | 0.60976 | 0.46296 | 0.36765 | 0.30488 | 0.22727 | 0.12346 | 0.057471 |  |  | M | 2.1142 | 1.4556 | 0.87719 | 0.60976 | 0.46296 | 0.36765 | 0.30488 | 0.22727 | 0.12346 | 0.057471 |  |  | M | 2.1142 | 1.4556 | 0.87719 | 0.60976 | 0.46296 | 0.36765 | 0.30488 | 0.22727 | 0.12346 | 0.057471 |  |  | M | 2.1142 | 1.4556 | 0.87719 | 0.60976 | 0.46296 | 0.36765 | 0.30488 | 0.22727 | 0.12346 | 0.057471
[7 empty] | 29.9339 | 23.7245 | 22.2445 | 24.609 | 28.3142 | 32.7789 | 37.4264 | 45.7179 | 61.3776 | 76.6758 |  |  |  | 82.3964 | 59.845 | 44.0118 | 39.7399 | 39.8025 | 41.902 | 44.9919 | 51.3576 | 64.4412 | 78.1019 |  |  |  | 187.265 | 132.0471 | 87.5231 | 69.9856 | 62.7668 | 60.1384 | 60.1147 | 62.631 | 70.565 | 80.9527 |  |  |  | 286.6112 | 200.447 | 128.7431 | 98.6385 | 84.5218 | 77.4144 | 74.4412 | 73.3107 | 76.3663 | 83.6533
[6 empty] | Vlv Trav @ Cv | 22.2445 | [11 empty] | Vlv Trav @ Cv | 39.7399 | [11 empty] | Vlv Trav @ Cv | 60.1147 | [11 empty] | Vlv Trav @ Cv | 73.3107
VALVE Cv TABLES
|  |  | FULL PORT BALL VALVES |  |  | TABLE NAME: | BALL_FP |  |  | Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 2 | 2.48 | 5.4 | 10.1 | 17.8 | 27.9 | 42.5 | 70.8 | 123 | 224 | 480
[6 empty] | 3 | 5.9 | 15.8 | 29.7 | 49.5 | 75.7 | 109 | 177 | 308 | 560 | 1200
[6 empty] | 4 | 9.7 | 25.9 | 48.6 | 81 | 124 | 179 | 313 | 545 | 989 | 2120
[6 empty] | 6 | 22 | 60 | 112 | 187 | 286 | 413 | 757 | 1318 | 2394 | 5100
[6 empty] | 8 | 40 | 106 | 199 | 331 | 506 | 732 | 1386 | 2413 | 4381 | 9300
[6 empty] | 10 | 63 | 167 | 314 | 523 | 800 | 1160 | 2244 | 3906 | 7092 | 15200
[6 empty] | 12 | 90 | 240 | 449 | 749 | 1150 | 1660 | 3306 | 5757 | 10452 | 22400
[6 empty] | 14 | 112 | 300 | 562 | 936 | 1430 | 2070 | 4177 | 7273 | 13205 | 28300
[6 empty] | 16 | 148 | 394 | 738 | 1230 | 1880 | 2720 | 5565 | 9689 | 17591 | 37700
[6 empty] | 18 | 188 | 502 | 942 | 1570 | 2400 | 3470 | 7085 | 12336 | 22397 | 48000
[6 empty] | 20 | 233 | 621 | 1160 | 1940 | 2790 | 4290 | 8782 | 15292 | 27763 | 59500
[6 empty] | 24 | 338 | 902 | 1690 | 2820 | 4310 | 6230 | 12738 | 22179 | 40268 | 86300
[6 empty] | 28 | 463 | 1240 | 2320 | 3860 | 5910 | 8530 | 17417 | 30326 | 55059 | 118000
[6 empty] | 30 | 533 | 1420 | 2660 | 4440 | 6790 | 9810 | 20074 | 34952 | 63458 | 136000
[6 empty] | 32 | 592 | 1580 | 2960 | 4942 | 7558 | 10915 | 22288 | 38807 | 70457 | 151000
[6 empty] | 36 | 752 | 2010 | 3760 | 6270 | 9590 | 13900 | 28339 | 49344 | 89587 | 192000
|  |  | REDUCED PORT BALL VALVES |  |  | TABLE NAME: | BALL_FP 10: BALL_RP; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  |  | Calc Cv | 38.9735 | [11 empty] | Calc Cv | 88.5763 | [11 empty] | Calc Cv | 135.5671
[6 empty] | Size, Inch | [11 empty] | Travel, % | Cv @ travel % | 0 | 3 | 7 | 15 | 26 | 45 | 74 | 105 | 165 | 245 | 350 | Travel, % | Cv @ travel % | 0 | 3 | 7 | 15 | 26 | 45 | 74 | 105 | 165 | 245 | 350 | Travel, % | Cv @ travel % | 0 | 3 | 7 | 15 | 26 | 45 | 74 | 105 | 165 | 245 | 350 | bar: Valve Travel, % 40
[6 empty] | 0.5 | 0.1 | 0.2 | 0.4 | 0.7 | 1.2 | 1.9 | 2.7 | 4.2 | 6.3 | 9 |  |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
[6 empty] | 0.75 | 0.2 | 0.4 | 0.9 | 1.4 | 2.5 | 4 | 5.7 | 9 | 13 | 19 |  |  | M | 3.3333 | 2.5 | 1.25 | 0.90909 | 0.52632 | 0.34483 | 0.32258 | 0.16667 | 0.125 | 0.095238 |  |  | M | 3.3333 | 2.5 | 1.25 | 0.90909 | 0.52632 | 0.34483 | 0.32258 | 0.16667 | 0.125 | 0.095238 |  |  | M | 3.3333 | 2.5 | 1.25 | 0.90909 | 0.52632 | 0.34483 | 0.32258 | 0.16667 | 0.125 | 0.095238
[6 empty] | 1 | 0.4 | 0.9 | 2 | 3.4 | 5.8 | 9.5 | 13.5 | 21 | 32 | 45 |  |  |  | 129.9116 | 99.9337 | 59.9669 | 51.7941 | 46.8282 | 47.9219 | 48.7011 | 58.9956 | 64.2467 | 70.3784 |  |  |  | 295.2545 | 223.9409 | 121.9704 | 96.8876 | 72.9349 | 65.0263 | 64.702 | 67.2627 | 70.447 | 75.1025 |  |  |  | 451.8903 | 341.4178 | 180.7089 | 139.6065 | 97.6669 | 81.23 | 79.8604 | 75.0945 | 76.3209 | 79.5778
[6 empty] | 1.5 | 1.1 | 2.4 | 5.6 | 9.4 | 16 | 26 | 38 | 58 | 88 | 125 |  |  | Vlv Trav @ Cv | 46.8282 | [11 empty] | Vlv Trav @ Cv | 64.702 | [11 empty] | Vlv Trav @ Cv | 75.0945
[6 empty] | 2 | 1.5 | 3.1 | 7.5 | 12 | 21 | 35 | 50 | 78 | 115 | 165
[6 empty] | 3 | 3 | 7 | 15 | 26 | 45 | 74 | 105 | 165 | 245 | 350
[6 empty] | 4 | 2 | 5 | 17 | 32 | 54 | 90 | 135 | 201 | 301 | 550
[6 empty] | 6 | 7 | 15 | 35 | 57 | 100 | 160 | 230 | 360 | 535 | 765
[6 empty] | 8 | 17 | 36 | 85 | 140 | 245 | 395 | 570 | 890 | 1325 | 1890
[6 empty] | 10 | 35 | 74 | 175 | 290 | 505 | 815 | 1180 | 1840 | 2735 | 3900
[6 empty] | 12 | 60 | 127 | 300 | 505 | 870 | 1400 | 2010 | 3150 | 4690 | 6700
[6 empty] | 14 | 42 | 102 | 240 | 400 | 700 | 1130 | 1620 | 2540 | 3780 | 5400
[6 empty] | 16 | 70 | 155 | 375 | 630 | 1100 | 1785 | 2550 | 3990 | 5950 | 8500
[6 empty] | 18 | 100 | 200 | 440 | 760 | 1275 | 2050 | 2940 | 4600 | 6860 | 9800
[6 empty] | 20 | 125 | 260 | 610 | 990 | 1700 | 2750 | 3900 | 6110 | 9100 | 13000
|  |  | SEGMENT BALL VALVES |  |  | TABLE NAME: | BALL_RP 10: BALL_SEG; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 1 | 0.52 | 1.13 | 2.23 | 3.83 | 5.95 | 8.58 | 11.7 | 16.2 | 24.1 | 45
[6 empty] | 1.5 | 1.33 | 3.27 | 6.44 | 11.1 | 17.2 | 24.8 | 33.9 | 46.5 | 69.3 | 110
[6 empty] | 2 | 2.05 | 5.07 | 10 | 17.2 | 26.6 | 38.4 | 52.5 | 72.4 | 108 | 180
[6 empty] | 2.5 | 3.26 | 8.02 | 15.9 | 27.3 | 42.3 | 61 | 83.4 | 114 | 170 | 280
[6 empty] | 3 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420
[6 empty] | 4 | 7.57 | 18.6 | 36.8 | 63.1 | 97.7 | 141 | 193 | 264 | 393 | 620
[6 empty] | 6 | 13.9 | 34.1 | 67.2 | 115 | 178 | 258 | 352 | 484 | 719 | 1260
[6 empty] | 8 | 22.5 | 55.3 | 109 | 187 | 290 | 418 | 571 | 784 | 1164 | 2030
[6 empty] | 10 | 35.3 | 86.9 | 171 | 294 | 455 | 658 | 900 | 1236 | 1831 | 3210
[6 empty] | 12 | 49.8 | 123 | 243 | 418 | 648 | 937 | 1278 | 1754 | 2601 | 4490
[6 empty] | 14 | 63.9 | 158 | 311 | 534 | 827 | 1193 | 1628 | 2237 | 3320 | 6440
[6 empty] | 16 | 85.4 | 210 | 414 | 713 | 1106 | 1599 | 2180 | 2989 | 4432 | 8510
[6 empty] | 20 | 130.6 | 321 | 633 | 1090 | 1692 | 2446 | 3334 | 4571 | 6778 | 13020
[6 empty] | 24 | 198 | 486 | 958 | 1649 | 2560 | 3701 | 5045 | 6916 | 10255 | 19700
[6 empty] | 28 | 254 | 624 | 1230 | 2118 | 3288 | 4753 | 6479 | 8882 | 13171 | 25300
[6 empty] | 32 | 321 | 789 | 1556 | 2679 | 4159 | 6012 | 8195 | 11234 | 16659 | 32000
|  |  | HIGH PERFORMANCE BUTTERFLY |  |  | TABLE NAME: | BALL_SEG 10: HPBF_150; Valve Travel, % 40: Valve Travel, %
|  |  | VALVES CLASS 150 |  |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 2.5 | 4 | 7 | 11 | 16 | 22 | 30 | 43 | 59 | 71 | 78
[6 empty] | 3 | 4 | 12 | 21 | 35 | 46 | 66 | 90 | 125 | 153 | 165
[6 empty] | 4 | 8 | 12 | 55 | 87 | 120 | 165 | 225 | 310 | 380 | 400
[6 empty] | 5 | 10 | 38 | 87 | 143 | 193 | 263 | 356 | 482 | 606 | 650
[6 empty] | 6 | 10 | 58 | 137 | 235 | 310 | 415 | 560 | 745 | 960 | 1050
[6 empty] | 8 | 15 | 130 | 315 | 475 | 695 | 970 | 1370 | 1865 | 2015 | 2200
[6 empty] | 10 | 25 | 155 | 340 | 540 | 835 | 1210 | 1665 | 2225 | 3030 | 3300
[6 empty] | 12 | 55 | 310 | 590 | 895 | 1410 | 2020 | 2790 | 3855 | 4900 | 5100
[6 empty] | 14 | 100 | 435 | 755 | 1220 | 1625 | 2320 | 3190 | 4410 | 5395 | 5800
[6 empty] | 16 | 165 | 630 | 1050 | 1530 | 2190 | 3080 | 4350 | 6100 | 7600 | 8000
[6 empty] | 18 | 285 | 790 | 1365 | 2200 | 2940 | 4200 | 5760 | 7970 | 9750 | 10500
[6 empty] | 20 | 350 | 880 | 1570 | 2540 | 3400 | 5080 | 7150 | 9450 | 12650 | 14000
[6 empty] | 24 | 405 | 1070 | 1980 | 3050 | 4430 | 6500 | 9550 | 13950 | 19100 | 21600
[6 empty] | 28 | 570 | 1562 | 2779 | 4200 | 6000 | 8700 | 12900 | 18882 | 26400 | 30000
[6 empty] | 30 | 650 | 1770 | 3150 | 4760 | 6800 | 9860 | 14620 | 21400 | 29920 | 34000
[6 empty] | 32 | 784 | 2134 | 3799 | 5740 | 8200 | 11890 | 17630 | 25806 | 36080 | 41000
[6 empty] | 36 | 1220 | 2980 | 5230 | 7650 | 11150 | 16100 | 23500 | 34100 | 49200 | 55500
[6 empty] | 40 | 1452 | 3893 | 6987 | 10481 | 15018 | 21688 | 32123 | 47278 | 65880 | 75000
[6 empty] | 42 | 1600 | 4290 | 7700 | 11550 | 16550 | 23900 | 35400 | 52100 | 72600 | 82650
[6 empty] | 48 | 2100 | 5600 | 10100 | 15200 | 21700 | 31400 | 46600 | 68200 | 95300 | 108300
[6 empty] | 54 | 2540 | 6950 | 12400 | 18700 | 26700 | 38700 | 57400 | 84100 | 117500 | 133500
[6 empty] | 56 | 2740 | 7497 | 13375 | 20171 | 28800 | 41744 | 61915 | 90715 | 126742 | 144000
[6 empty] | 60 | 3020 | 8270 | 14800 | 22250 | 31800 | 46100 | 68370 | 100200 | 139900 | 159000
|  |  | HIGH PERFORMANCE BUTTERFLY |  |  | TABLE NAME: | HPBF_150 10: HPBF_300; Valve Travel, % 40: Valve Travel, %
|  |  | VALVES CLASS 300 |  |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 2.5 | 4 | 7 | 11 | 16 | 22 | 30 | 43 | 59 | 71 | 78
[6 empty] | 3 | 4 | 12 | 21 | 35 | 46 | 66 | 90 | 125 | 153 | 165
[6 empty] | 4 | 8 | 12 | 55 | 87 | 120 | 165 | 225 | 310 | 380 | 400
[6 empty] | 6 | 10 | 58 | 137 | 235 | 310 | 415 | 560 | 745 | 960 | 1050
[6 empty] | 8 | 12 | 115 | 260 | 390 | 570 | 795 | 1120 | 1525 | 1650 | 1800
[6 empty] | 10 | 20 | 145 | 325 | 515 | 795 | 1155 | 1590 | 2125 | 2890 | 3150
[6 empty] | 12 | 45 | 280 | 550 | 835 | 1315 | 1880 | 2600 | 3590 | 4570 | 4750
[6 empty] | 14 | 90 | 430 | 750 | 1200 | 1580 | 2250 | 3100 | 4300 | 5100 | 5200
[6 empty] | 16 | 150 | 620 | 1030 | 1500 | 2100 | 2950 | 4050 | 5450 | 6750 | 6900
[6 empty] | 18 | 280 | 780 | 1350 | 2100 | 2790 | 4000 | 5450 | 7350 | 8900 | 9300
[6 empty] | 20 | 340 | 870 | 1550 | 2510 | 3250 | 4800 | 6550 | 8250 | 10600 | 11300
[6 empty] | 24 | 400 | 1020 | 1920 | 2960 | 4300 | 6200 | 9000 | 12700 | 17400 | 18500
|  |  | HIGH PERFORMANCE BUTTERFLY |  |  | TABLE NAME: | HPBF_300 10: HPBF_600; Valve Travel, % 40: Valve Travel, %
|  |  | VALVES CLASS 600 |  |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 3 | 4 | 11 | 20 | 33 | 43 | 62 | 85 | 117 | 144 | 155
[6 empty] | 4 | 5 | 16 | 36 | 57 | 78 | 107 | 146 | 202 | 247 | 260
[6 empty] | 6 | 7 | 41 | 98 | 168 | 221 | 296 | 400 | 532 | 686 | 750
[6 empty] | 8 | 9 | 86 | 195 | 293 | 428 | 596 | 840 | 1144 | 1238 | 1350
[6 empty] | 10 | 13 | 97 | 217 | 343 | 530 | 770 | 1060 | 1417 | 1927 | 2100
[6 empty] | 12 | 27 | 171 | 336 | 510 | 803 | 1148 | 1587 | 2192 | 2790 | 2900
[6 empty] | 14 | 69 | 331 | 577 | 923 | 1215 | 1731 | 2385 | 3308 | 3923 | 4000
[6 empty] | 16 | 111 | 458 | 761 | 1109 | 1552 | 2180 | 2993 | 4028 | 4989 | 5100
[6 empty] | 18 | 166 | 461 | 798 | 1242 | 1650 | 2366 | 3223 | 4347 | 5263 | 5500
[6 empty] | 20 | 239 | 612 | 1090 | 1766 | 2287 | 3377 | 4608 | 5804 | 7458 | 7950
[6 empty] | 24 | 244 | 623 | 1173 | 1808 | 2626 | 3787 | 5497 | 7757 | 10628 | 11300
|  |  | GLOBE CAGE GUIDED EQUALL PERCENT |  |  | TABLE NAME: | HPBF_600 10: GC_EQ; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  | Decimal sizes N.01, N.02, N.03 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  | represent "N" inch valve , 1, 2, 3 |  |  | 2 | 2 | 4 | 6 | 9 | 14 | 21 | 33 | 50 | 66 | 71
|  |  | sizes reduced. |  |  | 2.01 | 1.1 | 3.3 | 5.5 | 7.6 | 9.8 | 12.8 | 17.9 | 26.3 | 39.7 | 50
[6 empty] | 2.02 | 0.6 | 1.2 | 1.6 | 2.5 | 4.6 | 8.2 | 12.9 | 17.7 | 21.6 | 24
[6 empty] | 2.03 | 0.3 | 0.7 | 0.9 | 1.5 | 2.7 | 4.8 | 7.5 | 10.4 | 12.6 | 14
[6 empty] | 3 | 4 | 8.5 | 14.5 | 22 | 33.5 | 51 | 75 | 108 | 128 | 138
[6 empty] | 3.01 | 2.5 | 3.7 | 6.6 | 11.1 | 18.4 | 29.4 | 45.6 | 67.7 | 92 | 110
[6 empty] | 3.02 | 1.2 | 2.5 | 3.3 | 5.2 | 9.5 | 17 | 26.8 | 37 | 45 | 50
[6 empty] | 3.03 | 0.8 | 1.6 | 2.1 | 3.3 | 6.1 | 10.9 | 17.2 | 23.7 | 28.8 | 32
[6 empty] | 4 | 5.6 | 12.9 | 23.4 | 36.9 | 59.6 | 86.5 | 128.2 | 163.9 | 188.6 | 210
[6 empty] | 4.01 | 2.8 | 6.7 | 11.7 | 17.9 | 28.6 | 46.2 | 71.9 | 105.8 | 141.2 | 160
[6 empty] | 4.02 | 2 | 4.1 | 5.5 | 8.5 | 15.6 | 27.9 | 44 | 60.6 | 73.8 | 82
[6 empty] | 4.03 | 1.2 | 2.5 | 3.3 | 5.2 | 9.5 | 17 | 26.8 | 37 | 45 | 50
[6 empty] | 6 | 6.5 | 15 | 27.7 | 47.1 | 77.1 | 123.8 | 198.5 | 265.2 | 316 | 340
[6 empty] | 6.01 | 3.4 | 11.1 | 22 | 32.3 | 50.4 | 81.7 | 126.8 | 187.4 | 246.3 | 270
[6 empty] | 6.02 | 3.3 | 6.8 | 9.1 | 14.1 | 25.9 | 46.2 | 73 | 100.5 | 122.3 | 136
[6 empty] | 6.03 | 2 | 4.1 | 5.5 | 8.5 | 15.6 | 27.9 | 44 | 60.6 | 73.8 | 82
[6 empty] | 8 | 6.5 | 23 | 45 | 83 | 138 | 220 | 325 | 445 | 510 | 560
[6 empty] | 8.01 | 5.6 | 19 | 39 | 58 | 94 | 148 | 222 | 310 | 405 | 450
[6 empty] | 8.02 | 4 | 11.7 | 15.8 | 24.4 | 44.9 | 80.2 | 126.6 | 174.5 | 212.3 | 236
[6 empty] | 8.03 | 3 | 7.1 | 9.5 | 14.7 | 27 | 48.3 | 76.2 | 105 | 127.7 | 142
[6 empty] | 10 | 8.1 | 33.2 | 65.7 | 124.4 | 216.8 | 350.1 | 493.2 | 619.9 | 747.6 | 830
[6 empty] | 10.01 | 6.5 | 26.5 | 47.1 | 76.2 | 126.3 | 219.8 | 343.2 | 460 | 566.2 | 655
[6 empty] | 10.02 | 6.1 | 18.6 | 25 | 38.7 | 71.2 | 127.2 | 200.6 | 276.5 | 336.4 | 374
[6 empty] | 10.03 | 5.5 | 11.1 | 15 | 23.2 | 42.6 | 76.2 | 120.2 | 165.6 | 201.5 | 224
[6 empty] | 12 | 22.4 | 64.3 | 111.1 | 179.8 | 303.1 | 546.8 | 795 | 996 | 1155 | 1240
[6 empty] | 12.01 | 15.5 | 44.7 | 73.7 | 110.5 | 174.2 | 277.6 | 441.3 | 650.5 | 837.5 | 960
[6 empty] | 12.02 | 12.8 | 26 | 35 | 54.2 | 99.7 | 178.1 | 281.1 | 387.4 | 471.4 | 524
[6 empty] | 12.03 | 7.7 | 15.6 | 21 | 32.5 | 59.8 | 106.8 | 168.4 | 232.1 | 282.5 | 314
[6 empty] | 14 | 24.7 | 82.3 | 158.3 | 266.7 | 427 | 693.9 | 1015.8 | 1277.2 | 1514.7 | 1650
[6 empty] | 14.01 | 18.9 | 60.2 | 103.2 | 164.8 | 260.6 | 405.5 | 630.9 | 903.9 | 1141.5 | 1275
[6 empty] | 14.02 | 16.2 | 37.1 | 49.8 | 77.1 | 142 | 253.6 | 400.2 | 551.5 | 671.1 | 746
[6 empty] | 14.03 | 10.9 | 22.2 | 29.8 | 46.1 | 84.9 | 151.6 | 239.2 | 329.7 | 401.2 | 446
[6 empty] | 16 | 35.1 | 100.4 | 167 | 268.4 | 471 | 849.3 | 1265.1 | 1603.9 | 1911.6 | 2090
[6 empty] | 16.01 | 26.3 | 73 | 119.6 | 175.7 | 287 | 477.7 | 773.1 | 1125.4 | 1432.4 | 1680
[6 empty] | 16.02 | 20.9 | 42.4 | 57 | 88.3 | 162.6 | 290.3 | 458.1 | 631.4 | 768.2 | 854
[6 empty] | 16.03 | 12.5 | 25.4 | 34.2 | 52.9 | 97.5 | 174.1 | 274.7 | 378.5 | 460.6 | 512
[6 empty] | 18 | 45.3 | 129.7 | 215.7 | 346.7 | 608.5 | 1097.2 | 1634.3 | 2072 | 2469.5 | 2700
[6 empty] | 18.01 | 29.8 | 82.6 | 135.2 | 198.7 | 324.6 | 540.3 | 874.3 | 1272.8 | 1620 | 1900
[6 empty] | 18.02 | 27.8 | 56.6 | 76.1 | 117.8 | 217 | 387.6 | 611.5 | 842.8 | 1025.5 | 1140
[6 empty] | 18.03 | 16.6 | 33.8 | 45.4 | 70.3 | 129.4 | 231.2 | 364.8 | 502.7 | 611.7 | 680
[6 empty] | 20 | 60.5 | 172.9 | 287.7 | 462.3 | 811.3 | 1462.9 | 2179.1 | 2762.7 | 3292.7 | 3600
[6 empty] | 20.01 | 39.2 | 108.7 | 177.9 | 261.5 | 427.1 | 710.9 | 1150.4 | 1674.7 | 2131.6 | 2500
[6 empty] | 20.02 | 36.6 | 74.5 | 100.2 | 155 | 285.5 | 509.9 | 804.6 | 1108.9 | 1349.3 | 1500
[6 empty] | 20.03 | 22 | 44.7 | 60.1 | 93 | 171.3 | 306 | 482.8 | 665.4 | 809.6 | 900
[6 empty] | 24 | 87.3 | 249.8 | 415.5 | 667.8 | 1171.9 | 2113.1 | 3147.6 | 3990.6 | 4756.1 | 5200
[6 empty] | 24.01 | 57.2 | 158.7 | 259.7 | 381.7 | 623.5 | 1037.9 | 1679.6 | 2445.1 | 3112.1 | 3650
[6 empty] | 24.03 | 53.7 | 109.3 | 146.9 | 227.4 | 418.7 | 747.9 | 1180.1 | 1626.4 | 1979 | 2200
[6 empty] | 24.03 | 31.7 | 64.6 | 86.8 | 134.4 | 247.5 | 441.9 | 697.4 | 961.1 | 1169.4 | 1300
|  |  | GLOBE CAGE GUIDED LINEAR |  |  | TABLE NAME: | GC_EQ 10: GC_LIN; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  | Decimal sizes N.01, N.02, N.03 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  | represent "N" inch valve , 1, 2, 3 |  |  | 2 | 4.9 | 13.9 | 22.2 | 30.3 | 39.5 | 48.6 | 57.3 | 64.7 | 69.5 | 74
|  |  | sizes reduced. |  |  | 2.01 | 3.5 | 7.6 | 12.5 | 17.3 | 22.4 | 27.6 | 33.1 | 38.5 | 43.6 | 48
[6 empty] | 2.02 | 2.6 | 5.2 | 7.7 | 10.3 | 12.9 | 15.4 | 18 | 20.6 | 23.2 | 26
[6 empty] | 2.03 | 1.6 | 3.2 | 4.8 | 6.3 | 7.9 | 9.5 | 11.1 | 12.7 | 14.3 | 16
[6 empty] | 3 | 8 | 22 | 39 | 59 | 75 | 90 | 105 | 119 | 130 | 142
[6 empty] | 3.01 | 6.2 | 16.6 | 26.9 | 36.9 | 46.6 | 56.8 | 67.4 | 78 | 87.8 | 98
[6 empty] | 3.02 | 4.5 | 11.1 | 16.6 | 22.2 | 27.7 | 33.3 | 38.8 | 44.4 | 49.9 | 56
[6 empty] | 3.03 | 3.4 | 6.7 | 10.1 | 13.5 | 16.8 | 20.2 | 23.6 | 26.9 | 30.3 | 34
[6 empty] | 4 | 19.3 | 41.5 | 74.4 | 105.3 | 133.4 | 164.5 | 187.6 | 206.4 | 219.3 | 230
[6 empty] | 4.01 | 8 | 25.4 | 43.1 | 60.4 | 77.2 | 93.8 | 110.7 | 127.6 | 143.9 | 160
[6 empty] | 4.02 | 6 | 17 | 25.5 | 34.1 | 42.6 | 51.1 | 59.6 | 68.1 | 76.6 | 86
[6 empty] | 4.03 | 5.2 | 10.3 | 15.4 | 20.6 | 25.7 | 30.9 | 36 | 41.2 | 46.3 | 52
[6 empty] | 6 | 23 | 62 | 123.5 | 181 | 229.1 | 269.3 | 315.2 | 349.9 | 370.1 | 380
[6 empty] | 6.01 | 12 | 40.9 | 71.4 | 101.4 | 130.6 | 158.9 | 186.7 | 214.7 | 242.2 | 275
[6 empty] | 6.02 | 9.5 | 29.7 | 44.6 | 59.4 | 74.3 | 89.1 | 104 | 118.8 | 133.7 | 150
[6 empty] | 6.03 | 8 | 17.8 | 26.7 | 35.6 | 44.6 | 53.5 | 62.4 | 71.3 | 80.2 | 90
[6 empty] | 8 | 28.2 | 94.2 | 185.6 | 288 | 377.1 | 449.1 | 514.1 | 571.9 | 590 | 600
[6 empty] | 8.01 | 14.5 | 52.5 | 108 | 172 | 232 | 299 | 365 | 417 | 430 | 455
[6 empty] | 8.02 | 10 | 45 | 75.4 | 100.6 | 125.7 | 150.9 | 176 | 201.2 | 226.3 | 254
[6 empty] | 8.03 | 9 | 30.1 | 45.1 | 60.2 | 75.2 | 90.3 | 105.3 | 120.4 | 135.4 | 152
[6 empty] | 10 | 45.9 | 189.3 | 329.3 | 461.8 | 583.3 | 689.9 | 778.5 | 847.7 | 897.9 | 950
[6 empty] | 10.01 | 25 | 103.6 | 183.3 | 260.7 | 337.5 | 414.1 | 489.4 | 562.3 | 631.5 | 700
[6 empty] | 10.02 | 17 | 78.8 | 118.2 | 157.6 | 197 | 236.4 | 275.8 | 315.2 | 354.6 | 398
[6 empty] | 10.03 | 12 | 46.7 | 70.1 | 93.5 | 116.8 | 140.2 | 163.6 | 186.9 | 210.3 | 238
[6 empty] | 12 | 93.2 | 250 | 463.3 | 660 | 840 | 990 | 1115 | 1205 | 1250 | 1270
[6 empty] | 12.01 | 66.7 | 167.8 | 276.8 | 382.9 | 485.5 | 586.9 | 692.1 | 796.9 | 893 | 970
[6 empty] | 12.02 | 25 | 108.9 | 163.4 | 218 | 272.3 | 326.7 | 381.2 | 435.6 | 490.1 | 550
[6 empty] | 12.03 | 17 | 67.3 | 101 | 134.6 | 168.3 | 202 | 235.6 | 269.3 | 302.9 | 340
[6 empty] | 14.01 | 127.4 | 407.5 | 673.4 | 915.6 | 1128.5 | 1316.5 | 1474.2 | 1593.1 | 1671.4 | 1740
[6 empty] | 14.01 | 91.3 | 233.3 | 393 | 548.1 | 696.8 | 838 | 976.4 | 1105.4 | 1221.2 | 1300
[6 empty] | 14.02 | 52 | 153.7 | 230.5 | 307.3 | 384.1 | 460.9 | 537.8 | 614.6 | 691.4 | 776
[6 empty] | 14.03 | 27 | 91.9 | 137.8 | 183.7 | 229.7 | 275.6 | 321.6 | 367.5 | 413.4 | 464
[6 empty] | 16 | 189 | 497 | 891.8 | 1248 | 1535.4 | 1791.5 | 1950 | 2063 | 2161.6 | 2215
[6 empty] | 16.01 | 101.3 | 276.5 | 448.1 | 615 | 779.1 | 941.9 | 1101.6 | 1255.7 | 1398.9 | 1530
[6 empty] | 16.02 | 71 | 186.1 | 279.2 | 372.2 | 465.3 | 558.4 | 651.4 | 744.5 | 837.5 | 940
[6 empty] | 16.03 | 47 | 112.5 | 168.7 | 224.9 | 281.2 | 337.4 | 393.6 | 449.9 | 506.1 | 568
[6 empty] | 18 | 230.4 | 605.8 | 1087.1 | 1521.3 | 1871.6 | 2183.8 | 2377 | 2514.7 | 2634.9 | 2700
[6 empty] | 18.01 | 125.8 | 343.4 | 556.4 | 763.8 | 967.6 | 1169.7 | 1368 | 1559.4 | 1737.2 | 1900
[6 empty] | 18.02 | 86.1 | 225.7 | 338.6 | 451.4 | 564.3 | 677.2 | 790 | 902.9 | 1015.7 | 1140
[6 empty] | 18.03 | 56.3 | 134.6 | 202 | 269.3 | 336.6 | 403.9 | 471.2 | 538.6 | 605.9 | 680
[6 empty] | 20 | 307.2 | 807.8 | 1449.4 | 2028.4 | 2495.5 | 2911.7 | 3169.3 | 3353 | 3513.2 | 3600
[6 empty] | 20.01 | 165.5 | 451.8 | 732.1 | 1005 | 1273.1 | 1539 | 1800 | 2051.8 | 2285.8 | 2500
[6 empty] | 20.02 | 113.3 | 297 | 445.5 | 594 | 742.5 | 891 | 1039.5 | 1188 | 1336.5 | 1500
[6 empty] | 20.03 | 74.5 | 178.2 | 267.3 | 356.4 | 445.5 | 534.6 | 623.7 | 712.8 | 801.9 | 900
[6 empty] | 24 | 443.7 | 1166.8 | 2093.6 | 2929.8 | 3604.6 | 4205.8 | 4577.9 | 4843.2 | 5074.6 | 5200
[6 empty] | 24.01 | 241.6 | 659.6 | 1068.9 | 1467.3 | 1858.7 | 2247 | 2628 | 2995.6 | 3337.2 | 3650
[6 empty] | 24.02 | 166.2 | 435.6 | 653.4 | 871.2 | 1089 | 1306.8 | 1524.6 | 1742.4 | 1960.2 | 2200
[6 empty] | 24.03 | 107.6 | 257.4 | 386.1 | 514.8 | 643.5 | 772.2 | 900.9 | 1029.6 | 1158.3 | 1300
|  |  | GLOBE PARABOLIC PLUG EQUAL % |  |  | 20.03: TABLE NAME:; 74.5: GP_EQ; 356.4: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  | Decimal sizes N.01, N.02, N.03 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  | represent "N" inch valve , 1, 2, 3 … |  |  | 0.5 | 0.164 | 0.355 | 0.562 | 0.888 | 1.378 | 2.163 | 3.417 | 4.842 | 6.441 | 7
|  |  | sizes reduced. |  |  | 0.501 | 0.057 | 0.159 | 0.307 | 0.488 | 0.78 | 1.456 | 2.173 | 2.884 | 3.533 | 4
[6 empty] | 0.502 | 0.083 | 0.155 | 0.228 | 0.336 | 0.585 | 0.941 | 1.37 | 1.702 | 2.005 | 2.3
[6 empty] | 0.503 | 0.048 | 0.092 | 0.137 | 0.202 | 0.35 | 0.56 | 0.818 | 1.113 | 1.329 | 1.5
[6 empty] | 0.504 | 0.02 | 0.037 | 0.057 | 0.083 | 0.161 | 0.28 | 0.413 | 0.538 | 0.656 | 0.8
[6 empty] | 0.505 | 0.009 | 0.022 | 0.035 | 0.054 | 0.096 | 0.168 | 0.253 | 0.334 | 0.414 | 0.5
[6 empty] | 0.506 | 0.005 | 0.011 | 0.02 | 0.033 | 0.063 | 0.105 | 0.15 | 0.197 | 0.245 | 0.3
[6 empty] | 0.75 | 0.239 | 0.452 | 0.668 | 1.069 | 1.849 | 2.928 | 4.022 | 5.229 | 7.131 | 9
[6 empty] | 0.751 | 0.057 | 0.198 | 0.399 | 0.669 | 1.109 | 1.785 | 2.787 | 3.712 | 4.739 | 5.5
[6 empty] | 0.752 | 0.05 | 0.169 | 0.276 | 0.453 | 0.776 | 1.204 | 1.802 | 2.352 | 2.723 | 3
[6 empty] | 0.753 | 0.044 | 0.093 | 0.15 | 0.214 | 0.405 | 0.684 | 0.999 | 1.299 | 1.667 | 2
[6 empty] | 0.754 | 0.034 | 0.061 | 0.086 | 0.131 | 0.248 | 0.418 | 0.62 | 0.817 | 1.011 | 1.2
[6 empty] | 0.755 | 0.012 | 0.029 | 0.051 | 0.082 | 0.142 | 0.234 | 0.34 | 0.451 | 0.58 | 0.7
[6 empty] | 0.756 | 0.009 | 0.019 | 0.03 | 0.044 | 0.082 | 0.141 | 0.207 | 0.271 | 0.333 | 0.4
[6 empty] | 1 | 0.268 | 0.568 | 0.913 | 1.549 | 2.754 | 4.657 | 7.075 | 9.487 | 11.626 | 13.5
[6 empty] | 1.001 | 0.118 | 0.287 | 0.507 | 0.825 | 1.557 | 2.695 | 4.14 | 5.605 | 7.028 | 8.5
[6 empty] | 1.002 | 0.073 | 0.185 | 0.331 | 0.525 | 0.966 | 1.672 | 2.647 | 3.588 | 4.366 | 5.4
[6 empty] | 1.003 | 0.027 | 0.09 | 0.186 | 0.317 | 0.583 | 0.997 | 1.52 | 2.05 | 2.54 | 3.1
[6 empty] | 1.004 | 0.03 | 0.075 | 0.134 | 0.215 | 0.397 | 0.67 | 1.002 | 1.354 | 1.701 | 2
[6 empty] | 1.005 | 0.025 | 0.053 | 0.077 | 0.131 | 0.248 | 0.433 | 0.643 | 0.853 | 1.056 | 1.2
[6 empty] | 1.006 | 0.011 | 0.025 | 0.041 | 0.073 | 0.143 | 0.239 | 0.345 | 0.462 | 0.589 | 0.8
[6 empty] | 1.5 | 0.453 | 1.124 | 2 | 3.071 | 5.909 | 10.566 | 16.175 | 21.567 | 25.661 | 28
[6 empty] | 1.501 | 0.226 | 0.582 | 1.056 | 1.694 | 3.155 | 5.364 | 7.974 | 10.692 | 13.438 | 16
[6 empty] | 1.502 | 0.203 | 0.437 | 0.705 | 1.021 | 1.877 | 3.245 | 4.93 | 6.712 | 8.593 | 10.5
[6 empty] | 1.503 | 0.086 | 0.219 | 0.398 | 0.617 | 1.131 | 2.022 | 3.169 | 4.256 | 5.211 | 6
[6 empty] | 1.504 | 0.053 | 0.141 | 0.262 | 0.412 | 0.789 | 1.363 | 2.078 | 2.828 | 3.453 | 4
[6 empty] | 1.505 | 0.031 | 0.076 | 0.134 | 0.21 | 0.391 | 0.691 | 1.071 | 1.431 | 1.736 | 2.2
[6 empty] | 1.506 | 0.027 | 0.056 | 0.085 | 0.128 | 0.234 | 0.396 | 0.588 | 0.784 | 0.981 | 1.2
[6 empty] | 2 | 1.209 | 2.459 | 3.305 | 5.116 | 9.421 | 16.828 | 26.55 | 36.591 | 44.523 | 49
[6 empty] | 2.01 | 0.315 | 0.817 | 1.505 | 2.87 | 5.482 | 9.305 | 13.774 | 18.306 | 23.17 | 28
[6 empty] | 2.02 | 0.171 | 0.467 | 0.882 | 1.633 | 3.179 | 5.473 | 8.207 | 11.089 | 13.683 | 17
[6 empty] | 2.03 | 0.146 | 0.369 | 0.662 | 1.023 | 1.894 | 3.286 | 5.007 | 6.711 | 8.407 | 10
[6 empty] | 3 | 2.007 | 4.467 | 7.366 | 12.276 | 22.522 | 38.624 | 62.018 | 79.573 | 90.094 | 100
[6 empty] | 3.01 | 1.004 | 2.505 | 4.499 | 6.963 | 12.945 | 23.649 | 36.145 | 47.819 | 58.698 | 70
[6 empty] | 3.02 | 0.727 | 1.606 | 2.636 | 3.946 | 7.53 | 13.569 | 21.257 | 28.974 | 34.99 | 42
[6 empty] | 3.03 | 0.355 | 0.887 | 1.588 | 2.455 | 4.505 | 8.075 | 12.547 | 16.822 | 20.779 | 25
[6 empty] | 4 | 2.896 | 6.719 | 11.479 | 17.159 | 29.352 | 56.255 | 86.653 | 120.896 | 153.844 | 190
[6 empty] | 4.01 | 1.558 | 3.765 | 6.626 | 10.108 | 18.418 | 32.827 | 55.269 | 77.526 | 98.631 | 120
[6 empty] | 4.02 | 1.45 | 3.05 | 4.822 | 8.099 | 14.857 | 24.2 | 35.222 | 49.808 | 61.142 | 72
[6 empty] | 4.03 | 0.882 | 1.818 | 2.839 | 4.443 | 8.424 | 14.384 | 21.124 | 27.793 | 34.167 | 42
[6 empty] | 6 | 4.225 | 9.715 | 16.432 | 25.732 | 49.583 | 89.691 | 140.008 | 195.766 | 256.778 | 295
[6 empty] | 6.01 | 2.829 | 6.733 | 11.683 | 17.723 | 31.528 | 53.903 | 88.375 | 113.113 | 140.553 | 165
[6 empty] | 6.02 | 1.364 | 3.606 | 6.678 | 10.62 | 17.821 | 28.656 | 42.883 | 57.38 | 71.534 | 85
[6 empty] | 6.03 | 0.911 | 1.895 | 2.949 | 4.261 | 7.768 | 13.68 | 21.418 | 29.715 | 37.963 | 50
|  |  | GLOBE PARABOLIC PLUG LINEAR |  |  | TABLE NAME: | GP_EQ 10: GP_LIN; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  | Decimal sizes N.01, N.02, N.03 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  | represent "N" inch valve , 1, 2, 3 … |  |  | 0.5 | 0.531 | 1.268 | 1.949 | 2.659 | 3.377 | 4.085 | 4.764 | 5.51 | 6.672 | 7
|  |  | sizes reduced. |  |  | 0.501 | 0.358 | 0.744 | 1.225 | 1.61 | 1.992 | 2.365 | 2.719 | 3.049 | 3.411 | 4
[6 empty] | 0.502 | 0.278 | 0.532 | 0.785 | 1.069 | 1.319 | 1.52 | 1.707 | 1.879 | 2.033 | 2.3
[6 empty] | 0.503 | 0.19 | 0.356 | 0.515 | 0.669 | 0.819 | 0.971 | 1.15 | 1.275 | 1.377 | 1.5
[6 empty] | 0.504 | 0.092 | 0.172 | 0.249 | 0.324 | 0.397 | 0.47 | 0.542 | 0.612 | 0.683 | 0.8
[6 empty] | 0.505 | 0.055 | 0.105 | 0.154 | 0.202 | 0.251 | 0.3 | 0.351 | 0.401 | 0.452 | 0.5
[6 empty] | 0.506 | 0.035 | 0.065 | 0.095 | 0.124 | 0.153 | 0.182 | 0.211 | 0.24 | 0.27 | 0.3
[6 empty] | 0.75 | 0.845 | 1.678 | 2.573 | 3.311 | 4.036 | 4.743 | 5.425 | 6.179 | 7.609 | 9
[6 empty] | 0.751 | 0.347 | 0.819 | 1.402 | 2.167 | 2.779 | 3.388 | 3.977 | 4.53 | 5.031 | 5.5
[6 empty] | 0.752 | 0.294 | 0.742 | 1.078 | 1.403 | 1.731 | 2.125 | 2.372 | 2.597 | 2.799 | 3
[6 empty] | 0.753 | 0.237 | 0.438 | 0.628 | 0.811 | 0.987 | 1.155 | 1.317 | 1.47 | 1.615 | 2
[6 empty] | 0.754 | 0.125 | 0.241 | 0.358 | 0.478 | 0.599 | 0.721 | 0.842 | 0.964 | 1.084 | 1.2
[6 empty] | 0.755 | 0.078 | 0.148 | 0.215 | 0.284 | 0.352 | 0.42 | 0.49 | 0.559 | 0.63 | 0.7
[6 empty] | 0.756 | 0.048 | 0.089 | 0.129 | 0.169 | 0.207 | 0.245 | 0.284 | 0.322 | 0.36 | 0.4
[6 empty] | 1 | 1.288 | 2.619 | 4.023 | 5.415 | 6.826 | 8.125 | 8.899 | 10.246 | 11.931 | 13.5
[6 empty] | 1.001 | 0.773 | 1.538 | 2.307 | 3.147 | 3.919 | 4.679 | 5.415 | 6.122 | 7.003 | 8.5
[6 empty] | 1.002 | 0.463 | 0.939 | 1.433 | 1.937 | 2.458 | 3.02 | 3.519 | 3.997 | 4.441 | 5.4
[6 empty] | 1.003 | 0.277 | 0.562 | 0.857 | 1.16 | 1.468 | 1.772 | 2.071 | 2.358 | 2.658 | 3.1
[6 empty] | 1.004 | 0.178 | 0.367 | 0.566 | 0.775 | 0.988 | 1.201 | 1.408 | 1.606 | 1.789 | 2
[6 empty] | 1.005 | 0.114 | 0.23 | 0.348 | 0.468 | 0.589 | 0.711 | 0.831 | 0.949 | 1.065 | 1.2
[6 empty] | 1.006 | 0.07 | 0.138 | 0.207 | 0.276 | 0.344 | 0.413 | 0.482 | 0.55 | 0.619 | 0.8
[6 empty] | 1.5 | 2.636 | 5.382 | 8.457 | 11.766 | 15.22 | 18.767 | 21.562 | 24.09 | 26.5 | 28
[6 empty] | 1.501 | 1.625 | 3.16 | 4.699 | 6.25 | 7.896 | 9.519 | 11.12 | 12.681 | 14.181 | 16
[6 empty] | 1.502 | 0.946 | 1.885 | 2.86 | 3.86 | 4.875 | 5.884 | 6.901 | 7.918 | 8.855 | 10.5
[6 empty] | 1.503 | 0.565 | 1.128 | 1.72 | 2.333 | 2.955 | 3.579 | 4.19 | 4.779 | 5.332 | 6
[6 empty] | 1.504 | 0.369 | 0.743 | 1.135 | 1.543 | 1.961 | 2.379 | 2.788 | 3.182 | 3.549 | 4
[6 empty] | 1.505 | 0.188 | 0.377 | 0.573 | 0.777 | 0.985 | 1.194 | 1.4 | 1.598 | 1.784 | 2.2
[6 empty] | 1.506 | 0.123 | 0.239 | 0.355 | 0.472 | 0.59 | 0.71 | 0.828 | 0.946 | 1.063 | 1.2
[6 empty] | 2 | 4.13 | 9.242 | 14.478 | 19.708 | 25.087 | 30.564 | 35.974 | 40.012 | 44.642 | 49
[6 empty] | 2.01 | 2.274 | 4.969 | 7.877 | 10.938 | 13.724 | 16.509 | 19.277 | 22.026 | 24.965 | 28
[6 empty] | 2.02 | 1.264 | 2.764 | 4.372 | 6.054 | 7.773 | 9.527 | 11.227 | 12.727 | 14.317 | 17
[6 empty] | 2.03 | 0.816 | 1.779 | 2.804 | 3.86 | 4.927 | 5.981 | 7.006 | 7.98 | 8.889 | 10
[6 empty] | 3 | 9.958 | 21.061 | 32.395 | 42.652 | 52.98 | 63.698 | 76.666 | 86.071 | 91.149 | 100
[6 empty] | 3.01 | 5.353 | 11.637 | 18.738 | 26.583 | 33.661 | 40.457 | 47.179 | 53.741 | 60.338 | 70
[6 empty] | 3.02 | 3.465 | 7.212 | 11.2 | 15.378 | 19.686 | 24.058 | 28.448 | 31.986 | 35.659 | 42
[6 empty] | 3.03 | 2.171 | 4.467 | 6.858 | 9.318 | 11.806 | 14.291 | 16.726 | 19.075 | 21.29 | 25
[6 empty] | 4 | 12.667 | 27.122 | 47.273 | 66.038 | 85.993 | 106.882 | 127.853 | 147.47 | 167.929 | 190
[6 empty] | 4.01 | 7.319 | 15.766 | 25.332 | 36.426 | 51.054 | 63.296 | 75.776 | 88.317 | 103.943 | 120
[6 empty] | 4.02 | 7.018 | 13.838 | 20.643 | 27.411 | 34.071 | 43.442 | 50.854 | 57.09 | 63.09 | 72
[6 empty] | 4.03 | 4.032 | 8.164 | 12.452 | 16.817 | 21.179 | 25.44 | 29.513 | 33.306 | 37.671 | 42
[6 empty] | 6 | 28.431 | 57.146 | 86.052 | 112.257 | 136.072 | 159.161 | 181.587 | 212.574 | 263.118 | 295
[6 empty] | 6.01 | 16.09 | 32.01 | 47.67 | 63.09 | 78.18 | 93.11 | 105.76 | 117.42 | 137.91 | 165
[6 empty] | 6.02 | 8.775 | 17.429 | 25.904 | 34.147 | 42.126 | 49.781 | 57.066 | 63.938 | 71.485 | 85
[6 empty] | 6.03 | 4.321 | 9.065 | 14.143 | 19.449 | 24.875 | 30.315 | 35.638 | 40.718 | 45.424 | 50
|  |  |  | ECCENTRIC ROTARY PLUG |  |  | GP_LIN 10: TABLE NAME:; GP_LIN 20: ROT_PLUG; Valve Travel, % 50: Valve Travel, %
[8 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  |  | Decimal sizes N.01 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  |  | represent "N" inch valve , 1 |  |  | 1 | 1.09 | 2.01 | 2.97 | 3.86 | 4.97 | 6.19 | 8.04 | 10.1 | 12.4 | 14.5
|  |  |  | size reduced. |  |  | 1.01 | 0.74 | 1.65 | 2.13 | 2.66 | 3.18 | 3.72 | 4.58 | 5.72 | 7.01 | 7.9
[7 empty] | 1.5 | 2.1 | 4.6 | 7.5 | 10.2 | 13.7 | 17.6 | 21.7 | 26 | 29.4 | 31
[7 empty] | 1.51 | 2.1 | 4.6 | 6.2 | 7.4 | 9.4 | 11.4 | 13.5 | 14.8 | 15.2 | 15.5
[7 empty] | 2 | 4.3 | 9 | 14 | 19 | 25 | 31 | 39 | 45 | 50 | 52
[7 empty] | 2.01 | 3.8 | 8 | 10 | 13 | 16 | 19 | 23 | 25 | 25.5 | 26
[7 empty] | 3 | 10 | 20 | 30 | 41 | 52 | 66 | 85 | 103 | 121 | 137
[7 empty] | 3.01 | 10 | 20 | 26 | 32 | 40 | 48 | 57 | 63 | 65 | 66
[7 empty] | 4 | 17 | 35 | 50 | 70 | 89 | 113 | 145 | 176 | 206 | 239
[7 empty] | 4.01 | 17 | 35 | 48 | 58 | 73 | 88 | 104 | 114 | 117 | 120
[7 empty] | 6 | 49 | 103 | 160 | 216 | 272 | 328 | 380 | 434 | 485 | 520
[7 empty] | 6.01 | 37 | 75 | 104 | 125 | 158 | 191 | 226 | 247 | 254 | 260
[7 empty] | 8 | 75 | 151 | 220 | 301 | 388 | 499 | 603 | 719 | 823 | 870
[7 empty] | 8.01 | 58 | 128 | 175 | 211 | 267 | 323 | 383 | 419 | 431 | 440
[7 empty] | 10 | 115 | 231 | 336 | 460 | 593 | 763 | 922 | 1099 | 1258 | 1330
[7 empty] | 10.01 | 85 | 188 | 271 | 326 | 412 | 500 | 592 | 647 | 666 | 680

## Wall Thck.
NO USER INPUT IS REQUIRED FOR THIS TAB.
PIPE WALL THICKNESS
Note: this data is believed to be accurate, but it is the user's responsibility to determine its applicability to their purpose.
| NPS | Outside Diameter | Schedule
| (in) | (in) (mm) | 10 | 20 | 30 | STD | 40 | 60 | XS | 80 | 100 | 120 | 140 | 160 | XXS
Wall Thickness (in) (mm)
| 1/8 | 0.405 |  |  |  | 0.068 | 0.068 |  | 0.095 | 0.095
|  | 10.3 |  |  |  | 1.73 | 1.73 |  | 2.41 | 2.41
| 1/4 | 0.54 |  |  |  | 0.088 | 0.088 |  | 0.119 | 0.119
|  | 13.7 |  |  |  | 2.24 | 2.24 |  | 3.02 | 3.02
| 3/8 | 0.675 |  |  |  | 0.091 | 0.091 |  | 0.126 | 0.126
|  | 17.1 |  |  |  | 2.31 | 2.31 |  | 3.2 | 3.2
| 1/2 | 0.84 |  |  |  | 0.109 | 0.109 |  | 0.147 | 0.147 |  |  |  | 0.187 | 0.294
|  | 21.3 |  |  |  | 2.77 | 2.77 |  | 3.73 | 3.73 |  |  |  | 4.75 | 7.47
| 3/4 | 1.05 |  |  |  | 0.113 | 0.113 |  | 0.154 | 0.154 |  |  |  | 0.219 | 0.308
|  | 26.7 |  |  |  | 2.87 | 2.87 |  | 3.91 | 3.91 |  |  |  | 5.56 | 7.82
| 1 | 1.315 |  |  |  | 0.133 | 0.133 |  | 0.179 | 0.179 |  |  |  | 0.25 | 0.358
|  | 33.4 |  |  |  | 3.38 | 3.38 |  | 4.55 | 4.55 |  |  |  | 6.35 | 9.09
| 1.25 | 1.66 |  |  |  | 0.14 | 0.14 |  | 0.191 | 0.191 |  |  |  | 0.25 | 0.382
|  | 42.2 |  |  |  | 3.56 | 3.56 |  | 4.85 | 4.85 |  |  |  | 6.35 | 9.7
| 1.5 | 1.9 |  |  |  | 0.145 | 0.145 |  | 0.2 | 0.2 |  |  |  | 0.281 | 0.4
|  | 48.3 |  |  |  | 3.68 | 3.68 |  | 5.08 | 5.08 |  |  |  | 7.14 | 10.2
| 2 | 2.375 |  |  |  | 0.154 | 0.154 |  | 0.218 | 0.218 |  |  |  | 0.344 | 0.436
|  | 60.3 |  |  |  | 3.91 | 3.91 |  | 5.54 | 5.54 |  |  |  | 8.74 | 11.1
| 2.5 | 2.875 |  |  |  | 0.203 | 0.203 |  | 0.276 | 0.276 |  |  |  | 0.375 | 0.552
|  | 73 |  |  |  | 5.16 | 5.16 |  | 7.01 | 7.01 |  |  |  | 9.52 | 14
| 3 | 3.5 |  |  |  | 0.216 | 0.216 |  | 0.3 | 0.3 |  |  |  | 0.438 | 0.6
|  | 88.9 |  |  |  | 5.49 | 5.49 |  | 7.62 | 7.62 |  |  |  | 11.1 | 15.2
| 3.5 | 4 |  |  |  | 0.226 | 0.226 |  | 0.318 | 0.318
|  | 102 |  |  |  | 5.74 | 5.74 |  | 8.08 | 8.08
| 4 | 4.5 |  |  |  | 0.237 | 0.237 |  | 0.337 | 0.337 |  | 0.438 |  | 0.531 | 0.674
|  | 114 |  |  |  | 6.02 | 6.02 |  | 8.56 | 8.56 |  | 11.1 |  | 13.5 | 17.1
| 5 | 5.563 |  |  |  | 0.258 | 0.258 |  | 0.375 | 0.375 |  | 0.5 |  | 0.625 | 0.75
|  | 141 |  |  |  | 6.55 | 6.55 |  | 9.52 | 9.52 |  | 12.7 |  | 15.9 | 19
| 6 | 6.625 |  |  |  | 0.28 | 0.28 |  | 0.432 | 0.432 |  | 0.562 |  | 0.719 | 0.864
|  | 168 |  |  |  | 7.11 | 7.11 |  | 11 | 11 |  | 14.3 |  | 18.3 | 21.9
| 8 | 8.625 |  | 0.25 | 0.277 | 0.322 | 0.322 | 0.406 | 0.5 | 0.5 | 0.594 | 0.719 | 0.812 | 0.906 | 0.875
|  | 219 |  | 6.35 | 7.04 | 8.18 | 8.18 | 10.3 | 12.7 | 12.7 | 15.1 | 18.3 | 20.6 | 23 | 22.2
| 10 | 10.75 |  | 0.25 | 0.307 | 0.365 | 0.365 | 0.5 | 0.5 | 0.594 | 0.719 | 0.844 | 1 | 1.125 | 1
|  | 273 |  | 6.35 | 7.8 | 9.27 | 9.27 | 12.7 | 12.7 | 15.1 | 18.3 | 21.4 | 25.4 | 28.6 | 25.4
| 12 | 12.75 |  | 0.25 | 0.33 | 0.375 | 0.406 | 0.562 | 0.5 | 0.688 | 0.844 | 1 | 1.125 | 1.312 | 1
|  | 324 |  | 6.35 | 8.38 | 9.52 | 10.3 | 14.3 | 12.7 | 17.5 | 21.4 | 25.4 | 28.6 | 33.3 | 25.4
| 14 | 14 | 0.25 | 0.312 | 0.375 | 0.375 | 0.438 | 0.594 | 0.5 | 0.75 | 0.938 | 1.094 | 1.25 | 1.406
|  | 356 | 6.35 | 7.92 | 9.52 | 9.52 | 11.1 | 15.1 | 12.7 | 19 | 23.8 | 27.8 | 31.8 | 35.7
| 16 | 16 | 0.25 | 0.312 | 0.375 | 0.375 | 0.5 | 0.656 | 0.5 | 0.844 | 1.031 | 1.219 | 1.438 | 1.594
|  | 406 | 6.35 | 7.92 | 9.52 | 9.52 | 12.7 | 16.7 | 12.7 | 21.4 | 26.2 | 31 | 36.5 | 40.5
| 18 | 18 | 0.25 | 0.312 | 0.438 | 0.375 | 0.562 | 0.75 | 0.5 | 0.938 | 1.156 | 1.375 | 1.562 | 1.781
|  | 457 | 6.35 | 7.92 | 11.1 | 9.52 | 14.3 | 19 | 12.7 | 23.8 | 29.4 | 34.9 | 39.7 | 45.2
| 20 | 20 | 0.25 | 0.375 | 0.5 | 0.375 | 0.594 | 0.812 | 0.5 | 1.031 | 1.281 | 1.5 | 1.75 | 1.969
|  | 508 | 6.35 | 9.52 | 12.7 | 9.52 | 15.1 | 20.6 | 12.7 | 26.2 | 32.5 | 38.1 | 44.4 | 50
| 22 | 22 | 0.25 | 0.375 | 0.5 | 0.375 |  | 0.875 | 0.5 | 1.125 | 1.375 | 1.625 | 1.875 | 2.125
|  | 559 | 6.35 | 9.52 | 12.7 | 9.52 |  | 22.2 | 12.7 | 28.6 | 34.9 | 41.3 | 47.6 | 54
| 24 | 24 | 0.25 | 0.375 | 0.562 | 0.375 | 0.688 | 0.969 | 0.5 | 1.219 | 1.531 | 1.812 | 2.062 | 2.344
|  | 610 | 6.35 | 9.52 | 14.3 | 9.52 | 17.5 | 24.6 | 12.7 | 31 | 38.9 | 46 | 52.4 | 59.5
| 30 | 30 | 0.312 | 0.5 | 0.625 | 0.375 |  |  | 0.5
|  | 762 | 7.92 | 12.7 | 15.9 | 9.52 |  |  | 12.7
| 32 | 32 | 0.312 | 0.5 | 0.625 | 0.375 | 0.688
|  | 813 | 7.92 | 12.7 | 15.9 | 9.52 | 17.5
| 34 | 34 | 0.312 | 0.5 | 0.625 | 0.375 | 0.688
|  | 864 | 7.92 | 12.7 | 15.9 | 9.52 | 17.5
| 36 | 36 | 0.312 | 0.5 | 0.625 | 0.375 | 0.75
|  | 914 | 7.92 | 12.7 | 15.9 | 9.52 | 19
| 42 | 42 |  | 0.5 | 0.625 | 0.375 | 0.75
|  | 1067 |  | 12.7 | 15.9 | 9.52 | 19