## Valve Sizing
Unit selection: | 1 | 1 = US; 2 = SI (Cv, bar); 3 = SI (Cv, kPa); 4 = SI (Kv, bar); 5 = SI (Kv, kPa) | [6 empty] | Scroll to the right to view the intermediate calculations | Valve sizing per ISA S75.01.01 2007
CONTROL VALVE SIZING: STEAM or VAPOR - Mass flow |  |  | TAG: | PV123 | [5 empty] | DESCRIPTION OF VARIABLE | Eq | NAME OF VARIABLE | FORMULA
[7 empty] | Valve type | Valve style SPL code |  | CALCULATED IN COLUMN "S" |  | CALCULATED IN COLUMN "S"
Flow | lbm/h | W | 1145 | 2060 | 4960 | 7174 | Globe | 0 |  | Pressure drop ratio | 9 | x | 0.5 | 0.54586 | 0.47658 | 0.375
Inlet pressure | psiA | P_1 | 100 | 89.4 | 85.4 | 80 | Rotary eccentric plug | 1 |  | Ratio of specific heats factor | 11 | F_GAMMA | 1 | 1 | 1 | 1
Inlet temperature | F | T_1 | 100 | 100 | 100 | 100 | Segment ball | 2 |  | Absolute temperature |  | T_abs | 559.67 | 559.67 | 559.67 | 559.67
Pressure drop | psi | DELTA_P | 50 | 48.8 | 40.7 | 30 | Butterfly | 3
Density | lbm/ft^3 | RHO | 0.48238 | 0.43125 | 0.41195 | 0.38591 | Full ball | 4 |  | WITHOUT REDUCERS
Molecular mass* |  | M | 28.97 | ======> | ======> | ======> | Milti-stage globe | 5 |  | Expansion factor | 12 | Y | 0.73958 | 0.71118 | 0.73523 | 0.76415
Specific heat ratio |  | GAMMA | 1.4 | ======> | ======> | ======> |  |  |  | C Non choked | 5 | C_NonCh | 4.9801 | 9.9749 | 26.0274 | 43.589
Choked press drop ratio factor |  | x_T | 0.64 | 0.63 | 0.6 | 0.53 |  |  |  | C Choked | 5 | C_Ch | 4.8808 | 9.9 | 25.5695 | 42.0057
Inlet pipe diameter | inch | D_1 | 4 | ======> | ======> | ======> |  |  |  | Choked pressure drop ratio | 10 | CH_x | 0.64 | 0.63 | 0.6 | 0.53
Outlet pipe diameter | inch | D_2 | 4 | ======> | ======> | ======> |  |  |  | Select C Non choked or C choked |  | Select_C_Non_or_C_Ch | 4.9801 | 9.9749 | 26.0274 | 43.589
Valve size | inch | d | 2 | ======> | ======> | ======> |  |  |  | (This is the initial guess for
Valve style SPL code |  | VSC | 2 | ======> | ======> | ======> |  |  |  | the following iterative calculations)
Pipe wall correction | dB(A) | DeltaLp | -2 | ======> | ======> | ======>
Required flow coef. (Cv or Kv) | Cv | C_ | 4.9833 | 9.9998 | 26.4755 | 45.7136 |  |  |  | WITH REDUCERS
Flow calculated from C_ above | lbm/h |  | 1145 | 2060 | 4960 | 7174 |  |  |  | Reducer velocity head coefficients | 18 | ZETA_1 | 0.28125 | ======> | ======> | ======>
Outlet velocity | Mach |  | 0.052078 | 0.11539 | 0.25234 | 0.32629 |  |  |  |  | 17 | ZETA_B1 | 0.9375 | ======> | ======> | ======>
Sound pressure level | dB(A) |  | 78.9272 | 83.143 | 87.3935 | 87.5625 |  |  |  |  | 19 | ZETA_2 | 0.5625 | ======> | ======> | ======>
Selected valve style (VSC) |  |  | Segment ball | [7 empty] | 17 | ZETA_B2 | 0.9375 | ======> | ======> | ======>
[6 empty] | Data input |  |  |  | Sum of velocity head coefficients | 16 | SIGMA_ZETA | 0.84375 | ======> | ======> | ======>
[6 empty] | Final results |  |  |  | Sum of upstream velocity head coef |  | SIGMA_ZETA_1 | 1.2188 | ======> | ======> | ======>
*The Molecular mass entry is only used in the
noise calculation and the Mach number calculation. | [9 empty] | Beginning of iterative calculation
This worksheeet is distributed at no cost on an as-is basis. | [9 empty] | Assumed C for iterative purposes |  | C_i | 4.9801 | 9.9749 | 26.0274 | 43.589
The author assumes no liability for its use. | [9 empty] | Piping geometry factor | 15 | F_P | 0.99927 | 0.99707 | 0.98052 | 0.94806
[10 empty] | Choked Pres drop ratio factor with reducers | 22 | x_TP | 0.64017 | 0.6307 | 0.60534 | 0.54766
[10 empty] | Expansion factor | 12 | Y_W_Reducers | 0.73965 | 0.71151 | 0.73757 | 0.77176
[10 empty] | C Non choked w/ reducers | 5 | C_NonCh_W_Reducers | 4.9833 | 9.9997 | 26.4606 | 45.5242
[10 empty] | C Choked w/ reducers | 5 | C_Ch_W_Reducers | 4.8837 | 9.9236 | 25.9624 | 43.587
[10 empty] | Choked pressure drop ratio w/ reducers | 10 | CH_x_W_Reducers | 0.64017 | 0.6307 | 0.60534 | 0.54766
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9997 | 26.4606 | 45.5242
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9997 | 26.4606 | 45.5242
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97988 | 0.94373
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54914
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73764 | 0.77237
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.475 | 45.6963
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9754 | 43.7277
| The cells below (Row 47) detrmine if any input data is missing. | [8 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54914
| If it is, error messages are blanked out of the calculated results. | [8 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.475 | 45.6963
| DATA1 | DATA2 | DATA3 | DATA4
| -458778693430.6362 | -633797329035.9066 | -1.1061e+12 | -914084291913.9741 | [5 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.475 | 45.6963
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.94334
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54927
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
These Numerical constants are set by the units choises set by the user above the user interface | [9 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.712
which incllude all the options for the ISA Standard | [9 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7404
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54927
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.712
Numerical constants
N_2 * | 890 | [8 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.712
N_5 | 1000 | [8 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.94331
N_6 * | 63.3 | [8 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
FLAG_A ** | 1 | 1= Inlet Temp entered in F is converted to R in T_abs field | [7 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7134
|  | 2= Inlet Temp entered in C is coverted to K in T_abs field | [7 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7416
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7134
FLAG_1 *** | 1 | 1=flow coef is Cv 2=flow coef is Kv
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7134
FLAG_2 *** | 1 | 1=psiA, deg R, 2=bar, deg K, 3=kPa, deg K | [7 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
FLAG_1 and FLAG_2 only have an effect in the noise calculation | [9 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
NOTE: The constants in B53, 54, 55, 57, 61, 63 and 64 are set by formulas in those cells and are based on the unit selection made in Cell B1. | [9 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7135
* Using anything other than the exact numeric values in Table 1 of ISA S75.01.01 or Table 1 of the author's instructions may result in a logic error in the Mach number calc. | [9 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
** Using anything other than the exact numeric values for FLAG_A may result in a logic error in the valve capacity (C) calc. | [9 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
*** Using anything other than the exact numeric values for FLAG_1 or FLAG_2 may result in a logic error in the noise calculation. | [9 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7135
**** When the unit selection in B1 is set to 1 (US units), if cell B55 reads "7320" the Standard condition reference temperature is 15C (59F).
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7135
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Assumed C for iterative purposes |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 |  | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 |  | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | C Non choked w/ reducers | 5 |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | C Choked w/ reducers | 5 |  | 4.8837 | 9.9237 | 25.9759 | 43.7417
[10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select C Non choked or C choked |  |  | 4.9833 | 9.9998 | 26.4755 | 45.7136
Confirmation that the calculated C will produce the given flow rate
[10 empty] | Final C calculated above |  | Final_Calculated_C | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Piping geometry factor | 15 | Final_F_P | 0.99927 | 0.99705 | 0.97986 | 0.9433
[10 empty] | Presssure drop ratio factor w/reducers | 22 | Final_x_TP | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Expansion factor | 12 | Final_Y_W_Reducers | 0.73965 | 0.71151 | 0.73765 | 0.77243
[10 empty] | Flow Non choked w/ reducers | 7 | Final_Flow_NonCh_W_Reducers | 1145 | 2060 | 4960 | 7174
[10 empty] | Flow Choked w/ reducers | 7 | Final_Flow_Ch_W_Reducers | 1168.3311 | 2075.8011 | 5055.3977 | 7497.3965
[10 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 | Final_CH_x_W_Reducers | 0.64017 | 0.63071 | 0.60552 | 0.54928
[10 empty] | Select flow Non choked or flow choked |  | Calc_Flow_From_Final_ Calc_C | 1145 | 2060 | 4960 | 7174
Aerodynamic noise calculation based on VDMA 24422 - 1979 as presented in the Metso "Flow Control Manual"
[10 empty] | Valve flow capacity in Cv units |  | C_v | 4.9833 | 9.9998 | 26.4755 | 45.7136
[10 empty] | Upstream pressure, P1, in units of psiA |  | P_1_psia | 100 | 89.4 | 85.4 | 80
[10 empty] | Upstream temperature in units of degrees R |  | T_1_degR | 559.67 | 559.67 | 559.67 | 559.67
[10 empty] | Gas density in units lb/ft^3 at std cond (14.7 psiA, 60 F) |  | RHO_n | 0.076423 | ======> | ======> | ======>
VALVE SPECIFIC CORRECTION COEFFICIENT
[10 empty] | For globe valves |  | DeltaLg_0 | 0 | 0 | 0 | 0
[10 empty] | For eccentric rotary plug valves |  | DeltaLg_1 | -1 | -1 | -1 | -1
[10 empty] | For segment ball valves |  | DeltaLg_2 | 3.4663 | 3.1943 | 3.6052 | 3.745
[10 empty] | For butterfly valves |  | DeltaLg_3 | 2 | 2 | 2 | 2
[10 empty] | For ball valves |  | DeltaLg_4 | 2 | 2 | 2 | 2
[10 empty] | For multi-stage globe valves |  | DeltaLg_5 | -15 | -15 | -15 | -15
[10 empty] | For selected valve based on VSC (Valve Style Code) |  | DeltaLg | 3.4663 | 3.1943 | 3.6052 | 3.745
[10 empty] | P_2 in psiA |  | P_2_psia | 50 | 40.6 | 44.7 | 50
[10 empty] | High downstream pressure correction |  | DeltaLp2 | 0 | 0 | 0 | 0
[10 empty] | Calculated Sound Pressure Level (dBA) |  | L_A | 78.9272 | 83.143 | 87.3935 | 87.5625
Valve outlet Mach Number calculation
[10 empty] | Valve nominal size in inches |  | d_in | 2 | ======> | ======> | ======>
[10 empty] | Mass flow converted to lbm/h |  | W_to_lbm_h | 1145 | 2060 | 4960 | 7174
[10 empty] | Density in units of lb/ft^3 |  | RHO_lb_ft3 | 0.48238 | 0.43125 | 0.41195 | 0.38591
[10 empty] | Mass flow in lbm/h converted to scfh |  | lbm_h_to_scfh | 14988.1742 | 26965.6235 | 64926.9382 | 93908.4385
[10 empty] | Valve outlet velocity (Mach Number) |  | MN | 0.052078 | 0.11539 | 0.25234 | 0.32629

## Installed Flow
[13 empty] | Intermediate Calculations |  |  |  | 22.29
VALVE DATA | ` | [10 empty] | Scroll to the right to see the | DESCRIPTION OF VARIABLE | Eqn. | NAME OF VARIABLE | FORMULA
Valve style / model # | Neles RE Seg Ball | [10 empty] | intermediate calculations | CALCULATED IN COLUMN "P" |  | CALCULATED IN COLUMN "P"
Valve size | 2 inch
Relative travel, h | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 |  |  | CALCULATE PARAMETERS FOR UPSTREAM AND DOWNSTREAM PROCESS PRESSURE MODEL
C (Cv or Kv) | 2 | 5 | 10 | 17.2 | 26.6 | 38.4 | 52.5 | 72.4 | 108 | 180 |  |  | Minimum design flow (From Col D) |  | W_min | 1145
xT | 0.64 | 0.64 | 0.63 | 0.62 | 0.6 | 0.56 | 0.51 | 0.44 | 0.35 | 0.2 |  |  | Maximum design flow (From Col F) |  | W_max | 7174
[13 empty] | Valve inlet pressure at minimum des. Flow |  | P_1_minW | 100
| 2 inch 0.7: Neles RE Seg Ball |  | Scroll down for instructions for the Installed flow and gain graphs and | Valve inlet pressure at maximum des. flow |  | P_1_maxW | 80
| 2 inch 0.7: 2 inch |  | the calculation of the fully open flow, Qf. The accuracy of the calculations | Pressure drop at minimum des. flow |  | DELTA_P_minW | 50
| 2 inch 0.7: PV123 |  | on this and the Installed Gain tab depend on the accuracy of the process | Pressure drop at maximum des. flow |  | DELTA_P_maxW | 30
[12 empty] | data. | Valve outlet pressure at minimum des. Flow |  | P_2_minW | 50
[13 empty] | Valve outlet pressure at maximum des. flow |  | P_2_maxW | 50
[13 empty] | Upstream system drop |  | dp_up | 20
| 2 inch 0.7: Fully open Flow, Wf |  | INSTALED FLOW AND GAIN ERRORS | Upstream system resistance factor |  | R_up | 3.9876e-07
| 2 inch 0.7: Wf =; 2 inch 0.8: 9954.5293 |  | If there are any error messages below, the graphs and Wf are not valid | Downstream system drop |  | dp_dn | 0
[13 empty] | Downstream system resistance factor |  | R_dn | 0 | Relative Travel, h | 0.1 |  |  | 0.2 |  |  | 0.3 |  |  | 0.4 |  |  | 0.5 |  |  | 0.6 |  |  | 0.7 |  |  | 0.8 |  |  | 0.9 |  |  | 1
[13 empty] | Upstream system press drop an min flow |  | dpup_minQ | 0.52279 | Min C_h - Ci | 0.010675 |  |  | 0.00046375 |  |  | 0.018851 |  |  | 0.08093 |  |  | 0.1194 |  |  | 0.0077711 |  |  | 0.4147 |  |  | 0.36321 |  |  | 0.35313 |  |  | 3.5647
[13 empty] | Downstream system press drop an min flow |  | dpdn_minQ | 0 | Flow at C_h | 464.5555 |  |  | 1148.901 |  |  | 2237.766 |  |  | 3680.3011 |  |  | 5161.9056 |  |  | 6554.2504 |  |  | 7685.3741 |  |  | 8574.3286 |  |  | 9566.107 |  |  | 9954.5293
| 2 inch 0.7: Wmax = maximum | [6 empty] | Values found on Line | 2663 |  |  | 1319 |  |  | 983 |  |  | 745 |  |  | 521 |  |  | 381 |  |  | 269 |  |  | 199 |  |  | 199 |  |  | 101
[8 empty] | design flow = | 7174
CALCULATE FLOW AT EACH INCREMENT OF h
[13 empty] | Valve C at travel h (Cv or Kv) |  | C_h | 2 |  |  | 5 |  |  | 10 |  |  | 17.2 |  |  | 26.6 |  |  | 38.4 |  |  | 52.5 |  |  | 72.4 |  |  | 108 |  |  | 180
Wmin = minimum
[8 empty] | design flow = | 1145
Caculation of flow conditions
[13 empty] | Piping geometry factor at relative travel, h | 15 | F_P_h | 0.99988 |  |  | 0.99926 |  |  | 0.99705 |  |  | 0.99135 |  |  | 0.97967 |  |  | 0.95898 |  |  | 0.92715 |  |  | 0.87351 |  |  | 0.76898 |  |  | 0.58523
| 2 inch 0.8: Flow units are; 2 inch 0.9: lbm/h |  |  | Reducer corrected pressure drop ratio factor at choked flow | 21 | x_TP_h | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
400 iterations
[13 empty] | First iteration flow rate |  | W_i | 11.45 | Abs Value of | Flow this | 464.5555 | Abs Value of | Flow this | 1148.901 | Abs Value of | Flow this | 2237.766 | Abs Value of | Flow this | 3680.3011 | Abs Value of | Flow this | 5161.9056 | Abs Value of | Flow this | 6554.2504 | Abs Value of | Flow this | 7685.3741 | Abs Value of | Flow this | 8574.3286 | Abs Value of | Flow this | 9566.107 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  | P1_Wi | 100.5227 |  |  | 100.4367 |  |  | 99.9964 |  |  | 98.5259 |  |  | 95.1217 |  |  | 89.8977 |  |  | 83.3927 |  |  | 76.9699 |  |  | 71.2062 |  |  | 64.0319
Valve relative travel, h | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 |  | P2 at this iteration flow rate |  | P2_Wi | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
Relative Flow Q/Qf | 0 | 0.046668 | 0.11541 | 0.2248 | 0.36971 | 0.51855 | 0.65842 | 0.77205 | 0.86135 | 0.96098 | 1 |  | Density at this iteration |  | RHO_Wi | 0.4849 |  |  | 0.48449 |  |  | 0.48236 |  |  | 0.47527 |  |  | 0.45885 |  |  | 0.43365 |  |  | 0.40227 |  |  | 0.37129 |  |  | 0.34349 |  |  | 0.30888
Minimum Flow | 0.11502 | 0.11502 | 0.11502 | 0.11502 | 0.11502 | 0.11502 | 0.11502 | 0.11502 | 0.11502 | 0.11502 | 0.11502 |  | Delta P at this iteration flow rate |  | DELTA_P_Wi | 50.5227 |  |  | 50.4367 |  |  | 49.9964 |  |  | 48.5259 |  |  | 45.1217 |  |  | 39.8977 |  |  | 33.3927 |  |  | 26.9699 |  |  | 21.2062 |  |  | 14.0319
Maximum Flow | 0.72068 | 0.72068 | 0.72068 | 0.72068 | 0.72068 | 0.72068 | 0.72068 | 0.72068 | 0.72068 | 0.72068 | 0.72068 |  | Press drop ratio this iteration |  | x_Wi | 0.5026 |  |  | 0.50217 |  |  | 0.49998 |  |  | 0.49252 |  |  | 0.47436 |  |  | 0.44381 |  |  | 0.40043 |  |  | 0.3504 |  |  | 0.29781 |  |  | 0.21914
[13 empty] | Expansion factor | 12 | Y_C_h | 0.73824 |  |  | 0.73852 |  |  | 0.73576 |  |  | 0.73613 |  |  | 0.73889 |  |  | 0.74177 |  |  | 0.75094 |  |  | 0.76187 |  |  | 0.83274 |  |  | 0.81317
[13 empty] | C Non choked w/ reducers | 5 | C_N_Ch | 0.049509 |  |  | 2.0118 |  |  | 5.0381 |  |  | 10.0872 |  |  | 17.6518 |  |  | 27.5601 |  |  | 40.577 |  |  | 57.6521 |  |  | 78.3765 |  |  | 152.5364
INSTRUCTIONS FOR THE OPTIONAL INSTALLED FLOW AND GAIN GRAPHS AND FULLY OPEN FLOW CALCULATION The process pressure model is a curve fit based on the Flow, P1 and Delta P in Columns D and G on the Valve Sizing tab. The curve fit is based on the principle that piping pressure losses are approximately proportional to flow squared. The Density used in the installed flow calculation is the value entered in Column G on the Valve Sizing tab adjusted for pressure as determined by the process pressue model for each increment of valve relative travel. To calculate the fully open flow, Wf, the installed flow and the installed gain, on the Valve Sizing tab, enter the minimum design flow along with its associated values of P1 and Delta P in Column D and the maximum design flow along with its associated values of P1 and Delta P in Column G. The accuracy of these calculations depends on the accuracy of the process data that is used. Any process conditions entered in Columns E and F are not used in the calculation of the fully open flow, the installed flow and the installed gain. The process model, Wf, and the graphs are only valid if: 1. The flow in G2 on the Valve Sizing tab is greater than the flow in D2 2. P1 is either constant or decreasing with increasing flow 3. P2 is either constant or increasing with increasing flow NOTE: Extrapolating curve-fit data beyond the limits for which the curve fit was established can be uncertain. The farther beyond the limits, the greater is the potential for uncertainty. As such, the fully open flow, the Installed Flow and the Installed Gain should be treated as approximations. | [12 empty] | C Choked w/ reducers | 5 | C_Ch | 0.048559 |  |  | 1.9729 |  |  | 4.9481 |  |  | 9.905 |  |  | 17.3067 |  |  | 26.9767 |  |  | 39.4887 |  |  | 55.6592 |  |  | 69.3143 |  |  | 139.2242
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 | CH_x_W_Reducers | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  | C_i | 0.049509 |  |  | 2.0118 |  |  | 5.0381 |  |  | 10.0872 |  |  | 17.6518 |  |  | 27.5601 |  |  | 40.577 |  |  | 57.6521 |  |  | 78.3765 |  |  | 152.5364
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9505 | 11.45 |  | 2.9882 | 464.5555 |  | 4.9619 | 1148.901 |  | 7.1128 | 2237.766 |  | 8.9482 | 3680.3011 |  | 10.8399 | 5161.9056 |  | 11.923 | 6554.2504 |  | 14.7479 | 7685.3741 |  | 29.6235 | 8574.3286 |  | 27.4636 | 9566.107
[13 empty] | Next iteration flow rate |  |  | 11.679 | Abs Value of | Flow this | 469.2011 | Abs Value of | Flow this | 1160.39 | Abs Value of | Flow this | 2260.1436 | Abs Value of | Flow this | 3717.1041 | Abs Value of | Flow this | 5213.5247 | Abs Value of | Flow this | 6619.793 | Abs Value of | Flow this | 7762.2278 | Abs Value of | Flow this | 8660.0719 | Abs Value of | Flow this | 9661.7681 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.435 |  |  | 99.9859 |  |  | 98.4858 |  |  | 95.0131 |  |  | 89.6841 |  |  | 83.0484 |  |  | 76.4965 |  |  | 70.6169 |  |  | 63.2985
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48448 |  |  | 0.48231 |  |  | 0.47508 |  |  | 0.45833 |  |  | 0.43262 |  |  | 0.40061 |  |  | 0.36901 |  |  | 0.34064 |  |  | 0.30534
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.435 |  |  | 49.9859 |  |  | 48.4858 |  |  | 45.0131 |  |  | 39.6841 |  |  | 33.0484 |  |  | 26.4965 |  |  | 20.6169 |  |  | 13.2985
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50217 |  |  | 0.49993 |  |  | 0.49231 |  |  | 0.47376 |  |  | 0.44249 |  |  | 0.39794 |  |  | 0.34638 |  |  | 0.29195 |  |  | 0.21009
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73852 |  |  | 0.73578 |  |  | 0.73624 |  |  | 0.73922 |  |  | 0.74254 |  |  | 0.75248 |  |  | 0.7646 |  |  | 0.83604 |  |  | 0.82088
[13 empty] | C Non choked w/ reducers | 5 |  | 0.050499 |  |  | 2.0319 |  |  | 5.0891 |  |  | 10.1929 |  |  | 17.852 |  |  | 27.9148 |  |  | 41.1962 |  |  | 58.7175 |  |  | 80.3005 |  |  | 157.6717
[13 empty] | C Choked w/ reducers | 5 |  | 0.04953 |  |  | 1.9926 |  |  | 4.9982 |  |  | 10.0082 |  |  | 17.4997 |  |  | 27.3113 |  |  | 40.049 |  |  | 56.5637 |  |  | 70.5916 |  |  | 142.2458
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.050499 |  |  | 2.0319 |  |  | 5.0891 |  |  | 10.1929 |  |  | 17.852 |  |  | 27.9148 |  |  | 41.1962 |  |  | 58.7175 |  |  | 80.3005 |  |  | 157.6717
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9495 | 11.679 |  | 2.9681 | 469.2011 |  | 4.9109 | 1160.39 |  | 7.0071 | 2260.1436 |  | 8.748 | 3717.1041 |  | 10.4852 | 5213.5247 |  | 11.3038 | 6619.793 |  | 13.6825 | 7762.2278 |  | 27.6995 | 8660.0719 |  | 22.3283 | 9661.7681
[13 empty] | Next iteration flow rate |  |  | 11.9126 | Abs Value of | Flow this | 473.8931 | Abs Value of | Flow this | 1171.9939 | Abs Value of | Flow this | 2282.7451 | Abs Value of | Flow this | 3754.2752 | Abs Value of | Flow this | 5265.6599 | Abs Value of | Flow this | 6685.9909 | Abs Value of | Flow this | 7839.8501 | Abs Value of | Flow this | 8746.6726 | Abs Value of | Flow this | 9758.3858 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4332 |  |  | 99.9751 |  |  | 98.4449 |  |  | 94.9024 |  |  | 89.4662 |  |  | 82.6971 |  |  | 76.0136 |  |  | 70.0158 |  |  | 62.5503
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48447 |  |  | 0.48226 |  |  | 0.47488 |  |  | 0.45779 |  |  | 0.43157 |  |  | 0.39892 |  |  | 0.36668 |  |  | 0.33774 |  |  | 0.30173
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4332 |  |  | 49.9751 |  |  | 48.4449 |  |  | 44.9024 |  |  | 39.4662 |  |  | 32.6971 |  |  | 26.0136 |  |  | 20.0158 |  |  | 12.5503
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50216 |  |  | 0.49988 |  |  | 0.4921 |  |  | 0.47314 |  |  | 0.44113 |  |  | 0.39538 |  |  | 0.34222 |  |  | 0.28588 |  |  | 0.20064
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73853 |  |  | 0.73581 |  |  | 0.73635 |  |  | 0.73956 |  |  | 0.74333 |  |  | 0.75407 |  |  | 0.76743 |  |  | 0.83945 |  |  | 0.82894
[13 empty] | C Non choked w/ reducers | 5 |  | 0.051509 |  |  | 2.0523 |  |  | 5.1407 |  |  | 10.2997 |  |  | 18.055 |  |  | 28.2759 |  |  | 41.8313 |  |  | 59.8216 |  |  | 82.3287 |  |  | 163.3016
[13 empty] | C Choked w/ reducers | 5 |  | 0.050521 |  |  | 2.0126 |  |  | 5.0487 |  |  | 10.1124 |  |  | 17.6953 |  |  | 27.6516 |  |  | 40.6213 |  |  | 57.4923 |  |  | 71.9096 |  |  | 145.3868
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.051509 |  |  | 2.0523 |  |  | 5.1407 |  |  | 10.2997 |  |  | 18.055 |  |  | 28.2759 |  |  | 41.8313 |  |  | 59.8216 |  |  | 82.3287 |  |  | 163.3016
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9485 | 11.9126 |  | 2.9477 | 473.8931 |  | 4.8593 | 1171.9939 |  | 6.9003 | 2282.7451 |  | 8.545 | 3754.2752 |  | 10.1241 | 5265.6599 |  | 10.6687 | 6685.9909 |  | 12.5784 | 7839.8501 |  | 25.6713 | 8746.6726 |  | 16.6984 | 9758.3858
[13 empty] | Next iteration flow rate |  |  | 12.1508 | Abs Value of | Flow this | 478.632 | Abs Value of | Flow this | 1183.7139 | Abs Value of | Flow this | 2305.5725 | Abs Value of | Flow this | 3791.8179 | Abs Value of | Flow this | 5318.3165 | Abs Value of | Flow this | 6752.8508 | Abs Value of | Flow this | 7918.2486 | Abs Value of | Flow this | 8834.1394 | Abs Value of | Flow this | 9855.9696 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4314 |  |  | 99.9641 |  |  | 98.4031 |  |  | 94.7894 |  |  | 89.244 |  |  | 82.3389 |  |  | 75.521 |  |  | 69.4026 |  |  | 61.787
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48446 |  |  | 0.48221 |  |  | 0.47468 |  |  | 0.45725 |  |  | 0.4305 |  |  | 0.39719 |  |  | 0.3643 |  |  | 0.33479 |  |  | 0.29805
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4314 |  |  | 49.9641 |  |  | 48.4031 |  |  | 44.7894 |  |  | 39.244 |  |  | 32.3389 |  |  | 25.521 |  |  | 19.4026 |  |  | 11.787
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50215 |  |  | 0.49982 |  |  | 0.49189 |  |  | 0.47252 |  |  | 0.43974 |  |  | 0.39275 |  |  | 0.33793 |  |  | 0.27957 |  |  | 0.19077
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73853 |  |  | 0.73584 |  |  | 0.73647 |  |  | 0.73991 |  |  | 0.74414 |  |  | 0.75571 |  |  | 0.77034 |  |  | 0.84299 |  |  | 0.83736
[13 empty] | C Non choked w/ reducers | 5 |  | 0.052539 |  |  | 2.0729 |  |  | 5.1927 |  |  | 10.4078 |  |  | 18.2609 |  |  | 28.6439 |  |  | 42.4832 |  |  | 60.9672 |  |  | 84.4715 |  |  | 169.5173
[13 empty] | C Choked w/ reducers | 5 |  | 0.051531 |  |  | 2.0327 |  |  | 5.0997 |  |  | 10.2179 |  |  | 17.8936 |  |  | 27.9977 |  |  | 41.206 |  |  | 58.446 |  |  | 73.2704 |  |  | 148.6546
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.052539 |  |  | 2.0729 |  |  | 5.1927 |  |  | 10.4078 |  |  | 18.2609 |  |  | 28.6439 |  |  | 42.4832 |  |  | 60.9672 |  |  | 84.4715 |  |  | 169.5173
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9475 | 12.1508 |  | 2.9271 | 478.632 |  | 4.8073 | 1183.7139 |  | 6.7922 | 2305.5725 |  | 8.3391 | 3791.8179 |  | 9.7561 | 5318.3165 |  | 10.0168 | 6752.8508 |  | 11.4328 | 7918.2486 |  | 23.5285 | 8834.1394 |  | 10.4827 | 9855.9696
[13 empty] | Next iteration flow rate |  |  | 12.3938 | Abs Value of | Flow this | 483.4183 | Abs Value of | Flow this | 1195.551 | Abs Value of | Flow this | 2328.6282 | Abs Value of | Flow this | 3829.7361 | Abs Value of | Flow this | 5371.4997 | Abs Value of | Flow this | 6820.3793 | Abs Value of | Flow this | 7997.4311 | Abs Value of | Flow this | 8922.4807 | Abs Value of | Flow this | 9954.5293 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4296 |  |  | 99.9528 |  |  | 98.3605 |  |  | 94.6742 |  |  | 89.0173 |  |  | 81.9734 |  |  | 75.0184 |  |  | 68.7771 |  |  | 61.0084
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48445 |  |  | 0.48215 |  |  | 0.47447 |  |  | 0.45669 |  |  | 0.4294 |  |  | 0.39542 |  |  | 0.36188 |  |  | 0.33177 |  |  | 0.29429
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4296 |  |  | 49.9528 |  |  | 48.3605 |  |  | 44.6742 |  |  | 39.0173 |  |  | 31.9734 |  |  | 25.0184 |  |  | 18.7771 |  |  | 11.0084
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50214 |  |  | 0.49976 |  |  | 0.49167 |  |  | 0.47187 |  |  | 0.43831 |  |  | 0.39005 |  |  | 0.3335 |  |  | 0.27301 |  |  | 0.18044
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73854 |  |  | 0.73587 |  |  | 0.73659 |  |  | 0.74026 |  |  | 0.74497 |  |  | 0.75739 |  |  | 0.77336 |  |  | 0.84667 |  |  | 0.84616
[13 empty] | C Non choked w/ reducers | 5 |  | 0.05359 |  |  | 2.0936 |  |  | 5.2453 |  |  | 10.5171 |  |  | 18.4697 |  |  | 29.0188 |  |  | 43.1525 |  |  | 62.157 |  |  | 86.7404 |  |  | 176.4353
[13 empty] | C Choked w/ reducers | 5 |  | 0.052562 |  |  | 2.0531 |  |  | 5.1513 |  |  | 10.3246 |  |  | 18.0945 |  |  | 28.3497 |  |  | 41.8036 |  |  | 59.4259 |  |  | 74.6762 |  |  | 152.0572
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.05359 |  |  | 2.0936 |  |  | 5.2453 |  |  | 10.5171 |  |  | 18.4697 |  |  | 29.0188 |  |  | 43.1525 |  |  | 62.157 |  |  | 86.7404 |  |  | 176.4353
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9464 | 12.3938 |  | 2.9064 | 483.4183 |  | 4.7547 | 1195.551 |  | 6.6829 | 2328.6282 |  | 8.1303 | 3829.7361 |  | 9.3812 | 5371.4997 |  | 9.3475 | 6820.3793 |  | 10.243 | 7997.4311 |  | 21.2596 | 8922.4807 |  | 3.5647 | 9954.5293
[13 empty] | Next iteration flow rate |  |  | 12.6417 | Abs Value of | Flow this | 488.2525 | Abs Value of | Flow this | 1207.5065 | Abs Value of | Flow this | 2351.9145 | Abs Value of | Flow this | 3868.0335 | Abs Value of | Flow this | 5425.2147 | Abs Value of | Flow this | 6888.5831 | Abs Value of | Flow this | 8077.4054 | Abs Value of | Flow this | 9011.7056 | Abs Value of | Flow this | 10054.0746 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4277 |  |  | 99.9414 |  |  | 98.317 |  |  | 94.5566 |  |  | 88.786 |  |  | 81.6005 |  |  | 74.5058 |  |  | 68.139 |  |  | 60.2142
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48445 |  |  | 0.4821 |  |  | 0.47426 |  |  | 0.45612 |  |  | 0.42829 |  |  | 0.39363 |  |  | 0.3594 |  |  | 0.32869 |  |  | 0.29046
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4277 |  |  | 49.9414 |  |  | 48.317 |  |  | 44.5566 |  |  | 38.786 |  |  | 31.6005 |  |  | 24.5058 |  |  | 18.139 |  |  | 10.2142
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50213 |  |  | 0.49971 |  |  | 0.49144 |  |  | 0.47122 |  |  | 0.43685 |  |  | 0.38726 |  |  | 0.32891 |  |  | 0.26621 |  |  | 0.16963
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73854 |  |  | 0.7359 |  |  | 0.73671 |  |  | 0.74062 |  |  | 0.74582 |  |  | 0.75913 |  |  | 0.77647 |  |  | 0.8505 |  |  | 0.85538
[13 empty] | C Non choked w/ reducers | 5 |  | 0.054662 |  |  | 2.1146 |  |  | 5.2985 |  |  | 10.6276 |  |  | 18.6814 |  |  | 29.4009 |  |  | 43.8401 |  |  | 63.3942 |  |  | 89.1493 |  |  | 184.2079
[13 empty] | C Choked w/ reducers | 5 |  | 0.053613 |  |  | 2.0737 |  |  | 5.2034 |  |  | 10.4324 |  |  | 18.2982 |  |  | 28.7077 |  |  | 42.4146 |  |  | 60.4331 |  |  | 76.1292 |  |  | 155.6035
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.054662 |  |  | 2.1146 |  |  | 5.2985 |  |  | 10.6276 |  |  | 18.6814 |  |  | 29.4009 |  |  | 43.8401 |  |  | 63.3942 |  |  | 89.1493 |  |  | 184.2079
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9453 | 12.6417 |  | 2.8854 | 488.2525 |  | 4.7015 | 1207.5065 |  | 6.5724 | 2351.9145 |  | 7.9186 | 3868.0335 |  | 8.9991 | 5425.2147 |  | 8.6599 | 6888.5831 |  | 9.0058 | 8077.4054 |  | 18.8507 | 9011.7056 |  | 4.2079 | 10054.0746
[13 empty] | Next iteration flow rate |  |  | 12.8946 | Abs Value of | Flow this | 493.135 | Abs Value of | Flow this | 1219.5816 | Abs Value of | Flow this | 2375.4337 | Abs Value of | Flow this | 3906.7138 | Abs Value of | Flow this | 5479.4669 | Abs Value of | Flow this | 6957.4689 | Abs Value of | Flow this | 8158.1795 | Abs Value of | Flow this | 9101.8226 | Abs Value of | Flow this | 10154.6154 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4258 |  |  | 99.9297 |  |  | 98.2727 |  |  | 94.4367 |  |  | 88.5501 |  |  | 81.2202 |  |  | 73.9828 |  |  | 67.4881 |  |  | 59.404
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48444 |  |  | 0.48204 |  |  | 0.47405 |  |  | 0.45555 |  |  | 0.42715 |  |  | 0.39179 |  |  | 0.35688 |  |  | 0.32555 |  |  | 0.28655
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4258 |  |  | 49.9297 |  |  | 48.2727 |  |  | 44.4367 |  |  | 38.5501 |  |  | 31.2202 |  |  | 23.9828 |  |  | 17.4881 |  |  | 9.404
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50212 |  |  | 0.49965 |  |  | 0.49121 |  |  | 0.47054 |  |  | 0.43535 |  |  | 0.38439 |  |  | 0.32417 |  |  | 0.25913 |  |  | 0.15831
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73855 |  |  | 0.73593 |  |  | 0.73683 |  |  | 0.74099 |  |  | 0.7467 |  |  | 0.76091 |  |  | 0.7797 |  |  | 0.85447 |  |  | 0.86503
[13 empty] | C Non choked w/ reducers | 5 |  | 0.055755 |  |  | 2.1358 |  |  | 5.3522 |  |  | 10.7394 |  |  | 18.8963 |  |  | 29.7904 |  |  | 44.5468 |  |  | 64.6822 |  |  | 91.7137 |  |  | 193.0378
[13 empty] | C Choked w/ reducers | 5 |  | 0.054685 |  |  | 2.0944 |  |  | 5.2561 |  |  | 10.5415 |  |  | 18.5046 |  |  | 29.0721 |  |  | 43.0393 |  |  | 61.4689 |  |  | 77.6321 |  |  | 159.303
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.055755 |  |  | 2.1358 |  |  | 5.3522 |  |  | 10.7394 |  |  | 18.8963 |  |  | 29.7904 |  |  | 44.5468 |  |  | 64.6822 |  |  | 91.7137 |  |  | 193.0378
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9442 | 12.8946 |  | 2.8642 | 493.135 |  | 4.6478 | 1219.5816 |  | 6.4606 | 2375.4337 |  | 7.7037 | 3906.7138 |  | 8.6096 | 5479.4669 |  | 7.9532 | 6957.4689 |  | 7.7178 | 8158.1795 |  | 16.2863 | 9101.8226 |  | 13.0378 | 10154.6154
[13 empty] | Next iteration flow rate |  |  | 13.1525 | Abs Value of | Flow this | 498.0664 | Abs Value of | Flow this | 1231.7774 | Abs Value of | Flow this | 2399.188 | Abs Value of | Flow this | 3945.7809 | Abs Value of | Flow this | 5534.2615 | Abs Value of | Flow this | 7027.0436 | Abs Value of | Flow this | 8239.7613 | Abs Value of | Flow this | 9192.8408 | Abs Value of | Flow this | 10256.1615 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4239 |  |  | 99.9178 |  |  | 98.2275 |  |  | 94.3144 |  |  | 88.3095 |  |  | 80.8322 |  |  | 73.4494 |  |  | 66.8241 |  |  | 58.5775
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48443 |  |  | 0.48199 |  |  | 0.47383 |  |  | 0.45496 |  |  | 0.42599 |  |  | 0.38992 |  |  | 0.35431 |  |  | 0.32235 |  |  | 0.28257
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4239 |  |  | 49.9178 |  |  | 48.2275 |  |  | 44.3144 |  |  | 38.3095 |  |  | 30.8322 |  |  | 23.4494 |  |  | 16.8241 |  |  | 8.5775
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50211 |  |  | 0.49959 |  |  | 0.49098 |  |  | 0.46986 |  |  | 0.43381 |  |  | 0.38143 |  |  | 0.31926 |  |  | 0.25177 |  |  | 0.14643
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73855 |  |  | 0.73596 |  |  | 0.73696 |  |  | 0.74137 |  |  | 0.74759 |  |  | 0.76275 |  |  | 0.78303 |  |  | 0.8586 |  |  | 0.87516
[13 empty] | C Non choked w/ reducers | 5 |  | 0.05687 |  |  | 2.1572 |  |  | 5.4064 |  |  | 10.8526 |  |  | 19.1142 |  |  | 30.1876 |  |  | 45.2737 |  |  | 66.0249 |  |  | 94.4521 |  |  | 203.202
[13 empty] | C Choked w/ reducers | 5 |  | 0.055779 |  |  | 2.1154 |  |  | 5.3093 |  |  | 10.6518 |  |  | 18.7139 |  |  | 29.4428 |  |  | 43.6784 |  |  | 62.5345 |  |  | 79.1876 |  |  | 163.1662
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.05687 |  |  | 2.1572 |  |  | 5.4064 |  |  | 10.8526 |  |  | 19.1142 |  |  | 30.1876 |  |  | 45.2737 |  |  | 66.0249 |  |  | 94.4521 |  |  | 203.202
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9431 | 13.1525 |  | 2.8428 | 498.0664 |  | 4.5936 | 1231.7774 |  | 6.3474 | 2399.188 |  | 7.4858 | 3945.7809 |  | 8.2124 | 5534.2615 |  | 7.2263 | 7027.0436 |  | 6.3751 | 8239.7613 |  | 13.5479 | 9192.8408 |  | 23.202 | 10256.1615
[13 empty] | Next iteration flow rate |  |  | 13.4155 | Abs Value of | Flow this | 503.047 | Abs Value of | Flow this | 1244.0952 | Abs Value of | Flow this | 2423.1799 | Abs Value of | Flow this | 3985.2387 | Abs Value of | Flow this | 5589.6041 | Abs Value of | Flow this | 7097.314 | Abs Value of | Flow this | 8322.1589 | Abs Value of | Flow this | 9284.7692 | Abs Value of | Flow this | 10358.7232 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4219 |  |  | 99.9056 |  |  | 98.1813 |  |  | 94.1896 |  |  | 88.064 |  |  | 80.4364 |  |  | 72.9052 |  |  | 66.1467 |  |  | 57.7344
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48442 |  |  | 0.48193 |  |  | 0.47361 |  |  | 0.45435 |  |  | 0.42481 |  |  | 0.38801 |  |  | 0.35168 |  |  | 0.31908 |  |  | 0.2785
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4219 |  |  | 49.9056 |  |  | 48.1813 |  |  | 44.1896 |  |  | 38.064 |  |  | 30.4364 |  |  | 22.9052 |  |  | 16.1467 |  |  | 7.7344
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.5021 |  |  | 0.49953 |  |  | 0.49074 |  |  | 0.46916 |  |  | 0.43223 |  |  | 0.37839 |  |  | 0.31418 |  |  | 0.2441 |  |  | 0.13397
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73856 |  |  | 0.736 |  |  | 0.73708 |  |  | 0.74176 |  |  | 0.74851 |  |  | 0.76464 |  |  | 0.78649 |  |  | 0.86291 |  |  | 0.88578
[13 empty] | C Non choked w/ reducers | 5 |  | 0.058008 |  |  | 2.1788 |  |  | 5.4613 |  |  | 10.967 |  |  | 19.3353 |  |  | 30.5926 |  |  | 46.0216 |  |  | 67.4267 |  |  | 97.3862 |  |  | 215.0912
[13 empty] | C Choked w/ reducers | 5 |  | 0.056894 |  |  | 2.1366 |  |  | 5.363 |  |  | 10.7634 |  |  | 18.9261 |  |  | 29.8201 |  |  | 44.3322 |  |  | 63.6313 |  |  | 80.7984 |  |  | 167.2044
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.058008 |  |  | 2.1788 |  |  | 5.4613 |  |  | 10.967 |  |  | 19.3353 |  |  | 30.5926 |  |  | 46.0216 |  |  | 67.4267 |  |  | 97.3862 |  |  | 215.0912
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.942 | 13.4155 |  | 2.8212 | 503.047 |  | 4.5387 | 1244.0952 |  | 6.233 | 2423.1799 |  | 7.2647 | 3985.2387 |  | 7.8074 | 5589.6041 |  | 6.4784 | 7097.314 |  | 4.9733 | 8322.1589 |  | 10.6138 | 9284.7692 |  | 35.0912 | 10358.7232
[13 empty] | Next iteration flow rate |  |  | 13.6838 | Abs Value of | Flow this | 508.0775 | Abs Value of | Flow this | 1256.5361 | Abs Value of | Flow this | 2447.4117 | Abs Value of | Flow this | 4025.0911 | Abs Value of | Flow this | 5645.5002 | Abs Value of | Flow this | 7168.2872 | Abs Value of | Flow this | 8405.3805 | Abs Value of | Flow this | 9377.6169 | Abs Value of | Flow this | 10462.3104 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4198 |  |  | 99.8932 |  |  | 98.1343 |  |  | 94.0623 |  |  | 87.8136 |  |  | 80.0327 |  |  | 72.3501 |  |  | 65.4558 |  |  | 56.8743
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48441 |  |  | 0.48187 |  |  | 0.47338 |  |  | 0.45374 |  |  | 0.4236 |  |  | 0.38606 |  |  | 0.349 |  |  | 0.31575 |  |  | 0.27435
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4198 |  |  | 49.8932 |  |  | 48.1343 |  |  | 44.0623 |  |  | 37.8136 |  |  | 30.0327 |  |  | 22.3501 |  |  | 15.4558 |  |  | 6.8743
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50209 |  |  | 0.49947 |  |  | 0.49049 |  |  | 0.46844 |  |  | 0.43061 |  |  | 0.37526 |  |  | 0.30892 |  |  | 0.23613 |  |  | 0.12087
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73856 |  |  | 0.73603 |  |  | 0.73722 |  |  | 0.74215 |  |  | 0.74945 |  |  | 0.76659 |  |  | 0.79006 |  |  | 0.86739 |  |  | 0.89695
[13 empty] | C Non choked w/ reducers | 5 |  | 0.059168 |  |  | 2.2007 |  |  | 5.5166 |  |  | 11.0828 |  |  | 19.5596 |  |  | 31.0058 |  |  | 46.7918 |  |  | 68.8922 |  |  | 100.5417 |  |  | 229.277
[13 empty] | C Choked w/ reducers | 5 |  | 0.058032 |  |  | 2.158 |  |  | 5.4173 |  |  | 10.8762 |  |  | 19.1412 |  |  | 30.2042 |  |  | 45.0014 |  |  | 64.7607 |  |  | 82.4679 |  |  | 171.4302
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.059168 |  |  | 2.2007 |  |  | 5.5166 |  |  | 11.0828 |  |  | 19.5596 |  |  | 31.0058 |  |  | 46.7918 |  |  | 68.8922 |  |  | 100.5417 |  |  | 229.277
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9408 | 13.6838 |  | 2.7993 | 508.0775 |  | 4.4834 | 1256.5361 |  | 6.1172 | 2447.4117 |  | 7.0404 | 4025.0911 |  | 7.3942 | 5645.5002 |  | 5.7082 | 7168.2872 |  | 3.5078 | 8405.3805 |  | 7.4583 | 9377.6169 |  | 49.277 | 10462.3104
[13 empty] | Next iteration flow rate |  |  | 13.9575 | Abs Value of | Flow this | 513.1583 | Abs Value of | Flow this | 1269.1015 | Abs Value of | Flow this | 2471.8858 | Abs Value of | Flow this | 4065.342 | Abs Value of | Flow this | 5701.9552 | Abs Value of | Flow this | 7239.9701 | Abs Value of | Flow this | 8489.4343 | Abs Value of | Flow this | 9471.3931 | Abs Value of | Flow this | 10566.9335 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4178 |  |  | 99.8805 |  |  | 98.0863 |  |  | 93.9324 |  |  | 87.5581 |  |  | 79.6208 |  |  | 71.7838 |  |  | 64.7509 |  |  | 55.997
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.4844 |  |  | 0.48181 |  |  | 0.47315 |  |  | 0.45311 |  |  | 0.42236 |  |  | 0.38408 |  |  | 0.34627 |  |  | 0.31235 |  |  | 0.27012
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4178 |  |  | 49.8805 |  |  | 48.0863 |  |  | 43.9324 |  |  | 37.5581 |  |  | 29.6208 |  |  | 21.7838 |  |  | 14.7509 |  |  | 5.997
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50208 |  |  | 0.4994 |  |  | 0.49024 |  |  | 0.4677 |  |  | 0.42895 |  |  | 0.37202 |  |  | 0.30346 |  |  | 0.22781 |  |  | 0.1071
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73857 |  |  | 0.73606 |  |  | 0.73735 |  |  | 0.74256 |  |  | 0.75042 |  |  | 0.7686 |  |  | 0.79377 |  |  | 0.87206 |  |  | 0.90869
[13 empty] | C Non choked w/ reducers | 5 |  | 0.060351 |  |  | 2.2227 |  |  | 5.5726 |  |  | 11.1999 |  |  | 19.7873 |  |  | 31.4275 |  |  | 47.5852 |  |  | 70.4269 |  |  | 103.9495 |  |  | 246.6362
[13 empty] | C Choked w/ reducers | 5 |  | 0.059193 |  |  | 2.1797 |  |  | 5.4722 |  |  | 10.9904 |  |  | 19.3594 |  |  | 30.5953 |  |  | 45.6865 |  |  | 65.9243 |  |  | 84.1992 |  |  | 175.8572
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.060351 |  |  | 2.2227 |  |  | 5.5726 |  |  | 11.1999 |  |  | 19.7873 |  |  | 31.4275 |  |  | 47.5852 |  |  | 70.4269 |  |  | 103.9495 |  |  | 246.6362
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9396 | 13.9575 |  | 2.7773 | 513.1583 |  | 4.4274 | 1269.1015 |  | 6.0001 | 2471.8858 |  | 6.8127 | 4065.342 |  | 6.9725 | 5701.9552 |  | 4.9148 | 7239.9701 |  | 1.9731 | 8489.4343 |  | 4.0505 | 9471.3931 |  | 66.6362 | 10566.9335
[13 empty] | Next iteration flow rate |  |  | 14.2366 | Abs Value of | Flow this | 518.2899 | Abs Value of | Flow this | 1281.7925 | Abs Value of | Flow this | 2496.6047 | Abs Value of | Flow this | 4105.9955 | Abs Value of | Flow this | 5758.9747 | Abs Value of | Flow this | 7312.3698 | Abs Value of | Flow this | 8574.3286 | Abs Value of | Flow this | 9566.107 | Abs Value of | Flow this | 10672.6028 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4157 |  |  | 99.8676 |  |  | 98.0373 |  |  | 93.8 |  |  | 87.2975 |  |  | 79.2007 |  |  | 71.2062 |  |  | 64.0319 |  |  | 55.102
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48439 |  |  | 0.48174 |  |  | 0.47291 |  |  | 0.45247 |  |  | 0.42111 |  |  | 0.38205 |  |  | 0.34349 |  |  | 0.30888 |  |  | 0.2658
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4157 |  |  | 49.8676 |  |  | 48.0373 |  |  | 43.8 |  |  | 37.2975 |  |  | 29.2007 |  |  | 21.2062 |  |  | 14.0319 |  |  | 5.102
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50207 |  |  | 0.49934 |  |  | 0.48999 |  |  | 0.46695 |  |  | 0.42725 |  |  | 0.36869 |  |  | 0.29781 |  |  | 0.21914 |  |  | 0.092593
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73857 |  |  | 0.7361 |  |  | 0.73749 |  |  | 0.74297 |  |  | 0.75141 |  |  | 0.77067 |  |  | 0.79761 |  |  | 0.87693 |  |  | 0.92106
[13 empty] | C Non choked w/ reducers | 5 |  | 0.061558 |  |  | 2.245 |  |  | 5.6292 |  |  | 11.3184 |  |  | 20.0183 |  |  | 31.8579 |  |  | 48.4033 |  |  | 72.0368 |  |  | 107.6469 |  |  | 268.5979
[13 empty] | C Choked w/ reducers | 5 |  | 0.060377 |  |  | 2.2015 |  |  | 5.5276 |  |  | 11.1058 |  |  | 19.5806 |  |  | 30.9935 |  |  | 46.3882 |  |  | 67.1237 |  |  | 85.9961 |  |  | 180.5006
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.061558 |  |  | 2.245 |  |  | 5.6292 |  |  | 11.3184 |  |  | 20.0183 |  |  | 31.8579 |  |  | 48.4033 |  |  | 72.0368 |  |  | 107.6469 |  |  | 268.5979
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9384 | 14.2366 |  | 2.755 | 518.2899 |  | 4.3708 | 1281.7925 |  | 5.8816 | 2496.6047 |  | 6.5817 | 4105.9955 |  | 6.5421 | 5758.9747 |  | 4.0967 | 7312.3698 |  | 0.36321 | 8574.3286 |  | 0.35313 | 9566.107 |  | 88.5979 | 10672.6028
[13 empty] | Next iteration flow rate |  |  | 14.5214 | Abs Value of | Flow this | 523.4728 | Abs Value of | Flow this | 1294.6104 | Abs Value of | Flow this | 2521.5707 | Abs Value of | Flow this | 4147.0554 | Abs Value of | Flow this | 5816.5645 | Abs Value of | Flow this | 7385.4935 | Abs Value of | Flow this | 8660.0719 | Abs Value of | Flow this | 9661.7681 | Abs Value of | Flow this | 10779.3289 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4135 |  |  | 99.8545 |  |  | 97.9873 |  |  | 93.6649 |  |  | 87.0317 |  |  | 78.7721 |  |  | 70.6169 |  |  | 63.2985 |  |  | 54.1891
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48438 |  |  | 0.48168 |  |  | 0.47267 |  |  | 0.45182 |  |  | 0.41983 |  |  | 0.37998 |  |  | 0.34064 |  |  | 0.30534 |  |  | 0.2614
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4135 |  |  | 49.8545 |  |  | 47.9873 |  |  | 43.6649 |  |  | 37.0317 |  |  | 28.7721 |  |  | 20.6169 |  |  | 13.2985 |  |  | 4.1891
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50206 |  |  | 0.49927 |  |  | 0.48973 |  |  | 0.46618 |  |  | 0.4255 |  |  | 0.36526 |  |  | 0.29195 |  |  | 0.21009 |  |  | 0.077305
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73858 |  |  | 0.73613 |  |  | 0.73762 |  |  | 0.74339 |  |  | 0.75243 |  |  | 0.77281 |  |  | 0.80159 |  |  | 0.88201 |  |  | 0.93409
[13 empty] | C Non choked w/ reducers | 5 |  | 0.062789 |  |  | 2.2675 |  |  | 5.6863 |  |  | 11.4383 |  |  | 20.2528 |  |  | 32.2972 |  |  | 49.2474 |  |  | 73.7287 |  |  | 111.6794 |  |  | 297.6883
[13 empty] | C Choked w/ reducers | 5 |  | 0.061584 |  |  | 2.2236 |  |  | 5.5836 |  |  | 11.2226 |  |  | 19.8049 |  |  | 31.399 |  |  | 47.107 |  |  | 68.3606 |  |  | 87.8625 |  |  | 185.3771
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.062789 |  |  | 2.2675 |  |  | 5.6863 |  |  | 11.4383 |  |  | 20.2528 |  |  | 32.2972 |  |  | 49.2474 |  |  | 73.7287 |  |  | 111.6794 |  |  | 297.6883
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9372 | 14.5214 |  | 2.7325 | 523.4728 |  | 4.3137 | 1294.6104 |  | 5.7617 | 2521.5707 |  | 6.3472 | 4147.0554 |  | 6.1028 | 5816.5645 |  | 3.2526 | 7385.4935 |  | 1.3287 | 8660.0719 |  | 3.6794 | 9661.7681 |  | 117.6883 | 10779.3289
[13 empty] | Next iteration flow rate |  |  | 14.8118 | Abs Value of | Flow this | 528.7075 | Abs Value of | Flow this | 1307.5565 | Abs Value of | Flow this | 2546.7864 | Abs Value of | Flow this | 4188.526 | Abs Value of | Flow this | 5874.7301 | Abs Value of | Flow this | 7459.3484 | Abs Value of | Flow this | 8746.6726 | Abs Value of | Flow this | 9758.3858 | Abs Value of | Flow this | 10887.1221 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4113 |  |  | 99.841 |  |  | 97.9364 |  |  | 93.527 |  |  | 86.7605 |  |  | 78.3349 |  |  | 70.0158 |  |  | 62.5503 |  |  | 53.2578
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48437 |  |  | 0.48162 |  |  | 0.47243 |  |  | 0.45116 |  |  | 0.41852 |  |  | 0.37787 |  |  | 0.33774 |  |  | 0.30173 |  |  | 0.25691
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4113 |  |  | 49.841 |  |  | 47.9364 |  |  | 43.527 |  |  | 36.7605 |  |  | 28.3349 |  |  | 20.0158 |  |  | 12.5503 |  |  | 3.2578
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50205 |  |  | 0.4992 |  |  | 0.48946 |  |  | 0.4654 |  |  | 0.4237 |  |  | 0.36172 |  |  | 0.28588 |  |  | 0.20064 |  |  | 0.06117
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73859 |  |  | 0.73617 |  |  | 0.73777 |  |  | 0.74383 |  |  | 0.75347 |  |  | 0.77501 |  |  | 0.80572 |  |  | 0.88732 |  |  | 0.94785
[13 empty] | C Non choked w/ reducers | 5 |  | 0.064045 |  |  | 2.2902 |  |  | 5.7441 |  |  | 11.5596 |  |  | 20.4909 |  |  | 32.746 |  |  | 50.1189 |  |  | 75.5105 |  |  | 116.1037 |  |  | 338.92
[13 empty] | C Choked w/ reducers | 5 |  | 0.062816 |  |  | 2.2459 |  |  | 5.6402 |  |  | 11.3407 |  |  | 20.0325 |  |  | 31.8121 |  |  | 47.8436 |  |  | 69.637 |  |  | 89.8027 |  |  | 190.5049
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.064045 |  |  | 2.2902 |  |  | 5.7441 |  |  | 11.5596 |  |  | 20.4909 |  |  | 32.746 |  |  | 50.1189 |  |  | 75.5105 |  |  | 116.1037 |  |  | 338.92
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.936 | 14.8118 |  | 2.7098 | 528.7075 |  | 4.2559 | 1307.5565 |  | 5.6404 | 2546.7864 |  | 6.1091 | 4188.526 |  | 5.654 | 5874.7301 |  | 2.3811 | 7459.3484 |  | 3.1105 | 8746.6726 |  | 8.1037 | 9758.3858 |  | 158.92 | 10887.1221
[13 empty] | Next iteration flow rate |  |  | 15.108 | Abs Value of | Flow this | 533.9946 | Abs Value of | Flow this | 1320.6321 | Abs Value of | Flow this | 2572.2543 | Abs Value of | Flow this | 4230.4112 | Abs Value of | Flow this | 5933.4774 | Abs Value of | Flow this | 7533.9419 | Abs Value of | Flow this | 8834.1394 | Abs Value of | Flow this | 9855.9696 | Abs Value of | Flow this | 10995.9934 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4091 |  |  | 99.8273 |  |  | 97.8844 |  |  | 93.3864 |  |  | 86.4839 |  |  | 77.889 |  |  | 69.4026 |  |  | 61.787 |  |  | 52.3077
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48436 |  |  | 0.48155 |  |  | 0.47218 |  |  | 0.45048 |  |  | 0.41718 |  |  | 0.37572 |  |  | 0.33479 |  |  | 0.29805 |  |  | 0.25232
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4091 |  |  | 49.8273 |  |  | 47.8844 |  |  | 43.3864 |  |  | 36.4839 |  |  | 27.889 |  |  | 19.4026 |  |  | 11.787 |  |  | 2.3077
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50204 |  |  | 0.49914 |  |  | 0.48919 |  |  | 0.46459 |  |  | 0.42186 |  |  | 0.35806 |  |  | 0.27957 |  |  | 0.19077 |  |  | 0.044119
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73859 |  |  | 0.7362 |  |  | 0.73791 |  |  | 0.74427 |  |  | 0.75455 |  |  | 0.77729 |  |  | 0.81001 |  |  | 0.89286 |  |  | 0.96239
[13 empty] | C Non choked w/ reducers | 5 |  | 0.065326 |  |  | 2.3132 |  |  | 5.8024 |  |  | 11.6823 |  |  | 20.7325 |  |  | 33.2044 |  |  | 51.0194 |  |  | 77.3909 |  |  | 120.9907 |  |  | 404.1877
[13 empty] | C Choked w/ reducers | 5 |  | 0.064072 |  |  | 2.2684 |  |  | 5.6974 |  |  | 11.4602 |  |  | 20.2632 |  |  | 32.233 |  |  | 48.5987 |  |  | 70.9548 |  |  | 91.8211 |  |  | 195.9045
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.065326 |  |  | 2.3132 |  |  | 5.8024 |  |  | 11.6823 |  |  | 20.7325 |  |  | 33.2044 |  |  | 51.0194 |  |  | 77.3909 |  |  | 120.9907 |  |  | 404.1877
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9347 | 15.108 |  | 2.6868 | 533.9946 |  | 4.1976 | 1320.6321 |  | 5.5177 | 2572.2543 |  | 5.8675 | 4230.4112 |  | 5.1956 | 5933.4774 |  | 1.4806 | 7533.9419 |  | 4.9909 | 8834.1394 |  | 12.9907 | 9855.9696 |  | 224.1877 | 10995.9934
[13 empty] | Next iteration flow rate |  |  | 15.4102 | Abs Value of | Flow this | 539.3345 | Abs Value of | Flow this | 1333.8384 | Abs Value of | Flow this | 2597.9768 | Abs Value of | Flow this | 4272.7153 | Abs Value of | Flow this | 5992.8122 | Abs Value of | Flow this | 7609.2813 | Abs Value of | Flow this | 8922.4807 | Abs Value of | Flow this | 9954.5293 | Abs Value of | Flow this | 11105.9533 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4068 |  |  | 99.8133 |  |  | 97.8314 |  |  | 93.243 |  |  | 86.2017 |  |  | 77.434 |  |  | 68.7771 |  |  | 61.0084 |  |  | 51.3386
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48434 |  |  | 0.48148 |  |  | 0.47192 |  |  | 0.44979 |  |  | 0.41582 |  |  | 0.37353 |  |  | 0.33177 |  |  | 0.29429 |  |  | 0.24765
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4068 |  |  | 49.8133 |  |  | 47.8314 |  |  | 43.243 |  |  | 36.2017 |  |  | 27.434 |  |  | 18.7771 |  |  | 11.0084 |  |  | 1.3386
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50203 |  |  | 0.49906 |  |  | 0.48892 |  |  | 0.46377 |  |  | 0.41997 |  |  | 0.35429 |  |  | 0.27301 |  |  | 0.18044 |  |  | 0.026074
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.7386 |  |  | 0.73624 |  |  | 0.73806 |  |  | 0.74472 |  |  | 0.75565 |  |  | 0.77963 |  |  | 0.81446 |  |  | 0.89866 |  |  | 0.97777
[13 empty] | C Non choked w/ reducers | 5 |  | 0.066633 |  |  | 2.3364 |  |  | 5.8614 |  |  | 11.8065 |  |  | 20.9779 |  |  | 33.6728 |  |  | 51.9507 |  |  | 79.3802 |  |  | 126.4312 |  |  | 532.5281
[13 empty] | C Choked w/ reducers | 5 |  | 0.065354 |  |  | 2.2911 |  |  | 5.7552 |  |  | 11.5811 |  |  | 20.4974 |  |  | 32.6619 |  |  | 49.373 |  |  | 72.3161 |  |  | 93.9229 |  |  | 201.5987
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.066633 |  |  | 2.3364 |  |  | 5.8614 |  |  | 11.8065 |  |  | 20.9779 |  |  | 33.6728 |  |  | 51.9507 |  |  | 79.3802 |  |  | 126.4312 |  |  | 532.5281
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9334 | 15.4102 |  | 2.6636 | 539.3345 |  | 4.1386 | 1333.8384 |  | 5.3935 | 2597.9768 |  | 5.6221 | 4272.7153 |  | 4.7272 | 5992.8122 |  | 0.54926 | 7609.2813 |  | 6.9802 | 8922.4807 |  | 18.4312 | 9954.5293 |  | 352.5281 | 11105.9533
[13 empty] | Next iteration flow rate |  |  | 15.7184 | Abs Value of | Flow this | 544.7279 | Abs Value of | Flow this | 1347.1768 | Abs Value of | Flow this | 2623.9566 | Abs Value of | Flow this | 4315.4425 | Abs Value of | Flow this | 6052.7403 | Abs Value of | Flow this | 7685.3741 | Abs Value of | Flow this | 9011.7056 | Abs Value of | Flow this | 10054.0746 | Abs Value of | Flow this | 11217.0128 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4045 |  |  | 99.7991 |  |  | 97.7773 |  |  | 93.0966 |  |  | 85.9139 |  |  | 76.9699 |  |  | 68.139 |  |  | 60.2142 |  |  | 50.35
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48433 |  |  | 0.48141 |  |  | 0.47166 |  |  | 0.44908 |  |  | 0.41443 |  |  | 0.37129 |  |  | 0.32869 |  |  | 0.29046 |  |  | 0.24288
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4045 |  |  | 49.7991 |  |  | 47.7773 |  |  | 43.0966 |  |  | 35.9139 |  |  | 26.9699 |  |  | 18.139 |  |  | 10.2142 |  |  | 0.35002
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50201 |  |  | 0.49899 |  |  | 0.48863 |  |  | 0.46292 |  |  | 0.41802 |  |  | 0.3504 |  |  | 0.26621 |  |  | 0.16963 |  |  | 0.0069518
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.7386 |  |  | 0.73628 |  |  | 0.73821 |  |  | 0.74519 |  |  | 0.75678 |  |  | 0.78205 |  |  | 0.81909 |  |  | 0.90473 |  |  | 0.99407
[13 empty] | C Non choked w/ reducers | 5 |  | 0.067965 |  |  | 2.3598 |  |  | 5.921 |  |  | 11.9322 |  |  | 21.2271 |  |  | 34.1516 |  |  | 52.9147 |  |  | 81.4902 |  |  | 132.5433 |  |  | 1044.685
[13 empty] | C Choked w/ reducers | 5 |  | 0.066661 |  |  | 2.3141 |  |  | 5.8136 |  |  | 11.7034 |  |  | 20.7349 |  |  | 33.0991 |  |  | 50.1674 |  |  | 73.7232 |  |  | 96.1133 |  |  | 207.6126
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.067965 |  |  | 2.3598 |  |  | 5.921 |  |  | 11.9322 |  |  | 21.2271 |  |  | 34.1516 |  |  | 52.9147 |  |  | 81.4902 |  |  | 132.5433 |  |  | 1044.685
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.932 | 15.7184 |  | 2.6402 | 544.7279 |  | 4.079 | 1347.1768 |  | 5.2678 | 2623.9566 |  | 5.3729 | 4315.4425 |  | 4.2484 | 6052.7403 |  | 0.4147 | 7685.3741 |  | 9.0902 | 9011.7056 |  | 24.5433 | 10054.0746 |  | 864.685 | 11217.0128
[13 empty] | Next iteration flow rate |  |  | 16.0328 | Abs Value of | Flow this | 550.1751 | Abs Value of | Flow this | 1360.6486 | Abs Value of | Flow this | 2650.1961 | Abs Value of | Flow this | 4358.5969 | Abs Value of | Flow this | 6113.2677 | Abs Value of | Flow this | 7762.2278 | Abs Value of | Flow this | 9101.8226 | Abs Value of | Flow this | 10154.6154 | Abs Value of | Flow this | 11329.183 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.4021 |  |  | 99.7845 |  |  | 97.7221 |  |  | 92.9474 |  |  | 85.6202 |  |  | 76.4965 |  |  | 67.4881 |  |  | 59.404 |  |  | 49.3416
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48432 |  |  | 0.48134 |  |  | 0.47139 |  |  | 0.44836 |  |  | 0.41302 |  |  | 0.36901 |  |  | 0.32555 |  |  | 0.28655 |  |  | 0.23801
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.4021 |  |  | 49.7845 |  |  | 47.7221 |  |  | 42.9474 |  |  | 35.6202 |  |  | 26.4965 |  |  | 17.4881 |  |  | 9.404 |  |  | -0.65845
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.502 |  |  | 0.49892 |  |  | 0.48834 |  |  | 0.46206 |  |  | 0.41603 |  |  | 0.34638 |  |  | 0.25913 |  |  | 0.15831 |  |  | -0.013345
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73861 |  |  | 0.73632 |  |  | 0.73837 |  |  | 0.74566 |  |  | 0.75794 |  |  | 0.78456 |  |  | 0.8239 |  |  | 0.91109 |  |  | 1.0114
[13 empty] | C Non choked w/ reducers | 5 |  | 0.069325 |  |  | 2.3835 |  |  | 5.9812 |  |  | 12.0593 |  |  | 21.4801 |  |  | 34.6411 |  |  | 53.9134 |  |  | 83.7344 |  |  | 139.484 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.067994 |  |  | 2.3373 |  |  | 5.8726 |  |  | 11.8271 |  |  | 20.9759 |  |  | 33.5447 |  |  | 50.9827 |  |  | 75.1786 |  |  | 98.3985 |  |  | 213.9744
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.069325 |  |  | 2.3835 |  |  | 5.9812 |  |  | 12.0593 |  |  | 21.4801 |  |  | 34.6411 |  |  | 53.9134 |  |  | 83.7344 |  |  | 139.484 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9307 | 16.0328 |  | 2.6165 | 550.1751 |  | 4.0188 | 1360.6486 |  | 5.1407 | 2650.1961 |  | 5.1199 | 4358.5969 |  | 3.7589 | 6113.2677 |  | 1.4134 | 7762.2278 |  | 11.3344 | 9101.8226 |  | 31.484 | 10154.6154 |  | 7174 | 11329.183
[13 empty] | Next iteration flow rate |  |  | 16.3534 | Abs Value of | Flow this | 555.6769 | Abs Value of | Flow this | 1374.2551 | Abs Value of | Flow this | 2676.6981 | Abs Value of | Flow this | 4402.1829 | Abs Value of | Flow this | 6174.4004 | Abs Value of | Flow this | 7839.8501 | Abs Value of | Flow this | 9192.8408 | Abs Value of | Flow this | 10256.1615 | Abs Value of | Flow this | 11442.4748 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.3997 |  |  | 99.7697 |  |  | 97.6658 |  |  | 92.7951 |  |  | 85.3207 |  |  | 76.0136 |  |  | 66.8241 |  |  | 58.5775 |  |  | 48.3128
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48431 |  |  | 0.48127 |  |  | 0.47112 |  |  | 0.44763 |  |  | 0.41157 |  |  | 0.36668 |  |  | 0.32235 |  |  | 0.28257 |  |  | 0.23305
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.3997 |  |  | 49.7697 |  |  | 47.6658 |  |  | 42.7951 |  |  | 35.3207 |  |  | 26.0136 |  |  | 16.8241 |  |  | 8.5775 |  |  | -1.6872
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50199 |  |  | 0.49885 |  |  | 0.48805 |  |  | 0.46118 |  |  | 0.41398 |  |  | 0.34222 |  |  | 0.25177 |  |  | 0.14643 |  |  | -0.034922
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73862 |  |  | 0.73636 |  |  | 0.73852 |  |  | 0.74615 |  |  | 0.75913 |  |  | 0.78714 |  |  | 0.8289 |  |  | 0.91776 |  |  | 1.0298
[13 empty] | C Non choked w/ reducers | 5 |  | 0.070711 |  |  | 2.4074 |  |  | 6.042 |  |  | 12.188 |  |  | 21.7372 |  |  | 35.1419 |  |  | 54.949 |  |  | 86.1288 |  |  | 147.4674 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.069354 |  |  | 2.3607 |  |  | 5.9322 |  |  | 11.9522 |  |  | 21.2204 |  |  | 33.9991 |  |  | 51.8197 |  |  | 76.6849 |  |  | 100.7847 |  |  | 220.716
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.070711 |  |  | 2.4074 |  |  | 6.042 |  |  | 12.188 |  |  | 21.7372 |  |  | 35.1419 |  |  | 54.949 |  |  | 86.1288 |  |  | 147.4674 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9293 | 16.3534 |  | 2.5926 | 555.6769 |  | 3.958 | 1374.2551 |  | 5.012 | 2676.6981 |  | 4.8628 | 4402.1829 |  | 3.2581 | 6174.4004 |  | 2.449 | 7839.8501 |  | 13.7288 | 9192.8408 |  | 39.4674 | 10256.1615 |  | 7174 | 11442.4748
[13 empty] | Next iteration flow rate |  |  | 16.6805 | Abs Value of | Flow this | 561.2337 | Abs Value of | Flow this | 1387.9976 | Abs Value of | Flow this | 2703.4651 | Abs Value of | Flow this | 4446.2047 | Abs Value of | Flow this | 6236.1444 | Abs Value of | Flow this | 7918.2486 | Abs Value of | Flow this | 9284.7692 | Abs Value of | Flow this | 10358.7232 | Abs Value of | Flow this | 11556.8995 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.3972 |  |  | 99.7546 |  |  | 97.6083 |  |  | 92.6398 |  |  | 85.0151 |  |  | 75.521 |  |  | 66.1467 |  |  | 57.7344 |  |  | 47.2634
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.4843 |  |  | 0.4812 |  |  | 0.47085 |  |  | 0.44688 |  |  | 0.4101 |  |  | 0.3643 |  |  | 0.31908 |  |  | 0.2785 |  |  | 0.22799
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.3972 |  |  | 49.7546 |  |  | 47.6083 |  |  | 42.6398 |  |  | 35.0151 |  |  | 25.521 |  |  | 16.1467 |  |  | 7.7344 |  |  | -2.7366
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50198 |  |  | 0.49877 |  |  | 0.48775 |  |  | 0.46027 |  |  | 0.41187 |  |  | 0.33793 |  |  | 0.2441 |  |  | 0.13397 |  |  | -0.057901
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73862 |  |  | 0.7364 |  |  | 0.73869 |  |  | 0.74664 |  |  | 0.76036 |  |  | 0.78981 |  |  | 0.83411 |  |  | 0.92476 |  |  | 1.0494
[13 empty] | C Non choked w/ reducers | 5 |  | 0.072125 |  |  | 2.4315 |  |  | 6.1035 |  |  | 12.3183 |  |  | 21.9983 |  |  | 35.6543 |  |  | 56.0241 |  |  | 88.6922 |  |  | 156.7952 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.070741 |  |  | 2.3844 |  |  | 5.9924 |  |  | 12.0789 |  |  | 21.4685 |  |  | 34.4625 |  |  | 52.6793 |  |  | 78.2449 |  |  | 103.279 |  |  | 227.8728
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.072125 |  |  | 2.4315 |  |  | 6.1035 |  |  | 12.3183 |  |  | 21.9983 |  |  | 35.6543 |  |  | 56.0241 |  |  | 88.6922 |  |  | 156.7952 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9279 | 16.6805 |  | 2.5685 | 561.2337 |  | 3.8965 | 1387.9976 |  | 4.8817 | 2703.4651 |  | 4.6017 | 4446.2047 |  | 2.7457 | 6236.1444 |  | 3.5241 | 7918.2486 |  | 16.2922 | 9284.7692 |  | 48.7952 | 10358.7232 |  | 7174 | 11556.8995
[13 empty] | Next iteration flow rate |  |  | 17.0141 | Abs Value of | Flow this | 566.846 | Abs Value of | Flow this | 1401.8776 | Abs Value of | Flow this | 2730.4997 | Abs Value of | Flow this | 4490.6668 | Abs Value of | Flow this | 6298.5059 | Abs Value of | Flow this | 7997.4311 | Abs Value of | Flow this | 9377.6169 | Abs Value of | Flow this | 10462.3104 | Abs Value of | Flow this | 11672.4685 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.3947 |  |  | 99.7391 |  |  | 97.5498 |  |  | 92.4813 |  |  | 84.7034 |  |  | 75.0184 |  |  | 65.4558 |  |  | 56.8743 |  |  | 46.1929
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48429 |  |  | 0.48112 |  |  | 0.47056 |  |  | 0.44611 |  |  | 0.40859 |  |  | 0.36188 |  |  | 0.31575 |  |  | 0.27435 |  |  | 0.22283
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.3947 |  |  | 49.7391 |  |  | 47.5498 |  |  | 42.4813 |  |  | 34.7034 |  |  | 25.0184 |  |  | 15.4558 |  |  | 6.8743 |  |  | -3.8071
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50197 |  |  | 0.49869 |  |  | 0.48744 |  |  | 0.45935 |  |  | 0.40971 |  |  | 0.3335 |  |  | 0.23613 |  |  | 0.12087 |  |  | -0.082418
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73863 |  |  | 0.73644 |  |  | 0.73885 |  |  | 0.74715 |  |  | 0.76162 |  |  | 0.79257 |  |  | 0.83953 |  |  | 0.93212 |  |  | 1.0703
[13 empty] | C Non choked w/ reducers | 5 |  | 0.073568 |  |  | 2.4559 |  |  | 6.1656 |  |  | 12.4501 |  |  | 22.2635 |  |  | 36.1788 |  |  | 57.1413 |  |  | 91.4471 |  |  | 167.9075 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.072156 |  |  | 2.4083 |  |  | 6.0533 |  |  | 12.207 |  |  | 21.7204 |  |  | 34.9352 |  |  | 53.5625 |  |  | 79.8615 |  |  | 105.8892 |  |  | 235.4853
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.073568 |  |  | 2.4559 |  |  | 6.1656 |  |  | 12.4501 |  |  | 22.2635 |  |  | 36.1788 |  |  | 57.1413 |  |  | 91.4471 |  |  | 167.9075 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9264 | 17.0141 |  | 2.5441 | 566.846 |  | 3.8344 | 1401.8776 |  | 4.7499 | 2730.4997 |  | 4.3365 | 4490.6668 |  | 2.2212 | 6298.5059 |  | 4.6413 | 7997.4311 |  | 19.0471 | 9377.6169 |  | 59.9075 | 10462.3104 |  | 7174 | 11672.4685
[13 empty] | Next iteration flow rate |  |  | 17.3544 | Abs Value of | Flow this | 572.5145 | Abs Value of | Flow this | 1415.8964 | Abs Value of | Flow this | 2757.8047 | Abs Value of | Flow this | 4535.5734 | Abs Value of | Flow this | 6361.4909 | Abs Value of | Flow this | 8077.4054 | Abs Value of | Flow this | 9471.3931 | Abs Value of | Flow this | 10566.9335 | Abs Value of | Flow this | 11789.1932 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.3921 |  |  | 99.7234 |  |  | 97.49 |  |  | 92.3197 |  |  | 84.3855 |  |  | 74.5058 |  |  | 64.7509 |  |  | 55.997 |  |  | 45.1008
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48427 |  |  | 0.48105 |  |  | 0.47027 |  |  | 0.44533 |  |  | 0.40706 |  |  | 0.3594 |  |  | 0.31235 |  |  | 0.27012 |  |  | 0.21756
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.3921 |  |  | 49.7234 |  |  | 47.49 |  |  | 42.3197 |  |  | 34.3855 |  |  | 24.5058 |  |  | 14.7509 |  |  | 5.997 |  |  | -4.8992
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50195 |  |  | 0.49861 |  |  | 0.48713 |  |  | 0.4584 |  |  | 0.40748 |  |  | 0.32891 |  |  | 0.22781 |  |  | 0.1071 |  |  | -0.10863
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73863 |  |  | 0.73648 |  |  | 0.73902 |  |  | 0.74767 |  |  | 0.76291 |  |  | 0.79542 |  |  | 0.84518 |  |  | 0.93985 |  |  | 1.0926
[13 empty] | C Non choked w/ reducers | 5 |  | 0.075039 |  |  | 2.4805 |  |  | 6.2284 |  |  | 12.5835 |  |  | 22.5331 |  |  | 36.7158 |  |  | 58.3037 |  |  | 94.4201 |  |  | 181.479 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.073599 |  |  | 2.4324 |  |  | 6.1147 |  |  | 12.3366 |  |  | 21.976 |  |  | 35.4175 |  |  | 54.4703 |  |  | 81.5382 |  |  | 108.6237 |  |  | 243.599
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.075039 |  |  | 2.4805 |  |  | 6.2284 |  |  | 12.5835 |  |  | 22.5331 |  |  | 36.7158 |  |  | 58.3037 |  |  | 94.4201 |  |  | 181.479 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.925 | 17.3544 |  | 2.5195 | 572.5145 |  | 3.7716 | 1415.8964 |  | 4.6165 | 2757.8047 |  | 4.0669 | 4535.5734 |  | 1.6842 | 6361.4909 |  | 5.8037 | 8077.4054 |  | 22.0201 | 9471.3931 |  | 73.479 | 10566.9335 |  | 7174 | 11789.1932
[13 empty] | Next iteration flow rate |  |  | 17.7015 | Abs Value of | Flow this | 578.2396 | Abs Value of | Flow this | 1430.0553 | Abs Value of | Flow this | 2785.3828 | Abs Value of | Flow this | 4580.9292 | Abs Value of | Flow this | 6425.1058 | Abs Value of | Flow this | 8158.1795 | Abs Value of | Flow this | 9566.107 | Abs Value of | Flow this | 10672.6028 | Abs Value of | Flow this | 11907.0851 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.3895 |  |  | 99.7073 |  |  | 97.429 |  |  | 92.1548 |  |  | 84.0611 |  |  | 73.9828 |  |  | 64.0319 |  |  | 55.102 |  |  | 43.9869
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48426 |  |  | 0.48097 |  |  | 0.46998 |  |  | 0.44454 |  |  | 0.4055 |  |  | 0.35688 |  |  | 0.30888 |  |  | 0.2658 |  |  | 0.21218
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.3895 |  |  | 49.7073 |  |  | 47.429 |  |  | 42.1548 |  |  | 34.0611 |  |  | 23.9828 |  |  | 14.0319 |  |  | 5.102 |  |  | -6.0131
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50194 |  |  | 0.49853 |  |  | 0.48681 |  |  | 0.45743 |  |  | 0.40519 |  |  | 0.32417 |  |  | 0.21914 |  |  | 0.092593 |  |  | -0.1367
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73864 |  |  | 0.73652 |  |  | 0.73919 |  |  | 0.74821 |  |  | 0.76424 |  |  | 0.79837 |  |  | 0.85107 |  |  | 0.948 |  |  | 1.1165
[13 empty] | C Non choked w/ reducers | 5 |  | 0.07654 |  |  | 2.5054 |  |  | 6.2918 |  |  | 12.7185 |  |  | 22.807 |  |  | 37.266 |  |  | 59.5145 |  |  | 97.6437 |  |  | 198.6069 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.075071 |  |  | 2.4568 |  |  | 6.1769 |  |  | 12.4678 |  |  | 22.2354 |  |  | 35.9097 |  |  | 55.4039 |  |  | 83.2783 |  |  | 111.4918 |  |  | 252.2659
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.07654 |  |  | 2.5054 |  |  | 6.2918 |  |  | 12.7185 |  |  | 22.807 |  |  | 37.266 |  |  | 59.5145 |  |  | 97.6437 |  |  | 198.6069 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9235 | 17.7015 |  | 2.4946 | 578.2396 |  | 3.7082 | 1430.0553 |  | 4.4815 | 2785.3828 |  | 3.793 | 4580.9292 |  | 1.134 | 6425.1058 |  | 7.0145 | 8158.1795 |  | 25.2437 | 9566.107 |  | 90.6069 | 10672.6028 |  | 7174 | 11907.0851
[13 empty] | Next iteration flow rate |  |  | 18.0555 | Abs Value of | Flow this | 584.022 | Abs Value of | Flow this | 1444.3559 | Abs Value of | Flow this | 2813.2366 | Abs Value of | Flow this | 4626.7385 | Abs Value of | Flow this | 6489.3569 | Abs Value of | Flow this | 8239.7613 | Abs Value of | Flow this | 9661.7681 | Abs Value of | Flow this | 10779.3289 | Abs Value of | Flow this | 12026.156 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.3868 |  |  | 99.6909 |  |  | 97.3669 |  |  | 91.9866 |  |  | 83.7302 |  |  | 73.4494 |  |  | 63.2985 |  |  | 54.1891 |  |  | 42.8505
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48425 |  |  | 0.48089 |  |  | 0.46968 |  |  | 0.44373 |  |  | 0.4039 |  |  | 0.35431 |  |  | 0.30534 |  |  | 0.2614 |  |  | 0.2067
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.3868 |  |  | 49.6909 |  |  | 47.3669 |  |  | 41.9866 |  |  | 33.7302 |  |  | 23.4494 |  |  | 13.2985 |  |  | 4.1891 |  |  | -7.1495
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50193 |  |  | 0.49845 |  |  | 0.48648 |  |  | 0.45644 |  |  | 0.40284 |  |  | 0.31926 |  |  | 0.21009 |  |  | 0.077305 |  |  | -0.16685
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73865 |  |  | 0.73657 |  |  | 0.73937 |  |  | 0.74875 |  |  | 0.76561 |  |  | 0.80142 |  |  | 0.85722 |  |  | 0.95658 |  |  | 1.1423
[13 empty] | C Non choked w/ reducers | 5 |  | 0.078071 |  |  | 2.5306 |  |  | 6.3559 |  |  | 12.8552 |  |  | 23.0854 |  |  | 37.8298 |  |  | 60.7775 |  |  | 101.1577 |  |  | 221.2282 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.076572 |  |  | 2.4814 |  |  | 6.2397 |  |  | 12.6005 |  |  | 22.4989 |  |  | 36.4121 |  |  | 56.3643 |  |  | 85.0857 |  |  | 114.5039 |  |  | 261.5454
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.078071 |  |  | 2.5306 |  |  | 6.3559 |  |  | 12.8552 |  |  | 23.0854 |  |  | 37.8298 |  |  | 60.7775 |  |  | 101.1577 |  |  | 221.2282 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9219 | 18.0555 |  | 2.4694 | 584.022 |  | 3.6441 | 1444.3559 |  | 4.3448 | 2813.2366 |  | 3.5146 | 4626.7385 |  | 0.57023 | 6489.3569 |  | 8.2775 | 8239.7613 |  | 28.7577 | 9661.7681 |  | 113.2282 | 10779.3289 |  | 7174 | 12026.156
[13 empty] | Next iteration flow rate |  |  | 18.4166 | Abs Value of | Flow this | 589.8622 | Abs Value of | Flow this | 1458.7995 | Abs Value of | Flow this | 2841.369 | Abs Value of | Flow this | 4673.0058 | Abs Value of | Flow this | 6554.2504 | Abs Value of | Flow this | 8322.1589 | Abs Value of | Flow this | 9758.3858 | Abs Value of | Flow this | 10887.1221 | Abs Value of | Flow this | 12146.4176 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5227 |  |  | 100.384 |  |  | 99.6742 |  |  | 97.3034 |  |  | 91.815 |  |  | 83.3927 |  |  | 72.9052 |  |  | 62.5503 |  |  | 53.2578 |  |  | 41.6913
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48423 |  |  | 0.48081 |  |  | 0.46937 |  |  | 0.4429 |  |  | 0.40227 |  |  | 0.35168 |  |  | 0.30173 |  |  | 0.25691 |  |  | 0.20111
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5227 |  |  | 50.384 |  |  | 49.6742 |  |  | 47.3034 |  |  | 41.815 |  |  | 33.3927 |  |  | 22.9052 |  |  | 12.5503 |  |  | 3.2578 |  |  | -8.3087
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50191 |  |  | 0.49837 |  |  | 0.48614 |  |  | 0.45543 |  |  | 0.40043 |  |  | 0.31418 |  |  | 0.20064 |  |  | 0.06117 |  |  | -0.19929
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73866 |  |  | 0.73661 |  |  | 0.73955 |  |  | 0.74931 |  |  | 0.76701 |  |  | 0.80458 |  |  | 0.86364 |  |  | 0.96565 |  |  | 1.1699
[13 empty] | C Non choked w/ reducers | 5 |  | 0.079632 |  |  | 2.5559 |  |  | 6.4207 |  |  | 12.9935 |  |  | 23.3684 |  |  | 38.4078 |  |  | 62.0967 |  |  | 105.0112 |  |  | 253.1806 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.078104 |  |  | 2.5063 |  |  | 6.3031 |  |  | 12.7348 |  |  | 22.7663 |  |  | 36.9251 |  |  | 57.3529 |  |  | 86.9645 |  |  | 117.6713 |  |  | 271.5058
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.079632 |  |  | 2.5559 |  |  | 6.4207 |  |  | 12.9935 |  |  | 23.3684 |  |  | 38.4078 |  |  | 62.0967 |  |  | 105.0112 |  |  | 253.1806 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9204 | 18.4166 |  | 2.4441 | 589.8622 |  | 3.5793 | 1458.7995 |  | 4.2065 | 2841.369 |  | 3.2316 | 4673.0058 |  | 0.0077711 | 6554.2504 |  | 9.5967 | 8322.1589 |  | 32.6112 | 9758.3858 |  | 145.1806 | 10887.1221 |  | 7174 | 12146.4176
[13 empty] | Next iteration flow rate |  |  | 18.7849 | Abs Value of | Flow this | 595.7608 | Abs Value of | Flow this | 1473.3874 | Abs Value of | Flow this | 2869.7827 | Abs Value of | Flow this | 4719.7359 | Abs Value of | Flow this | 6619.793 | Abs Value of | Flow this | 8405.3805 | Abs Value of | Flow this | 9855.9696 | Abs Value of | Flow this | 10995.9934 | Abs Value of | Flow this | 12267.8817 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3813 |  |  | 99.6571 |  |  | 97.2387 |  |  | 91.64 |  |  | 83.0484 |  |  | 72.3501 |  |  | 61.787 |  |  | 52.3077 |  |  | 40.5088
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48422 |  |  | 0.48073 |  |  | 0.46906 |  |  | 0.44206 |  |  | 0.40061 |  |  | 0.349 |  |  | 0.29805 |  |  | 0.25232 |  |  | 0.19541
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3813 |  |  | 49.6571 |  |  | 47.2387 |  |  | 41.64 |  |  | 33.0484 |  |  | 22.3501 |  |  | 11.787 |  |  | 2.3077 |  |  | -9.4912
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.5019 |  |  | 0.49828 |  |  | 0.4858 |  |  | 0.45439 |  |  | 0.39794 |  |  | 0.30892 |  |  | 0.19077 |  |  | 0.044119 |  |  | -0.2343
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73866 |  |  | 0.73666 |  |  | 0.73973 |  |  | 0.74989 |  |  | 0.76846 |  |  | 0.80786 |  |  | 0.87035 |  |  | 0.97522 |  |  | 1.1998
[13 empty] | C Non choked w/ reducers | 5 |  | 0.081225 |  |  | 2.5816 |  |  | 6.4862 |  |  | 13.1335 |  |  | 23.6561 |  |  | 39.0006 |  |  | 63.4766 |  |  | 109.2662 |  |  | 303.5576 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.079666 |  |  | 2.5314 |  |  | 6.3673 |  |  | 12.8707 |  |  | 23.0379 |  |  | 37.449 |  |  | 58.3709 |  |  | 88.9192 |  |  | 121.0065 |  |  | 282.2258
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.081225 |  |  | 2.5816 |  |  | 6.4862 |  |  | 13.1335 |  |  | 23.6561 |  |  | 39.0006 |  |  | 63.4766 |  |  | 109.2662 |  |  | 303.5576 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9188 | 18.7849 |  | 2.4184 | 595.7608 |  | 3.5138 | 1473.3874 |  | 4.0665 | 2869.7827 |  | 2.9439 | 4719.7359 |  | 0.60061 | 6619.793 |  | 10.9766 | 8405.3805 |  | 36.8662 | 9855.9696 |  | 195.5576 | 10995.9934 |  | 7174 | 12267.8817
[13 empty] | Next iteration flow rate |  |  | 19.1606 | Abs Value of | Flow this | 601.7184 | Abs Value of | Flow this | 1488.1213 | Abs Value of | Flow this | 2898.4805 | Abs Value of | Flow this | 4766.9333 | Abs Value of | Flow this | 6685.9909 | Abs Value of | Flow this | 8489.4343 | Abs Value of | Flow this | 9954.5293 | Abs Value of | Flow this | 11105.9533 | Abs Value of | Flow this | 12390.5606 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3784 |  |  | 99.6397 |  |  | 97.1727 |  |  | 91.4615 |  |  | 82.6971 |  |  | 71.7838 |  |  | 61.0084 |  |  | 51.3386 |  |  | 39.3025
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48421 |  |  | 0.48064 |  |  | 0.46874 |  |  | 0.44119 |  |  | 0.39892 |  |  | 0.34627 |  |  | 0.29429 |  |  | 0.24765 |  |  | 0.18959
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3784 |  |  | 49.6397 |  |  | 47.1727 |  |  | 41.4615 |  |  | 32.6971 |  |  | 21.7838 |  |  | 11.0084 |  |  | 1.3386 |  |  | -10.6975
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50188 |  |  | 0.49819 |  |  | 0.48545 |  |  | 0.45332 |  |  | 0.39538 |  |  | 0.30346 |  |  | 0.18044 |  |  | 0.026074 |  |  | -0.27218
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73867 |  |  | 0.7367 |  |  | 0.73992 |  |  | 0.75047 |  |  | 0.76995 |  |  | 0.81125 |  |  | 0.87737 |  |  | 0.98536 |  |  | 1.2321
[13 empty] | C Non choked w/ reducers | 5 |  | 0.082849 |  |  | 2.6075 |  |  | 6.5524 |  |  | 13.2753 |  |  | 23.9487 |  |  | 39.6089 |  |  | 64.9224 |  |  | 114.002 |  |  | 402.1595 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.081259 |  |  | 2.5568 |  |  | 6.4321 |  |  | 13.0082 |  |  | 23.3137 |  |  | 37.9841 |  |  | 59.4197 |  |  | 90.9545 |  |  | 124.5237 |  |  | 293.7968
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.082849 |  |  | 2.6075 |  |  | 6.5524 |  |  | 13.2753 |  |  | 23.9487 |  |  | 39.6089 |  |  | 64.9224 |  |  | 114.002 |  |  | 402.1595 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9172 | 19.1606 |  | 2.3925 | 601.7184 |  | 3.4476 | 1488.1213 |  | 3.9247 | 2898.4805 |  | 2.6513 | 4766.9333 |  | 1.2089 | 6685.9909 |  | 12.4224 | 8489.4343 |  | 41.602 | 9954.5293 |  | 294.1595 | 11105.9533 |  | 7174 | 12390.5606
[13 empty] | Next iteration flow rate |  |  | 19.5439 | Abs Value of | Flow this | 607.7356 | Abs Value of | Flow this | 1503.0025 | Abs Value of | Flow this | 2927.4653 | Abs Value of | Flow this | 4814.6026 | Abs Value of | Flow this | 6752.8508 | Abs Value of | Flow this | 8574.3286 | Abs Value of | Flow this | 10054.0746 | Abs Value of | Flow this | 11217.0128 | Abs Value of | Flow this | 12514.4662 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3755 |  |  | 99.622 |  |  | 97.1054 |  |  | 91.2793 |  |  | 82.3389 |  |  | 71.2062 |  |  | 60.2142 |  |  | 50.35 |  |  | 38.072
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48419 |  |  | 0.48056 |  |  | 0.46842 |  |  | 0.44032 |  |  | 0.39719 |  |  | 0.34349 |  |  | 0.29046 |  |  | 0.24288 |  |  | 0.18365
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3755 |  |  | 49.622 |  |  | 47.1054 |  |  | 41.2793 |  |  | 32.3389 |  |  | 21.2062 |  |  | 10.2142 |  |  | 0.35002 |  |  | -11.928
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50187 |  |  | 0.4981 |  |  | 0.4851 |  |  | 0.45223 |  |  | 0.39275 |  |  | 0.29781 |  |  | 0.16963 |  |  | 0.0069518 |  |  | -0.3133
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73868 |  |  | 0.73675 |  |  | 0.74011 |  |  | 0.75107 |  |  | 0.77148 |  |  | 0.81476 |  |  | 0.88472 |  |  | 0.9961 |  |  | 1.2671
[13 empty] | C Non choked w/ reducers | 5 |  | 0.084506 |  |  | 2.6337 |  |  | 6.6193 |  |  | 13.4188 |  |  | 24.2463 |  |  | 40.2335 |  |  | 66.4399 |  |  | 119.3215 |  |  | 793.4419 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.082885 |  |  | 2.5825 |  |  | 6.4975 |  |  | 13.1474 |  |  | 23.5938 |  |  | 38.5309 |  |  | 60.5007 |  |  | 93.0757 |  |  | 128.2383 |  |  | 306.3256
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.084506 |  |  | 2.6337 |  |  | 6.6193 |  |  | 13.4188 |  |  | 24.2463 |  |  | 40.2335 |  |  | 66.4399 |  |  | 119.3215 |  |  | 793.4419 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9155 | 19.5439 |  | 2.3663 | 607.7356 |  | 3.3807 | 1503.0025 |  | 3.7812 | 2927.4653 |  | 2.3537 | 4814.6026 |  | 1.8335 | 6752.8508 |  | 13.9399 | 8574.3286 |  | 46.9215 | 10054.0746 |  | 685.4419 | 11217.0128 |  | 7174 | 12514.4662
[13 empty] | Next iteration flow rate |  |  | 19.9347 | Abs Value of | Flow this | 613.813 | Abs Value of | Flow this | 1518.0326 | Abs Value of | Flow this | 2956.74 | Abs Value of | Flow this | 4862.7486 | Abs Value of | Flow this | 6820.3793 | Abs Value of | Flow this | 8660.0719 | Abs Value of | Flow this | 10154.6154 | Abs Value of | Flow this | 11329.183 | Abs Value of | Flow this | 12639.6108 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3725 |  |  | 99.6039 |  |  | 97.0367 |  |  | 91.0935 |  |  | 81.9734 |  |  | 70.6169 |  |  | 59.404 |  |  | 49.3416 |  |  | 36.8167
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48418 |  |  | 0.48047 |  |  | 0.46809 |  |  | 0.43942 |  |  | 0.39542 |  |  | 0.34064 |  |  | 0.28655 |  |  | 0.23801 |  |  | 0.1776
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3725 |  |  | 49.6039 |  |  | 47.0367 |  |  | 41.0935 |  |  | 31.9734 |  |  | 20.6169 |  |  | 9.404 |  |  | -0.65845 |  |  | -13.1833
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50186 |  |  | 0.49801 |  |  | 0.48473 |  |  | 0.45111 |  |  | 0.39005 |  |  | 0.29195 |  |  | 0.15831 |  |  | -0.013345 |  |  | -0.35808
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73869 |  |  | 0.7368 |  |  | 0.7403 |  |  | 0.75169 |  |  | 0.77305 |  |  | 0.81841 |  |  | 0.89242 |  |  | 1.0075 |  |  | 1.3053
[13 empty] | C Non choked w/ reducers | 5 |  | 0.086197 |  |  | 2.6601 |  |  | 6.6868 |  |  | 13.5641 |  |  | 24.5489 |  |  | 40.8749 |  |  | 68.0356 |  |  | 125.362 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.084542 |  |  | 2.6084 |  |  | 6.5637 |  |  | 13.2883 |  |  | 23.8784 |  |  | 39.0897 |  |  | 61.6156 |  |  | 95.2886 |  |  | 132.1679 |  |  | 319.9374
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.086197 |  |  | 2.6601 |  |  | 6.6868 |  |  | 13.5641 |  |  | 24.5489 |  |  | 40.8749 |  |  | 68.0356 |  |  | 125.362 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9138 | 19.9347 |  | 2.3399 | 613.813 |  | 3.3132 | 1518.0326 |  | 3.6359 | 2956.74 |  | 2.0511 | 4862.7486 |  | 2.4749 | 6820.3793 |  | 15.5356 | 8660.0719 |  | 52.962 | 10154.6154 |  | 7174 | 11329.183 |  | 7174 | 12639.6108
[13 empty] | Next iteration flow rate |  |  | 20.3334 | Abs Value of | Flow this | 619.9511 | Abs Value of | Flow this | 1533.2129 | Abs Value of | Flow this | 2986.3074 | Abs Value of | Flow this | 4911.3761 | Abs Value of | Flow this | 6888.5831 | Abs Value of | Flow this | 8746.6726 | Abs Value of | Flow this | 10256.1615 | Abs Value of | Flow this | 11442.4748 | Abs Value of | Flow this | 12766.0069 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3695 |  |  | 99.5854 |  |  | 96.9666 |  |  | 90.904 |  |  | 81.6005 |  |  | 70.0158 |  |  | 58.5775 |  |  | 48.3128 |  |  | 35.5362
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48416 |  |  | 0.48038 |  |  | 0.46775 |  |  | 0.4385 |  |  | 0.39363 |  |  | 0.33774 |  |  | 0.28257 |  |  | 0.23305 |  |  | 0.17142
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3695 |  |  | 49.5854 |  |  | 46.9666 |  |  | 40.904 |  |  | 31.6005 |  |  | 20.0158 |  |  | 8.5775 |  |  | -1.6872 |  |  | -14.4638
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50184 |  |  | 0.49792 |  |  | 0.48436 |  |  | 0.44997 |  |  | 0.38726 |  |  | 0.28588 |  |  | 0.14643 |  |  | -0.034922 |  |  | -0.40702
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73869 |  |  | 0.73685 |  |  | 0.7405 |  |  | 0.75232 |  |  | 0.77468 |  |  | 0.82219 |  |  | 0.90049 |  |  | 1.0196 |  |  | 1.347
[13 empty] | C Non choked w/ reducers | 5 |  | 0.08792 |  |  | 2.6868 |  |  | 6.7551 |  |  | 13.7112 |  |  | 24.8569 |  |  | 41.5342 |  |  | 69.7168 |  |  | 132.3108 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.086233 |  |  | 2.6345 |  |  | 6.6306 |  |  | 13.4309 |  |  | 24.1674 |  |  | 39.661 |  |  | 62.7661 |  |  | 97.5994 |  |  | 136.3321 |  |  | 334.7805
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.08792 |  |  | 2.6868 |  |  | 6.7551 |  |  | 13.7112 |  |  | 24.8569 |  |  | 41.5342 |  |  | 69.7168 |  |  | 132.3108 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9121 | 20.3334 |  | 2.3132 | 619.9511 |  | 3.2449 | 1533.2129 |  | 3.4888 | 2986.3074 |  | 1.7431 | 4911.3761 |  | 3.1342 | 6888.5831 |  | 17.2168 | 8746.6726 |  | 59.9108 | 10256.1615 |  | 7174 | 11442.4748 |  | 7174 | 12766.0069
[13 empty] | Next iteration flow rate |  |  | 20.7401 | Abs Value of | Flow this | 626.1506 | Abs Value of | Flow this | 1548.545 | Abs Value of | Flow this | 3016.1704 | Abs Value of | Flow this | 4960.4899 | Abs Value of | Flow this | 6957.4689 | Abs Value of | Flow this | 8834.1394 | Abs Value of | Flow this | 10358.7232 | Abs Value of | Flow this | 11556.8995 | Abs Value of | Flow this | 12893.667 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3664 |  |  | 99.5666 |  |  | 96.8951 |  |  | 90.7107 |  |  | 81.2202 |  |  | 69.4026 |  |  | 57.7344 |  |  | 47.2634 |  |  | 34.23
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48415 |  |  | 0.48029 |  |  | 0.4674 |  |  | 0.43757 |  |  | 0.39179 |  |  | 0.33479 |  |  | 0.2785 |  |  | 0.22799 |  |  | 0.16512
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3664 |  |  | 49.5666 |  |  | 46.8951 |  |  | 40.7107 |  |  | 31.2202 |  |  | 19.4026 |  |  | 7.7344 |  |  | -2.7366 |  |  | -15.77
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50183 |  |  | 0.49782 |  |  | 0.48398 |  |  | 0.4488 |  |  | 0.38439 |  |  | 0.27957 |  |  | 0.13397 |  |  | -0.057901 |  |  | -0.46071
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.7387 |  |  | 0.7369 |  |  | 0.74071 |  |  | 0.75296 |  |  | 0.77635 |  |  | 0.82611 |  |  | 0.90896 |  |  | 1.0325 |  |  | 1.3928
[13 empty] | C Non choked w/ reducers | 5 |  | 0.089679 |  |  | 2.7137 |  |  | 6.8242 |  |  | 13.8602 |  |  | 25.1702 |  |  | 42.212 |  |  | 71.4919 |  |  | 140.4318 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.087958 |  |  | 2.661 |  |  | 6.6981 |  |  | 13.5752 |  |  | 24.4611 |  |  | 40.2452 |  |  | 63.9538 |  |  | 100.0149 |  |  | 140.7527 |  |  | 351.0314
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.089679 |  |  | 2.7137 |  |  | 6.8242 |  |  | 13.8602 |  |  | 25.1702 |  |  | 42.212 |  |  | 71.4919 |  |  | 140.4318 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9103 | 20.7401 |  | 2.2863 | 626.1506 |  | 3.1758 | 1548.545 |  | 3.3398 | 3016.1704 |  | 1.4298 | 4960.4899 |  | 3.812 | 6957.4689 |  | 18.9919 | 8834.1394 |  | 68.0318 | 10358.7232 |  | 7174 | 11556.8995 |  | 7174 | 12893.667
[13 empty] | Next iteration flow rate |  |  | 21.1549 | Abs Value of | Flow this | 632.4121 | Abs Value of | Flow this | 1564.0305 | Abs Value of | Flow this | 3046.3321 | Abs Value of | Flow this | 5010.0948 | Abs Value of | Flow this | 7027.0436 | Abs Value of | Flow this | 8922.4807 | Abs Value of | Flow this | 10462.3104 | Abs Value of | Flow this | 11672.4685 | Abs Value of | Flow this | 13022.6037 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3633 |  |  | 99.5473 |  |  | 96.8222 |  |  | 90.5134 |  |  | 80.8322 |  |  | 68.7771 |  |  | 56.8743 |  |  | 46.1929 |  |  | 32.8975
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48413 |  |  | 0.4802 |  |  | 0.46705 |  |  | 0.43662 |  |  | 0.38992 |  |  | 0.33177 |  |  | 0.27435 |  |  | 0.22283 |  |  | 0.15869
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3633 |  |  | 49.5473 |  |  | 46.8222 |  |  | 40.5134 |  |  | 30.8322 |  |  | 18.7771 |  |  | 6.8743 |  |  | -3.8071 |  |  | -17.1025
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50181 |  |  | 0.49773 |  |  | 0.48359 |  |  | 0.4476 |  |  | 0.38143 |  |  | 0.27301 |  |  | 0.12087 |  |  | -0.082418 |  |  | -0.51987
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73871 |  |  | 0.73695 |  |  | 0.74091 |  |  | 0.75362 |  |  | 0.77807 |  |  | 0.83019 |  |  | 0.91786 |  |  | 1.0463 |  |  | 1.4432
[13 empty] | C Non choked w/ reducers | 5 |  | 0.091472 |  |  | 2.741 |  |  | 6.8939 |  |  | 14.011 |  |  | 25.4891 |  |  | 42.9093 |  |  | 73.3708 |  |  | 150.1107 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.089717 |  |  | 2.6877 |  |  | 6.7664 |  |  | 13.7213 |  |  | 24.7596 |  |  | 40.8428 |  |  | 65.1808 |  |  | 102.5426 |  |  | 145.4548 |  |  | 368.9022
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.091472 |  |  | 2.741 |  |  | 6.8939 |  |  | 14.011 |  |  | 25.4891 |  |  | 42.9093 |  |  | 73.3708 |  |  | 150.1107 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9085 | 21.1549 |  | 2.259 | 632.4121 |  | 3.1061 | 1564.0305 |  | 3.189 | 3046.3321 |  | 1.1109 | 5010.0948 |  | 4.5093 | 7027.0436 |  | 20.8708 | 8922.4807 |  | 77.7107 | 10462.3104 |  | 7174 | 11672.4685 |  | 7174 | 13022.6037
[13 empty] | Next iteration flow rate |  |  | 21.578 | Abs Value of | Flow this | 638.7363 | Abs Value of | Flow this | 1579.6708 | Abs Value of | Flow this | 3076.7955 | Abs Value of | Flow this | 5060.1957 | Abs Value of | Flow this | 7097.314 | Abs Value of | Flow this | 9011.7056 | Abs Value of | Flow this | 10566.9335 | Abs Value of | Flow this | 11789.1932 | Abs Value of | Flow this | 13152.8297 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3601 |  |  | 99.5277 |  |  | 96.7478 |  |  | 90.3123 |  |  | 80.4364 |  |  | 68.139 |  |  | 55.997 |  |  | 45.1008 |  |  | 31.5382
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48412 |  |  | 0.4801 |  |  | 0.46669 |  |  | 0.43565 |  |  | 0.38801 |  |  | 0.32869 |  |  | 0.27012 |  |  | 0.21756 |  |  | 0.15213
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3601 |  |  | 49.5277 |  |  | 46.7478 |  |  | 40.3123 |  |  | 30.4364 |  |  | 18.139 |  |  | 5.997 |  |  | -4.8992 |  |  | -18.4618
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50179 |  |  | 0.49763 |  |  | 0.48319 |  |  | 0.44637 |  |  | 0.37839 |  |  | 0.26621 |  |  | 0.1071 |  |  | -0.10863 |  |  | -0.58538
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73872 |  |  | 0.737 |  |  | 0.74113 |  |  | 0.7543 |  |  | 0.77984 |  |  | 0.83442 |  |  | 0.92722 |  |  | 1.061 |  |  | 1.4991
[13 empty] | C Non choked w/ reducers | 5 |  | 0.093302 |  |  | 2.7685 |  |  | 6.9644 |  |  | 14.1638 |  |  | 25.8137 |  |  | 43.6272 |  |  | 75.3644 |  |  | 161.9386 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.091511 |  |  | 2.7146 |  |  | 6.8354 |  |  | 13.8691 |  |  | 25.0629 |  |  | 41.4542 |  |  | 66.4491 |  |  | 105.1907 |  |  | 150.4665 |  |  | 388.6496
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.093302 |  |  | 2.7685 |  |  | 6.9644 |  |  | 14.1638 |  |  | 25.8137 |  |  | 43.6272 |  |  | 75.3644 |  |  | 161.9386 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9067 | 21.578 |  | 2.2315 | 638.7363 |  | 3.0356 | 1579.6708 |  | 3.0362 | 3076.7955 |  | 0.78634 | 5060.1957 |  | 5.2272 | 7097.314 |  | 22.8644 | 9011.7056 |  | 89.5386 | 10566.9335 |  | 7174 | 11789.1932 |  | 7174 | 13152.8297
[13 empty] | Next iteration flow rate |  |  | 22.0095 | Abs Value of | Flow this | 645.1236 | Abs Value of | Flow this | 1595.4675 | Abs Value of | Flow this | 3107.5634 | Abs Value of | Flow this | 5110.7977 | Abs Value of | Flow this | 7168.2872 | Abs Value of | Flow this | 9101.8226 | Abs Value of | Flow this | 10672.6028 | Abs Value of | Flow this | 11907.0851 | Abs Value of | Flow this | 13284.358 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3568 |  |  | 99.5077 |  |  | 96.672 |  |  | 90.107 |  |  | 80.0327 |  |  | 67.4881 |  |  | 55.102 |  |  | 43.9869 |  |  | 30.1516
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.4841 |  |  | 0.48001 |  |  | 0.46633 |  |  | 0.43466 |  |  | 0.38606 |  |  | 0.32555 |  |  | 0.2658 |  |  | 0.21218 |  |  | 0.14545
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3568 |  |  | 49.5077 |  |  | 46.672 |  |  | 40.107 |  |  | 30.0327 |  |  | 17.4881 |  |  | 5.102 |  |  | -6.0131 |  |  | -19.8484
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50178 |  |  | 0.49753 |  |  | 0.48279 |  |  | 0.4451 |  |  | 0.37526 |  |  | 0.25913 |  |  | 0.092593 |  |  | -0.1367 |  |  | -0.65829
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73873 |  |  | 0.73705 |  |  | 0.74134 |  |  | 0.755 |  |  | 0.78166 |  |  | 0.83882 |  |  | 0.93707 |  |  | 1.0768 |  |  | 1.5612
[13 empty] | C Non choked w/ reducers | 5 |  | 0.095168 |  |  | 2.7963 |  |  | 7.0357 |  |  | 14.3184 |  |  | 26.1441 |  |  | 44.3666 |  |  | 77.4859 |  |  | 176.878 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.093341 |  |  | 2.7419 |  |  | 6.9052 |  |  | 14.0188 |  |  | 25.3711 |  |  | 42.0799 |  |  | 67.7609 |  |  | 107.9682 |  |  | 155.8199 |  |  | 410.5877
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.095168 |  |  | 2.7963 |  |  | 7.0357 |  |  | 14.3184 |  |  | 26.1441 |  |  | 44.3666 |  |  | 77.4859 |  |  | 176.878 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9048 | 22.0095 |  | 2.2037 | 645.1236 |  | 2.9643 | 1595.4675 |  | 2.8816 | 3107.5634 |  | 0.45589 | 5110.7977 |  | 5.9666 | 7168.2872 |  | 24.9859 | 9101.8226 |  | 104.478 | 10672.6028 |  | 7174 | 11907.0851 |  | 7174 | 13284.358
[13 empty] | Next iteration flow rate |  |  | 22.4497 | Abs Value of | Flow this | 651.5749 | Abs Value of | Flow this | 1611.4221 | Abs Value of | Flow this | 3138.639 | Abs Value of | Flow this | 5161.9056 | Abs Value of | Flow this | 7239.9701 | Abs Value of | Flow this | 9192.8408 | Abs Value of | Flow this | 10779.3289 | Abs Value of | Flow this | 12026.156 | Abs Value of | Flow this | 13417.2016 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3535 |  |  | 99.4873 |  |  | 96.5946 |  |  | 89.8977 |  |  | 79.6208 |  |  | 66.8241 |  |  | 54.1891 |  |  | 42.8505 |  |  | 28.7372
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48409 |  |  | 0.47991 |  |  | 0.46595 |  |  | 0.43365 |  |  | 0.38408 |  |  | 0.32235 |  |  | 0.2614 |  |  | 0.2067 |  |  | 0.13862
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3535 |  |  | 49.4873 |  |  | 46.5946 |  |  | 39.8977 |  |  | 29.6208 |  |  | 16.8241 |  |  | 4.1891 |  |  | -7.1495 |  |  | -21.2628
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50176 |  |  | 0.49742 |  |  | 0.48237 |  |  | 0.44381 |  |  | 0.37202 |  |  | 0.25177 |  |  | 0.077305 |  |  | -0.16685 |  |  | -0.73991
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73873 |  |  | 0.73711 |  |  | 0.74157 |  |  | 0.75571 |  |  | 0.78354 |  |  | 0.8434 |  |  | 0.94746 |  |  | 1.0937 |  |  | 1.6308
[13 empty] | C Non choked w/ reducers | 5 |  | 0.097071 |  |  | 2.8243 |  |  | 7.1077 |  |  | 14.4751 |  |  | 26.4806 |  |  | 45.1287 |  |  | 79.7502 |  |  | 196.6287 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.095208 |  |  | 2.7694 |  |  | 6.9757 |  |  | 14.1703 |  |  | 25.6845 |  |  | 42.7206 |  |  | 69.1186 |  |  | 110.8851 |  |  | 161.5516 |  |  | 435.105
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.097071 |  |  | 2.8243 |  |  | 7.1077 |  |  | 14.4751 |  |  | 26.4806 |  |  | 45.1287 |  |  | 79.7502 |  |  | 196.6287 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9029 | 22.4497 |  | 2.1757 | 651.5749 |  | 2.8923 | 1611.4221 |  | 2.7249 | 3138.639 |  | 0.1194 | 5161.9056 |  | 6.7287 | 7239.9701 |  | 27.2502 | 9192.8408 |  | 124.2287 | 10779.3289 |  | 7174 | 12026.156 |  | 7174 | 13417.2016
[13 empty] | Next iteration flow rate |  |  | 22.8987 | Abs Value of | Flow this | 658.0906 | Abs Value of | Flow this | 1627.5364 | Abs Value of | Flow this | 3170.0254 | Abs Value of | Flow this | 5213.5247 | Abs Value of | Flow this | 7312.3698 | Abs Value of | Flow this | 9284.7692 | Abs Value of | Flow this | 10887.1221 | Abs Value of | Flow this | 12146.4176 | Abs Value of | Flow this | 13551.3736 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3501 |  |  | 99.4665 |  |  | 96.5156 |  |  | 89.6841 |  |  | 79.2007 |  |  | 66.1467 |  |  | 53.2578 |  |  | 41.6913 |  |  | 27.2943
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48407 |  |  | 0.47981 |  |  | 0.46557 |  |  | 0.43262 |  |  | 0.38205 |  |  | 0.31908 |  |  | 0.25691 |  |  | 0.20111 |  |  | 0.13166
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3501 |  |  | 49.4665 |  |  | 46.5156 |  |  | 39.6841 |  |  | 29.2007 |  |  | 16.1467 |  |  | 3.2578 |  |  | -8.3087 |  |  | -22.7057
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50174 |  |  | 0.49732 |  |  | 0.48195 |  |  | 0.44249 |  |  | 0.36869 |  |  | 0.2441 |  |  | 0.06117 |  |  | -0.19929 |  |  | -0.83189
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73874 |  |  | 0.73716 |  |  | 0.74179 |  |  | 0.75644 |  |  | 0.78548 |  |  | 0.84817 |  |  | 0.95843 |  |  | 1.1119 |  |  | 1.7092
[13 empty] | C Non choked w/ reducers | 5 |  | 0.099013 |  |  | 2.8527 |  |  | 7.1805 |  |  | 14.6338 |  |  | 26.8233 |  |  | 45.9147 |  |  | 82.1754 |  |  | 224.561 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.097112 |  |  | 2.7972 |  |  | 7.0469 |  |  | 14.3238 |  |  | 26.0032 |  |  | 43.3767 |  |  | 70.5246 |  |  | 113.9524 |  |  | 167.704 |  |  | 462.6876
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.099013 |  |  | 2.8527 |  |  | 7.1805 |  |  | 14.6338 |  |  | 26.8233 |  |  | 45.9147 |  |  | 82.1754 |  |  | 224.561 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.901 | 22.8987 |  | 2.1473 | 658.0906 |  | 2.8195 | 1627.5364 |  | 2.5662 | 3170.0254 |  | 0.22331 | 5213.5247 |  | 7.5147 | 7312.3698 |  | 29.6754 | 9284.7692 |  | 152.161 | 10887.1221 |  | 7174 | 12146.4176 |  | 7174 | 13551.3736
[13 empty] | Next iteration flow rate |  |  | 23.3567 | Abs Value of | Flow this | 664.6715 | Abs Value of | Flow this | 1643.8117 | Abs Value of | Flow this | 3201.7257 | Abs Value of | Flow this | 5265.6599 | Abs Value of | Flow this | 7385.4935 | Abs Value of | Flow this | 9377.6169 | Abs Value of | Flow this | 10995.9934 | Abs Value of | Flow this | 12267.8817 | Abs Value of | Flow this | 13686.8873 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3466 |  |  | 99.4453 |  |  | 96.4351 |  |  | 89.4662 |  |  | 78.7721 |  |  | 65.4558 |  |  | 52.3077 |  |  | 40.5088 |  |  | 25.8224
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48405 |  |  | 0.47971 |  |  | 0.46519 |  |  | 0.43157 |  |  | 0.37998 |  |  | 0.31575 |  |  | 0.25232 |  |  | 0.19541 |  |  | 0.12456
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3466 |  |  | 49.4453 |  |  | 46.4351 |  |  | 39.4662 |  |  | 28.7721 |  |  | 15.4558 |  |  | 2.3077 |  |  | -9.4912 |  |  | -24.1776
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50173 |  |  | 0.49721 |  |  | 0.48152 |  |  | 0.44113 |  |  | 0.36526 |  |  | 0.23613 |  |  | 0.044119 |  |  | -0.2343 |  |  | -0.9363
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73875 |  |  | 0.73722 |  |  | 0.74203 |  |  | 0.75718 |  |  | 0.78748 |  |  | 0.85313 |  |  | 0.97002 |  |  | 1.1316 |  |  | 1.7983
[13 empty] | C Non choked w/ reducers | 5 |  | 0.10099 |  |  | 2.8813 |  |  | 7.2541 |  |  | 14.7945 |  |  | 27.1724 |  |  | 46.726 |  |  | 84.7825 |  |  | 268.6651 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.099055 |  |  | 2.8252 |  |  | 7.1189 |  |  | 14.4791 |  |  | 26.3271 |  |  | 44.0488 |  |  | 71.9818 |  |  | 117.1822 |  |  | 174.3255 |  |  | 493.9517
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.10099 |  |  | 2.8813 |  |  | 7.2541 |  |  | 14.7945 |  |  | 27.1724 |  |  | 46.726 |  |  | 84.7825 |  |  | 268.6651 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.899 | 23.3567 |  | 2.1187 | 664.6715 |  | 2.7459 | 1643.8117 |  | 2.4055 | 3201.7257 |  | 0.57242 | 5265.6599 |  | 8.326 | 7385.4935 |  | 32.2825 | 9377.6169 |  | 196.2651 | 10995.9934 |  | 7174 | 12267.8817 |  | 7174 | 13686.8873
[13 empty] | Next iteration flow rate |  |  | 23.8238 | Abs Value of | Flow this | 671.3182 | Abs Value of | Flow this | 1660.2499 | Abs Value of | Flow this | 3233.7429 | Abs Value of | Flow this | 5318.3165 | Abs Value of | Flow this | 7459.3484 | Abs Value of | Flow this | 9471.3931 | Abs Value of | Flow this | 11105.9533 | Abs Value of | Flow this | 12390.5606 | Abs Value of | Flow this | 13823.7562 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3431 |  |  | 99.4236 |  |  | 96.3529 |  |  | 89.244 |  |  | 78.3349 |  |  | 64.7509 |  |  | 51.3386 |  |  | 39.3025 |  |  | 24.3209
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48404 |  |  | 0.4796 |  |  | 0.46479 |  |  | 0.4305 |  |  | 0.37787 |  |  | 0.31235 |  |  | 0.24765 |  |  | 0.18959 |  |  | 0.11732
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3431 |  |  | 49.4236 |  |  | 46.3529 |  |  | 39.244 |  |  | 28.3349 |  |  | 14.7509 |  |  | 1.3386 |  |  | -10.6975 |  |  | -25.6791
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50171 |  |  | 0.4971 |  |  | 0.48107 |  |  | 0.43974 |  |  | 0.36172 |  |  | 0.22781 |  |  | 0.026074 |  |  | -0.27218 |  |  | -1.0558
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73876 |  |  | 0.73728 |  |  | 0.74226 |  |  | 0.75795 |  |  | 0.78954 |  |  | 0.8583 |  |  | 0.98228 |  |  | 1.1529 |  |  | 1.9002
[13 empty] | C Non choked w/ reducers | 5 |  | 0.10301 |  |  | 2.9103 |  |  | 7.3285 |  |  | 14.9572 |  |  | 27.5281 |  |  | 47.564 |  |  | 87.5971 |  |  | 355.1422 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.10104 |  |  | 2.8536 |  |  | 7.1916 |  |  | 14.6363 |  |  | 26.6566 |  |  | 44.7376 |  |  | 73.493 |  |  | 120.5882 |  |  | 181.4727 |  |  | 529.6909
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.10301 |  |  | 2.9103 |  |  | 7.3285 |  |  | 14.9572 |  |  | 27.5281 |  |  | 47.564 |  |  | 87.5971 |  |  | 355.1422 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.897 | 23.8238 |  | 2.0897 | 671.3182 |  | 2.6715 | 1660.2499 |  | 2.2428 | 3233.7429 |  | 0.92814 | 5318.3165 |  | 9.164 | 7459.3484 |  | 35.0971 | 9471.3931 |  | 282.7422 | 11105.9533 |  | 7174 | 12390.5606 |  | 7174 | 13823.7562
[13 empty] | Next iteration flow rate |  |  | 24.3003 | Abs Value of | Flow this | 678.0314 | Abs Value of | Flow this | 1676.8524 | Abs Value of | Flow this | 3266.0804 | Abs Value of | Flow this | 5371.4997 | Abs Value of | Flow this | 7533.9419 | Abs Value of | Flow this | 9566.107 | Abs Value of | Flow this | 11217.0128 | Abs Value of | Flow this | 12514.4662 | Abs Value of | Flow this | 13961.9938 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5226 |  |  | 100.3395 |  |  | 99.4015 |  |  | 96.2691 |  |  | 89.0173 |  |  | 77.889 |  |  | 64.0319 |  |  | 50.35 |  |  | 38.072 |  |  | 22.7892
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48402 |  |  | 0.4795 |  |  | 0.46438 |  |  | 0.4294 |  |  | 0.37572 |  |  | 0.30888 |  |  | 0.24288 |  |  | 0.18365 |  |  | 0.10993
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5226 |  |  | 50.3395 |  |  | 49.4015 |  |  | 46.2691 |  |  | 39.0173 |  |  | 27.889 |  |  | 14.0319 |  |  | 0.35002 |  |  | -11.928 |  |  | -27.2108
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50169 |  |  | 0.49699 |  |  | 0.48062 |  |  | 0.43831 |  |  | 0.35806 |  |  | 0.21914 |  |  | 0.0069518 |  |  | -0.3133 |  |  | -1.194
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73877 |  |  | 0.73734 |  |  | 0.7425 |  |  | 0.75873 |  |  | 0.79167 |  |  | 0.8637 |  |  | 0.99528 |  |  | 1.176 |  |  | 2.018
[13 empty] | C Non choked w/ reducers | 5 |  | 0.10507 |  |  | 2.9395 |  |  | 7.4036 |  |  | 15.1221 |  |  | 27.8907 |  |  | 48.4302 |  |  | 90.6497 |  |  | 699.0669 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.10306 |  |  | 2.8822 |  |  | 7.2652 |  |  | 14.7956 |  |  | 26.9918 |  |  | 45.4437 |  |  | 75.0614 |  |  | 124.1855 |  |  | 189.2115 |  |  | 570.9441
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.10507 |  |  | 2.9395 |  |  | 7.4036 |  |  | 15.1221 |  |  | 27.8907 |  |  | 48.4302 |  |  | 90.6497 |  |  | 699.0669 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8949 | 24.3003 |  | 2.0605 | 678.0314 |  | 2.5964 | 1676.8524 |  | 2.0779 | 3266.0804 |  | 1.2907 | 5371.4997 |  | 10.0302 | 7533.9419 |  | 38.1497 | 9566.107 |  | 626.6669 | 11217.0128 |  | 7174 | 12514.4662 |  | 7174 | 13961.9938
[13 empty] | Next iteration flow rate |  |  | 24.7863 | Abs Value of | Flow this | 684.8117 | Abs Value of | Flow this | 1693.6209 | Abs Value of | Flow this | 3298.7412 | Abs Value of | Flow this | 5425.2147 | Abs Value of | Flow this | 7609.2813 | Abs Value of | Flow this | 9661.7681 | Abs Value of | Flow this | 11329.183 | Abs Value of | Flow this | 12639.6108 | Abs Value of | Flow this | 14101.6137 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5225 |  |  | 100.3358 |  |  | 99.379 |  |  | 96.1836 |  |  | 88.786 |  |  | 77.434 |  |  | 63.2985 |  |  | 49.3416 |  |  | 36.8167 |  |  | 21.2268
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.484 |  |  | 0.47939 |  |  | 0.46397 |  |  | 0.42829 |  |  | 0.37353 |  |  | 0.30534 |  |  | 0.23801 |  |  | 0.1776 |  |  | 0.10239
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5225 |  |  | 50.3358 |  |  | 49.379 |  |  | 46.1836 |  |  | 38.786 |  |  | 27.434 |  |  | 13.2985 |  |  | -0.65845 |  |  | -13.1833 |  |  | -28.7732
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50167 |  |  | 0.49688 |  |  | 0.48016 |  |  | 0.43685 |  |  | 0.35429 |  |  | 0.21009 |  |  | -0.013345 |  |  | -0.35808 |  |  | -1.3555
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73878 |  |  | 0.7374 |  |  | 0.74275 |  |  | 0.75954 |  |  | 0.79386 |  |  | 0.86932 |  |  | 1.0091 |  |  | 1.2011 |  |  | 2.1557
[13 empty] | C Non choked w/ reducers | 5 |  | 0.10717 |  |  | 2.969 |  |  | 7.4796 |  |  | 15.2892 |  |  | 28.2602 |  |  | 49.3263 |  |  | 93.9781 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.10512 |  |  | 2.9112 |  |  | 7.3395 |  |  | 14.9568 |  |  | 27.3327 |  |  | 46.1678 |  |  | 76.6905 |  |  | 127.9909 |  |  | 197.6193 |  |  | 619.0994
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.10717 |  |  | 2.969 |  |  | 7.4796 |  |  | 15.2892 |  |  | 28.2602 |  |  | 49.3263 |  |  | 93.9781 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8928 | 24.7863 |  | 2.031 | 684.8117 |  | 2.5204 | 1693.6209 |  | 1.9108 | 3298.7412 |  | 1.6602 | 5425.2147 |  | 10.9263 | 7609.2813 |  | 41.4781 | 9661.7681 |  | 7174 | 11329.183 |  | 7174 | 12639.6108 |  | 7174 | 14101.6137
[13 empty] | Next iteration flow rate |  |  | 25.2821 | Abs Value of | Flow this | 691.6598 | Abs Value of | Flow this | 1710.5571 | Abs Value of | Flow this | 3331.7286 | Abs Value of | Flow this | 5479.4669 | Abs Value of | Flow this | 7685.3741 | Abs Value of | Flow this | 9758.3858 | Abs Value of | Flow this | 11442.4748 | Abs Value of | Flow this | 12766.0069 | Abs Value of | Flow this | 14242.6298 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5225 |  |  | 100.332 |  |  | 99.356 |  |  | 96.0964 |  |  | 88.5501 |  |  | 76.9699 |  |  | 62.5503 |  |  | 48.3128 |  |  | 35.5362 |  |  | 19.6329
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48398 |  |  | 0.47928 |  |  | 0.46355 |  |  | 0.42715 |  |  | 0.37129 |  |  | 0.30173 |  |  | 0.23305 |  |  | 0.17142 |  |  | 0.094706
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5225 |  |  | 50.332 |  |  | 49.356 |  |  | 46.0964 |  |  | 38.5501 |  |  | 26.9699 |  |  | 12.5503 |  |  | -1.6872 |  |  | -14.4638 |  |  | -30.3671
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50165 |  |  | 0.49676 |  |  | 0.47969 |  |  | 0.43535 |  |  | 0.3504 |  |  | 0.20064 |  |  | -0.034922 |  |  | -0.40702 |  |  | -1.5467
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73879 |  |  | 0.73746 |  |  | 0.743 |  |  | 0.76037 |  |  | 0.79613 |  |  | 0.8752 |  |  | 1.0237 |  |  | 1.2286 |  |  | 2.3187
[13 empty] | C Non choked w/ reducers | 5 |  | 0.10932 |  |  | 2.9988 |  |  | 7.5564 |  |  | 15.4584 |  |  | 28.637 |  |  | 50.2542 |  |  | 97.6289 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.10722 |  |  | 2.9404 |  |  | 7.4146 |  |  | 15.1201 |  |  | 27.6796 |  |  | 46.9106 |  |  | 78.3839 |  |  | 132.0234 |  |  | 206.7876 |  |  | 676.0529
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.10932 |  |  | 2.9988 |  |  | 7.5564 |  |  | 15.4584 |  |  | 28.637 |  |  | 50.2542 |  |  | 97.6289 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8907 | 25.2821 |  | 2.0012 | 691.6598 |  | 2.4436 | 1710.5571 |  | 1.7416 | 3331.7286 |  | 2.037 | 5479.4669 |  | 11.8542 | 7685.3741 |  | 45.1289 | 9758.3858 |  | 7174 | 11442.4748 |  | 7174 | 12766.0069 |  | 7174 | 14242.6298
[13 empty] | Next iteration flow rate |  |  | 25.7877 | Abs Value of | Flow this | 698.5764 | Abs Value of | Flow this | 1727.6627 | Abs Value of | Flow this | 3365.0459 | Abs Value of | Flow this | 5534.2615 | Abs Value of | Flow this | 7762.2278 | Abs Value of | Flow this | 9855.9696 | Abs Value of | Flow this | 11556.8995 | Abs Value of | Flow this | 12893.667 | Abs Value of | Flow this | 14385.0561 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5225 |  |  | 100.3282 |  |  | 99.3326 |  |  | 96.0074 |  |  | 88.3095 |  |  | 76.4965 |  |  | 61.787 |  |  | 47.2634 |  |  | 34.23 |  |  | 18.0071
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48397 |  |  | 0.47916 |  |  | 0.46312 |  |  | 0.42599 |  |  | 0.36901 |  |  | 0.29805 |  |  | 0.22799 |  |  | 0.16512 |  |  | 0.086863
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5225 |  |  | 50.3282 |  |  | 49.3326 |  |  | 46.0074 |  |  | 38.3095 |  |  | 26.4965 |  |  | 11.787 |  |  | -2.7366 |  |  | -15.77 |  |  | -31.9929
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50164 |  |  | 0.49664 |  |  | 0.47921 |  |  | 0.43381 |  |  | 0.34638 |  |  | 0.19077 |  |  | -0.057901 |  |  | -0.46071 |  |  | -1.7767
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.7388 |  |  | 0.73752 |  |  | 0.74326 |  |  | 0.76121 |  |  | 0.79846 |  |  | 0.88134 |  |  | 1.0393 |  |  | 1.2587 |  |  | 2.5148
[13 empty] | C Non choked w/ reducers | 5 |  | 0.1115 |  |  | 3.0289 |  |  | 7.6341 |  |  | 15.6299 |  |  | 29.0212 |  |  | 51.2159 |  |  | 101.6607 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.10936 |  |  | 2.9699 |  |  | 7.4905 |  |  | 15.2854 |  |  | 28.0325 |  |  | 47.6729 |  |  | 80.1457 |  |  | 136.3043 |  |  | 216.8255 |  |  | 744.4658
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.1115 |  |  | 3.0289 |  |  | 7.6341 |  |  | 15.6299 |  |  | 29.0212 |  |  | 51.2159 |  |  | 101.6607 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8885 | 25.7877 |  | 1.9711 | 698.5764 |  | 2.3659 | 1727.6627 |  | 1.5701 | 3365.0459 |  | 2.4212 | 5534.2615 |  | 12.8159 | 7762.2278 |  | 49.1607 | 9855.9696 |  | 7174 | 11556.8995 |  | 7174 | 12893.667 |  | 7174 | 14385.0561
[13 empty] | Next iteration flow rate |  |  | 26.3034 | Abs Value of | Flow this | 705.5622 | Abs Value of | Flow this | 1744.9393 | Abs Value of | Flow this | 3398.6963 | Abs Value of | Flow this | 5589.6041 | Abs Value of | Flow this | 7839.8501 | Abs Value of | Flow this | 9954.5293 | Abs Value of | Flow this | 11672.4685 | Abs Value of | Flow this | 13022.6037 | Abs Value of | Flow this | 14528.9067 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5225 |  |  | 100.3243 |  |  | 99.3086 |  |  | 95.9166 |  |  | 88.064 |  |  | 76.0136 |  |  | 61.0084 |  |  | 46.1929 |  |  | 32.8975 |  |  | 16.3485
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48395 |  |  | 0.47905 |  |  | 0.46268 |  |  | 0.42481 |  |  | 0.36668 |  |  | 0.29429 |  |  | 0.22283 |  |  | 0.15869 |  |  | 0.078862
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5225 |  |  | 50.3243 |  |  | 49.3086 |  |  | 45.9166 |  |  | 38.064 |  |  | 26.0136 |  |  | 11.0084 |  |  | -3.8071 |  |  | -17.1025 |  |  | -33.6515
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50162 |  |  | 0.49652 |  |  | 0.47871 |  |  | 0.43223 |  |  | 0.34222 |  |  | 0.18044 |  |  | -0.082418 |  |  | -0.51987 |  |  | -2.0584
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73881 |  |  | 0.73759 |  |  | 0.74353 |  |  | 0.76208 |  |  | 0.80088 |  |  | 0.88777 |  |  | 1.056 |  |  | 1.292 |  |  | 2.7549
[13 empty] | C Non choked w/ reducers | 5 |  | 0.11373 |  |  | 3.0594 |  |  | 7.7125 |  |  | 15.8037 |  |  | 29.4132 |  |  | 52.2136 |  |  | 106.1485 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.11155 |  |  | 2.9997 |  |  | 7.5672 |  |  | 15.4529 |  |  | 28.3918 |  |  | 48.4555 |  |  | 81.9802 |  |  | 140.8578 |  |  | 227.8639 |  |  | 828.1922
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.11373 |  |  | 3.0594 |  |  | 7.7125 |  |  | 15.8037 |  |  | 29.4132 |  |  | 52.2136 |  |  | 106.1485 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8863 | 26.3034 |  | 1.9406 | 705.5622 |  | 2.2875 | 1744.9393 |  | 1.3963 | 3398.6963 |  | 2.8132 | 5589.6041 |  | 13.8136 | 7839.8501 |  | 53.6485 | 9954.5293 |  | 7174 | 11672.4685 |  | 7174 | 13022.6037 |  | 7174 | 14528.9067
[13 empty] | Next iteration flow rate |  |  | 26.8295 | Abs Value of | Flow this | 712.6178 | Abs Value of | Flow this | 1762.3887 | Abs Value of | Flow this | 3432.6833 | Abs Value of | Flow this | 5645.5002 | Abs Value of | Flow this | 7918.2486 | Abs Value of | Flow this | 10054.0746 | Abs Value of | Flow this | 11789.1932 | Abs Value of | Flow this | 13152.8297 | Abs Value of | Flow this | 14674.1958 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5225 |  |  | 100.3203 |  |  | 99.2842 |  |  | 95.8241 |  |  | 87.8136 |  |  | 75.521 |  |  | 60.2142 |  |  | 45.1008 |  |  | 31.5382 |  |  | 14.6566
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48393 |  |  | 0.47893 |  |  | 0.46224 |  |  | 0.4236 |  |  | 0.3643 |  |  | 0.29046 |  |  | 0.21756 |  |  | 0.15213 |  |  | 0.070701
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5225 |  |  | 50.3203 |  |  | 49.2842 |  |  | 45.8241 |  |  | 37.8136 |  |  | 25.521 |  |  | 10.2142 |  |  | -4.8992 |  |  | -18.4618 |  |  | -35.3434
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.5016 |  |  | 0.4964 |  |  | 0.47821 |  |  | 0.43061 |  |  | 0.33793 |  |  | 0.16963 |  |  | -0.10863 |  |  | -0.58538 |  |  | -2.4114
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73882 |  |  | 0.73765 |  |  | 0.7438 |  |  | 0.76297 |  |  | 0.80338 |  |  | 0.89449 |  |  | 1.0738 |  |  | 1.3288 |  |  | 3.0559
[13 empty] | C Non choked w/ reducers | 5 |  | 0.11601 |  |  | 3.0901 |  |  | 7.7918 |  |  | 15.9797 |  |  | 29.8131 |  |  | 53.2497 |  |  | 111.1897 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.11378 |  |  | 3.0298 |  |  | 7.6448 |  |  | 15.6225 |  |  | 28.7575 |  |  | 49.2593 |  |  | 83.8922 |  |  | 145.7111 |  |  | 240.0615 |  |  | 933.0336
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.11601 |  |  | 3.0901 |  |  | 7.7918 |  |  | 15.9797 |  |  | 29.8131 |  |  | 53.2497 |  |  | 111.1897 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.884 | 26.8295 |  | 1.9099 | 712.6178 |  | 2.2082 | 1762.3887 |  | 1.2203 | 3432.6833 |  | 3.2131 | 5645.5002 |  | 14.8497 | 7918.2486 |  | 58.6897 | 10054.0746 |  | 7174 | 11789.1932 |  | 7174 | 13152.8297 |  | 7174 | 14674.1958
[13 empty] | Next iteration flow rate |  |  | 27.3661 | Abs Value of | Flow this | 719.744 | Abs Value of | Flow this | 1780.0126 | Abs Value of | Flow this | 3467.0101 | Abs Value of | Flow this | 5701.9552 | Abs Value of | Flow this | 7997.4311 | Abs Value of | Flow this | 10154.6154 | Abs Value of | Flow this | 11907.0851 | Abs Value of | Flow this | 13284.358 | Abs Value of | Flow this | 14820.9377 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5225 |  |  | 100.3162 |  |  | 99.2593 |  |  | 95.7296 |  |  | 87.5581 |  |  | 75.0184 |  |  | 59.404 |  |  | 43.9869 |  |  | 30.1516 |  |  | 12.9307
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48391 |  |  | 0.47881 |  |  | 0.46178 |  |  | 0.42236 |  |  | 0.36188 |  |  | 0.28655 |  |  | 0.21218 |  |  | 0.14545 |  |  | 0.062375
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5225 |  |  | 50.3162 |  |  | 49.2593 |  |  | 45.7296 |  |  | 37.5581 |  |  | 25.0184 |  |  | 9.404 |  |  | -6.0131 |  |  | -19.8484 |  |  | -37.0693
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50158 |  |  | 0.49627 |  |  | 0.4777 |  |  | 0.42895 |  |  | 0.3335 |  |  | 0.15831 |  |  | -0.1367 |  |  | -0.65829 |  |  | -2.8668
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73883 |  |  | 0.73772 |  |  | 0.74407 |  |  | 0.76389 |  |  | 0.80596 |  |  | 0.90153 |  |  | 1.0929 |  |  | 1.3697 |  |  | 3.4441
[13 empty] | C Non choked w/ reducers | 5 |  | 0.11833 |  |  | 3.1212 |  |  | 7.872 |  |  | 16.1582 |  |  | 30.2213 |  |  | 54.3268 |  |  | 116.914 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.11606 |  |  | 3.0602 |  |  | 7.7232 |  |  | 15.7943 |  |  | 29.1298 |  |  | 50.0852 |  |  | 85.8867 |  |  | 150.8953 |  |  | 253.6122 |  |  | 1068.1451
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.11833 |  |  | 3.1212 |  |  | 7.872 |  |  | 16.1582 |  |  | 30.2213 |  |  | 54.3268 |  |  | 116.914 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8817 | 27.3661 |  | 1.8788 | 719.744 |  | 2.128 | 1780.0126 |  | 1.0418 | 3467.0101 |  | 3.6213 | 5701.9552 |  | 15.9268 | 7997.4311 |  | 64.414 | 10154.6154 |  | 7174 | 11907.0851 |  | 7174 | 13284.358 |  | 7174 | 14820.9377
[13 empty] | Next iteration flow rate |  |  | 27.9134 | Abs Value of | Flow this | 726.9414 | Abs Value of | Flow this | 1797.8127 | Abs Value of | Flow this | 3501.6802 | Abs Value of | Flow this | 5758.9747 | Abs Value of | Flow this | 8077.4054 | Abs Value of | Flow this | 10256.1615 | Abs Value of | Flow this | 12026.156 | Abs Value of | Flow this | 13417.2016 | Abs Value of | Flow this | 14969.1471 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5225 |  |  | 100.3121 |  |  | 99.2339 |  |  | 95.6333 |  |  | 87.2975 |  |  | 74.5058 |  |  | 58.5775 |  |  | 42.8505 |  |  | 28.7372 |  |  | 11.1701
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48389 |  |  | 0.47869 |  |  | 0.46132 |  |  | 0.42111 |  |  | 0.3594 |  |  | 0.28257 |  |  | 0.2067 |  |  | 0.13862 |  |  | 0.053882
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5225 |  |  | 50.3121 |  |  | 49.2339 |  |  | 45.6333 |  |  | 37.2975 |  |  | 24.5058 |  |  | 8.5775 |  |  | -7.1495 |  |  | -21.2628 |  |  | -38.8299
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50156 |  |  | 0.49614 |  |  | 0.47717 |  |  | 0.42725 |  |  | 0.32891 |  |  | 0.14643 |  |  | -0.16685 |  |  | -0.73991 |  |  | -3.4762
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73884 |  |  | 0.73779 |  |  | 0.74435 |  |  | 0.76482 |  |  | 0.80863 |  |  | 0.90892 |  |  | 1.1134 |  |  | 1.4155 |  |  | 3.9638
[13 empty] | C Non choked w/ reducers | 5 |  | 0.1207 |  |  | 3.1525 |  |  | 7.9531 |  |  | 16.339 |  |  | 30.638 |  |  | 55.4478 |  |  | 123.4987 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.11838 |  |  | 3.091 |  |  | 7.8024 |  |  | 15.9683 |  |  | 29.5089 |  |  | 50.9341 |  |  | 87.9695 |  |  | 156.4459 |  |  | 268.7561 |  |  | 1248.8686
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.1207 |  |  | 3.1525 |  |  | 7.9531 |  |  | 16.339 |  |  | 30.638 |  |  | 55.4478 |  |  | 123.4987 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8793 | 27.9134 |  | 1.8475 | 726.9414 |  | 2.0469 | 1797.8127 |  | 0.86099 | 3501.6802 |  | 4.038 | 5758.9747 |  | 17.0478 | 8077.4054 |  | 70.9987 | 10256.1615 |  | 7174 | 12026.156 |  | 7174 | 13417.2016 |  | 7174 | 14969.1471
[13 empty] | Next iteration flow rate |  |  | 28.4717 | Abs Value of | Flow this | 734.2109 | Abs Value of | Flow this | 1815.7908 | Abs Value of | Flow this | 3536.697 | Abs Value of | Flow this | 5816.5645 | Abs Value of | Flow this | 8158.1795 | Abs Value of | Flow this | 10358.7232 | Abs Value of | Flow this | 12146.4176 | Abs Value of | Flow this | 13551.3736 | Abs Value of | Flow this | 15118.8386 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5225 |  |  | 100.3078 |  |  | 99.208 |  |  | 95.535 |  |  | 87.0317 |  |  | 73.9828 |  |  | 57.7344 |  |  | 41.6913 |  |  | 27.2943 |  |  | 9.3741
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48387 |  |  | 0.47856 |  |  | 0.46084 |  |  | 0.41983 |  |  | 0.35688 |  |  | 0.2785 |  |  | 0.20111 |  |  | 0.13166 |  |  | 0.045219
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5225 |  |  | 50.3078 |  |  | 49.208 |  |  | 45.535 |  |  | 37.0317 |  |  | 23.9828 |  |  | 7.7344 |  |  | -8.3087 |  |  | -22.7057 |  |  | -40.6259
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50153 |  |  | 0.49601 |  |  | 0.47663 |  |  | 0.4255 |  |  | 0.32417 |  |  | 0.13397 |  |  | -0.19929 |  |  | -0.83189 |  |  | -4.3338
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73885 |  |  | 0.73786 |  |  | 0.74464 |  |  | 0.76579 |  |  | 0.81139 |  |  | 0.91667 |  |  | 1.1354 |  |  | 1.4672 |  |  | 4.6949
[13 empty] | C Non choked w/ reducers | 5 |  | 0.12311 |  |  | 3.1842 |  |  | 8.035 |  |  | 16.5223 |  |  | 31.0636 |  |  | 56.6161 |  |  | 131.1928 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.12075 |  |  | 3.122 |  |  | 7.8825 |  |  | 16.1446 |  |  | 29.895 |  |  | 51.8071 |  |  | 90.1467 |  |  | 162.4038 |  |  | 285.7934 |  |  | 1503.0216
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.12311 |  |  | 3.1842 |  |  | 8.035 |  |  | 16.5223 |  |  | 31.0636 |  |  | 56.6161 |  |  | 131.1928 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8769 | 28.4717 |  | 1.8158 | 734.2109 |  | 1.965 | 1815.7908 |  | 0.67771 | 3536.697 |  | 4.4636 | 5816.5645 |  | 18.2161 | 8158.1795 |  | 78.6928 | 10358.7232 |  | 7174 | 12146.4176 |  | 7174 | 13551.3736 |  | 7174 | 15118.8386
[13 empty] | Next iteration flow rate |  |  | 29.0411 | Abs Value of | Flow this | 741.553 | Abs Value of | Flow this | 1833.9487 | Abs Value of | Flow this | 3572.064 | Abs Value of | Flow this | 5874.7301 | Abs Value of | Flow this | 8239.7613 | Abs Value of | Flow this | 10462.3104 | Abs Value of | Flow this | 12267.8817 | Abs Value of | Flow this | 13686.8873 | Abs Value of | Flow this | 15270.027 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5225 |  |  | 100.3035 |  |  | 99.1816 |  |  | 95.4347 |  |  | 86.7605 |  |  | 73.4494 |  |  | 56.8743 |  |  | 40.5088 |  |  | 25.8224 |  |  | 7.542
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48385 |  |  | 0.47843 |  |  | 0.46036 |  |  | 0.41852 |  |  | 0.35431 |  |  | 0.27435 |  |  | 0.19541 |  |  | 0.12456 |  |  | 0.036381
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5225 |  |  | 50.3035 |  |  | 49.1816 |  |  | 45.4347 |  |  | 36.7605 |  |  | 23.4494 |  |  | 6.8743 |  |  | -9.4912 |  |  | -24.1776 |  |  | -42.458
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50151 |  |  | 0.49587 |  |  | 0.47608 |  |  | 0.4237 |  |  | 0.31926 |  |  | 0.12087 |  |  | -0.2343 |  |  | -0.9363 |  |  | -5.6295
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73886 |  |  | 0.73793 |  |  | 0.74494 |  |  | 0.76678 |  |  | 0.81424 |  |  | 0.92482 |  |  | 1.1592 |  |  | 1.5258 |  |  | 5.7996
[13 empty] | C Non choked w/ reducers | 5 |  | 0.12557 |  |  | 3.2162 |  |  | 8.1178 |  |  | 16.7081 |  |  | 31.4982 |  |  | 57.835 |  |  | 140.3608 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.12316 |  |  | 3.1534 |  |  | 7.9634 |  |  | 16.3232 |  |  | 30.2884 |  |  | 52.7052 |  |  | 92.425 |  |  | 168.8161 |  |  | 305.1046 |  |  | 1886.814
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.12557 |  |  | 3.2162 |  |  | 8.1178 |  |  | 16.7081 |  |  | 31.4982 |  |  | 57.835 |  |  | 140.3608 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8744 | 29.0411 |  | 1.7838 | 741.553 |  | 1.8822 | 1833.9487 |  | 0.49192 | 3572.064 |  | 4.8982 | 5874.7301 |  | 19.435 | 8239.7613 |  | 87.8608 | 10462.3104 |  | 7174 | 12267.8817 |  | 7174 | 13686.8873 |  | 7174 | 15270.027
[13 empty] | Next iteration flow rate |  |  | 29.622 | Abs Value of | Flow this | 748.9685 | Abs Value of | Flow this | 1852.2882 | Abs Value of | Flow this | 3607.7846 | Abs Value of | Flow this | 5933.4774 | Abs Value of | Flow this | 8322.1589 | Abs Value of | Flow this | 10566.9335 | Abs Value of | Flow this | 12390.5606 | Abs Value of | Flow this | 13823.7562 | Abs Value of | Flow this | 15422.7272 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5224 |  |  | 100.2991 |  |  | 99.1546 |  |  | 95.3325 |  |  | 86.4839 |  |  | 72.9052 |  |  | 55.997 |  |  | 39.3025 |  |  | 24.3209 |  |  | 5.6731
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48383 |  |  | 0.4783 |  |  | 0.45987 |  |  | 0.41718 |  |  | 0.35168 |  |  | 0.27012 |  |  | 0.18959 |  |  | 0.11732 |  |  | 0.027366
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5224 |  |  | 50.2991 |  |  | 49.1546 |  |  | 45.3325 |  |  | 36.4839 |  |  | 22.9052 |  |  | 5.997 |  |  | -10.6975 |  |  | -25.6791 |  |  | -44.3269
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50149 |  |  | 0.49574 |  |  | 0.47552 |  |  | 0.42186 |  |  | 0.31418 |  |  | 0.1071 |  |  | -0.27218 |  |  | -1.0558 |  |  | -7.8135
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73888 |  |  | 0.738 |  |  | 0.74524 |  |  | 0.76779 |  |  | 0.8172 |  |  | 0.93339 |  |  | 1.185 |  |  | 1.593 |  |  | 7.6616
[13 empty] | C Non choked w/ reducers | 5 |  | 0.12808 |  |  | 3.2485 |  |  | 8.2016 |  |  | 16.8964 |  |  | 31.9423 |  |  | 59.1087 |  |  | 151.5607 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.12563 |  |  | 3.185 |  |  | 8.0453 |  |  | 16.5041 |  |  | 30.6891 |  |  | 53.6296 |  |  | 94.8118 |  |  | 175.7374 |  |  | 327.18 |  |  | 2533.4802
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.12808 |  |  | 3.2485 |  |  | 8.2016 |  |  | 16.8964 |  |  | 31.9423 |  |  | 59.1087 |  |  | 151.5607 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8719 | 29.622 |  | 1.7515 | 748.9685 |  | 1.7984 | 1852.2882 |  | 0.30358 | 3607.7846 |  | 5.3423 | 5933.4774 |  | 20.7087 | 8322.1589 |  | 99.0607 | 10566.9335 |  | 7174 | 12390.5606 |  | 7174 | 13823.7562 |  | 7174 | 15422.7272
[13 empty] | Next iteration flow rate |  |  | 30.2144 | Abs Value of | Flow this | 756.4582 | Abs Value of | Flow this | 1870.8111 | Abs Value of | Flow this | 3643.8625 | Abs Value of | Flow this | 5992.8122 | Abs Value of | Flow this | 8405.3805 | Abs Value of | Flow this | 10672.6028 | Abs Value of | Flow this | 12514.4662 | Abs Value of | Flow this | 13961.9938 | Abs Value of | Flow this | 15576.9545 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5224 |  |  | 100.2946 |  |  | 99.1271 |  |  | 95.2281 |  |  | 86.2017 |  |  | 72.3501 |  |  | 55.102 |  |  | 38.072 |  |  | 22.7892 |  |  | 3.7666
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.4838 |  |  | 0.47817 |  |  | 0.45936 |  |  | 0.41582 |  |  | 0.349 |  |  | 0.2658 |  |  | 0.18365 |  |  | 0.10993 |  |  | 0.018169
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5224 |  |  | 50.2946 |  |  | 49.1271 |  |  | 45.2281 |  |  | 36.2017 |  |  | 22.3501 |  |  | 5.102 |  |  | -11.928 |  |  | -27.2108 |  |  | -46.2334
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50147 |  |  | 0.4956 |  |  | 0.47495 |  |  | 0.41997 |  |  | 0.30892 |  |  | 0.092593 |  |  | -0.3133 |  |  | -1.194 |  |  | -12.2745
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73889 |  |  | 0.73807 |  |  | 0.74555 |  |  | 0.76883 |  |  | 0.82026 |  |  | 0.94241 |  |  | 1.2129 |  |  | 1.6706 |  |  | 11.465
[13 empty] | C Non choked w/ reducers | 5 |  | 0.13065 |  |  | 3.2812 |  |  | 8.2862 |  |  | 17.0873 |  |  | 32.3963 |  |  | 60.4416 |  |  | 165.7009 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.12814 |  |  | 3.217 |  |  | 8.128 |  |  | 16.6874 |  |  | 31.0974 |  |  | 54.5815 |  |  | 97.3152 |  |  | 183.2316 |  |  | 352.6614 |  |  | 3853.9647
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.13065 |  |  | 3.2812 |  |  | 8.2862 |  |  | 17.0873 |  |  | 32.3963 |  |  | 60.4416 |  |  | 165.7009 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8694 | 30.2144 |  | 1.7188 | 756.4582 |  | 1.7138 | 1870.8111 |  | 0.11265 | 3643.8625 |  | 5.7963 | 5992.8122 |  | 22.0416 | 8405.3805 |  | 113.2009 | 10672.6028 |  | 7174 | 12514.4662 |  | 7174 | 13961.9938 |  | 7174 | 15576.9545
[13 empty] | Next iteration flow rate |  |  | 30.8187 | Abs Value of | Flow this | 764.0228 | Abs Value of | Flow this | 1889.5192 | Abs Value of | Flow this | 3680.3011 | Abs Value of | Flow this | 6052.7403 | Abs Value of | Flow this | 8489.4343 | Abs Value of | Flow this | 10779.3289 | Abs Value of | Flow this | 12639.6108 | Abs Value of | Flow this | 14101.6137 | Abs Value of | Flow this | 15732.724 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5224 |  |  | 100.29 |  |  | 99.0991 |  |  | 95.1217 |  |  | 85.9139 |  |  | 71.7838 |  |  | 54.1891 |  |  | 36.8167 |  |  | 21.2268 |  |  | 1.8218
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48378 |  |  | 0.47804 |  |  | 0.45885 |  |  | 0.41443 |  |  | 0.34627 |  |  | 0.2614 |  |  | 0.1776 |  |  | 0.10239 |  |  | 0.0087881
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5224 |  |  | 50.29 |  |  | 49.0991 |  |  | 45.1217 |  |  | 35.9139 |  |  | 21.7838 |  |  | 4.1891 |  |  | -13.1833 |  |  | -28.7732 |  |  | -48.1782
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50145 |  |  | 0.49545 |  |  | 0.47436 |  |  | 0.41802 |  |  | 0.30346 |  |  | 0.077305 |  |  | -0.35808 |  |  | -1.3555 |  |  | -26.4452
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.7389 |  |  | 0.73815 |  |  | 0.74586 |  |  | 0.7699 |  |  | 0.82343 |  |  | 0.95192 |  |  | 1.2433 |  |  | 1.7613 |  |  | 23.5465
[13 empty] | C Non choked w/ reducers | 5 |  | 0.13326 |  |  | 3.3142 |  |  | 8.3718 |  |  | 17.2809 |  |  | 32.8604 |  |  | 61.8387 |  |  | 184.3854 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.1307 |  |  | 3.2494 |  |  | 8.2116 |  |  | 16.8731 |  |  | 31.5137 |  |  | 55.5621 |  |  | 99.9443 |  |  | 191.3737 |  |  | 382.406 |  |  | 8047.7825
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.13326 |  |  | 3.3142 |  |  | 8.3718 |  |  | 17.2809 |  |  | 32.8604 |  |  | 61.8387 |  |  | 184.3854 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8667 | 30.8187 |  | 1.6858 | 764.0228 |  | 1.6282 | 1889.5192 |  | 0.08093 | 3680.3011 |  | 6.2604 | 6052.7403 |  | 23.4387 | 8489.4343 |  | 131.8854 | 10779.3289 |  | 7174 | 12639.6108 |  | 7174 | 14101.6137 |  | 7174 | 15732.724
[13 empty] | Next iteration flow rate |  |  | 31.4351 | Abs Value of | Flow this | 771.663 | Abs Value of | Flow this | 1908.4144 | Abs Value of | Flow this | 3717.1041 | Abs Value of | Flow this | 6113.2677 | Abs Value of | Flow this | 8574.3286 | Abs Value of | Flow this | 10887.1221 | Abs Value of | Flow this | 12766.0069 | Abs Value of | Flow this | 14242.6298 | Abs Value of | Flow this | 15890.0513 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5224 |  |  | 100.2853 |  |  | 99.0705 |  |  | 95.0131 |  |  | 85.6202 |  |  | 71.2062 |  |  | 53.2578 |  |  | 35.5362 |  |  | 19.6329 |  |  | -0.16208
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48376 |  |  | 0.4779 |  |  | 0.45833 |  |  | 0.41302 |  |  | 0.34349 |  |  | 0.25691 |  |  | 0.17142 |  |  | 0.094706 |  |  | -0.00078183
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5224 |  |  | 50.2853 |  |  | 49.0705 |  |  | 45.0131 |  |  | 35.6202 |  |  | 21.2062 |  |  | 3.2578 |  |  | -14.4638 |  |  | -30.3671 |  |  | -50.1621
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50142 |  |  | 0.49531 |  |  | 0.47376 |  |  | 0.41603 |  |  | 0.29781 |  |  | 0.06117 |  |  | -0.40702 |  |  | -1.5467 |  |  | 309.4959
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73891 |  |  | 0.73823 |  |  | 0.74618 |  |  | 0.771 |  |  | 0.82672 |  |  | 0.96195 |  |  | 1.2766 |  |  | 1.8687 |  |  | -262.8686
[13 empty] | C Non choked w/ reducers | 5 |  | 0.13592 |  |  | 3.3475 |  |  | 8.4583 |  |  | 17.4772 |  |  | 33.335 |  |  | 63.3055 |  |  | 210.7932 |  |  | #NUM! |  |  | #NUM! |  |  | -8.2397
[13 empty] | C Choked w/ reducers | 5 |  | 0.13331 |  |  | 3.282 |  |  | 8.2961 |  |  | 17.0613 |  |  | 31.938 |  |  | 56.573 |  |  | 102.7089 |  |  | 200.2522 |  |  | 417.5851 |  |  | 91365.1761
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.13592 |  |  | 3.3475 |  |  | 8.4583 |  |  | 17.4772 |  |  | 33.335 |  |  | 63.3055 |  |  | 210.7932 |  |  | #NUM! |  |  | #NUM! |  |  | 91365.1761
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8641 | 31.4351 |  | 1.6525 | 771.663 |  | 1.5417 | 1908.4144 |  | 0.27721 | 3717.1041 |  | 6.735 | 6113.2677 |  | 24.9055 | 8574.3286 |  | 158.2932 | 10887.1221 |  | 7174 | 12766.0069 |  | 7174 | 14242.6298 |  | 7174 | 15890.0513
[13 empty] | Next iteration flow rate |  |  | 32.0638 | Abs Value of | Flow this | 779.3796 | Abs Value of | Flow this | 1927.4985 | Abs Value of | Flow this | 3754.2752 | Abs Value of | Flow this | 6174.4004 | Abs Value of | Flow this | 8660.0719 | Abs Value of | Flow this | 10995.9934 | Abs Value of | Flow this | 12893.667 | Abs Value of | Flow this | 14385.0561 | Abs Value of | Flow this | 16048.9518 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5224 |  |  | 100.2806 |  |  | 99.0413 |  |  | 94.9024 |  |  | 85.3207 |  |  | 70.6169 |  |  | 52.3077 |  |  | 34.23 |  |  | 18.0071 |  |  | -2.1858
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48374 |  |  | 0.47776 |  |  | 0.45779 |  |  | 0.41157 |  |  | 0.34064 |  |  | 0.25232 |  |  | 0.16512 |  |  | 0.086863 |  |  | -0.010544
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5224 |  |  | 50.2806 |  |  | 49.0413 |  |  | 44.9024 |  |  | 35.3207 |  |  | 20.6169 |  |  | 2.3077 |  |  | -15.77 |  |  | -31.9929 |  |  | -52.1858
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.5014 |  |  | 0.49516 |  |  | 0.47314 |  |  | 0.41398 |  |  | 0.29195 |  |  | 0.044119 |  |  | -0.46071 |  |  | -1.7767 |  |  | 23.8745
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73892 |  |  | 0.7383 |  |  | 0.74651 |  |  | 0.77213 |  |  | 0.83013 |  |  | 0.97256 |  |  | 1.3131 |  |  | 1.9978 |  |  | -19.3548
[13 empty] | C Non choked w/ reducers | 5 |  | 0.13864 |  |  | 3.3811 |  |  | 8.5458 |  |  | 17.6763 |  |  | 33.8206 |  |  | 64.8484 |  |  | 252.4589 |  |  | #NUM! |  |  | #NUM! |  |  | -30.175
[13 empty] | C Choked w/ reducers | 5 |  | 0.13598 |  |  | 3.315 |  |  | 8.3815 |  |  | 17.2521 |  |  | 32.3706 |  |  | 57.6155 |  |  | 105.6201 |  |  | 209.9729 |  |  | 459.8424 |  |  | 6842.3278
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.13864 |  |  | 3.3811 |  |  | 8.5458 |  |  | 17.6763 |  |  | 33.8206 |  |  | 64.8484 |  |  | 252.4589 |  |  | #NUM! |  |  | #NUM! |  |  | 6842.3278
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8614 | 32.0638 |  | 1.6189 | 779.3796 |  | 1.4542 | 1927.4985 |  | 0.47626 | 3754.2752 |  | 7.2206 | 6174.4004 |  | 26.4484 | 8660.0719 |  | 199.9589 | 10995.9934 |  | 7174 | 12893.667 |  | 7174 | 14385.0561 |  | 7174 | 16048.9518
[13 empty] | Next iteration flow rate |  |  | 32.705 | Abs Value of | Flow this | 787.1734 | Abs Value of | Flow this | 1946.7735 | Abs Value of | Flow this | 3791.8179 | Abs Value of | Flow this | 6236.1444 | Abs Value of | Flow this | 8746.6726 | Abs Value of | Flow this | 11105.9533 | Abs Value of | Flow this | 13022.6037 | Abs Value of | Flow this | 14528.9067 | Abs Value of | Flow this | 16209.4413 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5224 |  |  | 100.2757 |  |  | 99.0115 |  |  | 94.7894 |  |  | 85.0151 |  |  | 70.0158 |  |  | 51.3386 |  |  | 32.8975 |  |  | 16.3485 |  |  | -4.2503
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48371 |  |  | 0.47761 |  |  | 0.45725 |  |  | 0.4101 |  |  | 0.33774 |  |  | 0.24765 |  |  | 0.15869 |  |  | 0.078862 |  |  | -0.020503
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5224 |  |  | 50.2757 |  |  | 49.0115 |  |  | 44.7894 |  |  | 35.0151 |  |  | 20.0158 |  |  | 1.3386 |  |  | -17.1025 |  |  | -33.6515 |  |  | -54.2503
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50137 |  |  | 0.49501 |  |  | 0.47252 |  |  | 0.41187 |  |  | 0.28588 |  |  | 0.026074 |  |  | -0.51987 |  |  | -2.0584 |  |  | 12.7639
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73894 |  |  | 0.73838 |  |  | 0.74685 |  |  | 0.77329 |  |  | 0.83367 |  |  | 0.98378 |  |  | 1.3533 |  |  | 2.156 |  |  | -9.8822
[13 empty] | C Non choked w/ reducers | 5 |  | 0.14141 |  |  | 3.4151 |  |  | 8.6343 |  |  | 17.8781 |  |  | 34.3176 |  |  | 66.4746 |  |  | 334.0831 |  |  | #NUM! |  |  | #NUM! |  |  | -41.9835
[13 empty] | C Choked w/ reducers | 5 |  | 0.1387 |  |  | 3.3483 |  |  | 8.4679 |  |  | 17.4453 |  |  | 32.8118 |  |  | 58.6913 |  |  | 108.69 |  |  | 220.6624 |  |  | 511.5586 |  |  | 3554.0699
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.14141 |  |  | 3.4151 |  |  | 8.6343 |  |  | 17.8781 |  |  | 34.3176 |  |  | 66.4746 |  |  | 334.0831 |  |  | #NUM! |  |  | #NUM! |  |  | 3554.0699
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8586 | 32.705 |  | 1.5849 | 787.1734 |  | 1.3657 | 1946.7735 |  | 0.67811 | 3791.8179 |  | 7.7176 | 6236.1444 |  | 28.0746 | 8746.6726 |  | 281.5831 | 11105.9533 |  | 7174 | 13022.6037 |  | 7174 | 14528.9067 |  | 7174 | 16209.4413
[13 empty] | Next iteration flow rate |  |  | 33.3591 | Abs Value of | Flow this | 795.0451 | Abs Value of | Flow this | 1966.2413 | Abs Value of | Flow this | 3829.7361 | Abs Value of | Flow this | 6298.5059 | Abs Value of | Flow this | 8834.1394 | Abs Value of | Flow this | 11217.0128 | Abs Value of | Flow this | 13152.8297 | Abs Value of | Flow this | 14674.1958 | Abs Value of | Flow this | 16371.5357 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5223 |  |  | 100.2707 |  |  | 98.9811 |  |  | 94.6742 |  |  | 84.7034 |  |  | 69.4026 |  |  | 50.35 |  |  | 31.5382 |  |  | 14.6566 |  |  | -6.3562
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48369 |  |  | 0.47747 |  |  | 0.45669 |  |  | 0.40859 |  |  | 0.33479 |  |  | 0.24288 |  |  | 0.15213 |  |  | 0.070701 |  |  | -0.030661
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5223 |  |  | 50.2707 |  |  | 48.9811 |  |  | 44.6742 |  |  | 34.7034 |  |  | 19.4026 |  |  | 0.35002 |  |  | -18.4618 |  |  | -35.3434 |  |  | -56.3562
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50135 |  |  | 0.49485 |  |  | 0.47187 |  |  | 0.40971 |  |  | 0.27957 |  |  | 0.0069518 |  |  | -0.58538 |  |  | -2.4114 |  |  | 8.8663
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73895 |  |  | 0.73847 |  |  | 0.74719 |  |  | 0.77448 |  |  | 0.83734 |  |  | 0.99568 |  |  | 1.3978 |  |  | 2.3543 |  |  | -6.5592
[13 empty] | C Non choked w/ reducers | 5 |  | 0.14424 |  |  | 3.4495 |  |  | 8.7237 |  |  | 18.0828 |  |  | 34.8264 |  |  | 68.1923 |  |  | 658.3545 |  |  | #NUM! |  |  | #NUM! |  |  | -51.2558
[13 empty] | C Choked w/ reducers | 5 |  | 0.14147 |  |  | 3.3819 |  |  | 8.5552 |  |  | 17.6412 |  |  | 33.2619 |  |  | 59.8019 |  |  | 111.9323 |  |  | 232.4745 |  |  | 576.3172 |  |  | 2400.304
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.14424 |  |  | 3.4495 |  |  | 8.7237 |  |  | 18.0828 |  |  | 34.8264 |  |  | 68.1923 |  |  | 658.3545 |  |  | #NUM! |  |  | #NUM! |  |  | 2400.304
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8558 | 33.3591 |  | 1.5505 | 795.0451 |  | 1.2763 | 1966.2413 |  | 0.88284 | 3829.7361 |  | 8.2264 | 6298.5059 |  | 29.7923 | 8834.1394 |  | 605.8545 | 11217.0128 |  | 7174 | 13152.8297 |  | 7174 | 14674.1958 |  | 7174 | 16371.5357
[13 empty] | Next iteration flow rate |  |  | 34.0263 | Abs Value of | Flow this | 802.9956 | Abs Value of | Flow this | 1985.9037 | Abs Value of | Flow this | 3868.0335 | Abs Value of | Flow this | 6361.4909 | Abs Value of | Flow this | 8922.4807 | Abs Value of | Flow this | 11329.183 | Abs Value of | Flow this | 13284.358 | Abs Value of | Flow this | 14820.9377 | Abs Value of | Flow this | 16535.2511 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5223 |  |  | 100.2657 |  |  | 98.9501 |  |  | 94.5566 |  |  | 84.3855 |  |  | 68.7771 |  |  | 49.3416 |  |  | 30.1516 |  |  | 12.9307 |  |  | -8.5045
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48366 |  |  | 0.47732 |  |  | 0.45612 |  |  | 0.40706 |  |  | 0.33177 |  |  | 0.23801 |  |  | 0.14545 |  |  | 0.062375 |  |  | -0.041024
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5223 |  |  | 50.2657 |  |  | 48.9501 |  |  | 44.5566 |  |  | 34.3855 |  |  | 18.7771 |  |  | -0.65845 |  |  | -19.8484 |  |  | -37.0693 |  |  | -58.5045
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50132 |  |  | 0.4947 |  |  | 0.47122 |  |  | 0.40748 |  |  | 0.27301 |  |  | -0.013345 |  |  | -0.65829 |  |  | -2.8668 |  |  | 6.8792
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73896 |  |  | 0.73855 |  |  | 0.74754 |  |  | 0.7757 |  |  | 0.84115 |  |  | 1.0083 |  |  | 1.4474 |  |  | 2.61 |  |  | -4.8651
[13 empty] | C Non choked w/ reducers | 5 |  | 0.14713 |  |  | 3.4842 |  |  | 8.8141 |  |  | 18.2905 |  |  | 35.3476 |  |  | 70.011 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -59.2212
[13 empty] | C Choked w/ reducers | 5 |  | 0.1443 |  |  | 3.4159 |  |  | 8.6434 |  |  | 17.8398 |  |  | 33.7211 |  |  | 60.9493 |  |  | 115.3623 |  |  | 245.597 |  |  | 659.773 |  |  | 1811.9176
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.14713 |  |  | 3.4842 |  |  | 8.8141 |  |  | 18.2905 |  |  | 35.3476 |  |  | 70.011 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 1811.9176
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8529 | 34.0263 |  | 1.5158 | 802.9956 |  | 1.1859 | 1985.9037 |  | 1.0905 | 3868.0335 |  | 8.7476 | 6361.4909 |  | 31.611 | 8922.4807 |  | 7174 | 11329.183 |  | 7174 | 13284.358 |  | 7174 | 14820.9377 |  | 7174 | 16535.2511
[13 empty] | Next iteration flow rate |  |  | 34.7068 | Abs Value of | Flow this | 811.0256 | Abs Value of | Flow this | 2005.7627 | Abs Value of | Flow this | 3906.7138 | Abs Value of | Flow this | 6425.1058 | Abs Value of | Flow this | 9011.7056 | Abs Value of | Flow this | 11442.4748 | Abs Value of | Flow this | 13417.2016 | Abs Value of | Flow this | 14969.1471 | Abs Value of | Flow this | 16700.6036 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5223 |  |  | 100.2605 |  |  | 98.9185 |  |  | 94.4367 |  |  | 84.0611 |  |  | 68.139 |  |  | 48.3128 |  |  | 28.7372 |  |  | 11.1701 |  |  | -10.6959
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48364 |  |  | 0.47717 |  |  | 0.45555 |  |  | 0.4055 |  |  | 0.32869 |  |  | 0.23305 |  |  | 0.13862 |  |  | 0.053882 |  |  | -0.051595
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5223 |  |  | 50.2605 |  |  | 48.9185 |  |  | 44.4367 |  |  | 34.0611 |  |  | 18.139 |  |  | -1.6872 |  |  | -21.2628 |  |  | -38.8299 |  |  | -60.6959
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.5013 |  |  | 0.49453 |  |  | 0.47054 |  |  | 0.40519 |  |  | 0.26621 |  |  | -0.034922 |  |  | -0.73991 |  |  | -3.4762 |  |  | 5.6747
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73898 |  |  | 0.73864 |  |  | 0.7479 |  |  | 0.77696 |  |  | 0.84511 |  |  | 1.0217 |  |  | 1.5028 |  |  | 2.9523 |  |  | -3.8381
[13 empty] | C Non choked w/ reducers | 5 |  | 0.15007 |  |  | 3.5192 |  |  | 8.9055 |  |  | 18.5012 |  |  | 35.8816 |  |  | 71.9413 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -66.3748
[13 empty] | C Choked w/ reducers | 5 |  | 0.14719 |  |  | 3.4503 |  |  | 8.7326 |  |  | 18.0411 |  |  | 34.1897 |  |  | 62.1353 |  |  | 118.9969 |  |  | 260.2623 |  |  | 771.4024 |  |  | 1455.0879
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.15007 |  |  | 3.5192 |  |  | 8.9055 |  |  | 18.5012 |  |  | 35.8816 |  |  | 71.9413 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 1455.0879
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8499 | 34.7068 |  | 1.4808 | 811.0256 |  | 1.0945 | 2005.7627 |  | 1.3012 | 3906.7138 |  | 9.2816 | 6425.1058 |  | 33.5413 | 9011.7056 |  | 7174 | 11442.4748 |  | 7174 | 13417.2016 |  | 7174 | 14969.1471 |  | 7174 | 16700.6036
[13 empty] | Next iteration flow rate |  |  | 35.401 | Abs Value of | Flow this | 819.1358 | Abs Value of | Flow this | 2025.8203 | Abs Value of | Flow this | 3945.7809 | Abs Value of | Flow this | 6489.3569 | Abs Value of | Flow this | 9101.8226 | Abs Value of | Flow this | 11556.8995 | Abs Value of | Flow this | 13551.3736 | Abs Value of | Flow this | 15118.8386 | Abs Value of | Flow this | 16867.6096 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5223 |  |  | 100.2552 |  |  | 98.8863 |  |  | 94.3144 |  |  | 83.7302 |  |  | 67.4881 |  |  | 47.2634 |  |  | 27.2943 |  |  | 9.3741 |  |  | -12.9314
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48361 |  |  | 0.47701 |  |  | 0.45496 |  |  | 0.4039 |  |  | 0.32555 |  |  | 0.22799 |  |  | 0.13166 |  |  | 0.045219 |  |  | -0.062379
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5223 |  |  | 50.2552 |  |  | 48.8863 |  |  | 44.3144 |  |  | 33.7302 |  |  | 17.4881 |  |  | -2.7366 |  |  | -22.7057 |  |  | -40.6259 |  |  | -62.9314
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50127 |  |  | 0.49437 |  |  | 0.46986 |  |  | 0.40284 |  |  | 0.25913 |  |  | -0.057901 |  |  | -0.83189 |  |  | -4.3338 |  |  | 4.8665
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73899 |  |  | 0.73872 |  |  | 0.74827 |  |  | 0.77826 |  |  | 0.84923 |  |  | 1.036 |  |  | 1.5653 |  |  | 3.4339 |  |  | -3.1491
[13 empty] | C Non choked w/ reducers | 5 |  | 0.15307 |  |  | 3.5546 |  |  | 8.9979 |  |  | 18.7149 |  |  | 36.429 |  |  | 73.9961 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -72.9768
[13 empty] | C Choked w/ reducers | 5 |  | 0.15013 |  |  | 3.485 |  |  | 8.8229 |  |  | 18.2451 |  |  | 34.6681 |  |  | 63.3619 |  |  | 122.8555 |  |  | 276.7611 |  |  | 928.3879 |  |  | 1215.5779
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.15307 |  |  | 3.5546 |  |  | 8.9979 |  |  | 18.7149 |  |  | 36.429 |  |  | 73.9961 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 1215.5779
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8469 | 35.401 |  | 1.4454 | 819.1358 |  | 1.0021 | 2025.8203 |  | 1.5149 | 3945.7809 |  | 9.829 | 6489.3569 |  | 35.5961 | 9101.8226 |  | 7174 | 11556.8995 |  | 7174 | 13551.3736 |  | 7174 | 15118.8386 |  | 7174 | 16867.6096
[13 empty] | Next iteration flow rate |  |  | 36.109 | Abs Value of | Flow this | 827.3272 | Abs Value of | Flow this | 2046.0785 | Abs Value of | Flow this | 3985.2387 | Abs Value of | Flow this | 6554.2504 | Abs Value of | Flow this | 9192.8408 | Abs Value of | Flow this | 11672.4685 | Abs Value of | Flow this | 13686.8873 | Abs Value of | Flow this | 15270.027 | Abs Value of | Flow this | 17036.2857 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5223 |  |  | 100.2498 |  |  | 98.8534 |  |  | 94.1896 |  |  | 83.3927 |  |  | 66.8241 |  |  | 46.1929 |  |  | 25.8224 |  |  | 7.542 |  |  | -15.2119
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48359 |  |  | 0.47685 |  |  | 0.45435 |  |  | 0.40227 |  |  | 0.32235 |  |  | 0.22283 |  |  | 0.12456 |  |  | 0.036381 |  |  | -0.073379
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5223 |  |  | 50.2498 |  |  | 48.8534 |  |  | 44.1896 |  |  | 33.3927 |  |  | 16.8241 |  |  | -3.8071 |  |  | -24.1776 |  |  | -42.458 |  |  | -65.2119
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50125 |  |  | 0.4942 |  |  | 0.46916 |  |  | 0.40043 |  |  | 0.25177 |  |  | -0.082418 |  |  | -0.9363 |  |  | -5.6295 |  |  | 4.2869
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.739 |  |  | 0.73881 |  |  | 0.74865 |  |  | 0.77959 |  |  | 0.85351 |  |  | 1.0513 |  |  | 1.6363 |  |  | 4.1616 |  |  | -2.6549
[13 empty] | C Non choked w/ reducers | 5 |  | 0.15613 |  |  | 3.5904 |  |  | 9.0914 |  |  | 18.9317 |  |  | 36.9902 |  |  | 76.1899 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -79.1854
[13 empty] | C Choked w/ reducers | 5 |  | 0.15314 |  |  | 3.52 |  |  | 8.914 |  |  | 18.452 |  |  | 35.1565 |  |  | 64.6314 |  |  | 126.9597 |  |  | 295.462 |  |  | 1165.4492 |  |  | 1043.6826
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.15613 |  |  | 3.5904 |  |  | 9.0914 |  |  | 18.9317 |  |  | 36.9902 |  |  | 76.1899 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 1043.6826
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8439 | 36.109 |  | 1.4096 | 827.3272 |  | 0.90863 | 2046.0785 |  | 1.7317 | 3985.2387 |  | 10.3902 | 6554.2504 |  | 37.7899 | 9192.8408 |  | 7174 | 11672.4685 |  | 7174 | 13686.8873 |  | 7174 | 15270.027 |  | 7174 | 17036.2857
[13 empty] | Next iteration flow rate |  |  | 36.8312 | Abs Value of | Flow this | 835.6004 | Abs Value of | Flow this | 2066.5393 | Abs Value of | Flow this | 4025.0911 | Abs Value of | Flow this | 6619.793 | Abs Value of | Flow this | 9284.7692 | Abs Value of | Flow this | 11789.1932 | Abs Value of | Flow this | 13823.7562 | Abs Value of | Flow this | 15422.7272 | Abs Value of | Flow this | 17206.6486 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5222 |  |  | 100.2444 |  |  | 98.8198 |  |  | 94.0623 |  |  | 83.0484 |  |  | 66.1467 |  |  | 45.1008 |  |  | 24.3209 |  |  | 5.6731 |  |  | -17.5381
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48356 |  |  | 0.47669 |  |  | 0.45374 |  |  | 0.40061 |  |  | 0.31908 |  |  | 0.21756 |  |  | 0.11732 |  |  | 0.027366 |  |  | -0.084601
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5222 |  |  | 50.2444 |  |  | 48.8198 |  |  | 44.0623 |  |  | 33.0484 |  |  | 16.1467 |  |  | -4.8992 |  |  | -25.6791 |  |  | -44.3269 |  |  | -67.5381
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50122 |  |  | 0.49403 |  |  | 0.46844 |  |  | 0.39794 |  |  | 0.2441 |  |  | -0.10863 |  |  | -1.0558 |  |  | -7.8135 |  |  | 3.8509
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73902 |  |  | 0.7389 |  |  | 0.74903 |  |  | 0.78096 |  |  | 0.85797 |  |  | 1.0676 |  |  | 1.7175 |  |  | 5.3882 |  |  | -2.2832
[13 empty] | C Non choked w/ reducers | 5 |  | 0.15926 |  |  | 3.6265 |  |  | 9.1859 |  |  | 19.1517 |  |  | 37.5661 |  |  | 78.5402 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -85.1058
[13 empty] | C Choked w/ reducers | 5 |  | 0.1562 |  |  | 3.5554 |  |  | 9.0062 |  |  | 18.6617 |  |  | 35.6552 |  |  | 65.9462 |  |  | 131.3341 |  |  | 316.8397 |  |  | 1564.8826 |  |  | 914.3005
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.15926 |  |  | 3.6265 |  |  | 9.1859 |  |  | 19.1517 |  |  | 37.5661 |  |  | 78.5402 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 914.3005
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8407 | 36.8312 |  | 1.3735 | 835.6004 |  | 0.81413 | 2066.5393 |  | 1.9517 | 4025.0911 |  | 10.9661 | 6619.793 |  | 40.1402 | 9284.7692 |  | 7174 | 11789.1932 |  | 7174 | 13823.7562 |  | 7174 | 15422.7272 |  | 7174 | 17206.6486
[13 empty] | Next iteration flow rate |  |  | 37.5678 | Abs Value of | Flow this | 843.9564 | Abs Value of | Flow this | 2087.2047 | Abs Value of | Flow this | 4065.342 | Abs Value of | Flow this | 6685.9909 | Abs Value of | Flow this | 9377.6169 | Abs Value of | Flow this | 11907.0851 | Abs Value of | Flow this | 13961.9938 | Abs Value of | Flow this | 15576.9545 | Abs Value of | Flow this | 17378.7151 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5222 |  |  | 100.2388 |  |  | 98.7856 |  |  | 93.9324 |  |  | 82.6971 |  |  | 65.4558 |  |  | 43.9869 |  |  | 22.7892 |  |  | 3.7666 |  |  | -19.9112
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48353 |  |  | 0.47652 |  |  | 0.45311 |  |  | 0.39892 |  |  | 0.31575 |  |  | 0.21218 |  |  | 0.10993 |  |  | 0.018169 |  |  | -0.096048
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5222 |  |  | 50.2388 |  |  | 48.7856 |  |  | 43.9324 |  |  | 32.6971 |  |  | 15.4558 |  |  | -6.0131 |  |  | -27.2108 |  |  | -46.2334 |  |  | -69.9112
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50119 |  |  | 0.49385 |  |  | 0.4677 |  |  | 0.39538 |  |  | 0.23613 |  |  | -0.1367 |  |  | -1.194 |  |  | -12.2745 |  |  | 3.5112
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73903 |  |  | 0.73899 |  |  | 0.74943 |  |  | 0.78236 |  |  | 0.86261 |  |  | 1.085 |  |  | 1.8114 |  |  | 7.8935 |  |  | -1.9935
[13 empty] | C Non choked w/ reducers | 5 |  | 0.16244 |  |  | 3.663 |  |  | 9.2814 |  |  | 19.375 |  |  | 38.1572 |  |  | 81.0675 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -90.8133
[13 empty] | C Choked w/ reducers | 5 |  | 0.15932 |  |  | 3.5912 |  |  | 9.0995 |  |  | 18.8744 |  |  | 36.1647 |  |  | 67.3087 |  |  | 136.0068 |  |  | 341.5158 |  |  | 2380.5209 |  |  | 813.3869
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.16244 |  |  | 3.663 |  |  | 9.2814 |  |  | 19.375 |  |  | 38.1572 |  |  | 81.0675 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 813.3869
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8376 | 37.5678 |  | 1.337 | 843.9564 |  | 0.71858 | 2087.2047 |  | 2.175 | 4065.342 |  | 11.5572 | 6685.9909 |  | 42.6675 | 9377.6169 |  | 7174 | 11907.0851 |  | 7174 | 13961.9938 |  | 7174 | 15576.9545 |  | 7174 | 17378.7151
[13 empty] | Next iteration flow rate |  |  | 38.3192 | Abs Value of | Flow this | 852.396 | Abs Value of | Flow this | 2108.0768 | Abs Value of | Flow this | 4105.9955 | Abs Value of | Flow this | 6752.8508 | Abs Value of | Flow this | 9471.3931 | Abs Value of | Flow this | 12026.156 | Abs Value of | Flow this | 14101.6137 | Abs Value of | Flow this | 15732.724 | Abs Value of | Flow this | 17552.5022 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5222 |  |  | 100.2331 |  |  | 98.7507 |  |  | 93.8 |  |  | 82.3389 |  |  | 64.7509 |  |  | 42.8505 |  |  | 21.2268 |  |  | 1.8218 |  |  | -22.3319
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48351 |  |  | 0.47636 |  |  | 0.45247 |  |  | 0.39719 |  |  | 0.31235 |  |  | 0.2067 |  |  | 0.10239 |  |  | 0.0087881 |  |  | -0.10773
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5222 |  |  | 50.2331 |  |  | 48.7507 |  |  | 43.8 |  |  | 32.3389 |  |  | 14.7509 |  |  | -7.1495 |  |  | -28.7732 |  |  | -48.1782 |  |  | -72.3319
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50116 |  |  | 0.49367 |  |  | 0.46695 |  |  | 0.39275 |  |  | 0.22781 |  |  | -0.16685 |  |  | -1.3555 |  |  | -26.4452 |  |  | 3.239
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73905 |  |  | 0.73909 |  |  | 0.74983 |  |  | 0.78381 |  |  | 0.86745 |  |  | 1.1038 |  |  | 1.9212 |  |  | 15.8519 |  |  | -1.7615
[13 empty] | C Non choked w/ reducers | 5 |  | 0.16569 |  |  | 3.6999 |  |  | 9.3781 |  |  | 19.6016 |  |  | 38.7641 |  |  | 83.7965 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -96.3642
[13 empty] | C Choked w/ reducers | 5 |  | 0.16251 |  |  | 3.6273 |  |  | 9.1937 |  |  | 19.0901 |  |  | 36.6853 |  |  | 68.7218 |  |  | 141.0097 |  |  | 370.3203 |  |  | 4970.9626 |  |  | 732.4699
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.16569 |  |  | 3.6999 |  |  | 9.3781 |  |  | 19.6016 |  |  | 38.7641 |  |  | 83.7965 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 732.4699
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8343 | 38.3192 |  | 1.3001 | 852.396 |  | 0.62195 | 2108.0768 |  | 2.4016 | 4105.9955 |  | 12.1641 | 6752.8508 |  | 45.3965 | 9471.3931 |  | 7174 | 12026.156 |  | 7174 | 14101.6137 |  | 7174 | 15732.724 |  | 7174 | 17552.5022
[13 empty] | Next iteration flow rate |  |  | 39.0855 | Abs Value of | Flow this | 860.92 | Abs Value of | Flow this | 2129.1575 | Abs Value of | Flow this | 4147.0554 | Abs Value of | Flow this | 6820.3793 | Abs Value of | Flow this | 9566.107 | Abs Value of | Flow this | 12146.4176 | Abs Value of | Flow this | 14242.6298 | Abs Value of | Flow this | 15890.0513 | Abs Value of | Flow this | 17728.0272 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5222 |  |  | 100.2272 |  |  | 98.7151 |  |  | 93.6649 |  |  | 81.9734 |  |  | 64.0319 |  |  | 41.6913 |  |  | 19.6329 |  |  | -0.16208 |  |  | -24.8013
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48348 |  |  | 0.47618 |  |  | 0.45182 |  |  | 0.39542 |  |  | 0.30888 |  |  | 0.20111 |  |  | 0.094706 |  |  | -0.00078183 |  |  | -0.11964
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5222 |  |  | 50.2272 |  |  | 48.7151 |  |  | 43.6649 |  |  | 31.9734 |  |  | 14.0319 |  |  | -8.3087 |  |  | -30.3671 |  |  | -50.1621 |  |  | -74.8013
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50113 |  |  | 0.49349 |  |  | 0.46618 |  |  | 0.39005 |  |  | 0.21914 |  |  | -0.19929 |  |  | -1.5467 |  |  | 309.4959 |  |  | 3.016
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73906 |  |  | 0.73919 |  |  | 0.75024 |  |  | 0.7853 |  |  | 0.8725 |  |  | 1.124 |  |  | 2.0512 |  |  | -172.8165 |  |  | -1.5714
[13 empty] | C Non choked w/ reducers | 5 |  | 0.169 |  |  | 3.7372 |  |  | 9.4758 |  |  | 19.8316 |  |  | 39.3877 |  |  | 86.757 |  |  | #NUM! |  |  | #NUM! |  |  | -9.5385 |  |  | -101.8028
[13 empty] | C Choked w/ reducers | 5 |  | 0.16576 |  |  | 3.6638 |  |  | 9.289 |  |  | 19.3088 |  |  | 37.2174 |  |  | 70.1884 |  |  | 146.3798 |  |  | 404.3876 |  |  | 56434.5364 |  |  | 666.1357
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.169 |  |  | 3.7372 |  |  | 9.4758 |  |  | 19.8316 |  |  | 39.3877 |  |  | 86.757 |  |  | #NUM! |  |  | #NUM! |  |  | 56434.5364 |  |  | 666.1357
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.831 | 39.0855 |  | 1.2628 | 860.92 |  | 0.52423 | 2129.1575 |  | 2.6316 | 4147.0554 |  | 12.7877 | 6820.3793 |  | 48.357 | 9566.107 |  | 7174 | 12146.4176 |  | 7174 | 14242.6298 |  | 7174 | 15890.0513 |  | 7174 | 17728.0272
[13 empty] | Next iteration flow rate |  |  | 39.8673 | Abs Value of | Flow this | 869.5292 | Abs Value of | Flow this | 2150.4491 | Abs Value of | Flow this | 4188.526 | Abs Value of | Flow this | 6888.5831 | Abs Value of | Flow this | 9661.7681 | Abs Value of | Flow this | 12267.8817 | Abs Value of | Flow this | 14385.0561 | Abs Value of | Flow this | 16048.9518 | Abs Value of | Flow this | 17905.3075 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5222 |  |  | 100.2213 |  |  | 98.6787 |  |  | 93.527 |  |  | 81.6005 |  |  | 63.2985 |  |  | 40.5088 |  |  | 18.0071 |  |  | -2.1858 |  |  | -27.3203
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48345 |  |  | 0.47601 |  |  | 0.45116 |  |  | 0.39363 |  |  | 0.30534 |  |  | 0.19541 |  |  | 0.086863 |  |  | -0.010544 |  |  | -0.13179
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5222 |  |  | 50.2213 |  |  | 48.6787 |  |  | 43.527 |  |  | 31.6005 |  |  | 13.2985 |  |  | -9.4912 |  |  | -31.9929 |  |  | -52.1858 |  |  | -77.3203
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.5011 |  |  | 0.49331 |  |  | 0.4654 |  |  | 0.38726 |  |  | 0.21009 |  |  | -0.2343 |  |  | -1.7767 |  |  | 23.8745 |  |  | 2.8301
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73908 |  |  | 0.73928 |  |  | 0.75066 |  |  | 0.78684 |  |  | 0.87776 |  |  | 1.1457 |  |  | 2.2074 |  |  | -12.4082 |  |  | -1.4129
[13 empty] | C Non choked w/ reducers | 5 |  | 0.17238 |  |  | 3.7748 |  |  | 9.5746 |  |  | 20.0652 |  |  | 40.0287 |  |  | 89.9856 |  |  | #NUM! |  |  | #NUM! |  |  | -35.8212 |  |  | -107.165
[13 empty] | C Choked w/ reducers | 5 |  | 0.16908 |  |  | 3.7006 |  |  | 9.3853 |  |  | 19.5306 |  |  | 37.7613 |  |  | 71.7117 |  |  | 152.1593 |  |  | 445.3094 |  |  | 4226.3761 |  |  | 610.7631
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.17238 |  |  | 3.7748 |  |  | 9.5746 |  |  | 20.0652 |  |  | 40.0287 |  |  | 89.9856 |  |  | #NUM! |  |  | #NUM! |  |  | 4226.3761 |  |  | 610.7631
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8276 | 39.8673 |  | 1.2252 | 869.5292 |  | 0.42542 | 2150.4491 |  | 2.8652 | 4188.526 |  | 13.4287 | 6888.5831 |  | 51.5856 | 9661.7681 |  | 7174 | 12267.8817 |  | 7174 | 14385.0561 |  | 7174 | 16048.9518 |  | 7174 | 17905.3075
[13 empty] | Next iteration flow rate |  |  | 40.6646 | Abs Value of | Flow this | 878.2245 | Abs Value of | Flow this | 2171.9536 | Abs Value of | Flow this | 4230.4112 | Abs Value of | Flow this | 6957.4689 | Abs Value of | Flow this | 9758.3858 | Abs Value of | Flow this | 12390.5606 | Abs Value of | Flow this | 14528.9067 | Abs Value of | Flow this | 16209.4413 | Abs Value of | Flow this | 18084.3606 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5221 |  |  | 100.2152 |  |  | 98.6417 |  |  | 93.3864 |  |  | 81.2202 |  |  | 62.5503 |  |  | 39.3025 |  |  | 16.3485 |  |  | -4.2503 |  |  | -29.8899
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48342 |  |  | 0.47583 |  |  | 0.45048 |  |  | 0.39179 |  |  | 0.30173 |  |  | 0.18959 |  |  | 0.078862 |  |  | -0.020503 |  |  | -0.14418
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5221 |  |  | 50.2152 |  |  | 48.6417 |  |  | 43.3864 |  |  | 31.2202 |  |  | 12.5503 |  |  | -10.6975 |  |  | -33.6515 |  |  | -54.2503 |  |  | -79.8899
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50107 |  |  | 0.49311 |  |  | 0.46459 |  |  | 0.38439 |  |  | 0.20064 |  |  | -0.27218 |  |  | -2.0584 |  |  | 12.7639 |  |  | 2.6728
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73909 |  |  | 0.73938 |  |  | 0.75109 |  |  | 0.78842 |  |  | 0.88326 |  |  | 1.1693 |  |  | 2.3989 |  |  | -6.1684 |  |  | -1.2788
[13 empty] | C Non choked w/ reducers | 5 |  | 0.17583 |  |  | 3.8128 |  |  | 9.6745 |  |  | 20.3022 |  |  | 40.6879 |  |  | 93.5275 |  |  | #NUM! |  |  | #NUM! |  |  | -51.1888 |  |  | -112.4807
[13 empty] | C Choked w/ reducers | 5 |  | 0.17246 |  |  | 3.7378 |  |  | 9.4827 |  |  | 19.7556 |  |  | 38.3175 |  |  | 73.2952 |  |  | 158.3978 |  |  | 495.3912 |  |  | 2195.2816 |  |  | 563.8382
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.17583 |  |  | 3.8128 |  |  | 9.6745 |  |  | 20.3022 |  |  | 40.6879 |  |  | 93.5275 |  |  | #NUM! |  |  | #NUM! |  |  | 2195.2816 |  |  | 563.8382
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8242 | 40.6646 |  | 1.1872 | 878.2245 |  | 0.32549 | 2171.9536 |  | 3.1022 | 4230.4112 |  | 14.0879 | 6957.4689 |  | 55.1275 | 9758.3858 |  | 7174 | 12390.5606 |  | 7174 | 14528.9067 |  | 7174 | 16209.4413 |  | 7174 | 18084.3606
[13 empty] | Next iteration flow rate |  |  | 41.4779 | Abs Value of | Flow this | 887.0067 | Abs Value of | Flow this | 2193.6731 | Abs Value of | Flow this | 4272.7153 | Abs Value of | Flow this | 7027.0436 | Abs Value of | Flow this | 9855.9696 | Abs Value of | Flow this | 12514.4662 | Abs Value of | Flow this | 14674.1958 | Abs Value of | Flow this | 16371.5357 | Abs Value of | Flow this | 18265.2042 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5221 |  |  | 100.209 |  |  | 98.6039 |  |  | 93.243 |  |  | 80.8322 |  |  | 61.787 |  |  | 38.072 |  |  | 14.6566 |  |  | -6.3562 |  |  | -32.5112
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48339 |  |  | 0.47565 |  |  | 0.44979 |  |  | 0.38992 |  |  | 0.29805 |  |  | 0.18365 |  |  | 0.070701 |  |  | -0.030661 |  |  | -0.15683
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5221 |  |  | 50.209 |  |  | 48.6039 |  |  | 43.243 |  |  | 30.8322 |  |  | 11.787 |  |  | -11.928 |  |  | -35.3434 |  |  | -56.3562 |  |  | -82.5112
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50104 |  |  | 0.49292 |  |  | 0.46377 |  |  | 0.38143 |  |  | 0.19077 |  |  | -0.3133 |  |  | -2.4114 |  |  | 8.8663 |  |  | 2.5379
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73911 |  |  | 0.73949 |  |  | 0.75153 |  |  | 0.79004 |  |  | 0.889 |  |  | 1.1949 |  |  | 2.6388 |  |  | -3.9794 |  |  | -1.1638
[13 empty] | C Non choked w/ reducers | 5 |  | 0.17935 |  |  | 3.8512 |  |  | 9.7756 |  |  | 20.543 |  |  | 41.3663 |  |  | 97.4396 |  |  | #NUM! |  |  | #NUM! |  |  | -64.2964 |  |  | -117.7759
[13 empty] | C Choked w/ reducers | 5 |  | 0.17591 |  |  | 3.7755 |  |  | 9.5812 |  |  | 19.9839 |  |  | 38.8865 |  |  | 74.9427 |  |  | 165.1525 |  |  | 558.1031 |  |  | 1482.6222 |  |  | 523.5612
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.17935 |  |  | 3.8512 |  |  | 9.7756 |  |  | 20.543 |  |  | 41.3663 |  |  | 97.4396 |  |  | #NUM! |  |  | #NUM! |  |  | 1482.6222 |  |  | 523.5612
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8207 | 41.4779 |  | 1.1488 | 887.0067 |  | 0.22443 | 2193.6731 |  | 3.343 | 4272.7153 |  | 14.7663 | 7027.0436 |  | 59.0396 | 9855.9696 |  | 7174 | 12514.4662 |  | 7174 | 14674.1958 |  | 7174 | 16371.5357 |  | 7174 | 18265.2042
[13 empty] | Next iteration flow rate |  |  | 42.3074 | Abs Value of | Flow this | 895.8768 | Abs Value of | Flow this | 2215.6099 | Abs Value of | Flow this | 4315.4425 | Abs Value of | Flow this | 7097.314 | Abs Value of | Flow this | 9954.5293 | Abs Value of | Flow this | 12639.6108 | Abs Value of | Flow this | 14820.9377 | Abs Value of | Flow this | 16535.2511 | Abs Value of | Flow this | 18447.8562 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5221 |  |  | 100.2027 |  |  | 98.5653 |  |  | 93.0966 |  |  | 80.4364 |  |  | 61.0084 |  |  | 36.8167 |  |  | 12.9307 |  |  | -8.5045 |  |  | -35.1852
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48336 |  |  | 0.47546 |  |  | 0.44908 |  |  | 0.38801 |  |  | 0.29429 |  |  | 0.1776 |  |  | 0.062375 |  |  | -0.041024 |  |  | -0.16973
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5221 |  |  | 50.2027 |  |  | 48.5653 |  |  | 43.0966 |  |  | 30.4364 |  |  | 11.0084 |  |  | -13.1833 |  |  | -37.0693 |  |  | -58.5045 |  |  | -85.1852
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50101 |  |  | 0.49272 |  |  | 0.46292 |  |  | 0.37839 |  |  | 0.18044 |  |  | -0.35808 |  |  | -2.8668 |  |  | 6.8792 |  |  | 2.4211
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73912 |  |  | 0.73959 |  |  | 0.75199 |  |  | 0.79172 |  |  | 0.89501 |  |  | 1.2227 |  |  | 2.9482 |  |  | -2.8635 |  |  | -1.0641
[13 empty] | C Non choked w/ reducers | 5 |  | 0.18294 |  |  | 3.89 |  |  | 9.8778 |  |  | 20.7874 |  |  | 42.0649 |  |  | 101.7944 |  |  | #NUM! |  |  | #NUM! |  |  | -76.5751 |  |  | -123.0734
[13 empty] | C Choked w/ reducers | 5 |  | 0.17942 |  |  | 3.8134 |  |  | 9.6808 |  |  | 20.2154 |  |  | 39.4686 |  |  | 76.6581 |  |  | 172.4912 |  |  | 638.9213 |  |  | 1119.1871 |  |  | 488.6096
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.18294 |  |  | 3.89 |  |  | 9.8778 |  |  | 20.7874 |  |  | 42.0649 |  |  | 101.7944 |  |  | #NUM! |  |  | #NUM! |  |  | 1119.1871 |  |  | 488.6096
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8171 | 42.3074 |  | 1.11 | 895.8768 |  | 0.12222 | 2215.6099 |  | 3.5874 | 4315.4425 |  | 15.4649 | 7097.314 |  | 63.3944 | 9954.5293 |  | 7174 | 12639.6108 |  | 7174 | 14820.9377 |  | 7174 | 16535.2511 |  | 7174 | 18447.8562
[13 empty] | Next iteration flow rate |  |  | 43.1536 | Abs Value of | Flow this | 904.8355 | Abs Value of | Flow this | 2237.766 | Abs Value of | Flow this | 4358.5969 | Abs Value of | Flow this | 7168.2872 | Abs Value of | Flow this | 10054.0746 | Abs Value of | Flow this | 12766.0069 | Abs Value of | Flow this | 14969.1471 | Abs Value of | Flow this | 16700.6036 | Abs Value of | Flow this | 18632.3348 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.522 |  |  | 100.1963 |  |  | 98.5259 |  |  | 92.9474 |  |  | 80.0327 |  |  | 60.2142 |  |  | 35.5362 |  |  | 11.1701 |  |  | -10.6959 |  |  | -37.9129
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48333 |  |  | 0.47527 |  |  | 0.44836 |  |  | 0.38606 |  |  | 0.29046 |  |  | 0.17142 |  |  | 0.053882 |  |  | -0.051595 |  |  | -0.18289
[13 empty] | Delta P at this iteration flow rate |  |  | 50.522 |  |  | 50.1963 |  |  | 48.5259 |  |  | 42.9474 |  |  | 30.0327 |  |  | 10.2142 |  |  | -14.4638 |  |  | -38.8299 |  |  | -60.6959 |  |  | -87.9129
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50098 |  |  | 0.49252 |  |  | 0.46206 |  |  | 0.37526 |  |  | 0.16963 |  |  | -0.40702 |  |  | -3.4762 |  |  | 5.6747 |  |  | 2.3188
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73914 |  |  | 0.7397 |  |  | 0.75245 |  |  | 0.79344 |  |  | 0.9013 |  |  | 1.2532 |  |  | 3.3624 |  |  | -2.187 |  |  | -0.97696
[13 empty] | C Non choked w/ reducers | 5 |  | 0.18659 |  |  | 3.9292 |  |  | 9.9811 |  |  | 21.0357 |  |  | 42.7846 |  |  | 106.6867 |  |  | #NUM! |  |  | #NUM! |  |  | -88.6521 |  |  | -128.3939
[13 empty] | C Choked w/ reducers | 5 |  | 0.18301 |  |  | 3.8518 |  |  | 9.7816 |  |  | 20.4504 |  |  | 40.0644 |  |  | 78.4459 |  |  | 180.4937 |  |  | 747.0228 |  |  | 898.7802 |  |  | 457.99
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.18659 |  |  | 3.9292 |  |  | 9.9811 |  |  | 21.0357 |  |  | 42.7846 |  |  | 106.6867 |  |  | #NUM! |  |  | #NUM! |  |  | 898.7802 |  |  | 457.99
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8134 | 43.1536 |  | 1.0708 | 904.8355 |  | 0.018851 | 2237.766 |  | 3.8357 | 4358.5969 |  | 16.1846 | 7168.2872 |  | 68.2867 | 10054.0746 |  | 7174 | 12766.0069 |  | 7174 | 14969.1471 |  | 7174 | 16700.6036 |  | 7174 | 18632.3348
[13 empty] | Next iteration flow rate |  |  | 44.0167 | Abs Value of | Flow this | 913.8839 | Abs Value of | Flow this | 2260.1436 | Abs Value of | Flow this | 4402.1829 | Abs Value of | Flow this | 7239.9701 | Abs Value of | Flow this | 10154.6154 | Abs Value of | Flow this | 12893.667 | Abs Value of | Flow this | 15118.8386 | Abs Value of | Flow this | 16867.6096 | Abs Value of | Flow this | 18818.6582 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.522 |  |  | 100.1897 |  |  | 98.4858 |  |  | 92.7951 |  |  | 79.6208 |  |  | 59.404 |  |  | 34.23 |  |  | 9.3741 |  |  | -12.9314 |  |  | -40.6955
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.4833 |  |  | 0.47508 |  |  | 0.44763 |  |  | 0.38408 |  |  | 0.28655 |  |  | 0.16512 |  |  | 0.045219 |  |  | -0.062379 |  |  | -0.19631
[13 empty] | Delta P at this iteration flow rate |  |  | 50.522 |  |  | 50.1897 |  |  | 48.4858 |  |  | 42.7951 |  |  | 29.6208 |  |  | 9.404 |  |  | -15.77 |  |  | -40.6259 |  |  | -62.9314 |  |  | -90.6955
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50095 |  |  | 0.49231 |  |  | 0.46118 |  |  | 0.37202 |  |  | 0.15831 |  |  | -0.46071 |  |  | -4.3338 |  |  | 4.8665 |  |  | 2.2286
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73916 |  |  | 0.73981 |  |  | 0.75292 |  |  | 0.79522 |  |  | 0.90789 |  |  | 1.2866 |  |  | 3.9453 |  |  | -1.7331 |  |  | -0.90008
[13 empty] | C Non choked w/ reducers | 5 |  | 0.19033 |  |  | 3.9688 |  |  | 10.0857 |  |  | 21.2879 |  |  | 43.5267 |  |  | 112.2421 |  |  | #NUM! |  |  | #NUM! |  |  | -100.9155 |  |  | -133.7567
[13 empty] | C Choked w/ reducers | 5 |  | 0.18667 |  |  | 3.8906 |  |  | 9.8834 |  |  | 20.6888 |  |  | 40.6743 |  |  | 80.311 |  |  | 189.2553 |  |  | 899.0469 |  |  | 750.8394 |  |  | 430.9417
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.19033 |  |  | 3.9688 |  |  | 10.0857 |  |  | 21.2879 |  |  | 43.5267 |  |  | 112.2421 |  |  | #NUM! |  |  | #NUM! |  |  | 750.8394 |  |  | 430.9417
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8097 | 44.0167 |  | 1.0312 | 913.8839 |  | 0.085696 | 2260.1436 |  | 4.0879 | 4402.1829 |  | 16.9267 | 7239.9701 |  | 73.8421 | 10154.6154 |  | 7174 | 12893.667 |  | 7174 | 15118.8386 |  | 7174 | 16867.6096 |  | 7174 | 18818.6582
[13 empty] | Next iteration flow rate |  |  | 44.897 | Abs Value of | Flow this | 923.0227 | Abs Value of | Flow this | 2282.7451 | Abs Value of | Flow this | 4446.2047 | Abs Value of | Flow this | 7312.3698 | Abs Value of | Flow this | 10256.1615 | Abs Value of | Flow this | 13022.6037 | Abs Value of | Flow this | 15270.027 | Abs Value of | Flow this | 17036.2857 | Abs Value of | Flow this | 19006.8447 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.522 |  |  | 100.1831 |  |  | 98.4449 |  |  | 92.6398 |  |  | 79.2007 |  |  | 58.5775 |  |  | 32.8975 |  |  | 7.542 |  |  | -15.2119 |  |  | -43.534
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48327 |  |  | 0.47488 |  |  | 0.44688 |  |  | 0.38205 |  |  | 0.28257 |  |  | 0.15869 |  |  | 0.036381 |  |  | -0.073379 |  |  | -0.21
[13 empty] | Delta P at this iteration flow rate |  |  | 50.522 |  |  | 50.1831 |  |  | 48.4449 |  |  | 42.6398 |  |  | 29.2007 |  |  | 8.5775 |  |  | -17.1025 |  |  | -42.458 |  |  | -65.2119 |  |  | -93.534
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50091 |  |  | 0.4921 |  |  | 0.46027 |  |  | 0.36869 |  |  | 0.14643 |  |  | -0.51987 |  |  | -5.6295 |  |  | 4.2869 |  |  | 2.1485
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73918 |  |  | 0.73992 |  |  | 0.75341 |  |  | 0.79706 |  |  | 0.9148 |  |  | 1.3234 |  |  | 4.8258 |  |  | -1.4076 |  |  | -0.83178
[13 empty] | C Non choked w/ reducers | 5 |  | 0.19413 |  |  | 4.0088 |  |  | 10.1914 |  |  | 21.5441 |  |  | 44.2922 |  |  | 118.6321 |  |  | #NUM! |  |  | #NUM! |  |  | -113.6673 |  |  | -139.1798
[13 empty] | C Choked w/ reducers | 5 |  | 0.19041 |  |  | 3.9298 |  |  | 9.9864 |  |  | 20.9307 |  |  | 41.299 |  |  | 82.2585 |  |  | 198.8901 |  |  | 1128.616 |  |  | 644.663 |  |  | 406.872
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.19413 |  |  | 4.0088 |  |  | 10.1914 |  |  | 21.5441 |  |  | 44.2922 |  |  | 118.6321 |  |  | #NUM! |  |  | #NUM! |  |  | 644.663 |  |  | 406.872
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8059 | 44.897 |  | 0.99123 | 923.0227 |  | 0.19144 | 2282.7451 |  | 4.3441 | 4446.2047 |  | 17.6922 | 7312.3698 |  | 80.2321 | 10256.1615 |  | 7174 | 13022.6037 |  | 7174 | 15270.027 |  | 7174 | 17036.2857 |  | 7174 | 19006.8447
[13 empty] | Next iteration flow rate |  |  | 45.7949 | Abs Value of | Flow this | 932.253 | Abs Value of | Flow this | 2305.5725 | Abs Value of | Flow this | 4490.6668 | Abs Value of | Flow this | 7385.4935 | Abs Value of | Flow this | 10358.7232 | Abs Value of | Flow this | 13152.8297 | Abs Value of | Flow this | 15422.7272 | Abs Value of | Flow this | 17206.6486 | Abs Value of | Flow this | 19196.9132 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.522 |  |  | 100.1762 |  |  | 98.4031 |  |  | 92.4813 |  |  | 78.7721 |  |  | 57.7344 |  |  | 31.5382 |  |  | 5.6731 |  |  | -17.5381 |  |  | -46.4295
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48323 |  |  | 0.47468 |  |  | 0.44611 |  |  | 0.37998 |  |  | 0.2785 |  |  | 0.15213 |  |  | 0.027366 |  |  | -0.084601 |  |  | -0.22397
[13 empty] | Delta P at this iteration flow rate |  |  | 50.522 |  |  | 50.1762 |  |  | 48.4031 |  |  | 42.4813 |  |  | 28.7721 |  |  | 7.7344 |  |  | -18.4618 |  |  | -44.3269 |  |  | -67.5381 |  |  | -96.4295
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50088 |  |  | 0.49189 |  |  | 0.45935 |  |  | 0.36526 |  |  | 0.13397 |  |  | -0.58538 |  |  | -7.8135 |  |  | 3.8509 |  |  | 2.0769
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73919 |  |  | 0.74003 |  |  | 0.7539 |  |  | 0.79895 |  |  | 0.92205 |  |  | 1.3641 |  |  | 6.31 |  |  | -1.1627 |  |  | -0.77072
[13 empty] | C Non choked w/ reducers | 5 |  | 0.19802 |  |  | 4.0492 |  |  | 10.2984 |  |  | 21.8044 |  |  | 45.0826 |  |  | 126.0983 |  |  | #NUM! |  |  | #NUM! |  |  | -127.186 |  |  | -144.6806
[13 empty] | C Choked w/ reducers | 5 |  | 0.19422 |  |  | 3.9693 |  |  | 10.0905 |  |  | 21.1762 |  |  | 41.9389 |  |  | 84.2944 |  |  | 209.5367 |  |  | 1515.4257 |  |  | 564.7461 |  |  | 385.3127
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.19802 |  |  | 4.0492 |  |  | 10.2984 |  |  | 21.8044 |  |  | 45.0826 |  |  | 126.0983 |  |  | #NUM! |  |  | #NUM! |  |  | 564.7461 |  |  | 385.3127
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.802 | 45.7949 |  | 0.95083 | 932.253 |  | 0.29839 | 2305.5725 |  | 4.6044 | 4490.6668 |  | 18.4826 | 7385.4935 |  | 87.6983 | 10358.7232 |  | 7174 | 13152.8297 |  | 7174 | 15422.7272 |  | 7174 | 17206.6486 |  | 7174 | 19196.9132
[13 empty] | Next iteration flow rate |  |  | 46.7108 | Abs Value of | Flow this | 941.5755 | Abs Value of | Flow this | 2328.6282 | Abs Value of | Flow this | 4535.5734 | Abs Value of | Flow this | 7459.3484 | Abs Value of | Flow this | 10462.3104 | Abs Value of | Flow this | 13284.358 | Abs Value of | Flow this | 15576.9545 | Abs Value of | Flow this | 17378.7151 | Abs Value of | Flow this | 19388.8823 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5219 |  |  | 100.1693 |  |  | 98.3605 |  |  | 92.3197 |  |  | 78.3349 |  |  | 56.8743 |  |  | 30.1516 |  |  | 3.7666 |  |  | -19.9112 |  |  | -49.3833
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.4832 |  |  | 0.47447 |  |  | 0.44533 |  |  | 0.37787 |  |  | 0.27435 |  |  | 0.14545 |  |  | 0.018169 |  |  | -0.096048 |  |  | -0.23822
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5219 |  |  | 50.1693 |  |  | 48.3605 |  |  | 42.3197 |  |  | 28.3349 |  |  | 6.8743 |  |  | -19.8484 |  |  | -46.2334 |  |  | -69.9112 |  |  | -99.3833
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50084 |  |  | 0.49167 |  |  | 0.4584 |  |  | 0.36172 |  |  | 0.12087 |  |  | -0.65829 |  |  | -12.2745 |  |  | 3.5112 |  |  | 2.0125
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73921 |  |  | 0.74015 |  |  | 0.75441 |  |  | 0.8009 |  |  | 0.92967 |  |  | 1.4095 |  |  | 9.3417 |  |  | -0.97191 |  |  | -0.7158
[13 empty] | C Non choked w/ reducers | 5 |  | 0.20198 |  |  | 4.09 |  |  | 10.4066 |  |  | 22.0689 |  |  | 45.8992 |  |  | 134.9935 |  |  | #NUM! |  |  | #NUM! |  |  | -141.7618 |  |  | -150.2762
[13 empty] | C Choked w/ reducers | 5 |  | 0.1981 |  |  | 4.0093 |  |  | 10.1959 |  |  | 21.4254 |  |  | 42.5947 |  |  | 86.4247 |  |  | 221.3645 |  |  | 2305.2863 |  |  | 502.4137 |  |  | 365.8888
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.20198 |  |  | 4.09 |  |  | 10.4066 |  |  | 22.0689 |  |  | 45.8992 |  |  | 134.9935 |  |  | #NUM! |  |  | #NUM! |  |  | 502.4137 |  |  | 365.8888
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.798 | 46.7108 |  | 0.91001 | 941.5755 |  | 0.40657 | 2328.6282 |  | 4.8689 | 4535.5734 |  | 19.2992 | 7459.3484 |  | 96.5935 | 10462.3104 |  | 7174 | 13284.358 |  | 7174 | 15576.9545 |  | 7174 | 17378.7151 |  | 7174 | 19388.8823
[13 empty] | Next iteration flow rate |  |  | 47.6451 | Abs Value of | Flow this | 950.9912 | Abs Value of | Flow this | 2351.9145 | Abs Value of | Flow this | 4580.9292 | Abs Value of | Flow this | 7533.9419 | Abs Value of | Flow this | 10566.9335 | Abs Value of | Flow this | 13417.2016 | Abs Value of | Flow this | 15732.724 | Abs Value of | Flow this | 17552.5022 | Abs Value of | Flow this | 19582.7711 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5219 |  |  | 100.1622 |  |  | 98.317 |  |  | 92.1548 |  |  | 77.889 |  |  | 55.997 |  |  | 28.7372 |  |  | 1.8218 |  |  | -22.3319 |  |  | -52.3964
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48316 |  |  | 0.47426 |  |  | 0.44454 |  |  | 0.37572 |  |  | 0.27012 |  |  | 0.13862 |  |  | 0.0087881 |  |  | -0.10773 |  |  | -0.25275
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5219 |  |  | 50.1622 |  |  | 48.317 |  |  | 42.1548 |  |  | 27.889 |  |  | 5.997 |  |  | -21.2628 |  |  | -48.1782 |  |  | -72.3319 |  |  | -102.3964
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50081 |  |  | 0.49144 |  |  | 0.45743 |  |  | 0.35806 |  |  | 0.1071 |  |  | -0.73991 |  |  | -26.4452 |  |  | 3.239 |  |  | 1.9543
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73923 |  |  | 0.74027 |  |  | 0.75493 |  |  | 0.80291 |  |  | 0.93769 |  |  | 1.4602 |  |  | 18.972 |  |  | -0.81903 |  |  | -0.66616
[13 empty] | C Non choked w/ reducers | 5 |  | 0.20602 |  |  | 4.1312 |  |  | 10.516 |  |  | 22.3378 |  |  | 46.7435 |  |  | 145.8581 |  |  | #NUM! |  |  | #NUM! |  |  | -157.7238 |  |  | -155.9835
[13 empty] | C Choked w/ reducers | 5 |  | 0.20206 |  |  | 4.0497 |  |  | 10.3024 |  |  | 21.6784 |  |  | 43.267 |  |  | 88.6566 |  |  | 234.5828 |  |  | 4813.8591 |  |  | 452.4328 |  |  | 348.2964
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.20602 |  |  | 4.1312 |  |  | 10.516 |  |  | 22.3378 |  |  | 46.7435 |  |  | 145.8581 |  |  | #NUM! |  |  | #NUM! |  |  | 452.4328 |  |  | 348.2964
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.794 | 47.6451 |  | 0.86877 | 950.9912 |  | 0.516 | 2351.9145 |  | 5.1378 | 4580.9292 |  | 20.1435 | 7533.9419 |  | 107.4581 | 10566.9335 |  | 7174 | 13417.2016 |  | 7174 | 15732.724 |  | 7174 | 17552.5022 |  | 7174 | 19582.7711
[13 empty] | Next iteration flow rate |  |  | 48.598 | Abs Value of | Flow this | 960.5012 | Abs Value of | Flow this | 2375.4337 | Abs Value of | Flow this | 4626.7385 | Abs Value of | Flow this | 7609.2813 | Abs Value of | Flow this | 10672.6028 | Abs Value of | Flow this | 13551.3736 | Abs Value of | Flow this | 15890.0513 | Abs Value of | Flow this | 17728.0272 | Abs Value of | Flow this | 19778.5989 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5218 |  |  | 100.1549 |  |  | 98.2727 |  |  | 91.9866 |  |  | 77.434 |  |  | 55.102 |  |  | 27.2943 |  |  | -0.16208 |  |  | -24.8013 |  |  | -55.47
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48313 |  |  | 0.47405 |  |  | 0.44373 |  |  | 0.37353 |  |  | 0.2658 |  |  | 0.13166 |  |  | -0.00078183 |  |  | -0.11964 |  |  | -0.26758
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5218 |  |  | 50.1549 |  |  | 48.2727 |  |  | 41.9866 |  |  | 27.434 |  |  | 5.102 |  |  | -22.7057 |  |  | -50.1621 |  |  | -74.8013 |  |  | -105.47
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50077 |  |  | 0.49121 |  |  | 0.45644 |  |  | 0.35429 |  |  | 0.092593 |  |  | -0.83189 |  |  | 309.4959 |  |  | 3.016 |  |  | 1.9014
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73925 |  |  | 0.74039 |  |  | 0.75546 |  |  | 0.80498 |  |  | 0.94613 |  |  | 1.5174 |  |  | -209.3319 |  |  | -0.69384 |  |  | -0.62108
[13 empty] | C Non choked w/ reducers | 5 |  | 0.21014 |  |  | 4.1729 |  |  | 10.6267 |  |  | 22.611 |  |  | 47.6173 |  |  | 159.5715 |  |  | #NUM! |  |  | -6.9323 |  |  | -175.4687 |  |  | -161.8198
[13 empty] | C Choked w/ reducers | 5 |  | 0.2061 |  |  | 4.0905 |  |  | 10.4101 |  |  | 21.9352 |  |  | 43.9564 |  |  | 90.9975 |  |  | 249.4536 |  |  | 54650.9651 |  |  | 411.4594 |  |  | 332.2868
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.21014 |  |  | 4.1729 |  |  | 10.6267 |  |  | 22.611 |  |  | 47.6173 |  |  | 159.5715 |  |  | #NUM! |  |  | 54650.9651 |  |  | 411.4594 |  |  | 332.2868
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7899 | 48.598 |  | 0.82711 | 960.5012 |  | 0.6267 | 2375.4337 |  | 5.411 | 4626.7385 |  | 21.0173 | 7609.2813 |  | 121.1715 | 10672.6028 |  | 7174 | 13551.3736 |  | 7174 | 15890.0513 |  | 7174 | 17728.0272 |  | 7174 | 19778.5989
[13 empty] | Next iteration flow rate |  |  | 49.5699 | Abs Value of | Flow this | 970.1062 | Abs Value of | Flow this | 2399.188 | Abs Value of | Flow this | 4673.0058 | Abs Value of | Flow this | 7685.3741 | Abs Value of | Flow this | 10779.3289 | Abs Value of | Flow this | 13686.8873 | Abs Value of | Flow this | 16048.9518 | Abs Value of | Flow this | 17905.3075 | Abs Value of | Flow this | 19976.3848 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5218 |  |  | 100.1475 |  |  | 98.2275 |  |  | 91.815 |  |  | 76.9699 |  |  | 54.1891 |  |  | 25.8224 |  |  | -2.1858 |  |  | -27.3203 |  |  | -58.6055
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48309 |  |  | 0.47383 |  |  | 0.4429 |  |  | 0.37129 |  |  | 0.2614 |  |  | 0.12456 |  |  | -0.010544 |  |  | -0.13179 |  |  | -0.2827
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5218 |  |  | 50.1475 |  |  | 48.2275 |  |  | 41.815 |  |  | 26.9699 |  |  | 4.1891 |  |  | -24.1776 |  |  | -52.1858 |  |  | -77.3203 |  |  | -108.6055
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50074 |  |  | 0.49098 |  |  | 0.45543 |  |  | 0.3504 |  |  | 0.077305 |  |  | -0.9363 |  |  | 23.8745 |  |  | 2.8301 |  |  | 1.8532
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73927 |  |  | 0.74051 |  |  | 0.756 |  |  | 0.80713 |  |  | 0.95502 |  |  | 1.5824 |  |  | -15.225 |  |  | -0.58944 |  |  | -0.57996
[13 empty] | C Non choked w/ reducers | 5 |  | 0.21434 |  |  | 4.215 |  |  | 10.7387 |  |  | 22.8888 |  |  | 48.5223 |  |  | 177.686 |  |  | #NUM! |  |  | -25.7003 |  |  | -195.4966 |  |  | -167.8023
[13 empty] | C Choked w/ reducers | 5 |  | 0.21023 |  |  | 4.1317 |  |  | 10.519 |  |  | 22.196 |  |  | 44.6636 |  |  | 93.4559 |  |  | 266.3094 |  |  | 4092.8047 |  |  | 377.2568 |  |  | 317.6542
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.21434 |  |  | 4.215 |  |  | 10.7387 |  |  | 22.8888 |  |  | 48.5223 |  |  | 177.686 |  |  | #NUM! |  |  | 4092.8047 |  |  | 377.2568 |  |  | 317.6542
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7857 | 49.5699 |  | 0.78503 | 970.1062 |  | 0.73867 | 2399.188 |  | 5.6888 | 4673.0058 |  | 21.9223 | 7685.3741 |  | 139.286 | 10779.3289 |  | 7174 | 13686.8873 |  | 7174 | 16048.9518 |  | 7174 | 17905.3075 |  | 7174 | 19976.3848
[13 empty] | Next iteration flow rate |  |  | 50.5613 | Abs Value of | Flow this | 979.8072 | Abs Value of | Flow this | 2423.1799 | Abs Value of | Flow this | 4719.7359 | Abs Value of | Flow this | 7762.2278 | Abs Value of | Flow this | 10887.1221 | Abs Value of | Flow this | 13823.7562 | Abs Value of | Flow this | 16209.4413 | Abs Value of | Flow this | 18084.3606 | Abs Value of | Flow this | 20176.1487 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5218 |  |  | 100.14 |  |  | 98.1813 |  |  | 91.64 |  |  | 76.4965 |  |  | 53.2578 |  |  | 24.3209 |  |  | -4.2503 |  |  | -29.8899 |  |  | -61.804
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48306 |  |  | 0.47361 |  |  | 0.44206 |  |  | 0.36901 |  |  | 0.25691 |  |  | 0.11732 |  |  | -0.020503 |  |  | -0.14418 |  |  | -0.29813
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5218 |  |  | 50.14 |  |  | 48.1813 |  |  | 41.64 |  |  | 26.4965 |  |  | 3.2578 |  |  | -25.6791 |  |  | -54.2503 |  |  | -79.8899 |  |  | -111.804
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.5007 |  |  | 0.49074 |  |  | 0.45439 |  |  | 0.34638 |  |  | 0.06117 |  |  | -1.0558 |  |  | 12.7639 |  |  | 2.6728 |  |  | 1.809
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73929 |  |  | 0.74064 |  |  | 0.75656 |  |  | 0.80934 |  |  | 0.96441 |  |  | 1.6567 |  |  | -7.6743 |  |  | -0.50108 |  |  | -0.54232
[13 empty] | C Non choked w/ reducers | 5 |  | 0.21863 |  |  | 4.2575 |  |  | 10.8519 |  |  | 23.1713 |  |  | 49.4606 |  |  | 203.2776 |  |  | #NUM! |  |  | -36.2204 |  |  | -218.4622 |  |  | -173.9494
[13 empty] | C Choked w/ reducers | 5 |  | 0.21443 |  |  | 4.1733 |  |  | 10.6292 |  |  | 22.4608 |  |  | 45.3894 |  |  | 96.0411 |  |  | 285.5778 |  |  | 2125.9013 |  |  | 348.2722 |  |  | 304.2271
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.21863 |  |  | 4.2575 |  |  | 10.8519 |  |  | 23.1713 |  |  | 49.4606 |  |  | 203.2776 |  |  | #NUM! |  |  | 2125.9013 |  |  | 348.2722 |  |  | 304.2271
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7814 | 50.5613 |  | 0.74251 | 979.8072 |  | 0.85195 | 2423.1799 |  | 5.9713 | 4719.7359 |  | 22.8606 | 7762.2278 |  | 164.8776 | 10887.1221 |  | 7174 | 13823.7562 |  | 7174 | 16209.4413 |  | 7174 | 18084.3606 |  | 7174 | 20176.1487
[13 empty] | Next iteration flow rate |  |  | 51.5725 | Abs Value of | Flow this | 989.6053 | Abs Value of | Flow this | 2447.4117 | Abs Value of | Flow this | 4766.9333 | Abs Value of | Flow this | 7839.8501 | Abs Value of | Flow this | 10995.9934 | Abs Value of | Flow this | 13961.9938 | Abs Value of | Flow this | 16371.5357 | Abs Value of | Flow this | 18265.2042 | Abs Value of | Flow this | 20377.9102 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5217 |  |  | 100.1323 |  |  | 98.1343 |  |  | 91.4615 |  |  | 76.0136 |  |  | 52.3077 |  |  | 22.7892 |  |  | -6.3562 |  |  | -32.5112 |  |  | -65.0667
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48302 |  |  | 0.47338 |  |  | 0.44119 |  |  | 0.36668 |  |  | 0.25232 |  |  | 0.10993 |  |  | -0.030661 |  |  | -0.15683 |  |  | -0.31387
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5217 |  |  | 50.1323 |  |  | 48.1343 |  |  | 41.4615 |  |  | 26.0136 |  |  | 2.3077 |  |  | -27.2108 |  |  | -56.3562 |  |  | -82.5112 |  |  | -115.0667
[13 empty] | Press drop ratio this iteration |  |  | 0.5026 |  |  | 0.50066 |  |  | 0.49049 |  |  | 0.45332 |  |  | 0.34222 |  |  | 0.044119 |  |  | -1.194 |  |  | 8.8663 |  |  | 2.5379 |  |  | 1.7684
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73931 |  |  | 0.74077 |  |  | 0.75713 |  |  | 0.81163 |  |  | 0.97433 |  |  | 1.7427 |  |  | -5.0255 |  |  | -0.42533 |  |  | -0.50773
[13 empty] | C Non choked w/ reducers | 5 |  | 0.223 |  |  | 4.3004 |  |  | 10.9665 |  |  | 23.4585 |  |  | 50.4342 |  |  | 243.6356 |  |  | #NUM! |  |  | -44.8201 |  |  | -245.2511 |  |  | -180.2798
[13 empty] | C Choked w/ reducers | 5 |  | 0.21872 |  |  | 4.2154 |  |  | 10.7406 |  |  | 22.7297 |  |  | 46.1346 |  |  | 98.7632 |  |  | 307.8191 |  |  | 1435.7651 |  |  | 323.3938 |  |  | 291.8614
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.223 |  |  | 4.3004 |  |  | 10.9665 |  |  | 23.4585 |  |  | 50.4342 |  |  | 243.6356 |  |  | #NUM! |  |  | 1435.7651 |  |  | 323.3938 |  |  | 291.8614
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.777 | 51.5725 |  | 0.69956 | 989.6053 |  | 0.96654 | 2447.4117 |  | 6.2585 | 4766.9333 |  | 23.8342 | 7839.8501 |  | 205.2356 | 10995.9934 |  | 7174 | 13961.9938 |  | 7174 | 16371.5357 |  | 7174 | 18265.2042 |  | 7174 | 20377.9102
[13 empty] | Next iteration flow rate |  |  | 52.604 | Abs Value of | Flow this | 999.5014 | Abs Value of | Flow this | 2471.8858 | Abs Value of | Flow this | 4814.6026 | Abs Value of | Flow this | 7918.2486 | Abs Value of | Flow this | 11105.9533 | Abs Value of | Flow this | 14101.6137 | Abs Value of | Flow this | 16535.2511 | Abs Value of | Flow this | 18447.8562 | Abs Value of | Flow this | 20581.6893 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5217 |  |  | 100.1244 |  |  | 98.0863 |  |  | 91.2793 |  |  | 75.521 |  |  | 51.3386 |  |  | 21.2268 |  |  | -8.5045 |  |  | -35.1852 |  |  | -68.3951
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48298 |  |  | 0.47315 |  |  | 0.44032 |  |  | 0.3643 |  |  | 0.24765 |  |  | 0.10239 |  |  | -0.041024 |  |  | -0.16973 |  |  | -0.32993
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5217 |  |  | 50.1244 |  |  | 48.0863 |  |  | 41.2793 |  |  | 25.521 |  |  | 1.3386 |  |  | -28.7732 |  |  | -58.5045 |  |  | -85.1852 |  |  | -118.3951
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.50062 |  |  | 0.49024 |  |  | 0.45223 |  |  | 0.33793 |  |  | 0.026074 |  |  | -1.3555 |  |  | 6.8792 |  |  | 2.4211 |  |  | 1.731
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73933 |  |  | 0.7409 |  |  | 0.75772 |  |  | 0.81399 |  |  | 0.98483 |  |  | 1.8431 |  |  | -3.6751 |  |  | -0.35969 |  |  | -0.47585
[13 empty] | C Non choked w/ reducers | 5 |  | 0.22746 |  |  | 4.3438 |  |  | 11.0825 |  |  | 23.7507 |  |  | 51.4456 |  |  | 322.651 |  |  | #NUM! |  |  | -52.5238 |  |  | -277.103 |  |  | -186.8135
[13 empty] | C Choked w/ reducers | 5 |  | 0.22309 |  |  | 4.2579 |  |  | 10.8534 |  |  | 23.0028 |  |  | 46.8999 |  |  | 101.6339 |  |  | 333.7816 |  |  | 1083.8161 |  |  | 301.8049 |  |  | 280.435
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.22746 |  |  | 4.3438 |  |  | 11.0825 |  |  | 23.7507 |  |  | 51.4456 |  |  | 322.651 |  |  | #NUM! |  |  | 1083.8161 |  |  | 301.8049 |  |  | 280.435
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7725 | 52.604 |  | 0.65616 | 999.5014 |  | 1.0825 | 2471.8858 |  | 6.5507 | 4814.6026 |  | 24.8456 | 7918.2486 |  | 284.251 | 11105.9533 |  | 7174 | 14101.6137 |  | 7174 | 16535.2511 |  | 7174 | 18447.8562 |  | 7174 | 20581.6893
[13 empty] | Next iteration flow rate |  |  | 53.6561 | Abs Value of | Flow this | 1009.4964 | Abs Value of | Flow this | 2496.6047 | Abs Value of | Flow this | 4862.7486 | Abs Value of | Flow this | 7997.4311 | Abs Value of | Flow this | 11217.0128 | Abs Value of | Flow this | 14242.6298 | Abs Value of | Flow this | 16700.6036 | Abs Value of | Flow this | 18632.3348 | Abs Value of | Flow this | 20787.5062 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5216 |  |  | 100.1164 |  |  | 98.0373 |  |  | 91.0935 |  |  | 75.0184 |  |  | 50.35 |  |  | 19.6329 |  |  | -10.6959 |  |  | -37.9129 |  |  | -71.7903
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48294 |  |  | 0.47291 |  |  | 0.43942 |  |  | 0.36188 |  |  | 0.24288 |  |  | 0.094706 |  |  | -0.051595 |  |  | -0.18289 |  |  | -0.3463
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5216 |  |  | 50.1164 |  |  | 48.0373 |  |  | 41.0935 |  |  | 25.0184 |  |  | 0.35002 |  |  | -30.3671 |  |  | -60.6959 |  |  | -87.9129 |  |  | -121.7903
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.50058 |  |  | 0.48999 |  |  | 0.45111 |  |  | 0.3335 |  |  | 0.0069518 |  |  | -1.5467 |  |  | 5.6747 |  |  | 2.3188 |  |  | 1.6965
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73935 |  |  | 0.74104 |  |  | 0.75831 |  |  | 0.81643 |  |  | 0.99596 |  |  | 1.9621 |  |  | -2.8565 |  |  | -0.30227 |  |  | -0.44637
[13 empty] | C Non choked w/ reducers | 5 |  | 0.23201 |  |  | 4.3877 |  |  | 11.1998 |  |  | 24.0479 |  |  | 52.4973 |  |  | 636.3243 |  |  | #NUM! |  |  | -59.751 |  |  | -315.8181 |  |  | -193.5717
[13 empty] | C Choked w/ reducers | 5 |  | 0.22756 |  |  | 4.3008 |  |  | 10.9674 |  |  | 23.2802 |  |  | 47.6862 |  |  | 104.6657 |  |  | 364.4875 |  |  | 870.3749 |  |  | 282.8918 |  |  | 269.8438
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.23201 |  |  | 4.3877 |  |  | 11.1998 |  |  | 24.0479 |  |  | 52.4973 |  |  | 636.3243 |  |  | #NUM! |  |  | 870.3749 |  |  | 282.8918 |  |  | 269.8438
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.768 | 53.6561 |  | 0.61232 | 1009.4964 |  | 1.1998 | 2496.6047 |  | 6.8479 | 4862.7486 |  | 25.8973 | 7997.4311 |  | 597.9243 | 11217.0128 |  | 7174 | 14242.6298 |  | 7174 | 16700.6036 |  | 7174 | 18632.3348 |  | 7174 | 20787.5062
[13 empty] | Next iteration flow rate |  |  | 54.7292 | Abs Value of | Flow this | 1019.5913 | Abs Value of | Flow this | 2521.5707 | Abs Value of | Flow this | 4911.3761 | Abs Value of | Flow this | 8077.4054 | Abs Value of | Flow this | 11329.183 | Abs Value of | Flow this | 14385.0561 | Abs Value of | Flow this | 16867.6096 | Abs Value of | Flow this | 18818.6582 | Abs Value of | Flow this | 20995.3812 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5216 |  |  | 100.1082 |  |  | 97.9873 |  |  | 90.904 |  |  | 74.5058 |  |  | 49.3416 |  |  | 18.0071 |  |  | -12.9314 |  |  | -40.6955 |  |  | -75.2538
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.4829 |  |  | 0.47267 |  |  | 0.4385 |  |  | 0.3594 |  |  | 0.23801 |  |  | 0.086863 |  |  | -0.062379 |  |  | -0.19631 |  |  | -0.36301
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5216 |  |  | 50.1082 |  |  | 47.9873 |  |  | 40.904 |  |  | 24.5058 |  |  | -0.65845 |  |  | -31.9929 |  |  | -62.9314 |  |  | -90.6955 |  |  | -125.2538
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.50054 |  |  | 0.48973 |  |  | 0.44997 |  |  | 0.32891 |  |  | -0.013345 |  |  | -1.7767 |  |  | 4.8665 |  |  | 2.2286 |  |  | 1.6644
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73937 |  |  | 0.74117 |  |  | 0.75893 |  |  | 0.81895 |  |  | 1.0078 |  |  | 2.1051 |  |  | -2.3073 |  |  | -0.25163 |  |  | -0.41904
[13 empty] | C Non choked w/ reducers | 5 |  | 0.23665 |  |  | 4.432 |  |  | 11.3184 |  |  | 24.3502 |  |  | 53.5923 |  |  | #NUM! |  |  | #NUM! |  |  | -66.7312 |  |  | -364.1239 |  |  | -200.577
[13 empty] | C Choked w/ reducers | 5 |  | 0.23211 |  |  | 4.3442 |  |  | 11.0827 |  |  | 23.562 |  |  | 48.4944 |  |  | 107.873 |  |  | 401.3716 |  |  | 727.1097 |  |  | 266.1845 |  |  | 259.9987
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.23665 |  |  | 4.432 |  |  | 11.3184 |  |  | 24.3502 |  |  | 53.5923 |  |  | #NUM! |  |  | #NUM! |  |  | 727.1097 |  |  | 266.1845 |  |  | 259.9987
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7634 | 54.7292 |  | 0.56803 | 1019.5913 |  | 1.3184 | 2521.5707 |  | 7.1502 | 4911.3761 |  | 26.9923 | 8077.4054 |  | 7174 | 11329.183 |  | 7174 | 14385.0561 |  | 7174 | 16867.6096 |  | 7174 | 18818.6582 |  | 7174 | 20995.3812
[13 empty] | Next iteration flow rate |  |  | 55.8238 | Abs Value of | Flow this | 1029.7872 | Abs Value of | Flow this | 2546.7864 | Abs Value of | Flow this | 4960.4899 | Abs Value of | Flow this | 8158.1795 | Abs Value of | Flow this | 11442.4748 | Abs Value of | Flow this | 14528.9067 | Abs Value of | Flow this | 17036.2857 | Abs Value of | Flow this | 19006.8447 | Abs Value of | Flow this | 21205.335 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5215 |  |  | 100.0999 |  |  | 97.9364 |  |  | 90.7107 |  |  | 73.9828 |  |  | 48.3128 |  |  | 16.3485 |  |  | -15.2119 |  |  | -43.534 |  |  | -78.7869
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48286 |  |  | 0.47243 |  |  | 0.43757 |  |  | 0.35688 |  |  | 0.23305 |  |  | 0.078862 |  |  | -0.073379 |  |  | -0.21 |  |  | -0.38005
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5215 |  |  | 50.0999 |  |  | 47.9364 |  |  | 40.7107 |  |  | 23.9828 |  |  | -1.6872 |  |  | -33.6515 |  |  | -65.2119 |  |  | -93.534 |  |  | -128.7869
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.5005 |  |  | 0.48946 |  |  | 0.4488 |  |  | 0.32417 |  |  | -0.034922 |  |  | -2.0584 |  |  | 4.2869 |  |  | 2.1485 |  |  | 1.6346
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73939 |  |  | 0.74131 |  |  | 0.75955 |  |  | 0.82156 |  |  | 1.0203 |  |  | 2.2803 |  |  | -1.9134 |  |  | -0.20664 |  |  | -0.39364
[13 empty] | C Non choked w/ reducers | 5 |  | 0.24138 |  |  | 4.4767 |  |  | 11.4385 |  |  | 24.6579 |  |  | 54.7337 |  |  | #NUM! |  |  | #NUM! |  |  | -73.6134 |  |  | -426.37 |  |  | -207.854
[13 empty] | C Choked w/ reducers | 5 |  | 0.23675 |  |  | 4.388 |  |  | 11.1993 |  |  | 23.8483 |  |  | 49.3256 |  |  | 111.2717 |  |  | 446.512 |  |  | 624.2889 |  |  | 251.3171 |  |  | 250.8228
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.24138 |  |  | 4.4767 |  |  | 11.4385 |  |  | 24.6579 |  |  | 54.7337 |  |  | #NUM! |  |  | #NUM! |  |  | 624.2889 |  |  | 251.3171 |  |  | 250.8228
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7586 | 55.8238 |  | 0.52328 | 1029.7872 |  | 1.4385 | 2546.7864 |  | 7.4579 | 4960.4899 |  | 28.1337 | 8158.1795 |  | 7174 | 11442.4748 |  | 7174 | 14528.9067 |  | 7174 | 17036.2857 |  | 7174 | 19006.8447 |  | 7174 | 21205.335
[13 empty] | Next iteration flow rate |  |  | 56.9403 | Abs Value of | Flow this | 1040.0851 | Abs Value of | Flow this | 2572.2543 | Abs Value of | Flow this | 5010.0948 | Abs Value of | Flow this | 8239.7613 | Abs Value of | Flow this | 11556.8995 | Abs Value of | Flow this | 14674.1958 | Abs Value of | Flow this | 17206.6486 | Abs Value of | Flow this | 19196.9132 | Abs Value of | Flow this | 21417.3884 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5215 |  |  | 100.0914 |  |  | 97.8844 |  |  | 90.5134 |  |  | 73.4494 |  |  | 47.2634 |  |  | 14.6566 |  |  | -17.5381 |  |  | -46.4295 |  |  | -82.3911
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48282 |  |  | 0.47218 |  |  | 0.43662 |  |  | 0.35431 |  |  | 0.22799 |  |  | 0.070701 |  |  | -0.084601 |  |  | -0.22397 |  |  | -0.39744
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5215 |  |  | 50.0914 |  |  | 47.8844 |  |  | 40.5134 |  |  | 23.4494 |  |  | -2.7366 |  |  | -35.3434 |  |  | -67.5381 |  |  | -96.4295 |  |  | -132.3911
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.50046 |  |  | 0.48919 |  |  | 0.4476 |  |  | 0.31926 |  |  | -0.057901 |  |  | -2.4114 |  |  | 3.8509 |  |  | 2.0769 |  |  | 1.6069
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73941 |  |  | 0.74146 |  |  | 0.7602 |  |  | 0.82427 |  |  | 1.0337 |  |  | 2.4999 |  |  | -1.6171 |  |  | -0.16641 |  |  | -0.36997
[13 empty] | C Non choked w/ reducers | 5 |  | 0.24621 |  |  | 4.5219 |  |  | 11.56 |  |  | 24.9711 |  |  | 55.925 |  |  | #NUM! |  |  | #NUM! |  |  | -80.507 |  |  | -509.9546 |  |  | -215.429
[13 empty] | C Choked w/ reducers | 5 |  | 0.24148 |  |  | 4.4322 |  |  | 11.3173 |  |  | 24.1393 |  |  | 50.1807 |  |  | 114.8797 |  |  | 503.0362 |  |  | 546.8977 |  |  | 238.0004 |  |  | 242.2492
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.24621 |  |  | 4.5219 |  |  | 11.56 |  |  | 24.9711 |  |  | 55.925 |  |  | #NUM! |  |  | #NUM! |  |  | 546.8977 |  |  | 238.0004 |  |  | 242.2492
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7538 | 56.9403 |  | 0.47808 | 1040.0851 |  | 1.56 | 2572.2543 |  | 7.7711 | 5010.0948 |  | 29.325 | 8239.7613 |  | 7174 | 11556.8995 |  | 7174 | 14674.1958 |  | 7174 | 17206.6486 |  | 7174 | 19196.9132 |  | 7174 | 21417.3884
[13 empty] | Next iteration flow rate |  |  | 58.0791 | Abs Value of | Flow this | 1050.486 | Abs Value of | Flow this | 2597.9768 | Abs Value of | Flow this | 5060.1957 | Abs Value of | Flow this | 8322.1589 | Abs Value of | Flow this | 11672.4685 | Abs Value of | Flow this | 14820.9377 | Abs Value of | Flow this | 17378.7151 | Abs Value of | Flow this | 19388.8823 | Abs Value of | Flow this | 21631.5623 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5214 |  |  | 100.0827 |  |  | 97.8314 |  |  | 90.3123 |  |  | 72.9052 |  |  | 46.1929 |  |  | 12.9307 |  |  | -19.9112 |  |  | -49.3833 |  |  | -86.0676
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48278 |  |  | 0.47192 |  |  | 0.43565 |  |  | 0.35168 |  |  | 0.22283 |  |  | 0.062375 |  |  | -0.096048 |  |  | -0.23822 |  |  | -0.41517
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5214 |  |  | 50.0827 |  |  | 47.8314 |  |  | 40.3123 |  |  | 22.9052 |  |  | -3.8071 |  |  | -37.0693 |  |  | -69.9112 |  |  | -99.3833 |  |  | -136.0676
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.50041 |  |  | 0.48892 |  |  | 0.44637 |  |  | 0.31418 |  |  | -0.082418 |  |  | -2.8668 |  |  | 3.5112 |  |  | 2.0125 |  |  | 1.5809
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73944 |  |  | 0.7416 |  |  | 0.76086 |  |  | 0.82706 |  |  | 1.048 |  |  | 2.7831 |  |  | -1.3862 |  |  | -0.13024 |  |  | -0.34787
[13 empty] | C Non choked w/ reducers | 5 |  | 0.25113 |  |  | 4.5676 |  |  | 11.6829 |  |  | 25.2898 |  |  | 57.1702 |  |  | #NUM! |  |  | #NUM! |  |  | -87.5014 |  |  | -628.5757 |  |  | -223.3311
[13 empty] | C Choked w/ reducers | 5 |  | 0.24631 |  |  | 4.4769 |  |  | 11.4367 |  |  | 24.435 |  |  | 51.0608 |  |  | 118.7175 |  |  | 575.8803 |  |  | 486.5353 |  |  | 226.0026 |  |  | 234.22
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.25113 |  |  | 4.5676 |  |  | 11.6829 |  |  | 25.2898 |  |  | 57.1702 |  |  | #NUM! |  |  | #NUM! |  |  | 486.5353 |  |  | 226.0026 |  |  | 234.22
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7489 | 58.0791 |  | 0.4324 | 1050.486 |  | 1.6829 | 2597.9768 |  | 8.0898 | 5060.1957 |  | 30.5702 | 8322.1589 |  | 7174 | 11672.4685 |  | 7174 | 14820.9377 |  | 7174 | 17378.7151 |  | 7174 | 19388.8823 |  | 7174 | 21631.5623
[13 empty] | Next iteration flow rate |  |  | 59.2406 | Abs Value of | Flow this | 1060.9908 | Abs Value of | Flow this | 2623.9566 | Abs Value of | Flow this | 5110.7977 | Abs Value of | Flow this | 8405.3805 | Abs Value of | Flow this | 11789.1932 | Abs Value of | Flow this | 14969.1471 | Abs Value of | Flow this | 17552.5022 | Abs Value of | Flow this | 19582.7711 | Abs Value of | Flow this | 21847.8779 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5214 |  |  | 100.0739 |  |  | 97.7773 |  |  | 90.107 |  |  | 72.3501 |  |  | 45.1008 |  |  | 11.1701 |  |  | -22.3319 |  |  | -52.3964 |  |  | -89.8181
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48274 |  |  | 0.47166 |  |  | 0.43466 |  |  | 0.349 |  |  | 0.21756 |  |  | 0.053882 |  |  | -0.10773 |  |  | -0.25275 |  |  | -0.43327
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5214 |  |  | 50.0739 |  |  | 47.7773 |  |  | 40.107 |  |  | 22.3501 |  |  | -4.8992 |  |  | -38.8299 |  |  | -72.3319 |  |  | -102.3964 |  |  | -139.8181
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.50037 |  |  | 0.48863 |  |  | 0.4451 |  |  | 0.30892 |  |  | -0.10863 |  |  | -3.4762 |  |  | 3.239 |  |  | 1.9543 |  |  | 1.5567
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73946 |  |  | 0.74175 |  |  | 0.76153 |  |  | 0.82996 |  |  | 1.0632 |  |  | 3.1622 |  |  | -1.2012 |  |  | -0.097538 |  |  | -0.32719
[13 empty] | C Non choked w/ reducers | 5 |  | 0.25616 |  |  | 4.6137 |  |  | 11.8073 |  |  | 25.6144 |  |  | 58.4736 |  |  | #NUM! |  |  | #NUM! |  |  | -94.6757 |  |  | -810.7641 |  |  | -231.5919
[13 empty] | C Choked w/ reducers | 5 |  | 0.25124 |  |  | 4.5221 |  |  | 11.5575 |  |  | 24.7356 |  |  | 51.9671 |  |  | 122.8079 |  |  | 673.3156 |  |  | 438.134 |  |  | 215.1361 |  |  | 226.6843
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.25616 |  |  | 4.6137 |  |  | 11.8073 |  |  | 25.6144 |  |  | 58.4736 |  |  | #NUM! |  |  | #NUM! |  |  | 438.134 |  |  | 215.1361 |  |  | 226.6843
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7438 | 59.2406 |  | 0.38626 | 1060.9908 |  | 1.8073 | 2623.9566 |  | 8.4144 | 5110.7977 |  | 31.8736 | 8405.3805 |  | 7174 | 11789.1932 |  | 7174 | 14969.1471 |  | 7174 | 17552.5022 |  | 7174 | 19582.7711 |  | 7174 | 21847.8779
[13 empty] | Next iteration flow rate |  |  | 60.4255 | Abs Value of | Flow this | 1071.6007 | Abs Value of | Flow this | 2650.1961 | Abs Value of | Flow this | 5161.9056 | Abs Value of | Flow this | 8489.4343 | Abs Value of | Flow this | 11907.0851 | Abs Value of | Flow this | 15118.8386 | Abs Value of | Flow this | 17728.0272 | Abs Value of | Flow this | 19778.5989 | Abs Value of | Flow this | 22066.3567 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5213 |  |  | 100.0649 |  |  | 97.7221 |  |  | 89.8977 |  |  | 71.7838 |  |  | 43.9869 |  |  | 9.3741 |  |  | -24.8013 |  |  | -55.47 |  |  | -93.644
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.4827 |  |  | 0.47139 |  |  | 0.43365 |  |  | 0.34627 |  |  | 0.21218 |  |  | 0.045219 |  |  | -0.11964 |  |  | -0.26758 |  |  | -0.45172
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5213 |  |  | 50.0649 |  |  | 47.7221 |  |  | 39.8977 |  |  | 21.7838 |  |  | -6.0131 |  |  | -40.6259 |  |  | -74.8013 |  |  | -105.47 |  |  | -143.644
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.50032 |  |  | 0.48834 |  |  | 0.44381 |  |  | 0.30346 |  |  | -0.1367 |  |  | -4.3338 |  |  | 3.016 |  |  | 1.9014 |  |  | 1.5339
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73948 |  |  | 0.74191 |  |  | 0.76223 |  |  | 0.83296 |  |  | 1.0795 |  |  | 3.6956 |  |  | -1.0497 |  |  | -0.067842 |  |  | -0.3078
[13 empty] | C Non choked w/ reducers | 5 |  | 0.26128 |  |  | 4.6604 |  |  | 11.9332 |  |  | 25.9449 |  |  | 59.8402 |  |  | #NUM! |  |  | #NUM! |  |  | -102.1049 |  |  | -1127.4384 |  |  | -240.2465
[13 empty] | C Choked w/ reducers | 5 |  | 0.25626 |  |  | 4.5677 |  |  | 11.6796 |  |  | 25.0411 |  |  | 52.9008 |  |  | 127.1772 |  |  | 810.3398 |  |  | 398.4555 |  |  | 205.2473 |  |  | 219.5973
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.26128 |  |  | 4.6604 |  |  | 11.9332 |  |  | 25.9449 |  |  | 59.8402 |  |  | #NUM! |  |  | #NUM! |  |  | 398.4555 |  |  | 205.2473 |  |  | 219.5973
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7387 | 60.4255 |  | 0.33964 | 1071.6007 |  | 1.9332 | 2650.1961 |  | 8.7449 | 5161.9056 |  | 33.2402 | 8489.4343 |  | 7174 | 11907.0851 |  | 7174 | 15118.8386 |  | 7174 | 17728.0272 |  | 7174 | 19778.5989 |  | 7174 | 22066.3567
[13 empty] | Next iteration flow rate |  |  | 61.634 | Abs Value of | Flow this | 1082.3167 | Abs Value of | Flow this | 2676.6981 | Abs Value of | Flow this | 5213.5247 | Abs Value of | Flow this | 8574.3286 | Abs Value of | Flow this | 12026.156 | Abs Value of | Flow this | 15270.027 | Abs Value of | Flow this | 17905.3075 | Abs Value of | Flow this | 19976.3848 | Abs Value of | Flow this | 22287.0202 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5213 |  |  | 100.0557 |  |  | 97.6658 |  |  | 89.6841 |  |  | 71.2062 |  |  | 42.8505 |  |  | 7.542 |  |  | -27.3203 |  |  | -58.6055 |  |  | -97.5467
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48265 |  |  | 0.47112 |  |  | 0.43262 |  |  | 0.34349 |  |  | 0.2067 |  |  | 0.036381 |  |  | -0.13179 |  |  | -0.2827 |  |  | -0.47055
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5213 |  |  | 50.0557 |  |  | 47.6658 |  |  | 39.6841 |  |  | 21.2062 |  |  | -7.1495 |  |  | -42.458 |  |  | -77.3203 |  |  | -108.6055 |  |  | -147.5467
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.50028 |  |  | 0.48805 |  |  | 0.44249 |  |  | 0.29781 |  |  | -0.16685 |  |  | -5.6295 |  |  | 2.8301 |  |  | 1.8532 |  |  | 1.5126
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73951 |  |  | 0.74206 |  |  | 0.76294 |  |  | 0.83607 |  |  | 1.0971 |  |  | 4.5016 |  |  | -0.92335 |  |  | -0.040758 |  |  | -0.28958
[13 empty] | C Non choked w/ reducers | 5 |  | 0.26651 |  |  | 4.7075 |  |  | 12.0606 |  |  | 26.2816 |  |  | 61.2754 |  |  | #NUM! |  |  | #NUM! |  |  | -109.8649 |  |  | -1817.1821 |  |  | -249.3335
[13 empty] | C Choked w/ reducers | 5 |  | 0.26139 |  |  | 4.6138 |  |  | 11.8032 |  |  | 25.3517 |  |  | 53.8633 |  |  | 131.8554 |  |  | 1017.2578 |  |  | 365.3339 |  |  | 196.209 |  |  | 212.9195
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.26651 |  |  | 4.7075 |  |  | 12.0606 |  |  | 26.2816 |  |  | 61.2754 |  |  | #NUM! |  |  | #NUM! |  |  | 365.3339 |  |  | 196.209 |  |  | 212.9195
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7335 | 61.634 |  | 0.29254 | 1082.3167 |  | 2.0606 | 2676.6981 |  | 9.0816 | 5213.5247 |  | 34.6754 | 8574.3286 |  | 7174 | 12026.156 |  | 7174 | 15270.027 |  | 7174 | 17905.3075 |  | 7174 | 19976.3848 |  | 7174 | 22287.0202
[13 empty] | Next iteration flow rate |  |  | 62.8666 | Abs Value of | Flow this | 1093.1399 | Abs Value of | Flow this | 2703.4651 | Abs Value of | Flow this | 5265.6599 | Abs Value of | Flow this | 8660.0719 | Abs Value of | Flow this | 12146.4176 | Abs Value of | Flow this | 15422.7272 | Abs Value of | Flow this | 18084.3606 | Abs Value of | Flow this | 20176.1487 | Abs Value of | Flow this | 22509.8904 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5212 |  |  | 100.0463 |  |  | 97.6083 |  |  | 89.4662 |  |  | 70.6169 |  |  | 41.6913 |  |  | 5.6731 |  |  | -29.8899 |  |  | -61.804 |  |  | -101.5279
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48261 |  |  | 0.47085 |  |  | 0.43157 |  |  | 0.34064 |  |  | 0.20111 |  |  | 0.027366 |  |  | -0.14418 |  |  | -0.29813 |  |  | -0.48975
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5212 |  |  | 50.0463 |  |  | 47.6083 |  |  | 39.4662 |  |  | 20.6169 |  |  | -8.3087 |  |  | -44.3269 |  |  | -79.8899 |  |  | -111.804 |  |  | -151.5279
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.50023 |  |  | 0.48775 |  |  | 0.44113 |  |  | 0.29195 |  |  | -0.19929 |  |  | -7.8135 |  |  | 2.6728 |  |  | 1.809 |  |  | 1.4925
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73953 |  |  | 0.74222 |  |  | 0.76366 |  |  | 0.8393 |  |  | 1.116 |  |  | 5.86 |  |  | -0.81642 |  |  | -0.015961 |  |  | -0.27245
[13 empty] | C Non choked w/ reducers | 5 |  | 0.27184 |  |  | 4.755 |  |  | 12.1895 |  |  | 26.6246 |  |  | 62.7855 |  |  | #NUM! |  |  | #NUM! |  |  | -118.0353 |  |  | -4498.083 |  |  | -258.8961
[13 empty] | C Choked w/ reducers | 5 |  | 0.26662 |  |  | 4.6604 |  |  | 11.9283 |  |  | 25.6676 |  |  | 54.8558 |  |  | 136.8768 |  |  | 1365.9018 |  |  | 337.2653 |  |  | 187.9153 |  |  | 206.616
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.27184 |  |  | 4.755 |  |  | 12.1895 |  |  | 26.6246 |  |  | 62.7855 |  |  | #NUM! |  |  | #NUM! |  |  | 337.2653 |  |  | 187.9153 |  |  | 206.616
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7282 | 62.8666 |  | 0.24495 | 1093.1399 |  | 2.1895 | 2703.4651 |  | 9.4246 | 5265.6599 |  | 36.1855 | 8660.0719 |  | 7174 | 12146.4176 |  | 7174 | 15422.7272 |  | 7174 | 18084.3606 |  | 7174 | 20176.1487 |  | 7174 | 22509.8904
[13 empty] | Next iteration flow rate |  |  | 64.124 | Abs Value of | Flow this | 1104.0713 | Abs Value of | Flow this | 2730.4997 | Abs Value of | Flow this | 5318.3165 | Abs Value of | Flow this | 8746.6726 | Abs Value of | Flow this | 12267.8817 | Abs Value of | Flow this | 15576.9545 | Abs Value of | Flow this | 18265.2042 | Abs Value of | Flow this | 20377.9102 | Abs Value of | Flow this | 22734.9894 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5211 |  |  | 100.0367 |  |  | 97.5498 |  |  | 89.244 |  |  | 70.0158 |  |  | 40.5088 |  |  | 3.7666 |  |  | -32.5112 |  |  | -65.0667 |  |  | -105.5891
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48256 |  |  | 0.47056 |  |  | 0.4305 |  |  | 0.33774 |  |  | 0.19541 |  |  | 0.018169 |  |  | -0.15683 |  |  | -0.31387 |  |  | -0.50934
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5211 |  |  | 50.0367 |  |  | 47.5498 |  |  | 39.244 |  |  | 20.0158 |  |  | -9.4912 |  |  | -46.2334 |  |  | -82.5112 |  |  | -115.0667 |  |  | -155.5891
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.50018 |  |  | 0.48744 |  |  | 0.43974 |  |  | 0.28588 |  |  | -0.2343 |  |  | -12.2745 |  |  | 2.5379 |  |  | 1.7684 |  |  | 1.4735
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73956 |  |  | 0.74238 |  |  | 0.76441 |  |  | 0.84264 |  |  | 1.1363 |  |  | 8.6347 |  |  | -0.72477 |  |  | 0.0068223 |  |  | -0.2563
[13 empty] | C Non choked w/ reducers | 5 |  | 0.27727 |  |  | 4.8031 |  |  | 12.32 |  |  | 26.9741 |  |  | 64.3775 |  |  | #NUM! |  |  | #NUM! |  |  | -126.7031 |  |  | 10210.8963 |  |  | -268.9825
[13 empty] | C Choked w/ reducers | 5 |  | 0.27195 |  |  | 4.7075 |  |  | 12.0548 |  |  | 25.9888 |  |  | 55.8801 |  |  | 142.2812 |  |  | 2077.8285 |  |  | 313.1732 |  |  | 180.2772 |  |  | 200.6558
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.27727 |  |  | 4.8031 |  |  | 12.32 |  |  | 26.9741 |  |  | 64.3775 |  |  | #NUM! |  |  | #NUM! |  |  | 313.1732 |  |  | 180.2772 |  |  | 200.6558
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7227 | 64.124 |  | 0.19687 | 1104.0713 |  | 2.32 | 2730.4997 |  | 9.7741 | 5318.3165 |  | 37.7775 | 8746.6726 |  | 7174 | 12267.8817 |  | 7174 | 15576.9545 |  | 7174 | 18265.2042 |  | 7174 | 20377.9102 |  | 7174 | 22734.9894
[13 empty] | Next iteration flow rate |  |  | 65.4065 | Abs Value of | Flow this | 1115.112 | Abs Value of | Flow this | 2757.8047 | Abs Value of | Flow this | 5371.4997 | Abs Value of | Flow this | 8834.1394 | Abs Value of | Flow this | 12390.5606 | Abs Value of | Flow this | 15732.724 | Abs Value of | Flow this | 18447.8562 | Abs Value of | Flow this | 20581.6893 | Abs Value of | Flow this | 22962.3392 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5211 |  |  | 100.0269 |  |  | 97.49 |  |  | 89.0173 |  |  | 69.4026 |  |  | 39.3025 |  |  | 1.8218 |  |  | -35.1852 |  |  | -68.3951 |  |  | -109.732
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48251 |  |  | 0.47027 |  |  | 0.4294 |  |  | 0.33479 |  |  | 0.18959 |  |  | 0.0087881 |  |  | -0.16973 |  |  | -0.32993 |  |  | -0.52933
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5211 |  |  | 50.0269 |  |  | 47.49 |  |  | 39.0173 |  |  | 19.4026 |  |  | -10.6975 |  |  | -48.1782 |  |  | -85.1852 |  |  | -118.3951 |  |  | -159.732
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.50013 |  |  | 0.48713 |  |  | 0.43831 |  |  | 0.27957 |  |  | -0.27218 |  |  | -26.4452 |  |  | 2.4211 |  |  | 1.731 |  |  | 1.4557
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73958 |  |  | 0.74255 |  |  | 0.76517 |  |  | 0.84611 |  |  | 1.1584 |  |  | 17.4488 |  |  | -0.64534 |  |  | 0.027824 |  |  | -0.24106
[13 empty] | C Non choked w/ reducers | 5 |  | 0.28282 |  |  | 4.8517 |  |  | 12.452 |  |  | 27.3303 |  |  | 66.0596 |  |  | #NUM! |  |  | #NUM! |  |  | -135.9665 |  |  | 2431.4904 |  |  | -279.6468
[13 empty] | C Choked w/ reducers | 5 |  | 0.27739 |  |  | 4.755 |  |  | 12.1828 |  |  | 26.3156 |  |  | 56.9375 |  |  | 148.1146 |  |  | 4338.8856 |  |  | 292.2666 |  |  | 173.2193 |  |  | 195.0109
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.28282 |  |  | 4.8517 |  |  | 12.452 |  |  | 27.3303 |  |  | 66.0596 |  |  | #NUM! |  |  | #NUM! |  |  | 292.2666 |  |  | 173.2193 |  |  | 195.0109
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7172 | 65.4065 |  | 0.1483 | 1115.112 |  | 2.452 | 2757.8047 |  | 10.1303 | 5371.4997 |  | 39.4596 | 8834.1394 |  | 7174 | 12390.5606 |  | 7174 | 15732.724 |  | 7174 | 18447.8562 |  | 7174 | 20581.6893 |  | 7174 | 22962.3392
[13 empty] | Next iteration flow rate |  |  | 66.7146 | Abs Value of | Flow this | 1126.2631 | Abs Value of | Flow this | 2785.3828 | Abs Value of | Flow this | 5425.2147 | Abs Value of | Flow this | 8922.4807 | Abs Value of | Flow this | 12514.4662 | Abs Value of | Flow this | 15890.0513 | Abs Value of | Flow this | 18632.3348 | Abs Value of | Flow this | 20787.5062 | Abs Value of | Flow this | 23191.9626 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.521 |  |  | 100.017 |  |  | 97.429 |  |  | 88.786 |  |  | 68.7771 |  |  | 38.072 |  |  | -0.16208 |  |  | -37.9129 |  |  | -71.7903 |  |  | -113.9581
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48246 |  |  | 0.46998 |  |  | 0.42829 |  |  | 0.33177 |  |  | 0.18365 |  |  | -0.00078183 |  |  | -0.18289 |  |  | -0.3463 |  |  | -0.54971
[13 empty] | Delta P at this iteration flow rate |  |  | 50.521 |  |  | 50.017 |  |  | 47.429 |  |  | 38.786 |  |  | 18.7771 |  |  | -11.928 |  |  | -50.1621 |  |  | -87.9129 |  |  | -121.7903 |  |  | -163.9581
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.50008 |  |  | 0.48681 |  |  | 0.43685 |  |  | 0.27301 |  |  | -0.3133 |  |  | 309.4959 |  |  | 2.3188 |  |  | 1.6965 |  |  | 1.4388
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73961 |  |  | 0.74272 |  |  | 0.76596 |  |  | 0.84972 |  |  | 1.1823 |  |  | -191.5055 |  |  | -0.57585 |  |  | 0.047241 |  |  | -0.22665
[13 empty] | C Non choked w/ reducers | 5 |  | 0.28848 |  |  | 4.9008 |  |  | 12.5857 |  |  | 27.6934 |  |  | 67.8409 |  |  | #NUM! |  |  | -7.1391 |  |  | -145.9382 |  |  | 1391.9739 |  |  | -290.95
[13 empty] | C Choked w/ reducers | 5 |  | 0.28294 |  |  | 4.803 |  |  | 12.3123 |  |  | 26.648 |  |  | 58.0299 |  |  | 154.4308 |  |  | 49258.6674 |  |  | 273.9512 |  |  | 166.6774 |  |  | 189.6568
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.28848 |  |  | 4.9008 |  |  | 12.5857 |  |  | 27.6934 |  |  | 67.8409 |  |  | #NUM! |  |  | 49258.6674 |  |  | 273.9512 |  |  | 166.6774 |  |  | 189.6568
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7115 | 66.7146 |  | 0.099221 | 1126.2631 |  | 2.5857 | 2785.3828 |  | 10.4934 | 5425.2147 |  | 41.2409 | 8922.4807 |  | 7174 | 12514.4662 |  | 7174 | 15890.0513 |  | 7174 | 18632.3348 |  | 7174 | 20787.5062 |  | 7174 | 23191.9626
[13 empty] | Next iteration flow rate |  |  | 68.0489 | Abs Value of | Flow this | 1137.5258 | Abs Value of | Flow this | 2813.2366 | Abs Value of | Flow this | 5479.4669 | Abs Value of | Flow this | 9011.7056 | Abs Value of | Flow this | 12639.6108 | Abs Value of | Flow this | 16048.9518 | Abs Value of | Flow this | 18818.6582 | Abs Value of | Flow this | 20995.3812 | Abs Value of | Flow this | 23423.8823 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5209 |  |  | 100.0068 |  |  | 97.3669 |  |  | 88.5501 |  |  | 68.139 |  |  | 36.8167 |  |  | -2.1858 |  |  | -40.6955 |  |  | -75.2538 |  |  | -118.2692
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4849 |  |  | 0.48242 |  |  | 0.46968 |  |  | 0.42715 |  |  | 0.32869 |  |  | 0.1776 |  |  | -0.010544 |  |  | -0.19631 |  |  | -0.36301 |  |  | -0.57051
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5209 |  |  | 50.0068 |  |  | 47.3669 |  |  | 38.5501 |  |  | 18.139 |  |  | -13.1833 |  |  | -52.1858 |  |  | -90.6955 |  |  | -125.2538 |  |  | -168.2692
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.50003 |  |  | 0.48648 |  |  | 0.43535 |  |  | 0.26621 |  |  | -0.35808 |  |  | 23.8745 |  |  | 2.2286 |  |  | 1.6644 |  |  | 1.4228
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73963 |  |  | 0.74289 |  |  | 0.76676 |  |  | 0.85347 |  |  | 1.2083 |  |  | -13.8499 |  |  | -0.51457 |  |  | 0.065243 |  |  | -0.21301
[13 empty] | C Non choked w/ reducers | 5 |  | 0.29424 |  |  | 4.9504 |  |  | 12.721 |  |  | 28.0637 |  |  | 69.7322 |  |  | #NUM! |  |  | -26.6173 |  |  | -156.7511 |  |  | 980.4283 |  |  | -302.9614
[13 empty] | C Choked w/ reducers | 5 |  | 0.2886 |  |  | 4.8516 |  |  | 12.4434 |  |  | 26.9861 |  |  | 59.1591 |  |  | 161.2931 |  |  | 3688.9761 |  |  | 257.7719 |  |  | 160.5963 |  |  | 184.571
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.29424 |  |  | 4.9504 |  |  | 12.721 |  |  | 28.0637 |  |  | 69.7322 |  |  | #NUM! |  |  | 3688.9761 |  |  | 257.7719 |  |  | 160.5963 |  |  | 184.571
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7058 | 68.0489 |  | 0.049635 | 1137.5258 |  | 2.721 | 2813.2366 |  | 10.8637 | 5479.4669 |  | 43.1322 | 9011.7056 |  | 7174 | 12639.6108 |  | 7174 | 16048.9518 |  | 7174 | 18818.6582 |  | 7174 | 20995.3812 |  | 7174 | 23423.8823
[13 empty] | Next iteration flow rate |  |  | 69.4099 | Abs Value of | Flow this | 1148.901 | Abs Value of | Flow this | 2841.369 | Abs Value of | Flow this | 5534.2615 | Abs Value of | Flow this | 9101.8226 | Abs Value of | Flow this | 12766.0069 | Abs Value of | Flow this | 16209.4413 | Abs Value of | Flow this | 19006.8447 | Abs Value of | Flow this | 21205.335 | Abs Value of | Flow this | 23658.1211 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5209 |  |  | 99.9964 |  |  | 97.3034 |  |  | 88.3095 |  |  | 67.4881 |  |  | 35.5362 |  |  | -4.2503 |  |  | -43.534 |  |  | -78.7869 |  |  | -122.6669
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48236 |  |  | 0.46937 |  |  | 0.42599 |  |  | 0.32555 |  |  | 0.17142 |  |  | -0.020503 |  |  | -0.21 |  |  | -0.38005 |  |  | -0.59172
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5209 |  |  | 49.9964 |  |  | 47.3034 |  |  | 38.3095 |  |  | 17.4881 |  |  | -14.4638 |  |  | -54.2503 |  |  | -93.534 |  |  | -128.7869 |  |  | -172.6669
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.49998 |  |  | 0.48614 |  |  | 0.43381 |  |  | 0.25913 |  |  | -0.40702 |  |  | 12.7639 |  |  | 2.1485 |  |  | 1.6346 |  |  | 1.4076
[13 empty] | Expansion factor | 12 |  | 0.73824 |  |  | 0.73966 |  |  | 0.74307 |  |  | 0.76758 |  |  | 0.85736 |  |  | 1.2368 |  |  | -6.9391 |  |  | -0.46013 |  |  | 0.081976 |  |  | -0.20009
[13 empty] | C Non choked w/ reducers | 5 |  | 0.30013 |  |  | 5.0005 |  |  | 12.8579 |  |  | 28.4414 |  |  | 71.7459 |  |  | #NUM! |  |  | -37.7401 |  |  | -168.5639 |  |  | 759.5916 |  |  | -315.7599
[13 empty] | C Choked w/ reducers | 5 |  | 0.29437 |  |  | 4.9006 |  |  | 12.576 |  |  | 27.3303 |  |  | 60.3269 |  |  | 168.7761 |  |  | 1916.143 |  |  | 243.3744 |  |  | 154.9285 |  |  | 179.7335
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.30013 |  |  | 5.0005 |  |  | 12.8579 |  |  | 28.4414 |  |  | 71.7459 |  |  | #NUM! |  |  | 1916.143 |  |  | 243.3744 |  |  | 154.9285 |  |  | 179.7335
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6999 | 69.4099 |  | 0.00046375 | 1148.901 |  | 2.8579 | 2841.369 |  | 11.2414 | 5534.2615 |  | 45.1459 | 9101.8226 |  | 7174 | 12766.0069 |  | 7174 | 16209.4413 |  | 7174 | 19006.8447 |  | 7174 | 21205.335 |  | 7174 | 23658.1211
[13 empty] | Next iteration flow rate |  |  | 70.798 | Abs Value of | Flow this | 1160.39 | Abs Value of | Flow this | 2869.7827 | Abs Value of | Flow this | 5589.6041 | Abs Value of | Flow this | 9192.8408 | Abs Value of | Flow this | 12893.667 | Abs Value of | Flow this | 16371.5357 | Abs Value of | Flow this | 19196.9132 | Abs Value of | Flow this | 21417.3884 | Abs Value of | Flow this | 23894.7023 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5208 |  |  | 99.9859 |  |  | 97.2387 |  |  | 88.064 |  |  | 66.8241 |  |  | 34.23 |  |  | -6.3562 |  |  | -46.4295 |  |  | -82.3911 |  |  | -127.153
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48231 |  |  | 0.46906 |  |  | 0.42481 |  |  | 0.32235 |  |  | 0.16512 |  |  | -0.030661 |  |  | -0.22397 |  |  | -0.39744 |  |  | -0.61336
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5208 |  |  | 49.9859 |  |  | 47.2387 |  |  | 38.064 |  |  | 16.8241 |  |  | -15.77 |  |  | -56.3562 |  |  | -96.4295 |  |  | -132.3911 |  |  | -177.153
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.49993 |  |  | 0.4858 |  |  | 0.43223 |  |  | 0.25177 |  |  | -0.46071 |  |  | 8.8663 |  |  | 2.0769 |  |  | 1.6069 |  |  | 1.3932
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.73969 |  |  | 0.74325 |  |  | 0.76843 |  |  | 0.86142 |  |  | 1.2681 |  |  | -4.5148 |  |  | -0.41145 |  |  | 0.097567 |  |  | -0.18783
[13 empty] | C Non choked w/ reducers | 5 |  | 0.30613 |  |  | 5.0511 |  |  | 12.9966 |  |  | 28.8267 |  |  | 73.8963 |  |  | #NUM! |  |  | -47.0033 |  |  | -181.5698 |  |  | 621.6983 |  |  | -329.436
[13 empty] | C Choked w/ reducers | 5 |  | 0.30026 |  |  | 4.9501 |  |  | 12.7102 |  |  | 27.6805 |  |  | 61.5356 |  |  | 176.9688 |  |  | 1294.1011 |  |  | 230.4785 |  |  | 149.6328 |  |  | 175.1262
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.30613 |  |  | 5.0511 |  |  | 12.9966 |  |  | 28.8267 |  |  | 73.8963 |  |  | #NUM! |  |  | 1294.1011 |  |  | 230.4785 |  |  | 149.6328 |  |  | 175.1262
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6939 | 70.798 |  | 0.051082 | 1160.39 |  | 2.9966 | 2869.7827 |  | 11.6267 | 5589.6041 |  | 47.2963 | 9192.8408 |  | 7174 | 12893.667 |  | 7174 | 16371.5357 |  | 7174 | 19196.9132 |  | 7174 | 21417.3884 |  | 7174 | 23894.7023
[13 empty] | Next iteration flow rate |  |  | 72.214 | Abs Value of | Flow this | 1171.9939 | Abs Value of | Flow this | 2898.4805 | Abs Value of | Flow this | 5645.5002 | Abs Value of | Flow this | 9284.7692 | Abs Value of | Flow this | 13022.6037 | Abs Value of | Flow this | 16535.2511 | Abs Value of | Flow this | 19388.8823 | Abs Value of | Flow this | 21631.5623 | Abs Value of | Flow this | 24133.6493 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5207 |  |  | 99.9751 |  |  | 97.1727 |  |  | 87.8136 |  |  | 66.1467 |  |  | 32.8975 |  |  | -8.5045 |  |  | -49.3833 |  |  | -86.0676 |  |  | -131.7293
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48226 |  |  | 0.46874 |  |  | 0.4236 |  |  | 0.31908 |  |  | 0.15869 |  |  | -0.041024 |  |  | -0.23822 |  |  | -0.41517 |  |  | -0.63544
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5207 |  |  | 49.9751 |  |  | 47.1727 |  |  | 37.8136 |  |  | 16.1467 |  |  | -17.1025 |  |  | -58.5045 |  |  | -99.3833 |  |  | -136.0676 |  |  | -181.7293
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.49988 |  |  | 0.48545 |  |  | 0.43061 |  |  | 0.2441 |  |  | -0.51987 |  |  | 6.8792 |  |  | 2.0125 |  |  | 1.5809 |  |  | 1.3796
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.73972 |  |  | 0.74343 |  |  | 0.7693 |  |  | 0.86563 |  |  | 1.3025 |  |  | -3.2789 |  |  | -0.36768 |  |  | 0.11213 |  |  | -0.17618
[13 empty] | C Non choked w/ reducers | 5 |  | 0.31226 |  |  | 5.1022 |  |  | 13.1369 |  |  | 29.2198 |  |  | 76.2007 |  |  | #NUM! |  |  | -55.4647 |  |  | -196.0074 |  |  | 527.3153 |  |  | -344.0936
[13 empty] | C Choked w/ reducers | 5 |  | 0.30626 |  |  | 5.0001 |  |  | 12.8461 |  |  | 28.0371 |  |  | 62.7874 |  |  | 185.9782 |  |  | 976.8782 |  |  | 218.8599 |  |  | 144.6733 |  |  | 170.7327
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.31226 |  |  | 5.1022 |  |  | 13.1369 |  |  | 29.2198 |  |  | 76.2007 |  |  | #NUM! |  |  | 976.8782 |  |  | 218.8599 |  |  | 144.6733 |  |  | 170.7327
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6877 | 72.214 |  | 0.10223 | 1171.9939 |  | 3.1369 | 2898.4805 |  | 12.0198 | 5645.5002 |  | 49.6007 | 9284.7692 |  | 7174 | 13022.6037 |  | 7174 | 16535.2511 |  | 7174 | 19388.8823 |  | 7174 | 21631.5623 |  | 7174 | 24133.6493
[13 empty] | Next iteration flow rate |  |  | 73.6583 | Abs Value of | Flow this | 1183.7139 | Abs Value of | Flow this | 2927.4653 | Abs Value of | Flow this | 5701.9552 | Abs Value of | Flow this | 9377.6169 | Abs Value of | Flow this | 13152.8297 | Abs Value of | Flow this | 16700.6036 | Abs Value of | Flow this | 19582.7711 | Abs Value of | Flow this | 21847.8779 | Abs Value of | Flow this | 24374.9858 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5206 |  |  | 99.9641 |  |  | 97.1054 |  |  | 87.5581 |  |  | 65.4558 |  |  | 31.5382 |  |  | -10.6959 |  |  | -52.3964 |  |  | -89.8181 |  |  | -136.3975
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48221 |  |  | 0.46842 |  |  | 0.42236 |  |  | 0.31575 |  |  | 0.15213 |  |  | -0.051595 |  |  | -0.25275 |  |  | -0.43327 |  |  | -0.65796
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5206 |  |  | 49.9641 |  |  | 47.1054 |  |  | 37.5581 |  |  | 15.4558 |  |  | -18.4618 |  |  | -60.6959 |  |  | -102.3964 |  |  | -139.8181 |  |  | -186.3975
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.49982 |  |  | 0.4851 |  |  | 0.42895 |  |  | 0.23613 |  |  | -0.58538 |  |  | 5.6747 |  |  | 1.9543 |  |  | 1.5567 |  |  | 1.3666
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.73975 |  |  | 0.74362 |  |  | 0.77019 |  |  | 0.87003 |  |  | 1.3406 |  |  | -2.5296 |  |  | -0.32811 |  |  | 0.12575 |  |  | -0.16511
[13 empty] | C Non choked w/ reducers | 5 |  | 0.3185 |  |  | 5.1539 |  |  | 13.279 |  |  | 29.6211 |  |  | 78.6791 |  |  | #NUM! |  |  | -63.5675 |  |  | -212.1763 |  |  | 458.5912 |  |  | -359.8534
[13 empty] | C Choked w/ reducers | 5 |  | 0.31239 |  |  | 5.0507 |  |  | 12.9835 |  |  | 28.4001 |  |  | 64.0847 |  |  | 195.9336 |  |  | 784.4968 |  |  | 208.3369 |  |  | 140.0186 |  |  | 166.5382
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.3185 |  |  | 5.1539 |  |  | 13.279 |  |  | 29.6211 |  |  | 78.6791 |  |  | #NUM! |  |  | 784.4968 |  |  | 208.3369 |  |  | 140.0186 |  |  | 166.5382
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6815 | 73.6583 |  | 0.1539 | 1183.7139 |  | 3.279 | 2927.4653 |  | 12.4211 | 5701.9552 |  | 52.0791 | 9377.6169 |  | 7174 | 13152.8297 |  | 7174 | 16700.6036 |  | 7174 | 19582.7711 |  | 7174 | 21847.8779 |  | 7174 | 24374.9858
[13 empty] | Next iteration flow rate |  |  | 75.1315 | Abs Value of | Flow this | 1195.551 | Abs Value of | Flow this | 2956.74 | Abs Value of | Flow this | 5758.9747 | Abs Value of | Flow this | 9471.3931 | Abs Value of | Flow this | 13284.358 | Abs Value of | Flow this | 16867.6096 | Abs Value of | Flow this | 19778.5989 | Abs Value of | Flow this | 22066.3567 | Abs Value of | Flow this | 24618.7357 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5205 |  |  | 99.9528 |  |  | 97.0367 |  |  | 87.2975 |  |  | 64.7509 |  |  | 30.1516 |  |  | -12.9314 |  |  | -55.47 |  |  | -93.644 |  |  | -141.1596
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48215 |  |  | 0.46809 |  |  | 0.42111 |  |  | 0.31235 |  |  | 0.14545 |  |  | -0.062379 |  |  | -0.26758 |  |  | -0.45172 |  |  | -0.68093
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5205 |  |  | 49.9528 |  |  | 47.0367 |  |  | 37.2975 |  |  | 14.7509 |  |  | -19.8484 |  |  | -62.9314 |  |  | -105.47 |  |  | -143.644 |  |  | -191.1596
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.49976 |  |  | 0.48473 |  |  | 0.42725 |  |  | 0.22781 |  |  | -0.65829 |  |  | 4.8665 |  |  | 1.9014 |  |  | 1.5339 |  |  | 1.3542
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.73977 |  |  | 0.74382 |  |  | 0.7711 |  |  | 0.8746 |  |  | 1.383 |  |  | -2.027 |  |  | -0.29217 |  |  | 0.13852 |  |  | -0.15457
[13 empty] | C Non choked w/ reducers | 5 |  | 0.32487 |  |  | 5.2061 |  |  | 13.4229 |  |  | 30.0308 |  |  | 81.3558 |  |  | #NUM! |  |  | -71.5643 |  |  | -230.4592 |  |  | 406.2688 |  |  | -376.8557
[13 empty] | C Choked w/ reducers | 5 |  | 0.31864 |  |  | 5.1018 |  |  | 13.1226 |  |  | 28.7697 |  |  | 65.4301 |  |  | 206.9935 |  |  | 655.3673 |  |  | 198.7606 |  |  | 135.6411 |  |  | 162.5291
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.32487 |  |  | 5.2061 |  |  | 13.4229 |  |  | 30.0308 |  |  | 81.3558 |  |  | #NUM! |  |  | 655.3673 |  |  | 198.7606 |  |  | 135.6411 |  |  | 162.5291
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6751 | 75.1315 |  | 0.20611 | 1195.551 |  | 3.4229 | 2956.74 |  | 12.8308 | 5758.9747 |  | 54.7558 | 9471.3931 |  | 7174 | 13284.358 |  | 7174 | 16867.6096 |  | 7174 | 19778.5989 |  | 7174 | 22066.3567 |  | 7174 | 24618.7357
[13 empty] | Next iteration flow rate |  |  | 76.6341 | Abs Value of | Flow this | 1207.5065 | Abs Value of | Flow this | 2986.3074 | Abs Value of | Flow this | 5816.5645 | Abs Value of | Flow this | 9566.107 | Abs Value of | Flow this | 13417.2016 | Abs Value of | Flow this | 17036.2857 | Abs Value of | Flow this | 19976.3848 | Abs Value of | Flow this | 22287.0202 | Abs Value of | Flow this | 24864.923 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5204 |  |  | 99.9414 |  |  | 96.9666 |  |  | 87.0317 |  |  | 64.0319 |  |  | 28.7372 |  |  | -15.2119 |  |  | -58.6055 |  |  | -97.5467 |  |  | -146.0175
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.4821 |  |  | 0.46775 |  |  | 0.41983 |  |  | 0.30888 |  |  | 0.13862 |  |  | -0.073379 |  |  | -0.2827 |  |  | -0.47055 |  |  | -0.70436
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5204 |  |  | 49.9414 |  |  | 46.9666 |  |  | 37.0317 |  |  | 14.0319 |  |  | -21.2628 |  |  | -65.2119 |  |  | -108.6055 |  |  | -147.5467 |  |  | -196.0175
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.49971 |  |  | 0.48436 |  |  | 0.4255 |  |  | 0.21914 |  |  | -0.73991 |  |  | 4.2869 |  |  | 1.8532 |  |  | 1.5126 |  |  | 1.3424
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.7398 |  |  | 0.74401 |  |  | 0.77204 |  |  | 0.87938 |  |  | 1.4305 |  |  | -1.6664 |  |  | -0.2594 |  |  | 0.15052 |  |  | -0.14452
[13 empty] | C Non choked w/ reducers | 5 |  | 0.33137 |  |  | 5.2589 |  |  | 13.5685 |  |  | 30.4492 |  |  | 84.2602 |  |  | #NUM! |  |  | -79.6304 |  |  | -251.3537 |  |  | 365.0682 |  |  | -395.2653
[13 empty] | C Choked w/ reducers | 5 |  | 0.32501 |  |  | 5.1534 |  |  | 13.2634 |  |  | 29.1461 |  |  | 66.8265 |  |  | 219.3537 |  |  | 562.6916 |  |  | 190.0079 |  |  | 131.5163 |  |  | 158.6932
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.33137 |  |  | 5.2589 |  |  | 13.5685 |  |  | 30.4492 |  |  | 84.2602 |  |  | #NUM! |  |  | 562.6916 |  |  | 190.0079 |  |  | 131.5163 |  |  | 158.6932
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6686 | 76.6341 |  | 0.25886 | 1207.5065 |  | 3.5685 | 2986.3074 |  | 13.2492 | 5816.5645 |  | 57.6602 | 9566.107 |  | 7174 | 13417.2016 |  | 7174 | 17036.2857 |  | 7174 | 19976.3848 |  | 7174 | 22287.0202 |  | 7174 | 24864.923
[13 empty] | Next iteration flow rate |  |  | 78.1668 | Abs Value of | Flow this | 1219.5816 | Abs Value of | Flow this | 3016.1704 | Abs Value of | Flow this | 5874.7301 | Abs Value of | Flow this | 9661.7681 | Abs Value of | Flow this | 13551.3736 | Abs Value of | Flow this | 17206.6486 | Abs Value of | Flow this | 20176.1487 | Abs Value of | Flow this | 22509.8904 | Abs Value of | Flow this | 25113.5723 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5204 |  |  | 99.9297 |  |  | 96.8951 |  |  | 86.7605 |  |  | 63.2985 |  |  | 27.2943 |  |  | -17.5381 |  |  | -61.804 |  |  | -101.5279 |  |  | -150.9729
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48204 |  |  | 0.4674 |  |  | 0.41852 |  |  | 0.30534 |  |  | 0.13166 |  |  | -0.084601 |  |  | -0.29813 |  |  | -0.48975 |  |  | -0.72827
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5204 |  |  | 49.9297 |  |  | 46.8951 |  |  | 36.7605 |  |  | 13.2985 |  |  | -22.7057 |  |  | -67.5381 |  |  | -111.804 |  |  | -151.5279 |  |  | -200.9729
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.49965 |  |  | 0.48398 |  |  | 0.4237 |  |  | 0.21009 |  |  | -0.83189 |  |  | 3.8509 |  |  | 1.809 |  |  | 1.4925 |  |  | 1.3312
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.73983 |  |  | 0.74421 |  |  | 0.773 |  |  | 0.88436 |  |  | 1.484 |  |  | -1.3953 |  |  | -0.22939 |  |  | 0.16181 |  |  | -0.13494
[13 empty] | C Non choked w/ reducers | 5 |  | 0.338 |  |  | 5.3122 |  |  | 13.716 |  |  | 30.8767 |  |  | 87.428 |  |  | #NUM! |  |  | -87.9066 |  |  | -275.5198 |  |  | 331.7579 |  |  | -415.2766
[13 empty] | C Choked w/ reducers | 5 |  | 0.33151 |  |  | 5.2055 |  |  | 13.406 |  |  | 29.5296 |  |  | 68.2769 |  |  | 233.2591 |  |  | 492.9365 |  |  | 181.9764 |  |  | 127.6228 |  |  | 155.0192
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.338 |  |  | 5.3122 |  |  | 13.716 |  |  | 30.8767 |  |  | 87.428 |  |  | #NUM! |  |  | 492.9365 |  |  | 181.9764 |  |  | 127.6228 |  |  | 155.0192
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.662 | 78.1668 |  | 0.31216 | 1219.5816 |  | 3.716 | 3016.1704 |  | 13.6767 | 5874.7301 |  | 60.828 | 9661.7681 |  | 7174 | 13551.3736 |  | 7174 | 17206.6486 |  | 7174 | 20176.1487 |  | 7174 | 22509.8904 |  | 7174 | 25113.5723
[13 empty] | Next iteration flow rate |  |  | 79.7301 | Abs Value of | Flow this | 1231.7774 | Abs Value of | Flow this | 3046.3321 | Abs Value of | Flow this | 5933.4774 | Abs Value of | Flow this | 9758.3858 | Abs Value of | Flow this | 13686.8873 | Abs Value of | Flow this | 17378.7151 | Abs Value of | Flow this | 20377.9102 | Abs Value of | Flow this | 22734.9894 | Abs Value of | Flow this | 25364.708 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5203 |  |  | 99.9178 |  |  | 96.8222 |  |  | 86.4839 |  |  | 62.5503 |  |  | 25.8224 |  |  | -19.9112 |  |  | -65.0667 |  |  | -105.5891 |  |  | -156.028
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48199 |  |  | 0.46705 |  |  | 0.41718 |  |  | 0.30173 |  |  | 0.12456 |  |  | -0.096048 |  |  | -0.31387 |  |  | -0.50934 |  |  | -0.75265
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5203 |  |  | 49.9178 |  |  | 46.8222 |  |  | 36.4839 |  |  | 12.5503 |  |  | -24.1776 |  |  | -69.9112 |  |  | -115.0667 |  |  | -155.5891 |  |  | -206.028
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.49959 |  |  | 0.48359 |  |  | 0.42186 |  |  | 0.20064 |  |  | -0.9363 |  |  | 3.5112 |  |  | 1.7684 |  |  | 1.4735 |  |  | 1.3205
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.73987 |  |  | 0.74442 |  |  | 0.77399 |  |  | 0.88956 |  |  | 1.5448 |  |  | -1.1839 |  |  | -0.20182 |  |  | 0.17245 |  |  | -0.12579
[13 empty] | C Non choked w/ reducers | 5 |  | 0.34476 |  |  | 5.366 |  |  | 13.8653 |  |  | 31.3134 |  |  | 90.9038 |  |  | #NUM! |  |  | -96.5206 |  |  | -303.8541 |  |  | 304.2492 |  |  | -437.1209
[13 empty] | C Choked w/ reducers | 5 |  | 0.33814 |  |  | 5.2582 |  |  | 13.5502 |  |  | 29.9203 |  |  | 69.7845 |  |  | 249.0206 |  |  | 438.5299 |  |  | 174.5797 |  |  | 123.9413 |  |  | 151.4968
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.34476 |  |  | 5.366 |  |  | 13.8653 |  |  | 31.3134 |  |  | 90.9038 |  |  | #NUM! |  |  | 438.5299 |  |  | 174.5797 |  |  | 123.9413 |  |  | 151.4968
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6552 | 79.7301 |  | 0.36602 | 1231.7774 |  | 3.8653 | 3046.3321 |  | 14.1134 | 5933.4774 |  | 64.3038 | 9758.3858 |  | 7174 | 13686.8873 |  | 7174 | 17378.7151 |  | 7174 | 20377.9102 |  | 7174 | 22734.9894 |  | 7174 | 25364.708
[13 empty] | Next iteration flow rate |  |  | 81.3247 | Abs Value of | Flow this | 1244.0952 | Abs Value of | Flow this | 3076.7955 | Abs Value of | Flow this | 5992.8122 | Abs Value of | Flow this | 9855.9696 | Abs Value of | Flow this | 13823.7562 | Abs Value of | Flow this | 17552.5022 | Abs Value of | Flow this | 20581.6893 | Abs Value of | Flow this | 22962.3392 | Abs Value of | Flow this | 25618.3551 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5201 |  |  | 99.9056 |  |  | 96.7478 |  |  | 86.2017 |  |  | 61.787 |  |  | 24.3209 |  |  | -22.3319 |  |  | -68.3951 |  |  | -109.732 |  |  | -161.1847
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48193 |  |  | 0.46669 |  |  | 0.41582 |  |  | 0.29805 |  |  | 0.11732 |  |  | -0.10773 |  |  | -0.32993 |  |  | -0.52933 |  |  | -0.77753
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5201 |  |  | 49.9056 |  |  | 46.7478 |  |  | 36.2017 |  |  | 11.787 |  |  | -25.6791 |  |  | -72.3319 |  |  | -118.3951 |  |  | -159.732 |  |  | -211.1847
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.49953 |  |  | 0.48319 |  |  | 0.41997 |  |  | 0.19077 |  |  | -1.0558 |  |  | 3.239 |  |  | 1.731 |  |  | 1.4557 |  |  | 1.3102
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.7399 |  |  | 0.74463 |  |  | 0.775 |  |  | 0.89499 |  |  | 1.6143 |  |  | -1.0146 |  |  | -0.17641 |  |  | 0.18249 |  |  | -0.11705
[13 empty] | C Non choked w/ reducers | 5 |  | 0.35165 |  |  | 5.4204 |  |  | 14.0165 |  |  | 31.7599 |  |  | 94.7432 |  |  | #NUM! |  |  | -105.5985 |  |  | -337.6059 |  |  | 281.1319 |  |  | -461.0755
[13 empty] | C Choked w/ reducers | 5 |  | 0.3449 |  |  | 5.3115 |  |  | 13.6962 |  |  | 30.3184 |  |  | 71.353 |  |  | 267.0381 |  |  | 394.9042 |  |  | 167.7449 |  |  | 120.4546 |  |  | 148.1166
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.35165 |  |  | 5.4204 |  |  | 14.0165 |  |  | 31.7599 |  |  | 94.7432 |  |  | #NUM! |  |  | 394.9042 |  |  | 167.7449 |  |  | 120.4546 |  |  | 148.1166
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6483 | 81.3247 |  | 0.42044 | 1244.0952 |  | 4.0165 | 3076.7955 |  | 14.5599 | 5992.8122 |  | 68.1432 | 9855.9696 |  | 7174 | 13823.7562 |  | 7174 | 17552.5022 |  | 7174 | 20581.6893 |  | 7174 | 22962.3392 |  | 7174 | 25618.3551
[13 empty] | Next iteration flow rate |  |  | 82.9512 | Abs Value of | Flow this | 1256.5361 | Abs Value of | Flow this | 3107.5634 | Abs Value of | Flow this | 6052.7403 | Abs Value of | Flow this | 9954.5293 | Abs Value of | Flow this | 13961.9938 | Abs Value of | Flow this | 17728.0272 | Abs Value of | Flow this | 20787.5062 | Abs Value of | Flow this | 23191.9626 | Abs Value of | Flow this | 25874.5386 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.52 |  |  | 99.8932 |  |  | 96.672 |  |  | 85.9139 |  |  | 61.0084 |  |  | 22.7892 |  |  | -24.8013 |  |  | -71.7903 |  |  | -113.9581 |  |  | -166.445
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48187 |  |  | 0.46633 |  |  | 0.41443 |  |  | 0.29429 |  |  | 0.10993 |  |  | -0.11964 |  |  | -0.3463 |  |  | -0.54971 |  |  | -0.8029
[13 empty] | Delta P at this iteration flow rate |  |  | 50.52 |  |  | 49.8932 |  |  | 46.672 |  |  | 35.9139 |  |  | 11.0084 |  |  | -27.2108 |  |  | -74.8013 |  |  | -121.7903 |  |  | -163.9581 |  |  | -216.445
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.49947 |  |  | 0.48279 |  |  | 0.41802 |  |  | 0.18044 |  |  | -1.194 |  |  | 3.016 |  |  | 1.6965 |  |  | 1.4388 |  |  | 1.3004
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.73993 |  |  | 0.74484 |  |  | 0.77604 |  |  | 0.90068 |  |  | 1.6947 |  |  | -0.87596 |  |  | -0.15291 |  |  | 0.19198 |  |  | -0.10869
[13 empty] | C Non choked w/ reducers | 5 |  | 0.35869 |  |  | 5.4754 |  |  | 14.1697 |  |  | 32.2164 |  |  | 99.0177 |  |  | #NUM! |  |  | -115.2747 |  |  | -378.5716 |  |  | 261.4192 |  |  | -487.4762
[13 empty] | C Choked w/ reducers | 5 |  | 0.3518 |  |  | 5.3652 |  |  | 13.8441 |  |  | 30.7242 |  |  | 72.9863 |  |  | 287.8355 |  |  | 359.1408 |  |  | 161.4097 |  |  | 117.1474 |  |  | 144.8698
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.35869 |  |  | 5.4754 |  |  | 14.1697 |  |  | 32.2164 |  |  | 99.0177 |  |  | #NUM! |  |  | 359.1408 |  |  | 161.4097 |  |  | 117.1474 |  |  | 144.8698
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6413 | 82.9512 |  | 0.47543 | 1256.5361 |  | 4.1697 | 3107.5634 |  | 15.0164 | 6052.7403 |  | 72.4177 | 9954.5293 |  | 7174 | 13961.9938 |  | 7174 | 17728.0272 |  | 7174 | 20787.5062 |  | 7174 | 23191.9626 |  | 7174 | 25874.5386
[13 empty] | Next iteration flow rate |  |  | 84.6102 | Abs Value of | Flow this | 1269.1015 | Abs Value of | Flow this | 3138.639 | Abs Value of | Flow this | 6113.2677 | Abs Value of | Flow this | 10054.0746 | Abs Value of | Flow this | 14101.6137 | Abs Value of | Flow this | 17905.3075 | Abs Value of | Flow this | 20995.3812 | Abs Value of | Flow this | 23423.8823 | Abs Value of | Flow this | 26133.284 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5199 |  |  | 99.8805 |  |  | 96.5946 |  |  | 85.6202 |  |  | 60.2142 |  |  | 21.2268 |  |  | -27.3203 |  |  | -75.2538 |  |  | -118.2692 |  |  | -171.811
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48181 |  |  | 0.46595 |  |  | 0.41302 |  |  | 0.29046 |  |  | 0.10239 |  |  | -0.13179 |  |  | -0.36301 |  |  | -0.57051 |  |  | -0.82879
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5199 |  |  | 49.8805 |  |  | 46.5946 |  |  | 35.6202 |  |  | 10.2142 |  |  | -28.7732 |  |  | -77.3203 |  |  | -125.2538 |  |  | -168.2692 |  |  | -221.811
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.4994 |  |  | 0.48237 |  |  | 0.41603 |  |  | 0.16963 |  |  | -1.3555 |  |  | 2.8301 |  |  | 1.6644 |  |  | 1.4228 |  |  | 1.291
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.73996 |  |  | 0.74506 |  |  | 0.77711 |  |  | 0.90663 |  |  | 1.7887 |  |  | -0.76034 |  |  | -0.13113 |  |  | 0.20096 |  |  | -0.10069
[13 empty] | C Non choked w/ reducers | 5 |  | 0.36586 |  |  | 5.531 |  |  | 14.3248 |  |  | 32.6834 |  |  | 103.8199 |  |  | #NUM! |  |  | -125.6995 |  |  | -429.432 |  |  | 244.4002 |  |  | -516.7329
[13 empty] | C Choked w/ reducers | 5 |  | 0.35884 |  |  | 5.4196 |  |  | 13.9937 |  |  | 31.1379 |  |  | 74.6884 |  |  | 312.1125 |  |  | 329.2871 |  |  | 155.5207 |  |  | 114.006 |  |  | 141.7487
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.36586 |  |  | 5.531 |  |  | 14.3248 |  |  | 32.6834 |  |  | 103.8199 |  |  | #NUM! |  |  | 329.2871 |  |  | 155.5207 |  |  | 114.006 |  |  | 141.7487
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6341 | 84.6102 |  | 0.53098 | 1269.1015 |  | 4.3248 | 3138.639 |  | 15.4834 | 6113.2677 |  | 77.2199 | 10054.0746 |  | 7174 | 14101.6137 |  | 7174 | 17905.3075 |  | 7174 | 20995.3812 |  | 7174 | 23423.8823 |  | 7174 | 26133.284
[13 empty] | Next iteration flow rate |  |  | 86.3024 | Abs Value of | Flow this | 1281.7925 | Abs Value of | Flow this | 3170.0254 | Abs Value of | Flow this | 6174.4004 | Abs Value of | Flow this | 10154.6154 | Abs Value of | Flow this | 14242.6298 | Abs Value of | Flow this | 18084.3606 | Abs Value of | Flow this | 21205.335 | Abs Value of | Flow this | 23658.1211 | Abs Value of | Flow this | 26394.6168 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5198 |  |  | 99.8676 |  |  | 96.5156 |  |  | 85.3207 |  |  | 59.404 |  |  | 19.6329 |  |  | -29.8899 |  |  | -78.7869 |  |  | -122.6669 |  |  | -177.2849
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48174 |  |  | 0.46557 |  |  | 0.41157 |  |  | 0.28655 |  |  | 0.094706 |  |  | -0.14418 |  |  | -0.38005 |  |  | -0.59172 |  |  | -0.85519
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5198 |  |  | 49.8676 |  |  | 46.5156 |  |  | 35.3207 |  |  | 9.404 |  |  | -30.3671 |  |  | -79.8899 |  |  | -128.7869 |  |  | -172.6669 |  |  | -227.2849
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.49934 |  |  | 0.48195 |  |  | 0.41398 |  |  | 0.15831 |  |  | -1.5467 |  |  | 2.6728 |  |  | 1.6346 |  |  | 1.4076 |  |  | 1.282
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74 |  |  | 0.74529 |  |  | 0.77821 |  |  | 0.91286 |  |  | 1.9 |  |  | -0.66248 |  |  | -0.11088 |  |  | 0.20947 |  |  | -0.093029
[13 empty] | C Non choked w/ reducers | 5 |  | 0.37318 |  |  | 5.5871 |  |  | 14.4819 |  |  | 33.1612 |  |  | 109.2732 |  |  | #NUM! |  |  | -137.0482 |  |  | -494.3741 |  |  | 229.5494 |  |  | -549.3521
[13 empty] | C Choked w/ reducers | 5 |  | 0.36601 |  |  | 5.4745 |  |  | 14.1452 |  |  | 31.5597 |  |  | 76.4642 |  |  | 340.825 |  |  | 303.988 |  |  | 150.0321 |  |  | 111.018 |  |  | 138.7457
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.37318 |  |  | 5.5871 |  |  | 14.4819 |  |  | 33.1612 |  |  | 109.2732 |  |  | #NUM! |  |  | 303.988 |  |  | 150.0321 |  |  | 111.018 |  |  | 138.7457
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6268 | 86.3024 |  | 0.58712 | 1281.7925 |  | 4.4819 | 3170.0254 |  | 15.9612 | 6174.4004 |  | 82.6732 | 10154.6154 |  | 7174 | 14242.6298 |  | 7174 | 18084.3606 |  | 7174 | 21205.335 |  | 7174 | 23658.1211 |  | 7174 | 26394.6168
[13 empty] | Next iteration flow rate |  |  | 88.0285 | Abs Value of | Flow this | 1294.6104 | Abs Value of | Flow this | 3201.7257 | Abs Value of | Flow this | 6236.1444 | Abs Value of | Flow this | 10256.1615 | Abs Value of | Flow this | 14385.0561 | Abs Value of | Flow this | 18265.2042 | Abs Value of | Flow this | 21417.3884 | Abs Value of | Flow this | 23894.7023 | Abs Value of | Flow this | 26658.563 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5197 |  |  | 99.8545 |  |  | 96.4351 |  |  | 85.0151 |  |  | 58.5775 |  |  | 18.0071 |  |  | -32.5112 |  |  | -82.3911 |  |  | -127.153 |  |  | -182.8689
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48168 |  |  | 0.46519 |  |  | 0.4101 |  |  | 0.28257 |  |  | 0.086863 |  |  | -0.15683 |  |  | -0.39744 |  |  | -0.61336 |  |  | -0.88213
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5197 |  |  | 49.8545 |  |  | 46.4351 |  |  | 35.0151 |  |  | 8.5775 |  |  | -31.9929 |  |  | -82.5112 |  |  | -132.3911 |  |  | -177.153 |  |  | -232.8689
[13 empty] | Press drop ratio this iteration |  |  | 0.50259 |  |  | 0.49927 |  |  | 0.48152 |  |  | 0.41187 |  |  | 0.14643 |  |  | -1.7767 |  |  | 2.5379 |  |  | 1.6069 |  |  | 1.3932 |  |  | 1.2734
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74003 |  |  | 0.74551 |  |  | 0.77934 |  |  | 0.9194 |  |  | 2.0338 |  |  | -0.57859 |  |  | -0.092015 |  |  | 0.21755 |  |  | -0.085687
[13 empty] | C Non choked w/ reducers | 5 |  | 0.38064 |  |  | 5.6439 |  |  | 14.641 |  |  | 33.6502 |  |  | 115.5458 |  |  | #NUM! |  |  | -149.5316 |  |  | -580.3231 |  |  | 216.4701 |  |  | -585.9663
[13 empty] | C Choked w/ reducers | 5 |  | 0.37334 |  |  | 5.5299 |  |  | 14.2986 |  |  | 31.9898 |  |  | 78.3185 |  |  | 375.3146 |  |  | 282.273 |  |  | 144.9037 |  |  | 108.1721 |  |  | 135.8542
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.38064 |  |  | 5.6439 |  |  | 14.641 |  |  | 33.6502 |  |  | 115.5458 |  |  | #NUM! |  |  | 282.273 |  |  | 144.9037 |  |  | 108.1721 |  |  | 135.8542
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6194 | 88.0285 |  | 0.64385 | 1294.6104 |  | 4.641 | 3201.7257 |  | 16.4502 | 6236.1444 |  | 88.9458 | 10256.1615 |  | 7174 | 14385.0561 |  | 7174 | 18265.2042 |  | 7174 | 21417.3884 |  | 7174 | 23894.7023 |  | 7174 | 26658.563
[13 empty] | Next iteration flow rate |  |  | 89.789 | Abs Value of | Flow this | 1307.5565 | Abs Value of | Flow this | 3233.7429 | Abs Value of | Flow this | 6298.5059 | Abs Value of | Flow this | 10358.7232 | Abs Value of | Flow this | 14528.9067 | Abs Value of | Flow this | 18447.8562 | Abs Value of | Flow this | 21631.5623 | Abs Value of | Flow this | 24133.6493 | Abs Value of | Flow this | 26925.1486 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5196 |  |  | 99.841 |  |  | 96.3529 |  |  | 84.7034 |  |  | 57.7344 |  |  | 16.3485 |  |  | -35.1852 |  |  | -86.0676 |  |  | -131.7293 |  |  | -188.565
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48162 |  |  | 0.46479 |  |  | 0.40859 |  |  | 0.2785 |  |  | 0.078862 |  |  | -0.16973 |  |  | -0.41517 |  |  | -0.63544 |  |  | -0.9096
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5196 |  |  | 49.841 |  |  | 46.3529 |  |  | 34.7034 |  |  | 7.7344 |  |  | -33.6515 |  |  | -85.1852 |  |  | -136.0676 |  |  | -181.7293 |  |  | -238.565
[13 empty] | Press drop ratio this iteration |  |  | 0.50258 |  |  | 0.4992 |  |  | 0.48107 |  |  | 0.40971 |  |  | 0.13397 |  |  | -2.0584 |  |  | 2.4211 |  |  | 1.5809 |  |  | 1.3796 |  |  | 1.2652
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74007 |  |  | 0.74575 |  |  | 0.7805 |  |  | 0.92626 |  |  | 2.1977 |  |  | -0.50589 |  |  | -0.074398 |  |  | 0.22522 |  |  | -0.078645
[13 empty] | C Non choked w/ reducers | 5 |  | 0.38826 |  |  | 5.7012 |  |  | 14.8022 |  |  | 34.1509 |  |  | 122.8746 |  |  | #NUM! |  |  | -163.4102 |  |  | -699.621 |  |  | 204.8572 |  |  | -627.3771
[13 empty] | C Choked w/ reducers | 5 |  | 0.3808 |  |  | 5.586 |  |  | 14.4539 |  |  | 32.4286 |  |  | 80.2568 |  |  | 417.5245 |  |  | 263.4292 |  |  | 140.101 |  |  | 105.4584 |  |  | 133.0678
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.38826 |  |  | 5.7012 |  |  | 14.8022 |  |  | 34.1509 |  |  | 122.8746 |  |  | #NUM! |  |  | 263.4292 |  |  | 140.101 |  |  | 105.4584 |  |  | 133.0678
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6117 | 89.789 |  | 0.70117 | 1307.5565 |  | 4.8022 | 3233.7429 |  | 16.9509 | 6298.5059 |  | 96.2746 | 10358.7232 |  | 7174 | 14528.9067 |  | 7174 | 18447.8562 |  | 7174 | 21631.5623 |  | 7174 | 24133.6493 |  | 7174 | 26925.1486
[13 empty] | Next iteration flow rate |  |  | 91.5848 | Abs Value of | Flow this | 1320.6321 | Abs Value of | Flow this | 3266.0804 | Abs Value of | Flow this | 6361.4909 | Abs Value of | Flow this | 10462.3104 | Abs Value of | Flow this | 14674.1958 | Abs Value of | Flow this | 18632.3348 | Abs Value of | Flow this | 21847.8779 | Abs Value of | Flow this | 24374.9858 | Abs Value of | Flow this | 27194.4001 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5194 |  |  | 99.8273 |  |  | 96.2691 |  |  | 84.3855 |  |  | 56.8743 |  |  | 14.6566 |  |  | -37.9129 |  |  | -89.8181 |  |  | -136.3975 |  |  | -194.3757
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48155 |  |  | 0.46438 |  |  | 0.40706 |  |  | 0.27435 |  |  | 0.070701 |  |  | -0.18289 |  |  | -0.43327 |  |  | -0.65796 |  |  | -0.93763
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5194 |  |  | 49.8273 |  |  | 46.2691 |  |  | 34.3855 |  |  | 6.8743 |  |  | -35.3434 |  |  | -87.9129 |  |  | -139.8181 |  |  | -186.3975 |  |  | -244.3757
[13 empty] | Press drop ratio this iteration |  |  | 0.50258 |  |  | 0.49914 |  |  | 0.48062 |  |  | 0.40748 |  |  | 0.12087 |  |  | -2.4114 |  |  | 2.3188 |  |  | 1.5567 |  |  | 1.3666 |  |  | 1.2572
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.7401 |  |  | 0.74599 |  |  | 0.78169 |  |  | 0.93347 |  |  | 2.4031 |  |  | -0.44229 |  |  | -0.057912 |  |  | 0.23252 |  |  | -0.071887
[13 empty] | C Non choked w/ reducers | 5 |  | 0.39602 |  |  | 5.7591 |  |  | 14.9655 |  |  | 34.6639 |  |  | 131.6052 |  |  | #NUM! |  |  | -179.0133 |  |  | -876.6108 |  |  | 194.4721 |  |  | -674.6143
[13 empty] | C Choked w/ reducers | 5 |  | 0.38842 |  |  | 5.6426 |  |  | 14.6111 |  |  | 32.8763 |  |  | 82.2851 |  |  | 470.3792 |  |  | 246.921 |  |  | 135.5934 |  |  | 102.8675 |  |  | 130.3808
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.39602 |  |  | 5.7591 |  |  | 14.9655 |  |  | 34.6639 |  |  | 131.6052 |  |  | #NUM! |  |  | 246.921 |  |  | 135.5934 |  |  | 102.8675 |  |  | 130.3808
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.604 | 91.5848 |  | 0.75909 | 1320.6321 |  | 4.9655 | 3266.0804 |  | 17.4639 | 6361.4909 |  | 105.0052 | 10462.3104 |  | 7174 | 14674.1958 |  | 7174 | 18632.3348 |  | 7174 | 21847.8779 |  | 7174 | 24374.9858 |  | 7174 | 27194.4001
[13 empty] | Next iteration flow rate |  |  | 93.4165 | Abs Value of | Flow this | 1333.8384 | Abs Value of | Flow this | 3298.7412 | Abs Value of | Flow this | 6425.1058 | Abs Value of | Flow this | 10566.9335 | Abs Value of | Flow this | 14820.9377 | Abs Value of | Flow this | 18818.6582 | Abs Value of | Flow this | 22066.3567 | Abs Value of | Flow this | 24618.7357 | Abs Value of | Flow this | 27466.3441 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5193 |  |  | 99.8133 |  |  | 96.1836 |  |  | 84.0611 |  |  | 55.997 |  |  | 12.9307 |  |  | -40.6955 |  |  | -93.644 |  |  | -141.1596 |  |  | -200.3032
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48148 |  |  | 0.46397 |  |  | 0.4055 |  |  | 0.27012 |  |  | 0.062375 |  |  | -0.19631 |  |  | -0.45172 |  |  | -0.68093 |  |  | -0.96623
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5193 |  |  | 49.8133 |  |  | 46.1836 |  |  | 34.0611 |  |  | 5.997 |  |  | -37.0693 |  |  | -90.6955 |  |  | -143.644 |  |  | -191.1596 |  |  | -250.3032
[13 empty] | Press drop ratio this iteration |  |  | 0.50258 |  |  | 0.49906 |  |  | 0.48016 |  |  | 0.40519 |  |  | 0.1071 |  |  | -2.8668 |  |  | 2.2286 |  |  | 1.5339 |  |  | 1.3542 |  |  | 1.2496
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74014 |  |  | 0.74623 |  |  | 0.78292 |  |  | 0.94105 |  |  | 2.668 |  |  | -0.38621 |  |  | -0.042456 |  |  | 0.23946 |  |  | -0.065397
[13 empty] | C Non choked w/ reducers | 5 |  | 0.40394 |  |  | 5.8176 |  |  | 15.1309 |  |  | 35.1895 |  |  | 142.2674 |  |  | #NUM! |  |  | -196.7672 |  |  | -1166.9151 |  |  | 185.1255 |  |  | -729.0246
[13 empty] | C Choked w/ reducers | 5 |  | 0.39619 |  |  | 5.6999 |  |  | 14.7704 |  |  | 33.3332 |  |  | 84.4101 |  |  | 538.4942 |  |  | 232.3381 |  |  | 131.3542 |  |  | 100.3912 |  |  | 127.7877
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.40394 |  |  | 5.8176 |  |  | 15.1309 |  |  | 35.1895 |  |  | 142.2674 |  |  | #NUM! |  |  | 232.3381 |  |  | 131.3542 |  |  | 100.3912 |  |  | 127.7877
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5961 | 93.4165 |  | 0.81762 | 1333.8384 |  | 5.1309 | 3298.7412 |  | 17.9895 | 6425.1058 |  | 115.6674 | 10566.9335 |  | 7174 | 14820.9377 |  | 7174 | 18818.6582 |  | 7174 | 22066.3567 |  | 7174 | 24618.7357 |  | 7174 | 27466.3441
[13 empty] | Next iteration flow rate |  |  | 95.2849 | Abs Value of | Flow this | 1347.1768 | Abs Value of | Flow this | 3331.7286 | Abs Value of | Flow this | 6489.3569 | Abs Value of | Flow this | 10672.6028 | Abs Value of | Flow this | 14969.1471 | Abs Value of | Flow this | 19006.8447 | Abs Value of | Flow this | 22287.0202 | Abs Value of | Flow this | 24864.923 | Abs Value of | Flow this | 27741.0076 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5192 |  |  | 99.7991 |  |  | 96.0964 |  |  | 83.7302 |  |  | 55.102 |  |  | 11.1701 |  |  | -43.534 |  |  | -97.5467 |  |  | -146.0175 |  |  | -206.3498
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48141 |  |  | 0.46355 |  |  | 0.4039 |  |  | 0.2658 |  |  | 0.053882 |  |  | -0.21 |  |  | -0.47055 |  |  | -0.70436 |  |  | -0.99539
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5192 |  |  | 49.7991 |  |  | 46.0964 |  |  | 33.7302 |  |  | 5.102 |  |  | -38.8299 |  |  | -93.534 |  |  | -147.5467 |  |  | -196.0175 |  |  | -256.3498
[13 empty] | Press drop ratio this iteration |  |  | 0.50258 |  |  | 0.49899 |  |  | 0.47969 |  |  | 0.40284 |  |  | 0.092593 |  |  | -3.4762 |  |  | 2.1485 |  |  | 1.5126 |  |  | 1.3424 |  |  | 1.2423
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74018 |  |  | 0.74648 |  |  | 0.78417 |  |  | 0.94903 |  |  | 3.0226 |  |  | -0.33638 |  |  | -0.027938 |  |  | 0.24608 |  |  | -0.059161
[13 empty] | C Non choked w/ reducers | 5 |  | 0.41202 |  |  | 5.8768 |  |  | 15.2985 |  |  | 35.7283 |  |  | 155.7228 |  |  | #NUM! |  |  | -217.2362 |  |  | -1731.4568 |  |  | 176.6653 |  |  | -792.4035
[13 empty] | C Choked w/ reducers | 5 |  | 0.40411 |  |  | 5.7577 |  |  | 14.9316 |  |  | 33.7996 |  |  | 86.6389 |  |  | 629.6041 |  |  | 219.3612 |  |  | 127.3599 |  |  | 98.0218 |  |  | 125.2836
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.41202 |  |  | 5.8768 |  |  | 15.2985 |  |  | 35.7283 |  |  | 155.7228 |  |  | #NUM! |  |  | 219.3612 |  |  | 127.3599 |  |  | 98.0218 |  |  | 125.2836
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.588 | 95.2849 |  | 0.87676 | 1347.1768 |  | 5.2985 | 3331.7286 |  | 18.5283 | 6489.3569 |  | 129.1228 | 10672.6028 |  | 7174 | 14969.1471 |  | 7174 | 19006.8447 |  | 7174 | 22287.0202 |  | 7174 | 24864.923 |  | 7174 | 27741.0076
[13 empty] | Next iteration flow rate |  |  | 97.1905 | Abs Value of | Flow this | 1360.6486 | Abs Value of | Flow this | 3365.0459 | Abs Value of | Flow this | 6554.2504 | Abs Value of | Flow this | 10779.3289 | Abs Value of | Flow this | 15118.8386 | Abs Value of | Flow this | 19196.9132 | Abs Value of | Flow this | 22509.8904 | Abs Value of | Flow this | 25113.5723 | Abs Value of | Flow this | 28018.4176 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.519 |  |  | 99.7845 |  |  | 96.0074 |  |  | 83.3927 |  |  | 54.1891 |  |  | 9.3741 |  |  | -46.4295 |  |  | -101.5279 |  |  | -150.9729 |  |  | -212.5179
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48134 |  |  | 0.46312 |  |  | 0.40227 |  |  | 0.2614 |  |  | 0.045219 |  |  | -0.22397 |  |  | -0.48975 |  |  | -0.72827 |  |  | -1.0251
[13 empty] | Delta P at this iteration flow rate |  |  | 50.519 |  |  | 49.7845 |  |  | 46.0074 |  |  | 33.3927 |  |  | 4.1891 |  |  | -40.6259 |  |  | -96.4295 |  |  | -151.5279 |  |  | -200.9729 |  |  | -262.5179
[13 empty] | Press drop ratio this iteration |  |  | 0.50258 |  |  | 0.49892 |  |  | 0.47921 |  |  | 0.40043 |  |  | 0.077305 |  |  | -4.3338 |  |  | 2.0769 |  |  | 1.4925 |  |  | 1.3312 |  |  | 1.2353
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74021 |  |  | 0.74674 |  |  | 0.78547 |  |  | 0.95745 |  |  | 3.5216 |  |  | -0.29183 |  |  | -0.014279 |  |  | 0.25239 |  |  | -0.053165
[13 empty] | C Non choked w/ reducers | 5 |  | 0.42026 |  |  | 5.9365 |  |  | 15.4683 |  |  | 36.2809 |  |  | 173.4922 |  |  | #NUM! |  |  | -241.1869 |  |  | -3309.572 |  |  | 168.9679 |  |  | -867.1986
[13 empty] | C Choked w/ reducers | 5 |  | 0.4122 |  |  | 5.8161 |  |  | 15.0949 |  |  | 34.2757 |  |  | 88.9795 |  |  | 757.7327 |  |  | 207.7377 |  |  | 123.5894 |  |  | 95.7524 |  |  | 122.8639
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.42026 |  |  | 5.9365 |  |  | 15.4683 |  |  | 36.2809 |  |  | 173.4922 |  |  | #NUM! |  |  | 207.7377 |  |  | 123.5894 |  |  | 95.7524 |  |  | 122.8639
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5797 | 97.1905 |  | 0.93652 | 1360.6486 |  | 5.4683 | 3365.0459 |  | 19.0809 | 6554.2504 |  | 146.8922 | 10779.3289 |  | 7174 | 15118.8386 |  | 7174 | 19196.9132 |  | 7174 | 22509.8904 |  | 7174 | 25113.5723 |  | 7174 | 28018.4176
[13 empty] | Next iteration flow rate |  |  | 99.1344 | Abs Value of | Flow this | 1374.2551 | Abs Value of | Flow this | 3398.6963 | Abs Value of | Flow this | 6619.793 | Abs Value of | Flow this | 10887.1221 | Abs Value of | Flow this | 15270.027 | Abs Value of | Flow this | 19388.8823 | Abs Value of | Flow this | 22734.9894 | Abs Value of | Flow this | 25364.708 | Abs Value of | Flow this | 28298.6018 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5189 |  |  | 99.7697 |  |  | 95.9166 |  |  | 83.0484 |  |  | 53.2578 |  |  | 7.542 |  |  | -49.3833 |  |  | -105.5891 |  |  | -156.028 |  |  | -218.81
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48489 |  |  | 0.48127 |  |  | 0.46268 |  |  | 0.40061 |  |  | 0.25691 |  |  | 0.036381 |  |  | -0.23822 |  |  | -0.50934 |  |  | -0.75265 |  |  | -1.0555
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5189 |  |  | 49.7697 |  |  | 45.9166 |  |  | 33.0484 |  |  | 3.2578 |  |  | -42.458 |  |  | -99.3833 |  |  | -155.5891 |  |  | -206.028 |  |  | -268.81
[13 empty] | Press drop ratio this iteration |  |  | 0.50258 |  |  | 0.49885 |  |  | 0.47871 |  |  | 0.39794 |  |  | 0.06117 |  |  | -5.6295 |  |  | 2.0125 |  |  | 1.4735 |  |  | 1.3205 |  |  | 1.2285
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74025 |  |  | 0.747 |  |  | 0.7868 |  |  | 0.96633 |  |  | 4.2755 |  |  | -0.25176 |  |  | -0.0014062 |  |  | 0.25842 |  |  | -0.047396
[13 empty] | C Non choked w/ reducers | 5 |  | 0.42867 |  |  | 5.9969 |  |  | 15.6403 |  |  | 36.8479 |  |  | 198.5888 |  |  | #NUM! |  |  | -269.6899 |  |  | -32846.7415 |  |  | 161.9319 |  |  | -956.8362
[13 empty] | C Choked w/ reducers | 5 |  | 0.42044 |  |  | 5.8751 |  |  | 15.2603 |  |  | 34.762 |  |  | 91.4408 |  |  | 951.2176 |  |  | 197.2655 |  |  | 120.0242 |  |  | 93.5767 |  |  | 120.5241
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.42867 |  |  | 5.9969 |  |  | 15.6403 |  |  | 36.8479 |  |  | 198.5888 |  |  | #NUM! |  |  | 197.2655 |  |  | 120.0242 |  |  | 93.5767 |  |  | 120.5241
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5713 | 99.1344 |  | 0.99691 | 1374.2551 |  | 5.6403 | 3398.6963 |  | 19.6479 | 6619.793 |  | 171.9888 | 10887.1221 |  | 7174 | 15270.027 |  | 7174 | 19388.8823 |  | 7174 | 22734.9894 |  | 7174 | 25364.708 |  | 7174 | 28298.6018
[13 empty] | Next iteration flow rate |  |  | 101.117 | Abs Value of | Flow this | 1387.9976 | Abs Value of | Flow this | 3432.6833 | Abs Value of | Flow this | 6685.9909 | Abs Value of | Flow this | 10995.9934 | Abs Value of | Flow this | 15422.7272 | Abs Value of | Flow this | 19582.7711 | Abs Value of | Flow this | 22962.3392 | Abs Value of | Flow this | 25618.3551 | Abs Value of | Flow this | 28581.5878 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5187 |  |  | 99.7546 |  |  | 95.8241 |  |  | 82.6971 |  |  | 52.3077 |  |  | 5.6731 |  |  | -52.3964 |  |  | -109.732 |  |  | -161.1847 |  |  | -225.2286
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48488 |  |  | 0.4812 |  |  | 0.46224 |  |  | 0.39892 |  |  | 0.25232 |  |  | 0.027366 |  |  | -0.25275 |  |  | -0.52933 |  |  | -0.77753 |  |  | -1.0865
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5187 |  |  | 49.7546 |  |  | 45.8241 |  |  | 32.6971 |  |  | 2.3077 |  |  | -44.3269 |  |  | -102.3964 |  |  | -159.732 |  |  | -211.1847 |  |  | -275.2286
[13 empty] | Press drop ratio this iteration |  |  | 0.50258 |  |  | 0.49877 |  |  | 0.47821 |  |  | 0.39538 |  |  | 0.044119 |  |  | -7.8135 |  |  | 1.9543 |  |  | 1.4557 |  |  | 1.3102 |  |  | 1.222
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74029 |  |  | 0.74726 |  |  | 0.78817 |  |  | 0.97572 |  |  | 5.5462 |  |  | -0.21555 |  |  | 0.010744 |  |  | 0.26417 |  |  | -0.041844
[13 empty] | C Non choked w/ reducers | 5 |  | 0.43724 |  |  | 6.0579 |  |  | 15.8147 |  |  | 37.4299 |  |  | 238.1513 |  |  | #NUM! |  |  | -304.2906 |  |  | 4203.7621 |  |  | 155.473 |  |  | -1066.2646
[13 empty] | C Choked w/ reducers | 5 |  | 0.42885 |  |  | 5.9348 |  |  | 15.4278 |  |  | 35.2588 |  |  | 94.0326 |  |  | 1277.2276 |  |  | 187.7807 |  |  | 116.6477 |  |  | 91.4888 |  |  | 118.2603
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.43724 |  |  | 6.0579 |  |  | 15.8147 |  |  | 37.4299 |  |  | 238.1513 |  |  | #NUM! |  |  | 187.7807 |  |  | 116.6477 |  |  | 91.4888 |  |  | 118.2603
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5628 | 101.117 |  | 1.0579 | 1387.9976 |  | 5.8147 | 3432.6833 |  | 20.2299 | 6685.9909 |  | 211.5513 | 10995.9934 |  | 7174 | 15422.7272 |  | 7174 | 19582.7711 |  | 7174 | 22962.3392 |  | 7174 | 25618.3551 |  | 7174 | 28581.5878
[13 empty] | Next iteration flow rate |  |  | 103.1394 | Abs Value of | Flow this | 1401.8776 | Abs Value of | Flow this | 3467.0101 | Abs Value of | Flow this | 6752.8508 | Abs Value of | Flow this | 11105.9533 | Abs Value of | Flow this | 15576.9545 | Abs Value of | Flow this | 19778.5989 | Abs Value of | Flow this | 23191.9626 | Abs Value of | Flow this | 25874.5386 | Abs Value of | Flow this | 28867.4037 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5185 |  |  | 99.7391 |  |  | 95.7296 |  |  | 82.3389 |  |  | 51.3386 |  |  | 3.7666 |  |  | -55.47 |  |  | -113.9581 |  |  | -166.445 |  |  | -231.7762
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48488 |  |  | 0.48112 |  |  | 0.46178 |  |  | 0.39719 |  |  | 0.24765 |  |  | 0.018169 |  |  | -0.26758 |  |  | -0.54971 |  |  | -0.8029 |  |  | -1.118
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5185 |  |  | 49.7391 |  |  | 45.7296 |  |  | 32.3389 |  |  | 1.3386 |  |  | -46.2334 |  |  | -105.47 |  |  | -163.9581 |  |  | -216.445 |  |  | -281.7762
[13 empty] | Press drop ratio this iteration |  |  | 0.50258 |  |  | 0.49869 |  |  | 0.4777 |  |  | 0.39275 |  |  | 0.026074 |  |  | -12.2745 |  |  | 1.9014 |  |  | 1.4388 |  |  | 1.3004 |  |  | 1.2157
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74033 |  |  | 0.74753 |  |  | 0.78958 |  |  | 0.98565 |  |  | 8.1418 |  |  | -0.18266 |  |  | 0.022227 |  |  | 0.26968 |  |  | -0.036498
[13 empty] | C Non choked w/ reducers | 5 |  | 0.44599 |  |  | 6.1196 |  |  | 15.9914 |  |  | 38.0277 |  |  | 315.5741 |  |  | #NUM! |  |  | -347.3069 |  |  | 1987.6715 |  |  | 149.5209 |  |  | -1202.9045
[13 empty] | C Choked w/ reducers | 5 |  | 0.43743 |  |  | 5.9951 |  |  | 15.5974 |  |  | 35.7663 |  |  | 96.7658 |  |  | 1942.9361 |  |  | 179.1493 |  |  | 113.445 |  |  | 89.4834 |  |  | 116.0686
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.44599 |  |  | 6.1196 |  |  | 15.9914 |  |  | 38.0277 |  |  | 315.5741 |  |  | #NUM! |  |  | 179.1493 |  |  | 113.445 |  |  | 89.4834 |  |  | 116.0686
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.554 | 103.1394 |  | 1.1196 | 1401.8776 |  | 5.9914 | 3467.0101 |  | 20.8277 | 6752.8508 |  | 288.9741 | 11105.9533 |  | 7174 | 15576.9545 |  | 7174 | 19778.5989 |  | 7174 | 23191.9626 |  | 7174 | 25874.5386 |  | 7174 | 28867.4037
[13 empty] | Next iteration flow rate |  |  | 105.2022 | Abs Value of | Flow this | 1415.8964 | Abs Value of | Flow this | 3501.6802 | Abs Value of | Flow this | 6820.3793 | Abs Value of | Flow this | 11217.0128 | Abs Value of | Flow this | 15732.724 | Abs Value of | Flow this | 19976.3848 | Abs Value of | Flow this | 23423.8823 | Abs Value of | Flow this | 26133.284 | Abs Value of | Flow this | 29156.0778 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5184 |  |  | 99.7234 |  |  | 95.6333 |  |  | 81.9734 |  |  | 50.35 |  |  | 1.8218 |  |  | -58.6055 |  |  | -118.2692 |  |  | -171.811 |  |  | -238.4554
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48488 |  |  | 0.48105 |  |  | 0.46132 |  |  | 0.39542 |  |  | 0.24288 |  |  | 0.0087881 |  |  | -0.2827 |  |  | -0.57051 |  |  | -0.82879 |  |  | -1.1503
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5184 |  |  | 49.7234 |  |  | 45.6333 |  |  | 31.9734 |  |  | 0.35002 |  |  | -48.1782 |  |  | -108.6055 |  |  | -168.2692 |  |  | -221.811 |  |  | -288.4554
[13 empty] | Press drop ratio this iteration |  |  | 0.50258 |  |  | 0.49861 |  |  | 0.47717 |  |  | 0.39005 |  |  | 0.0069518 |  |  | -26.4452 |  |  | 1.8532 |  |  | 1.4228 |  |  | 1.291 |  |  | 1.2097
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74037 |  |  | 0.74781 |  |  | 0.79103 |  |  | 0.99617 |  |  | 16.3869 |  |  | -0.15266 |  |  | 0.033096 |  |  | 0.27495 |  |  | -0.031346
[13 empty] | C Non choked w/ reducers | 5 |  | 0.45491 |  |  | 6.1819 |  |  | 16.1705 |  |  | 38.6419 |  |  | 622.7484 |  |  | #NUM! |  |  | -402.3845 |  |  | 1306.3961 |  |  | 144.0163 |  |  | -1378.4146
[13 empty] | C Choked w/ reducers | 5 |  | 0.44618 |  |  | 6.056 |  |  | 15.7693 |  |  | 36.285 |  |  | 99.6524 |  |  | 4057.2056 |  |  | 171.2602 |  |  | 110.4029 |  |  | 87.5555 |  |  | 113.9457
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.45491 |  |  | 6.1819 |  |  | 16.1705 |  |  | 38.6419 |  |  | 622.7484 |  |  | #NUM! |  |  | 171.2602 |  |  | 110.4029 |  |  | 87.5555 |  |  | 113.9457
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5451 | 105.2022 |  | 1.1819 | 1415.8964 |  | 6.1705 | 3501.6802 |  | 21.4419 | 6820.3793 |  | 596.1484 | 11217.0128 |  | 7174 | 15732.724 |  | 7174 | 19976.3848 |  | 7174 | 23423.8823 |  | 7174 | 26133.284 |  | 7174 | 29156.0778
[13 empty] | Next iteration flow rate |  |  | 107.3062 | Abs Value of | Flow this | 1430.0553 | Abs Value of | Flow this | 3536.697 | Abs Value of | Flow this | 6888.5831 | Abs Value of | Flow this | 11329.183 | Abs Value of | Flow this | 15890.0513 | Abs Value of | Flow this | 20176.1487 | Abs Value of | Flow this | 23658.1211 | Abs Value of | Flow this | 26394.6168 | Abs Value of | Flow this | 29447.6385 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5182 |  |  | 99.7073 |  |  | 95.535 |  |  | 81.6005 |  |  | 49.3416 |  |  | -0.16208 |  |  | -61.804 |  |  | -122.6669 |  |  | -177.2849 |  |  | -245.2689
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48488 |  |  | 0.48097 |  |  | 0.46084 |  |  | 0.39363 |  |  | 0.23801 |  |  | -0.00078183 |  |  | -0.29813 |  |  | -0.59172 |  |  | -0.85519 |  |  | -1.1831
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5182 |  |  | 49.7073 |  |  | 45.535 |  |  | 31.6005 |  |  | -0.65845 |  |  | -50.1621 |  |  | -111.804 |  |  | -172.6669 |  |  | -227.2849 |  |  | -295.2689
[13 empty] | Press drop ratio this iteration |  |  | 0.50258 |  |  | 0.49853 |  |  | 0.47663 |  |  | 0.38726 |  |  | -0.013345 |  |  | 309.4959 |  |  | 1.809 |  |  | 1.4076 |  |  | 1.282 |  |  | 1.2039
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74042 |  |  | 0.7481 |  |  | 0.79252 |  |  | 1.0073 |  |  | -179.0777 |  |  | -0.1252 |  |  | 0.043397 |  |  | 0.28 |  |  | -0.02638
[13 empty] | C Non choked w/ reducers | 5 |  | 0.46401 |  |  | 6.2449 |  |  | 16.352 |  |  | 39.2733 |  |  | #NUM! |  |  | -7.3812 |  |  | -475.61 |  |  | 975.4164 |  |  | 138.9089 |  |  | -1612.2202
[13 empty] | C Choked w/ reducers | 5 |  | 0.4551 |  |  | 6.1175 |  |  | 15.9433 |  |  | 36.8153 |  |  | 102.706 |  |  | 46060.7999 |  |  | 164.0212 |  |  | 107.5093 |  |  | 85.7006 |  |  | 111.8881
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.46401 |  |  | 6.2449 |  |  | 16.352 |  |  | 39.2733 |  |  | #NUM! |  |  | 46060.7999 |  |  | 164.0212 |  |  | 107.5093 |  |  | 85.7006 |  |  | 111.8881
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.536 | 107.3062 |  | 1.2449 | 1430.0553 |  | 6.352 | 3536.697 |  | 22.0733 | 6888.5831 |  | 7174 | 11329.183 |  | 7174 | 15890.0513 |  | 7174 | 20176.1487 |  | 7174 | 23658.1211 |  | 7174 | 26394.6168 |  | 7174 | 29447.6385
[13 empty] | Next iteration flow rate |  |  | 109.4523 | Abs Value of | Flow this | 1444.3559 | Abs Value of | Flow this | 3572.064 | Abs Value of | Flow this | 6957.4689 | Abs Value of | Flow this | 11442.4748 | Abs Value of | Flow this | 16048.9518 | Abs Value of | Flow this | 20377.9102 | Abs Value of | Flow this | 23894.7023 | Abs Value of | Flow this | 26658.563 | Abs Value of | Flow this | 29742.1149 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.518 |  |  | 99.6909 |  |  | 95.4347 |  |  | 81.2202 |  |  | 48.3128 |  |  | -2.1858 |  |  | -65.0667 |  |  | -127.153 |  |  | -182.8689 |  |  | -252.2193
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48488 |  |  | 0.48089 |  |  | 0.46036 |  |  | 0.39179 |  |  | 0.23305 |  |  | -0.010544 |  |  | -0.31387 |  |  | -0.61336 |  |  | -0.88213 |  |  | -1.2167
[13 empty] | Delta P at this iteration flow rate |  |  | 50.518 |  |  | 49.6909 |  |  | 45.4347 |  |  | 31.2202 |  |  | -1.6872 |  |  | -52.1858 |  |  | -115.0667 |  |  | -177.153 |  |  | -232.8689 |  |  | -302.2193
[13 empty] | Press drop ratio this iteration |  |  | 0.50258 |  |  | 0.49845 |  |  | 0.47608 |  |  | 0.38439 |  |  | -0.034922 |  |  | 23.8745 |  |  | 1.7684 |  |  | 1.3932 |  |  | 1.2734 |  |  | 1.1982
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74046 |  |  | 0.74839 |  |  | 0.79406 |  |  | 1.0192 |  |  | -12.8912 |  |  | -0.099966 |  |  | 0.05317 |  |  | 0.28483 |  |  | -0.02159
[13 empty] | C Non choked w/ reducers | 5 |  | 0.47329 |  |  | 6.3085 |  |  | 16.536 |  |  | 39.9229 |  |  | #NUM! |  |  | -27.6476 |  |  | -577.9679 |  |  | 779.7093 |  |  | 134.1557 |  |  | -1939.2735
[13 empty] | C Choked w/ reducers | 5 |  | 0.4642 |  |  | 6.1797 |  |  | 16.1197 |  |  | 37.3576 |  |  | 105.9419 |  |  | 3449.4881 |  |  | 157.3543 |  |  | 104.7534 |  |  | 83.9146 |  |  | 109.8929
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.47329 |  |  | 6.3085 |  |  | 16.536 |  |  | 39.9229 |  |  | #NUM! |  |  | 3449.4881 |  |  | 157.3543 |  |  | 104.7534 |  |  | 83.9146 |  |  | 109.8929
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5267 | 109.4523 |  | 1.3085 | 1444.3559 |  | 6.536 | 3572.064 |  | 22.7229 | 6957.4689 |  | 7174 | 11442.4748 |  | 7174 | 16048.9518 |  | 7174 | 20377.9102 |  | 7174 | 23894.7023 |  | 7174 | 26658.563 |  | 7174 | 29742.1149
[13 empty] | Next iteration flow rate |  |  | 111.6414 | Abs Value of | Flow this | 1458.7995 | Abs Value of | Flow this | 3607.7846 | Abs Value of | Flow this | 7027.0436 | Abs Value of | Flow this | 11556.8995 | Abs Value of | Flow this | 16209.4413 | Abs Value of | Flow this | 20581.6893 | Abs Value of | Flow this | 24133.6493 | Abs Value of | Flow this | 26925.1486 | Abs Value of | Flow this | 30039.5361 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5178 |  |  | 99.6742 |  |  | 95.3325 |  |  | 80.8322 |  |  | 47.2634 |  |  | -4.2503 |  |  | -68.3951 |  |  | -131.7293 |  |  | -188.565 |  |  | -259.3094
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48488 |  |  | 0.48081 |  |  | 0.45987 |  |  | 0.38992 |  |  | 0.22799 |  |  | -0.020503 |  |  | -0.32993 |  |  | -0.63544 |  |  | -0.9096 |  |  | -1.2509
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5178 |  |  | 49.6742 |  |  | 45.3325 |  |  | 30.8322 |  |  | -2.7366 |  |  | -54.2503 |  |  | -118.3951 |  |  | -181.7293 |  |  | -238.565 |  |  | -309.3094
[13 empty] | Press drop ratio this iteration |  |  | 0.50258 |  |  | 0.49837 |  |  | 0.47552 |  |  | 0.38143 |  |  | -0.057901 |  |  | 12.7639 |  |  | 1.731 |  |  | 1.3796 |  |  | 1.2652 |  |  | 1.1928
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.7405 |  |  | 0.74868 |  |  | 0.79564 |  |  | 1.0319 |  |  | -6.4266 |  |  | -0.076706 |  |  | 0.062454 |  |  | 0.28947 |  |  | -0.016969
[13 empty] | C Non choked w/ reducers | 5 |  | 0.48276 |  |  | 6.3729 |  |  | 16.7225 |  |  | 40.5913 |  |  | #NUM! |  |  | -39.3974 |  |  | -731.5125 |  |  | 650.3479 |  |  | 129.7199 |  |  | -2429.4419
[13 empty] | C Choked w/ reducers | 5 |  | 0.47349 |  |  | 6.2426 |  |  | 16.2984 |  |  | 37.9123 |  |  | 109.3771 |  |  | 1791.7472 |  |  | 151.1938 |  |  | 102.1254 |  |  | 82.1935 |  |  | 107.957
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.48276 |  |  | 6.3729 |  |  | 16.7225 |  |  | 40.5913 |  |  | #NUM! |  |  | 1791.7472 |  |  | 151.1938 |  |  | 102.1254 |  |  | 82.1935 |  |  | 107.957
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5172 | 111.6414 |  | 1.3729 | 1458.7995 |  | 6.7225 | 3607.7846 |  | 23.3913 | 7027.0436 |  | 7174 | 11556.8995 |  | 7174 | 16209.4413 |  | 7174 | 20581.6893 |  | 7174 | 24133.6493 |  | 7174 | 26925.1486 |  | 7174 | 30039.5361
[13 empty] | Next iteration flow rate |  |  | 113.8742 | Abs Value of | Flow this | 1473.3874 | Abs Value of | Flow this | 3643.8625 | Abs Value of | Flow this | 7097.314 | Abs Value of | Flow this | 11672.4685 | Abs Value of | Flow this | 16371.5357 | Abs Value of | Flow this | 20787.5062 | Abs Value of | Flow this | 24374.9858 | Abs Value of | Flow this | 27194.4001 | Abs Value of | Flow this | 30339.9314 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5176 |  |  | 99.6571 |  |  | 95.2281 |  |  | 80.4364 |  |  | 46.1929 |  |  | -6.3562 |  |  | -71.7903 |  |  | -136.3975 |  |  | -194.3757 |  |  | -266.542
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48488 |  |  | 0.48073 |  |  | 0.45936 |  |  | 0.38801 |  |  | 0.22283 |  |  | -0.030661 |  |  | -0.3463 |  |  | -0.65796 |  |  | -0.93763 |  |  | -1.2858
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5176 |  |  | 49.6571 |  |  | 45.2281 |  |  | 30.4364 |  |  | -3.8071 |  |  | -56.3562 |  |  | -121.7903 |  |  | -186.3975 |  |  | -244.3757 |  |  | -316.542
[13 empty] | Press drop ratio this iteration |  |  | 0.50257 |  |  | 0.49828 |  |  | 0.47495 |  |  | 0.37839 |  |  | -0.082418 |  |  | 8.8663 |  |  | 1.6965 |  |  | 1.3666 |  |  | 1.2572 |  |  | 1.1876
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74055 |  |  | 0.74899 |  |  | 0.79728 |  |  | 1.0454 |  |  | -4.1588 |  |  | -0.055201 |  |  | 0.071282 |  |  | 0.29392 |  |  | -0.012508
[13 empty] | C Non choked w/ reducers | 5 |  | 0.49241 |  |  | 6.4379 |  |  | 16.9116 |  |  | 41.2797 |  |  | #NUM! |  |  | -49.3334 |  |  | -988.0193 |  |  | 558.4371 |  |  | 125.5694 |  |  | -3245.618
[13 empty] | C Choked w/ reducers | 5 |  | 0.48296 |  |  | 6.3061 |  |  | 16.4794 |  |  | 38.4798 |  |  | 113.0311 |  |  | 1210.0882 |  |  | 145.4837 |  |  | 99.6164 |  |  | 80.5337 |  |  | 106.0779
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.49241 |  |  | 6.4379 |  |  | 16.9116 |  |  | 41.2797 |  |  | #NUM! |  |  | 1210.0882 |  |  | 145.4837 |  |  | 99.6164 |  |  | 80.5337 |  |  | 106.0779
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5076 | 113.8742 |  | 1.4379 | 1473.3874 |  | 6.9116 | 3643.8625 |  | 24.0797 | 7097.314 |  | 7174 | 11672.4685 |  | 7174 | 16371.5357 |  | 7174 | 20787.5062 |  | 7174 | 24374.9858 |  | 7174 | 27194.4001 |  | 7174 | 30339.9314
[13 empty] | Next iteration flow rate |  |  | 116.1517 | Abs Value of | Flow this | 1488.1213 | Abs Value of | Flow this | 3680.3011 | Abs Value of | Flow this | 7168.2872 | Abs Value of | Flow this | 11789.1932 | Abs Value of | Flow this | 16535.2511 | Abs Value of | Flow this | 20995.3812 | Abs Value of | Flow this | 24618.7357 | Abs Value of | Flow this | 27466.3441 | Abs Value of | Flow this | 30643.3307 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5174 |  |  | 99.6397 |  |  | 95.1217 |  |  | 80.0327 |  |  | 45.1008 |  |  | -8.5045 |  |  | -75.2538 |  |  | -141.1596 |  |  | -200.3032 |  |  | -273.92
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48488 |  |  | 0.48064 |  |  | 0.45885 |  |  | 0.38606 |  |  | 0.21756 |  |  | -0.041024 |  |  | -0.36301 |  |  | -0.68093 |  |  | -0.96623 |  |  | -1.3213
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5174 |  |  | 49.6397 |  |  | 45.1217 |  |  | 30.0327 |  |  | -4.8992 |  |  | -58.5045 |  |  | -125.2538 |  |  | -191.1596 |  |  | -250.3032 |  |  | -323.92
[13 empty] | Press drop ratio this iteration |  |  | 0.50257 |  |  | 0.49819 |  |  | 0.47436 |  |  | 0.37526 |  |  | -0.10863 |  |  | 6.8792 |  |  | 1.6644 |  |  | 1.3542 |  |  | 1.2496 |  |  | 1.1825
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74059 |  |  | 0.7493 |  |  | 0.79896 |  |  | 1.0598 |  |  | -3.0026 |  |  | -0.035263 |  |  | 0.079686 |  |  | 0.2982 |  |  | -0.0082004
[13 empty] | C Non choked w/ reducers | 5 |  | 0.50226 |  |  | 6.5035 |  |  | 17.1033 |  |  | 41.9891 |  |  | #NUM! |  |  | -58.557 |  |  | -1504.5003 |  |  | 489.7358 |  |  | 121.6765 |  |  | -4875.7925
[13 empty] | C Choked w/ reducers | 5 |  | 0.49262 |  |  | 6.3702 |  |  | 16.6628 |  |  | 39.0607 |  |  | 116.9256 |  |  | 913.4593 |  |  | 140.1758 |  |  | 97.2184 |  |  | 78.932 |  |  | 104.2529
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.50226 |  |  | 6.5035 |  |  | 17.1033 |  |  | 41.9891 |  |  | #NUM! |  |  | 913.4593 |  |  | 140.1758 |  |  | 97.2184 |  |  | 78.932 |  |  | 104.2529
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.4977 | 116.1517 |  | 1.5035 | 1488.1213 |  | 7.1033 | 3680.3011 |  | 24.7891 | 7168.2872 |  | 7174 | 11789.1932 |  | 7174 | 16535.2511 |  | 7174 | 20995.3812 |  | 7174 | 24618.7357 |  | 7174 | 27466.3441 |  | 7174 | 30643.3307
[13 empty] | Next iteration flow rate |  |  | 118.4747 | Abs Value of | Flow this | 1503.0025 | Abs Value of | Flow this | 3717.1041 | Abs Value of | Flow this | 7239.9701 | Abs Value of | Flow this | 11907.0851 | Abs Value of | Flow this | 16700.6036 | Abs Value of | Flow this | 21205.335 | Abs Value of | Flow this | 24864.923 | Abs Value of | Flow this | 27741.0076 | Abs Value of | Flow this | 30949.764 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5172 |  |  | 99.622 |  |  | 95.0131 |  |  | 79.6208 |  |  | 43.9869 |  |  | -10.6959 |  |  | -78.7869 |  |  | -146.0175 |  |  | -206.3498 |  |  | -281.4463
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48488 |  |  | 0.48056 |  |  | 0.45833 |  |  | 0.38408 |  |  | 0.21218 |  |  | -0.051595 |  |  | -0.38005 |  |  | -0.70436 |  |  | -0.99539 |  |  | -1.3576
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5172 |  |  | 49.622 |  |  | 45.0131 |  |  | 29.6208 |  |  | -6.0131 |  |  | -60.6959 |  |  | -128.7869 |  |  | -196.0175 |  |  | -256.3498 |  |  | -331.4463
[13 empty] | Press drop ratio this iteration |  |  | 0.50257 |  |  | 0.4981 |  |  | 0.47376 |  |  | 0.37202 |  |  | -0.1367 |  |  | 5.6747 |  |  | 1.6346 |  |  | 1.3424 |  |  | 1.2423 |  |  | 1.1777
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74064 |  |  | 0.74962 |  |  | 0.80069 |  |  | 1.0752 |  |  | -2.3018 |  |  | -0.016731 |  |  | 0.087695 |  |  | 0.30231 |  |  | -0.0040388
[13 empty] | C Non choked w/ reducers | 5 |  | 0.51231 |  |  | 6.5699 |  |  | 17.2977 |  |  | 42.7205 |  |  | #NUM! |  |  | -67.5417 |  |  | -3086.8651 |  |  | 436.4125 |  |  | 118.0171 |  |  | -9751.7096
[13 empty] | C Choked w/ reducers | 5 |  | 0.50247 |  |  | 6.4351 |  |  | 16.8487 |  |  | 39.6554 |  |  | 121.0856 |  |  | 733.5674 |  |  | 135.2287 |  |  | 94.9239 |  |  | 77.3853 |  |  | 102.4797
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.51231 |  |  | 6.5699 |  |  | 17.2977 |  |  | 42.7205 |  |  | #NUM! |  |  | 733.5674 |  |  | 135.2287 |  |  | 94.9239 |  |  | 77.3853 |  |  | 102.4797
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.4877 | 118.4747 |  | 1.5699 | 1503.0025 |  | 7.2977 | 3717.1041 |  | 25.5205 | 7239.9701 |  | 7174 | 11907.0851 |  | 7174 | 16700.6036 |  | 7174 | 21205.335 |  | 7174 | 24864.923 |  | 7174 | 27741.0076 |  | 7174 | 30949.764
[13 empty] | Next iteration flow rate |  |  | 120.8442 | Abs Value of | Flow this | 1518.0326 | Abs Value of | Flow this | 3754.2752 | Abs Value of | Flow this | 7312.3698 | Abs Value of | Flow this | 12026.156 | Abs Value of | Flow this | 16867.6096 | Abs Value of | Flow this | 21417.3884 | Abs Value of | Flow this | 25113.5723 | Abs Value of | Flow this | 28018.4176 | Abs Value of | Flow this | 31259.2617 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.517 |  |  | 99.6039 |  |  | 94.9024 |  |  | 79.2007 |  |  | 42.8505 |  |  | -12.9314 |  |  | -82.3911 |  |  | -150.9729 |  |  | -212.5179 |  |  | -289.1239
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48488 |  |  | 0.48047 |  |  | 0.45779 |  |  | 0.38205 |  |  | 0.2067 |  |  | -0.062379 |  |  | -0.39744 |  |  | -0.72827 |  |  | -1.0251 |  |  | -1.3947
[13 empty] | Delta P at this iteration flow rate |  |  | 50.517 |  |  | 49.6039 |  |  | 44.9024 |  |  | 29.2007 |  |  | -7.1495 |  |  | -62.9314 |  |  | -132.3911 |  |  | -200.9729 |  |  | -262.5179 |  |  | -339.1239
[13 empty] | Press drop ratio this iteration |  |  | 0.50257 |  |  | 0.49801 |  |  | 0.47314 |  |  | 0.36869 |  |  | -0.16685 |  |  | 4.8665 |  |  | 1.6069 |  |  | 1.3312 |  |  | 1.2353 |  |  | 1.1729
[13 empty] | Expansion factor | 12 |  | 0.73825 |  |  | 0.74069 |  |  | 0.74994 |  |  | 0.80247 |  |  | 1.0918 |  |  | -1.8316 |  |  | 0.0005366 |  |  | 0.095333 |  |  | 0.30626 |  |  | -1.67e-05
[13 empty] | C Non choked w/ reducers | 5 |  | 0.52256 |  |  | 6.637 |  |  | 17.4948 |  |  | 43.4752 |  |  | #NUM! |  |  | -76.571 |  |  | 93755.0994 |  |  | 393.8037 |  |  | 114.5698 |  |  | -2323403.9883
[13 empty] | C Choked w/ reducers | 5 |  | 0.51252 |  |  | 6.5006 |  |  | 17.037 |  |  | 40.2644 |  |  | 125.5397 |  |  | 612.8209 |  |  | 130.6064 |  |  | 92.7262 |  |  | 75.8907 |  |  | 100.756
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.52256 |  |  | 6.637 |  |  | 17.4948 |  |  | 43.4752 |  |  | #NUM! |  |  | 612.8209 |  |  | 130.6064 |  |  | 92.7262 |  |  | 75.8907 |  |  | 100.756
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.4774 | 120.8442 |  | 1.637 | 1518.0326 |  | 7.4948 | 3754.2752 |  | 26.2752 | 7312.3698 |  | 7174 | 12026.156 |  | 7174 | 16867.6096 |  | 7174 | 21417.3884 |  | 7174 | 25113.5723 |  | 7174 | 28018.4176 |  | 7174 | 31259.2617
[13 empty] | Next iteration flow rate |  |  | 123.2611 | Abs Value of | Flow this | 1533.2129 | Abs Value of | Flow this | 3791.8179 | Abs Value of | Flow this | 7385.4935 | Abs Value of | Flow this | 12146.4176 | Abs Value of | Flow this | 17036.2857 | Abs Value of | Flow this | 21631.5623 | Abs Value of | Flow this | 25364.708 | Abs Value of | Flow this | 28298.6018 | Abs Value of | Flow this | 31571.8543 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5167 |  |  | 99.5854 |  |  | 94.7894 |  |  | 78.7721 |  |  | 41.6913 |  |  | -15.2119 |  |  | -86.0676 |  |  | -156.028 |  |  | -218.81 |  |  | -296.9558
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48487 |  |  | 0.48038 |  |  | 0.45725 |  |  | 0.37998 |  |  | 0.20111 |  |  | -0.073379 |  |  | -0.41517 |  |  | -0.75265 |  |  | -1.0555 |  |  | -1.4325
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5167 |  |  | 49.5854 |  |  | 44.7894 |  |  | 28.7721 |  |  | -8.3087 |  |  | -65.2119 |  |  | -136.0676 |  |  | -206.028 |  |  | -268.81 |  |  | -346.9558
[13 empty] | Press drop ratio this iteration |  |  | 0.50257 |  |  | 0.49792 |  |  | 0.47252 |  |  | 0.36526 |  |  | -0.19929 |  |  | 4.2869 |  |  | 1.5809 |  |  | 1.3205 |  |  | 1.2285 |  |  | 1.1684
[13 empty] | Expansion factor | 12 |  | 0.73826 |  |  | 0.74074 |  |  | 0.75027 |  |  | 0.80431 |  |  | 1.1097 |  |  | -1.4943 |  |  | 0.016661 |  |  | 0.10263 |  |  | 0.31006 |  |  | 0.0038719
[13 empty] | C Non choked w/ reducers | 5 |  | 0.53301 |  |  | 6.7048 |  |  | 17.6948 |  |  | 44.2545 |  |  | #NUM! |  |  | -85.8561 |  |  | 2943.3438 |  |  | 358.9594 |  |  | 111.3159 |  |  | 9873.4054
[13 empty] | C Choked w/ reducers | 5 |  | 0.52278 |  |  | 6.5668 |  |  | 17.2279 |  |  | 40.8883 |  |  | 130.3206 |  |  | 526.1617 |  |  | 126.2775 |  |  | 90.6193 |  |  | 74.4454 |  |  | 99.0796
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.53301 |  |  | 6.7048 |  |  | 17.6948 |  |  | 44.2545 |  |  | #NUM! |  |  | 526.1617 |  |  | 126.2775 |  |  | 90.6193 |  |  | 74.4454 |  |  | 99.0796
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.467 | 123.2611 |  | 1.7048 | 1533.2129 |  | 7.6948 | 3791.8179 |  | 27.0545 | 7385.4935 |  | 7174 | 12146.4176 |  | 7174 | 17036.2857 |  | 7174 | 21631.5623 |  | 7174 | 25364.708 |  | 7174 | 28298.6018 |  | 7174 | 31571.8543
[13 empty] | Next iteration flow rate |  |  | 125.7263 | Abs Value of | Flow this | 1548.545 | Abs Value of | Flow this | 3829.7361 | Abs Value of | Flow this | 7459.3484 | Abs Value of | Flow this | 12267.8817 | Abs Value of | Flow this | 17206.6486 | Abs Value of | Flow this | 21847.8779 | Abs Value of | Flow this | 25618.3551 | Abs Value of | Flow this | 28581.5878 | Abs Value of | Flow this | 31887.5728 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5165 |  |  | 99.5666 |  |  | 94.6742 |  |  | 78.3349 |  |  | 40.5088 |  |  | -17.5381 |  |  | -89.8181 |  |  | -161.1847 |  |  | -225.2286 |  |  | -304.9451
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48487 |  |  | 0.48029 |  |  | 0.45669 |  |  | 0.37787 |  |  | 0.19541 |  |  | -0.084601 |  |  | -0.43327 |  |  | -0.77753 |  |  | -1.0865 |  |  | -1.471
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5165 |  |  | 49.5666 |  |  | 44.6742 |  |  | 28.3349 |  |  | -9.4912 |  |  | -67.5381 |  |  | -139.8181 |  |  | -211.1847 |  |  | -275.2286 |  |  | -354.9451
[13 empty] | Press drop ratio this iteration |  |  | 0.50257 |  |  | 0.49782 |  |  | 0.47187 |  |  | 0.36172 |  |  | -0.2343 |  |  | 3.8509 |  |  | 1.5567 |  |  | 1.3102 |  |  | 1.222 |  |  | 1.164
[13 empty] | Expansion factor | 12 |  | 0.73826 |  |  | 0.74078 |  |  | 0.75061 |  |  | 0.80621 |  |  | 1.129 |  |  | -1.2406 |  |  | 0.031749 |  |  | 0.10959 |  |  | 0.31371 |  |  | 0.0076329
[13 empty] | C Non choked w/ reducers | 5 |  | 0.54367 |  |  | 6.7733 |  |  | 17.8975 |  |  | 45.0597 |  |  | #NUM! |  |  | -95.582 |  |  | 1506.4752 |  |  | 329.922 |  |  | 108.239 |  |  | 4935.3382
[13 empty] | C Choked w/ reducers | 5 |  | 0.53323 |  |  | 6.6338 |  |  | 17.4213 |  |  | 41.5276 |  |  | 135.4661 |  |  | 460.9351 |  |  | 122.2147 |  |  | 88.5974 |  |  | 73.0471 |  |  | 97.4486
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.54367 |  |  | 6.7733 |  |  | 17.8975 |  |  | 45.0597 |  |  | #NUM! |  |  | 460.9351 |  |  | 122.2147 |  |  | 88.5974 |  |  | 73.0471 |  |  | 97.4486
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.4563 | 125.7263 |  | 1.7733 | 1548.545 |  | 7.8975 | 3829.7361 |  | 27.8597 | 7459.3484 |  | 7174 | 12267.8817 |  | 7174 | 17206.6486 |  | 7174 | 21847.8779 |  | 7174 | 25618.3551 |  | 7174 | 28581.5878 |  | 7174 | 31887.5728
[13 empty] | Next iteration flow rate |  |  | 128.2409 | Abs Value of | Flow this | 1564.0305 | Abs Value of | Flow this | 3868.0335 | Abs Value of | Flow this | 7533.9419 | Abs Value of | Flow this | 12390.5606 | Abs Value of | Flow this | 17378.7151 | Abs Value of | Flow this | 22066.3567 | Abs Value of | Flow this | 25874.5386 | Abs Value of | Flow this | 28867.4037 | Abs Value of | Flow this | 32206.4486 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5162 |  |  | 99.5473 |  |  | 94.5566 |  |  | 77.889 |  |  | 39.3025 |  |  | -19.9112 |  |  | -93.644 |  |  | -166.445 |  |  | -231.7762 |  |  | -313.0951
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48487 |  |  | 0.4802 |  |  | 0.45612 |  |  | 0.37572 |  |  | 0.18959 |  |  | -0.096048 |  |  | -0.45172 |  |  | -0.8029 |  |  | -1.118 |  |  | -1.5103
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5162 |  |  | 49.5473 |  |  | 44.5566 |  |  | 27.889 |  |  | -10.6975 |  |  | -69.9112 |  |  | -143.644 |  |  | -216.445 |  |  | -281.7762 |  |  | -363.0951
[13 empty] | Press drop ratio this iteration |  |  | 0.50257 |  |  | 0.49773 |  |  | 0.47122 |  |  | 0.35806 |  |  | -0.27218 |  |  | 3.5112 |  |  | 1.5339 |  |  | 1.3004 |  |  | 1.2157 |  |  | 1.1597
[13 empty] | Expansion factor | 12 |  | 0.73826 |  |  | 0.74084 |  |  | 0.75096 |  |  | 0.80817 |  |  | 1.1498 |  |  | -1.0429 |  |  | 0.045895 |  |  | 0.11625 |  |  | 0.31723 |  |  | 0.011272
[13 empty] | C Non choked w/ reducers | 5 |  | 0.55455 |  |  | 6.8426 |  |  | 18.1032 |  |  | 45.8924 |  |  | #NUM! |  |  | -105.932 |  |  | 1017.012 |  |  | 305.3414 |  |  | 105.3243 |  |  | 3293.6796
[13 empty] | C Choked w/ reducers | 5 |  | 0.5439 |  |  | 6.7014 |  |  | 17.6174 |  |  | 42.1831 |  |  | 141.0201 |  |  | 410.0605 |  |  | 118.3938 |  |  | 86.6553 |  |  | 71.6934 |  |  | 95.8612
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.55455 |  |  | 6.8426 |  |  | 18.1032 |  |  | 45.8924 |  |  | #NUM! |  |  | 410.0605 |  |  | 118.3938 |  |  | 86.6553 |  |  | 71.6934 |  |  | 95.8612
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.4455 | 128.2409 |  | 1.8426 | 1564.0305 |  | 8.1032 | 3868.0335 |  | 28.6924 | 7533.9419 |  | 7174 | 12390.5606 |  | 7174 | 17378.7151 |  | 7174 | 22066.3567 |  | 7174 | 25874.5386 |  | 7174 | 28867.4037 |  | 7174 | 32206.4486
[13 empty] | Next iteration flow rate |  |  | 130.8057 | Abs Value of | Flow this | 1579.6708 | Abs Value of | Flow this | 3906.7138 | Abs Value of | Flow this | 7609.2813 | Abs Value of | Flow this | 12514.4662 | Abs Value of | Flow this | 17552.5022 | Abs Value of | Flow this | 22287.0202 | Abs Value of | Flow this | 26133.284 | Abs Value of | Flow this | 29156.0778 | Abs Value of | Flow this | 32528.5131 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.516 |  |  | 99.5277 |  |  | 94.4367 |  |  | 77.434 |  |  | 38.072 |  |  | -22.3319 |  |  | -97.5467 |  |  | -171.811 |  |  | -238.4554 |  |  | -321.4088
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48487 |  |  | 0.4801 |  |  | 0.45555 |  |  | 0.37353 |  |  | 0.18365 |  |  | -0.10773 |  |  | -0.47055 |  |  | -0.82879 |  |  | -1.1503 |  |  | -1.5504
[13 empty] | Delta P at this iteration flow rate |  |  | 50.516 |  |  | 49.5277 |  |  | 44.4367 |  |  | 27.434 |  |  | -11.928 |  |  | -72.3319 |  |  | -147.5467 |  |  | -221.811 |  |  | -288.4554 |  |  | -371.4088
[13 empty] | Press drop ratio this iteration |  |  | 0.50257 |  |  | 0.49763 |  |  | 0.47054 |  |  | 0.35429 |  |  | -0.3133 |  |  | 3.239 |  |  | 1.5126 |  |  | 1.291 |  |  | 1.2097 |  |  | 1.1556
[13 empty] | Expansion factor | 12 |  | 0.73826 |  |  | 0.74089 |  |  | 0.75131 |  |  | 0.81019 |  |  | 1.1725 |  |  | -0.88456 |  |  | 0.059183 |  |  | 0.12263 |  |  | 0.32063 |  |  | 0.014793
[13 empty] | C Non choked w/ reducers | 5 |  | 0.56564 |  |  | 6.9126 |  |  | 18.3119 |  |  | 46.7543 |  |  | #NUM! |  |  | -117.1047 |  |  | 770.0776 |  |  | 284.2564 |  |  | 102.5586 |  |  | 2473.5137
[13 empty] | C Choked w/ reducers | 5 |  | 0.55478 |  |  | 6.7697 |  |  | 17.8162 |  |  | 42.8552 |  |  | 147.0338 |  |  | 369.2671 |  |  | 114.7935 |  |  | 84.7883 |  |  | 70.3821 |  |  | 94.3154
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.56564 |  |  | 6.9126 |  |  | 18.3119 |  |  | 46.7543 |  |  | #NUM! |  |  | 369.2671 |  |  | 114.7935 |  |  | 84.7883 |  |  | 70.3821 |  |  | 94.3154
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.4344 | 130.8057 |  | 1.9126 | 1579.6708 |  | 8.3119 | 3906.7138 |  | 29.5543 | 7609.2813 |  | 7174 | 12514.4662 |  | 7174 | 17552.5022 |  | 7174 | 22287.0202 |  | 7174 | 26133.284 |  | 7174 | 29156.0778 |  | 7174 | 32528.5131
[13 empty] | Next iteration flow rate |  |  | 133.4218 | Abs Value of | Flow this | 1595.4675 | Abs Value of | Flow this | 3945.7809 | Abs Value of | Flow this | 7685.3741 | Abs Value of | Flow this | 12639.6108 | Abs Value of | Flow this | 17728.0272 | Abs Value of | Flow this | 22509.8904 | Abs Value of | Flow this | 26394.6168 | Abs Value of | Flow this | 29447.6385 | Abs Value of | Flow this | 32853.7982 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5157 |  |  | 99.5077 |  |  | 94.3144 |  |  | 76.9699 |  |  | 36.8167 |  |  | -24.8013 |  |  | -101.5279 |  |  | -177.2849 |  |  | -245.2689 |  |  | -329.8896
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48487 |  |  | 0.48001 |  |  | 0.45496 |  |  | 0.37129 |  |  | 0.1776 |  |  | -0.11964 |  |  | -0.48975 |  |  | -0.85519 |  |  | -1.1831 |  |  | -1.5913
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5157 |  |  | 49.5077 |  |  | 44.3144 |  |  | 26.9699 |  |  | -13.1833 |  |  | -74.8013 |  |  | -151.5279 |  |  | -227.2849 |  |  | -295.2689 |  |  | -379.8896
[13 empty] | Press drop ratio this iteration |  |  | 0.50257 |  |  | 0.49753 |  |  | 0.46986 |  |  | 0.3504 |  |  | -0.35808 |  |  | 3.016 |  |  | 1.4925 |  |  | 1.282 |  |  | 1.2039 |  |  | 1.1516
[13 empty] | Expansion factor | 12 |  | 0.73826 |  |  | 0.74094 |  |  | 0.75168 |  |  | 0.81227 |  |  | 1.1971 |  |  | -0.75485 |  |  | 0.071685 |  |  | 0.12874 |  |  | 0.3239 |  |  | 0.018203
[13 empty] | C Non choked w/ reducers | 5 |  | 0.57695 |  |  | 6.9833 |  |  | 18.5236 |  |  | 47.6471 |  |  | #NUM! |  |  | -129.3294 |  |  | 621.094 |  |  | 265.9638 |  |  | 99.9305 |  |  | 1981.5311
[13 empty] | C Choked w/ reducers | 5 |  | 0.56587 |  |  | 6.8388 |  |  | 18.0177 |  |  | 43.5447 |  |  | 153.5674 |  |  | 335.8254 |  |  | 111.3951 |  |  | 82.9921 |  |  | 69.1112 |  |  | 92.8096
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.57695 |  |  | 6.9833 |  |  | 18.5236 |  |  | 47.6471 |  |  | #NUM! |  |  | 335.8254 |  |  | 111.3951 |  |  | 82.9921 |  |  | 69.1112 |  |  | 92.8096
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.423 | 133.4218 |  | 1.9833 | 1595.4675 |  | 8.5236 | 3945.7809 |  | 30.4471 | 7685.3741 |  | 7174 | 12639.6108 |  | 7174 | 17728.0272 |  | 7174 | 22509.8904 |  | 7174 | 26394.6168 |  | 7174 | 29447.6385 |  | 7174 | 32853.7982
[13 empty] | Next iteration flow rate |  |  | 136.0902 | Abs Value of | Flow this | 1611.4221 | Abs Value of | Flow this | 3985.2387 | Abs Value of | Flow this | 7762.2278 | Abs Value of | Flow this | 12766.0069 | Abs Value of | Flow this | 17905.3075 | Abs Value of | Flow this | 22734.9894 | Abs Value of | Flow this | 26658.563 | Abs Value of | Flow this | 29742.1149 | Abs Value of | Flow this | 33182.3362 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5154 |  |  | 99.4873 |  |  | 94.1896 |  |  | 76.4965 |  |  | 35.5362 |  |  | -27.3203 |  |  | -105.5891 |  |  | -182.8689 |  |  | -252.2193 |  |  | -338.5409
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48487 |  |  | 0.47991 |  |  | 0.45435 |  |  | 0.36901 |  |  | 0.17142 |  |  | -0.13179 |  |  | -0.50934 |  |  | -0.88213 |  |  | -1.2167 |  |  | -1.6331
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5154 |  |  | 49.4873 |  |  | 44.1896 |  |  | 26.4965 |  |  | -14.4638 |  |  | -77.3203 |  |  | -155.5891 |  |  | -232.8689 |  |  | -302.2193 |  |  | -388.5409
[13 empty] | Press drop ratio this iteration |  |  | 0.50256 |  |  | 0.49742 |  |  | 0.46916 |  |  | 0.34638 |  |  | -0.40702 |  |  | 2.8301 |  |  | 1.4735 |  |  | 1.2734 |  |  | 1.1982 |  |  | 1.1477
[13 empty] | Expansion factor | 12 |  | 0.73826 |  |  | 0.74099 |  |  | 0.75205 |  |  | 0.81443 |  |  | 1.224 |  |  | -0.6467 |  |  | 0.083466 |  |  | 0.13459 |  |  | 0.32705 |  |  | 0.021505
[13 empty] | C Non choked w/ reducers | 5 |  | 0.58849 |  |  | 7.0548 |  |  | 18.7383 |  |  | 48.5728 |  |  | #NUM! |  |  | -142.8834 |  |  | 521.3543 |  |  | 249.9375 |  |  | 97.4292 |  |  | 1653.527
[13 empty] | C Choked w/ reducers | 5 |  | 0.57719 |  |  | 6.9086 |  |  | 18.222 |  |  | 44.2524 |  |  | 160.692 |  |  | 307.9099 |  |  | 108.1816 |  |  | 81.2625 |  |  | 67.8788 |  |  | 91.3423
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.58849 |  |  | 7.0548 |  |  | 18.7383 |  |  | 48.5728 |  |  | #NUM! |  |  | 307.9099 |  |  | 108.1816 |  |  | 81.2625 |  |  | 67.8788 |  |  | 91.3423
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.4115 | 136.0902 |  | 2.0548 | 1611.4221 |  | 8.7383 | 3985.2387 |  | 31.3728 | 7762.2278 |  | 7174 | 12766.0069 |  | 7174 | 17905.3075 |  | 7174 | 22734.9894 |  | 7174 | 26658.563 |  | 7174 | 29742.1149 |  | 7174 | 33182.3362
[13 empty] | Next iteration flow rate |  |  | 138.812 | Abs Value of | Flow this | 1627.5364 | Abs Value of | Flow this | 4025.0911 | Abs Value of | Flow this | 7839.8501 | Abs Value of | Flow this | 12893.667 | Abs Value of | Flow this | 18084.3606 | Abs Value of | Flow this | 22962.3392 | Abs Value of | Flow this | 26925.1486 | Abs Value of | Flow this | 30039.5361 | Abs Value of | Flow this | 33514.1595 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5151 |  |  | 99.4665 |  |  | 94.0623 |  |  | 76.0136 |  |  | 34.23 |  |  | -29.8899 |  |  | -109.732 |  |  | -188.565 |  |  | -259.3094 |  |  | -347.3661
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48487 |  |  | 0.47981 |  |  | 0.45374 |  |  | 0.36668 |  |  | 0.16512 |  |  | -0.14418 |  |  | -0.52933 |  |  | -0.9096 |  |  | -1.2509 |  |  | -1.6756
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5151 |  |  | 49.4665 |  |  | 44.0623 |  |  | 26.0136 |  |  | -15.77 |  |  | -79.8899 |  |  | -159.732 |  |  | -238.565 |  |  | -309.3094 |  |  | -397.3661
[13 empty] | Press drop ratio this iteration |  |  | 0.50256 |  |  | 0.49732 |  |  | 0.46844 |  |  | 0.34222 |  |  | -0.46071 |  |  | 2.6728 |  |  | 1.4557 |  |  | 1.2652 |  |  | 1.1928 |  |  | 1.1439
[13 empty] | Expansion factor | 12 |  | 0.73826 |  |  | 0.74105 |  |  | 0.75243 |  |  | 0.81665 |  |  | 1.2536 |  |  | -0.55515 |  |  | 0.094586 |  |  | 0.1402 |  |  | 0.3301 |  |  | 0.024704
[13 empty] | C Non choked w/ reducers | 5 |  | 0.60027 |  |  | 7.1271 |  |  | 18.9563 |  |  | 49.5335 |  |  | #NUM! |  |  | -158.1152 |  |  | 449.8564 |  |  | 235.776 |  |  | 95.0455 |  |  | 1419.1844
[13 empty] | C Choked w/ reducers | 5 |  | 0.58874 |  |  | 6.9792 |  |  | 18.4291 |  |  | 44.9789 |  |  | 168.4923 |  |  | 284.2531 |  |  | 105.1383 |  |  | 79.5958 |  |  | 66.683 |  |  | 89.9119
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.60027 |  |  | 7.1271 |  |  | 18.9563 |  |  | 49.5335 |  |  | #NUM! |  |  | 284.2531 |  |  | 105.1383 |  |  | 79.5958 |  |  | 66.683 |  |  | 89.9119
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.3997 | 138.812 |  | 2.1271 | 1627.5364 |  | 8.9563 | 4025.0911 |  | 32.3335 | 7839.8501 |  | 7174 | 12893.667 |  | 7174 | 18084.3606 |  | 7174 | 22962.3392 |  | 7174 | 26925.1486 |  | 7174 | 30039.5361 |  | 7174 | 33514.1595
[13 empty] | Next iteration flow rate |  |  | 141.5883 | Abs Value of | Flow this | 1643.8117 | Abs Value of | Flow this | 4065.342 | Abs Value of | Flow this | 7918.2486 | Abs Value of | Flow this | 13022.6037 | Abs Value of | Flow this | 18265.2042 | Abs Value of | Flow this | 23191.9626 | Abs Value of | Flow this | 27194.4001 | Abs Value of | Flow this | 30339.9314 | Abs Value of | Flow this | 33849.3011 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5148 |  |  | 99.4453 |  |  | 93.9324 |  |  | 75.521 |  |  | 32.8975 |  |  | -32.5112 |  |  | -113.9581 |  |  | -194.3757 |  |  | -266.542 |  |  | -356.3686
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48487 |  |  | 0.47971 |  |  | 0.45311 |  |  | 0.3643 |  |  | 0.15869 |  |  | -0.15683 |  |  | -0.54971 |  |  | -0.93763 |  |  | -1.2858 |  |  | -1.7191
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5148 |  |  | 49.4453 |  |  | 43.9324 |  |  | 25.521 |  |  | -17.1025 |  |  | -82.5112 |  |  | -163.9581 |  |  | -244.3757 |  |  | -316.542 |  |  | -406.3686
[13 empty] | Press drop ratio this iteration |  |  | 0.50256 |  |  | 0.49721 |  |  | 0.4677 |  |  | 0.33793 |  |  | -0.51987 |  |  | 2.5379 |  |  | 1.4388 |  |  | 1.2572 |  |  | 1.1876 |  |  | 1.1403
[13 empty] | Expansion factor | 12 |  | 0.73826 |  |  | 0.7411 |  |  | 0.75282 |  |  | 0.81895 |  |  | 1.2862 |  |  | -0.47668 |  |  | 0.1051 |  |  | 0.14559 |  |  | 0.33304 |  |  | 0.027805
[13 empty] | C Non choked w/ reducers | 5 |  | 0.61227 |  |  | 7.2001 |  |  | 19.1775 |  |  | 50.5316 |  |  | #NUM! |  |  | -175.4763 |  |  | 396.0571 |  |  | 223.1675 |  |  | 92.7708 |  |  | 1243.3634
[13 empty] | C Choked w/ reducers | 5 |  | 0.60052 |  |  | 7.0505 |  |  | 18.6391 |  |  | 45.725 |  |  | 177.0701 |  |  | 263.9479 |  |  | 102.2517 |  |  | 77.9885 |  |  | 65.5223 |  |  | 88.5169
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.61227 |  |  | 7.2001 |  |  | 19.1775 |  |  | 50.5316 |  |  | #NUM! |  |  | 263.9479 |  |  | 102.2517 |  |  | 77.9885 |  |  | 65.5223 |  |  | 88.5169
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.3877 | 141.5883 |  | 2.2001 | 1643.8117 |  | 9.1775 | 4065.342 |  | 33.3316 | 7918.2486 |  | 7174 | 13022.6037 |  | 7174 | 18265.2042 |  | 7174 | 23191.9626 |  | 7174 | 27194.4001 |  | 7174 | 30339.9314 |  | 7174 | 33849.3011
[13 empty] | Next iteration flow rate |  |  | 144.42 | Abs Value of | Flow this | 1660.2499 | Abs Value of | Flow this | 4105.9955 | Abs Value of | Flow this | 7997.4311 | Abs Value of | Flow this | 13152.8297 | Abs Value of | Flow this | 18447.8562 | Abs Value of | Flow this | 23423.8823 | Abs Value of | Flow this | 27466.3441 | Abs Value of | Flow this | 30643.3307 | Abs Value of | Flow this | 34187.7941 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5145 |  |  | 99.4236 |  |  | 93.8 |  |  | 75.0184 |  |  | 31.5382 |  |  | -35.1852 |  |  | -118.2692 |  |  | -200.3032 |  |  | -273.92 |  |  | -365.5521
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48486 |  |  | 0.4796 |  |  | 0.45247 |  |  | 0.36188 |  |  | 0.15213 |  |  | -0.16973 |  |  | -0.57051 |  |  | -0.96623 |  |  | -1.3213 |  |  | -1.7634
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5145 |  |  | 49.4236 |  |  | 43.8 |  |  | 25.0184 |  |  | -18.4618 |  |  | -85.1852 |  |  | -168.2692 |  |  | -250.3032 |  |  | -323.92 |  |  | -415.5521
[13 empty] | Press drop ratio this iteration |  |  | 0.50256 |  |  | 0.4971 |  |  | 0.46695 |  |  | 0.3335 |  |  | -0.58538 |  |  | 2.4211 |  |  | 1.4228 |  |  | 1.2496 |  |  | 1.1825 |  |  | 1.1368
[13 empty] | Expansion factor | 12 |  | 0.73826 |  |  | 0.74116 |  |  | 0.75321 |  |  | 0.82133 |  |  | 1.3222 |  |  | -0.40867 |  |  | 0.11504 |  |  | 0.15076 |  |  | 0.33587 |  |  | 0.03081
[13 empty] | C Non choked w/ reducers | 5 |  | 0.62452 |  |  | 7.274 |  |  | 19.402 |  |  | 51.5697 |  |  | #NUM! |  |  | -195.5692 |  |  | 354.0817 |  |  | 211.8661 |  |  | 90.5974 |  |  | 1106.5489
[13 empty] | C Choked w/ reducers | 5 |  | 0.61253 |  |  | 7.1225 |  |  | 18.8521 |  |  | 46.4916 |  |  | 186.5487 |  |  | 246.3274 |  |  | 99.5097 |  |  | 76.4375 |  |  | 64.395 |  |  | 87.1561
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.62452 |  |  | 7.274 |  |  | 19.402 |  |  | 51.5697 |  |  | #NUM! |  |  | 246.3274 |  |  | 99.5097 |  |  | 76.4375 |  |  | 64.395 |  |  | 87.1561
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.3755 | 144.42 |  | 2.274 | 1660.2499 |  | 9.402 | 4105.9955 |  | 34.3697 | 7997.4311 |  | 7174 | 13152.8297 |  | 7174 | 18447.8562 |  | 7174 | 23423.8823 |  | 7174 | 27466.3441 |  | 7174 | 30643.3307 |  | 7174 | 34187.7941
[13 empty] | Next iteration flow rate |  |  | 147.3084 | Abs Value of | Flow this | 1676.8524 | Abs Value of | Flow this | 4147.0554 | Abs Value of | Flow this | 8077.4054 | Abs Value of | Flow this | 13284.358 | Abs Value of | Flow this | 18632.3348 | Abs Value of | Flow this | 23658.1211 | Abs Value of | Flow this | 27741.0076 | Abs Value of | Flow this | 30949.764 | Abs Value of | Flow this | 34529.6721 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5141 |  |  | 99.4015 |  |  | 93.6649 |  |  | 74.5058 |  |  | 30.1516 |  |  | -37.9129 |  |  | -122.6669 |  |  | -206.3498 |  |  | -281.4463 |  |  | -374.9203
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48486 |  |  | 0.4795 |  |  | 0.45182 |  |  | 0.3594 |  |  | 0.14545 |  |  | -0.18289 |  |  | -0.59172 |  |  | -0.99539 |  |  | -1.3576 |  |  | -1.8085
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5141 |  |  | 49.4015 |  |  | 43.6649 |  |  | 24.5058 |  |  | -19.8484 |  |  | -87.9129 |  |  | -172.6669 |  |  | -256.3498 |  |  | -331.4463 |  |  | -424.9203
[13 empty] | Press drop ratio this iteration |  |  | 0.50256 |  |  | 0.49699 |  |  | 0.46618 |  |  | 0.32891 |  |  | -0.65829 |  |  | 2.3188 |  |  | 1.4076 |  |  | 1.2423 |  |  | 1.1777 |  |  | 1.1334
[13 empty] | Expansion factor | 12 |  | 0.73826 |  |  | 0.74122 |  |  | 0.75362 |  |  | 0.82378 |  |  | 1.3623 |  |  | -0.34918 |  |  | 0.12447 |  |  | 0.15573 |  |  | 0.33862 |  |  | 0.033724
[13 empty] | C Non choked w/ reducers | 5 |  | 0.63701 |  |  | 7.3486 |  |  | 19.6299 |  |  | 52.6506 |  |  | #NUM! |  |  | -219.2223 |  |  | 320.3979 |  |  | 201.6754 |  |  | 88.5183 |  |  | 997.0353
[13 empty] | C Choked w/ reducers | 5 |  | 0.62478 |  |  | 7.1953 |  |  | 19.0681 |  |  | 47.2796 |  |  | 197.0788 |  |  | 230.8909 |  |  | 96.9016 |  |  | 74.9396 |  |  | 63.2998 |  |  | 85.8281
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.63701 |  |  | 7.3486 |  |  | 19.6299 |  |  | 52.6506 |  |  | #NUM! |  |  | 230.8909 |  |  | 96.9016 |  |  | 74.9396 |  |  | 63.2998 |  |  | 85.8281
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.363 | 147.3084 |  | 2.3486 | 1676.8524 |  | 9.6299 | 4147.0554 |  | 35.4506 | 8077.4054 |  | 7174 | 13284.358 |  | 7174 | 18632.3348 |  | 7174 | 23658.1211 |  | 7174 | 27741.0076 |  | 7174 | 30949.764 |  | 7174 | 34529.6721
[13 empty] | Next iteration flow rate |  |  | 150.2546 | Abs Value of | Flow this | 1693.6209 | Abs Value of | Flow this | 4188.526 | Abs Value of | Flow this | 8158.1795 | Abs Value of | Flow this | 13417.2016 | Abs Value of | Flow this | 18818.6582 | Abs Value of | Flow this | 23894.7023 | Abs Value of | Flow this | 28018.4176 | Abs Value of | Flow this | 31259.2617 | Abs Value of | Flow this | 34874.9688 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5138 |  |  | 99.379 |  |  | 93.527 |  |  | 73.9828 |  |  | 28.7372 |  |  | -40.6955 |  |  | -127.153 |  |  | -212.5179 |  |  | -289.1239 |  |  | -384.4767
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48486 |  |  | 0.47939 |  |  | 0.45116 |  |  | 0.35688 |  |  | 0.13862 |  |  | -0.19631 |  |  | -0.61336 |  |  | -1.0251 |  |  | -1.3947 |  |  | -1.8546
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5138 |  |  | 49.379 |  |  | 43.527 |  |  | 23.9828 |  |  | -21.2628 |  |  | -90.6955 |  |  | -177.153 |  |  | -262.5179 |  |  | -339.1239 |  |  | -434.4767
[13 empty] | Press drop ratio this iteration |  |  | 0.50256 |  |  | 0.49688 |  |  | 0.4654 |  |  | 0.32417 |  |  | -0.73991 |  |  | 2.2286 |  |  | 1.3932 |  |  | 1.2353 |  |  | 1.1729 |  |  | 1.13
[13 empty] | Expansion factor | 12 |  | 0.73826 |  |  | 0.74128 |  |  | 0.75403 |  |  | 0.82633 |  |  | 1.4073 |  |  | -0.29672 |  |  | 0.13342 |  |  | 0.16051 |  |  | 0.34127 |  |  | 0.03655
[13 empty] | C Non choked w/ reducers | 5 |  | 0.64976 |  |  | 7.424 |  |  | 19.8612 |  |  | 53.7775 |  |  | #NUM! |  |  | -247.6125 |  |  | 292.7538 |  |  | 192.4366 |  |  | 86.5273 |  |  | 907.3751
[13 empty] | C Choked w/ reducers | 5 |  | 0.63728 |  |  | 7.2689 |  |  | 19.2872 |  |  | 48.0899 |  |  | 208.847 |  |  | 217.2547 |  |  | 94.4176 |  |  | 73.4922 |  |  | 62.235 |  |  | 84.5318
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.64976 |  |  | 7.424 |  |  | 19.8612 |  |  | 53.7775 |  |  | #NUM! |  |  | 217.2547 |  |  | 94.4176 |  |  | 73.4922 |  |  | 62.235 |  |  | 84.5318
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.3502 | 150.2546 |  | 2.424 | 1693.6209 |  | 9.8612 | 4188.526 |  | 36.5775 | 8158.1795 |  | 7174 | 13417.2016 |  | 7174 | 18818.6582 |  | 7174 | 23894.7023 |  | 7174 | 28018.4176 |  | 7174 | 31259.2617 |  | 7174 | 34874.9688
[13 empty] | Next iteration flow rate |  |  | 153.2597 | Abs Value of | Flow this | 1710.5571 | Abs Value of | Flow this | 4230.4112 | Abs Value of | Flow this | 8239.7613 | Abs Value of | Flow this | 13551.3736 | Abs Value of | Flow this | 19006.8447 | Abs Value of | Flow this | 24133.6493 | Abs Value of | Flow this | 28298.6018 | Abs Value of | Flow this | 31571.8543 | Abs Value of | Flow this | 35223.7185 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5134 |  |  | 99.356 |  |  | 93.3864 |  |  | 73.4494 |  |  | 27.2943 |  |  | -43.534 |  |  | -131.7293 |  |  | -218.81 |  |  | -296.9558 |  |  | -394.2251
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48486 |  |  | 0.47928 |  |  | 0.45048 |  |  | 0.35431 |  |  | 0.13166 |  |  | -0.21 |  |  | -0.63544 |  |  | -1.0555 |  |  | -1.4325 |  |  | -1.9017
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5134 |  |  | 49.356 |  |  | 43.3864 |  |  | 23.4494 |  |  | -22.7057 |  |  | -93.534 |  |  | -181.7293 |  |  | -268.81 |  |  | -346.9558 |  |  | -444.2251
[13 empty] | Press drop ratio this iteration |  |  | 0.50255 |  |  | 0.49676 |  |  | 0.46459 |  |  | 0.31926 |  |  | -0.83189 |  |  | 2.1485 |  |  | 1.3796 |  |  | 1.2285 |  |  | 1.1684 |  |  | 1.1268
[13 empty] | Expansion factor | 12 |  | 0.73826 |  |  | 0.74134 |  |  | 0.75446 |  |  | 0.82896 |  |  | 1.4579 |  |  | -0.2501 |  |  | 0.14191 |  |  | 0.16511 |  |  | 0.34383 |  |  | 0.039291
[13 empty] | C Non choked w/ reducers | 5 |  | 0.66275 |  |  | 7.5002 |  |  | 20.0961 |  |  | 54.9538 |  |  | #NUM! |  |  | -282.4748 |  |  | 269.646 |  |  | 184.0198 |  |  | 84.6184 |  |  | 832.6042
[13 empty] | C Choked w/ reducers | 5 |  | 0.65003 |  |  | 7.3433 |  |  | 19.5094 |  |  | 48.9236 |  |  | 222.0864 |  |  | 205.1203 |  |  | 92.0489 |  |  | 72.0926 |  |  | 61.1996 |  |  | 83.2659
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.66275 |  |  | 7.5002 |  |  | 20.0961 |  |  | 54.9538 |  |  | #NUM! |  |  | 205.1203 |  |  | 92.0489 |  |  | 72.0926 |  |  | 61.1996 |  |  | 83.2659
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.3372 | 153.2597 |  | 2.5002 | 1710.5571 |  | 10.0961 | 4230.4112 |  | 37.7538 | 8239.7613 |  | 7174 | 13551.3736 |  | 7174 | 19006.8447 |  | 7174 | 24133.6493 |  | 7174 | 28298.6018 |  | 7174 | 31571.8543 |  | 7174 | 35223.7185
[13 empty] | Next iteration flow rate |  |  | 156.3249 | Abs Value of | Flow this | 1727.6627 | Abs Value of | Flow this | 4272.7153 | Abs Value of | Flow this | 8322.1589 | Abs Value of | Flow this | 13686.8873 | Abs Value of | Flow this | 19196.9132 | Abs Value of | Flow this | 24374.9858 | Abs Value of | Flow this | 28581.5878 | Abs Value of | Flow this | 31887.5728 | Abs Value of | Flow this | 35575.9557 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.513 |  |  | 99.3326 |  |  | 93.243 |  |  | 72.9052 |  |  | 25.8224 |  |  | -46.4295 |  |  | -136.3975 |  |  | -225.2286 |  |  | -304.9451 |  |  | -404.1696
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48486 |  |  | 0.47916 |  |  | 0.44979 |  |  | 0.35168 |  |  | 0.12456 |  |  | -0.22397 |  |  | -0.65796 |  |  | -1.0865 |  |  | -1.471 |  |  | -1.9496
[13 empty] | Delta P at this iteration flow rate |  |  | 50.513 |  |  | 49.3326 |  |  | 43.243 |  |  | 22.9052 |  |  | -24.1776 |  |  | -96.4295 |  |  | -186.3975 |  |  | -275.2286 |  |  | -354.9451 |  |  | -454.1696
[13 empty] | Press drop ratio this iteration |  |  | 0.50255 |  |  | 0.49664 |  |  | 0.46377 |  |  | 0.31418 |  |  | -0.9363 |  |  | 2.0769 |  |  | 1.3666 |  |  | 1.222 |  |  | 1.164 |  |  | 1.1237
[13 empty] | Expansion factor | 12 |  | 0.73827 |  |  | 0.7414 |  |  | 0.7549 |  |  | 0.83168 |  |  | 1.5154 |  |  | -0.20843 |  |  | 0.14999 |  |  | 0.16954 |  |  | 0.3463 |  |  | 0.041952
[13 empty] | C Non choked w/ reducers | 5 |  | 0.67601 |  |  | 7.5773 |  |  | 20.3346 |  |  | 56.1835 |  |  | #NUM! |  |  | -326.4838 |  |  | 250.0323 |  |  | 176.3179 |  |  | 82.7865 |  |  | 769.2863
[13 empty] | C Choked w/ reducers | 5 |  | 0.66303 |  |  | 7.4185 |  |  | 19.7348 |  |  | 49.7817 |  |  | 237.0929 |  |  | 194.2514 |  |  | 89.7875 |  |  | 70.7385 |  |  | 60.1922 |  |  | 82.0293
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.67601 |  |  | 7.5773 |  |  | 20.3346 |  |  | 56.1835 |  |  | #NUM! |  |  | 194.2514 |  |  | 89.7875 |  |  | 70.7385 |  |  | 60.1922 |  |  | 82.0293
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.324 | 156.3249 |  | 2.5773 | 1727.6627 |  | 10.3346 | 4272.7153 |  | 38.9835 | 8322.1589 |  | 7174 | 13686.8873 |  | 7174 | 19196.9132 |  | 7174 | 24374.9858 |  | 7174 | 28581.5878 |  | 7174 | 31887.5728 |  | 7174 | 35575.9557
[13 empty] | Next iteration flow rate |  |  | 159.4514 | Abs Value of | Flow this | 1744.9393 | Abs Value of | Flow this | 4315.4425 | Abs Value of | Flow this | 8405.3805 | Abs Value of | Flow this | 13823.7562 | Abs Value of | Flow this | 19388.8823 | Abs Value of | Flow this | 24618.7357 | Abs Value of | Flow this | 28867.4037 | Abs Value of | Flow this | 32206.4486 | Abs Value of | Flow this | 35931.7152 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5126 |  |  | 99.3086 |  |  | 93.0966 |  |  | 72.3501 |  |  | 24.3209 |  |  | -49.3833 |  |  | -141.1596 |  |  | -231.7762 |  |  | -313.0951 |  |  | -414.3139
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48486 |  |  | 0.47905 |  |  | 0.44908 |  |  | 0.349 |  |  | 0.11732 |  |  | -0.23822 |  |  | -0.68093 |  |  | -1.118 |  |  | -1.5103 |  |  | -1.9986
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5126 |  |  | 49.3086 |  |  | 43.0966 |  |  | 22.3501 |  |  | -25.6791 |  |  | -99.3833 |  |  | -191.1596 |  |  | -281.7762 |  |  | -363.0951 |  |  | -464.3139
[13 empty] | Press drop ratio this iteration |  |  | 0.50255 |  |  | 0.49652 |  |  | 0.46292 |  |  | 0.30892 |  |  | -1.0558 |  |  | 2.0125 |  |  | 1.3542 |  |  | 1.2157 |  |  | 1.1597 |  |  | 1.1207
[13 empty] | Expansion factor | 12 |  | 0.73827 |  |  | 0.74146 |  |  | 0.75534 |  |  | 0.8345 |  |  | 1.5812 |  |  | -0.17095 |  |  | 0.15769 |  |  | 0.1738 |  |  | 0.3487 |  |  | 0.044534
[13 empty] | C Non choked w/ reducers | 5 |  | 0.68954 |  |  | 7.6552 |  |  | 20.5768 |  |  | 57.4708 |  |  | #NUM! |  |  | -383.9942 |  |  | 233.1676 |  |  | 169.2415 |  |  | 81.0268 |  |  | 714.9673
[13 empty] | C Choked w/ reducers | 5 |  | 0.67629 |  |  | 7.4945 |  |  | 19.9634 |  |  | 50.6652 |  |  | 254.2474 |  |  | 184.459 |  |  | 87.626 |  |  | 69.4276 |  |  | 59.2116 |  |  | 80.8211
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.68954 |  |  | 7.6552 |  |  | 20.5768 |  |  | 57.4708 |  |  | #NUM! |  |  | 184.459 |  |  | 87.626 |  |  | 69.4276 |  |  | 59.2116 |  |  | 80.8211
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.3105 | 159.4514 |  | 2.6552 | 1744.9393 |  | 10.5768 | 4315.4425 |  | 40.2708 | 8405.3805 |  | 7174 | 13823.7562 |  | 7174 | 19388.8823 |  | 7174 | 24618.7357 |  | 7174 | 28867.4037 |  | 7174 | 32206.4486 |  | 7174 | 35931.7152
[13 empty] | Next iteration flow rate |  |  | 162.6404 | Abs Value of | Flow this | 1762.3887 | Abs Value of | Flow this | 4358.5969 | Abs Value of | Flow this | 8489.4343 | Abs Value of | Flow this | 13961.9938 | Abs Value of | Flow this | 19582.7711 | Abs Value of | Flow this | 24864.923 | Abs Value of | Flow this | 29156.0778 | Abs Value of | Flow this | 32528.5131 | Abs Value of | Flow this | 36291.0324 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5122 |  |  | 99.2842 |  |  | 92.9474 |  |  | 71.7838 |  |  | 22.7892 |  |  | -52.3964 |  |  | -146.0175 |  |  | -238.4554 |  |  | -321.4088 |  |  | -424.6621
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48485 |  |  | 0.47893 |  |  | 0.44836 |  |  | 0.34627 |  |  | 0.10993 |  |  | -0.25275 |  |  | -0.70436 |  |  | -1.1503 |  |  | -1.5504 |  |  | -2.0485
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5122 |  |  | 49.2842 |  |  | 42.9474 |  |  | 21.7838 |  |  | -27.2108 |  |  | -102.3964 |  |  | -196.0175 |  |  | -288.4554 |  |  | -371.4088 |  |  | -474.6621
[13 empty] | Press drop ratio this iteration |  |  | 0.50255 |  |  | 0.4964 |  |  | 0.46206 |  |  | 0.30346 |  |  | -1.194 |  |  | 1.9543 |  |  | 1.3424 |  |  | 1.2097 |  |  | 1.1556 |  |  | 1.1177
[13 empty] | Expansion factor | 12 |  | 0.73827 |  |  | 0.74153 |  |  | 0.7558 |  |  | 0.83742 |  |  | 1.6572 |  |  | -0.13707 |  |  | 0.16502 |  |  | 0.17791 |  |  | 0.35102 |  |  | 0.047042
[13 empty] | C Non choked w/ reducers | 5 |  | 0.70333 |  |  | 7.734 |  |  | 20.8228 |  |  | 58.8207 |  |  | #NUM! |  |  | -462.6126 |  |  | 218.5049 |  |  | 162.7159 |  |  | 79.3348 |  |  | 667.8475
[13 empty] | C Choked w/ reducers | 5 |  | 0.68982 |  |  | 7.5713 |  |  | 20.1955 |  |  | 51.5756 |  |  | 274.0486 |  |  | 175.59 |  |  | 85.5579 |  |  | 68.1577 |  |  | 58.2568 |  |  | 79.6401
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.70333 |  |  | 7.734 |  |  | 20.8228 |  |  | 58.8207 |  |  | #NUM! |  |  | 175.59 |  |  | 85.5579 |  |  | 68.1577 |  |  | 58.2568 |  |  | 79.6401
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.2967 | 162.6404 |  | 2.734 | 1762.3887 |  | 10.8228 | 4358.5969 |  | 41.6207 | 8489.4343 |  | 7174 | 13961.9938 |  | 7174 | 19582.7711 |  | 7174 | 24864.923 |  | 7174 | 29156.0778 |  | 7174 | 32528.5131 |  | 7174 | 36291.0324
[13 empty] | Next iteration flow rate |  |  | 165.8932 | Abs Value of | Flow this | 1780.0126 | Abs Value of | Flow this | 4402.1829 | Abs Value of | Flow this | 8574.3286 | Abs Value of | Flow this | 14101.6137 | Abs Value of | Flow this | 19778.5989 | Abs Value of | Flow this | 25113.5723 | Abs Value of | Flow this | 29447.6385 | Abs Value of | Flow this | 32853.7982 | Abs Value of | Flow this | 36653.9427 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5118 |  |  | 99.2593 |  |  | 92.7951 |  |  | 71.2062 |  |  | 21.2268 |  |  | -55.47 |  |  | -150.9729 |  |  | -245.2689 |  |  | -329.8896 |  |  | -435.2183
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48485 |  |  | 0.47881 |  |  | 0.44763 |  |  | 0.34349 |  |  | 0.10239 |  |  | -0.26758 |  |  | -0.72827 |  |  | -1.1831 |  |  | -1.5913 |  |  | -2.0994
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5118 |  |  | 49.2593 |  |  | 42.7951 |  |  | 21.2062 |  |  | -28.7732 |  |  | -105.47 |  |  | -200.9729 |  |  | -295.2689 |  |  | -379.8896 |  |  | -485.2183
[13 empty] | Press drop ratio this iteration |  |  | 0.50255 |  |  | 0.49627 |  |  | 0.46118 |  |  | 0.29781 |  |  | -1.3555 |  |  | 1.9014 |  |  | 1.3312 |  |  | 1.2039 |  |  | 1.1516 |  |  | 1.1149
[13 empty] | Expansion factor | 12 |  | 0.73827 |  |  | 0.74159 |  |  | 0.75626 |  |  | 0.84044 |  |  | 1.7461 |  |  | -0.10631 |  |  | 0.17201 |  |  | 0.18186 |  |  | 0.35327 |  |  | 0.049476
[13 empty] | C Non choked w/ reducers | 5 |  | 0.7174 |  |  | 7.8136 |  |  | 21.0726 |  |  | 60.2386 |  |  | #NUM! |  |  | -576.9368 |  |  | 205.6335 |  |  | 156.6775 |  |  | 77.7064 |  |  | 626.5774
[13 empty] | C Choked w/ reducers | 5 |  | 0.70362 |  |  | 7.6489 |  |  | 20.4309 |  |  | 52.5139 |  |  | 297.1628 |  |  | 167.5189 |  |  | 83.5771 |  |  | 66.927 |  |  | 57.3267 |  |  | 78.4855
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.7174 |  |  | 7.8136 |  |  | 21.0726 |  |  | 60.2386 |  |  | #NUM! |  |  | 167.5189 |  |  | 83.5771 |  |  | 66.927 |  |  | 57.3267 |  |  | 78.4855
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.2826 | 165.8932 |  | 2.8136 | 1780.0126 |  | 11.0726 | 4402.1829 |  | 43.0386 | 8574.3286 |  | 7174 | 14101.6137 |  | 7174 | 19778.5989 |  | 7174 | 25113.5723 |  | 7174 | 29447.6385 |  | 7174 | 32853.7982 |  | 7174 | 36653.9427
[13 empty] | Next iteration flow rate |  |  | 169.2111 | Abs Value of | Flow this | 1797.8127 | Abs Value of | Flow this | 4446.2047 | Abs Value of | Flow this | 8660.0719 | Abs Value of | Flow this | 14242.6298 | Abs Value of | Flow this | 19976.3848 | Abs Value of | Flow this | 25364.708 | Abs Value of | Flow this | 29742.1149 | Abs Value of | Flow this | 33182.3362 | Abs Value of | Flow this | 37020.4821 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5114 |  |  | 99.2339 |  |  | 92.6398 |  |  | 70.6169 |  |  | 19.6329 |  |  | -58.6055 |  |  | -156.028 |  |  | -252.2193 |  |  | -338.5409 |  |  | -445.9867
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48485 |  |  | 0.47869 |  |  | 0.44688 |  |  | 0.34064 |  |  | 0.094706 |  |  | -0.2827 |  |  | -0.75265 |  |  | -1.2167 |  |  | -1.6331 |  |  | -2.1514
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5114 |  |  | 49.2339 |  |  | 42.6398 |  |  | 20.6169 |  |  | -30.3671 |  |  | -108.6055 |  |  | -206.028 |  |  | -302.2193 |  |  | -388.5409 |  |  | -495.9867
[13 empty] | Press drop ratio this iteration |  |  | 0.50254 |  |  | 0.49614 |  |  | 0.46027 |  |  | 0.29195 |  |  | -1.5467 |  |  | 1.8532 |  |  | 1.3205 |  |  | 1.1982 |  |  | 1.1477 |  |  | 1.1121
[13 empty] | Expansion factor | 12 |  | 0.73827 |  |  | 0.74166 |  |  | 0.75674 |  |  | 0.84358 |  |  | 1.8514 |  |  | -0.078248 |  |  | 0.17868 |  |  | 0.18568 |  |  | 0.35544 |  |  | 0.051841
[13 empty] | C Non choked w/ reducers | 5 |  | 0.73175 |  |  | 7.894 |  |  | 21.3265 |  |  | 61.7307 |  |  | #NUM! |  |  | -758.9952 |  |  | 194.2393 |  |  | 151.0725 |  |  | 76.138 |  |  | 590.1249
[13 empty] | C Choked w/ reducers | 5 |  | 0.7177 |  |  | 7.7274 |  |  | 20.6698 |  |  | 53.4816 |  |  | 324.5 |  |  | 160.1421 |  |  | 81.6781 |  |  | 65.7335 |  |  | 56.4204 |  |  | 77.3564
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.73175 |  |  | 7.894 |  |  | 21.3265 |  |  | 61.7307 |  |  | #NUM! |  |  | 160.1421 |  |  | 81.6781 |  |  | 65.7335 |  |  | 56.4204 |  |  | 77.3564
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.2682 | 169.2111 |  | 2.894 | 1797.8127 |  | 11.3265 | 4446.2047 |  | 44.5307 | 8660.0719 |  | 7174 | 14242.6298 |  | 7174 | 19976.3848 |  | 7174 | 25364.708 |  | 7174 | 29742.1149 |  | 7174 | 33182.3362 |  | 7174 | 37020.4821
[13 empty] | Next iteration flow rate |  |  | 172.5953 | Abs Value of | Flow this | 1815.7908 | Abs Value of | Flow this | 4490.6668 | Abs Value of | Flow this | 8746.6726 | Abs Value of | Flow this | 14385.0561 | Abs Value of | Flow this | 20176.1487 | Abs Value of | Flow this | 25618.3551 | Abs Value of | Flow this | 30039.5361 | Abs Value of | Flow this | 33514.1595 | Abs Value of | Flow this | 37390.687 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5109 |  |  | 99.208 |  |  | 92.4813 |  |  | 70.0158 |  |  | 18.0071 |  |  | -61.804 |  |  | -161.1847 |  |  | -259.3094 |  |  | -347.3661 |  |  | -456.9716
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48485 |  |  | 0.47856 |  |  | 0.44611 |  |  | 0.33774 |  |  | 0.086863 |  |  | -0.29813 |  |  | -0.77753 |  |  | -1.2509 |  |  | -1.6756 |  |  | -2.2043
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5109 |  |  | 49.208 |  |  | 42.4813 |  |  | 20.0158 |  |  | -31.9929 |  |  | -111.804 |  |  | -211.1847 |  |  | -309.3094 |  |  | -397.3661 |  |  | -506.9716
[13 empty] | Press drop ratio this iteration |  |  | 0.50254 |  |  | 0.49601 |  |  | 0.45935 |  |  | 0.28588 |  |  | -1.7767 |  |  | 1.809 |  |  | 1.3102 |  |  | 1.1928 |  |  | 1.1439 |  |  | 1.1094
[13 empty] | Expansion factor | 12 |  | 0.73827 |  |  | 0.74173 |  |  | 0.75723 |  |  | 0.84684 |  |  | 1.978 |  |  | -0.052558 |  |  | 0.18506 |  |  | 0.18937 |  |  | 0.35755 |  |  | 0.054139
[13 empty] | C Non choked w/ reducers | 5 |  | 0.74639 |  |  | 7.9754 |  |  | 21.5844 |  |  | 63.3039 |  |  | #NUM! |  |  | -1095.3512 |  |  | 184.0775 |  |  | 145.8545 |  |  | 74.626 |  |  | 557.6876
[13 empty] | C Choked w/ reducers | 5 |  | 0.73205 |  |  | 7.8067 |  |  | 20.9123 |  |  | 54.4802 |  |  | 357.3376 |  |  | 153.3729 |  |  | 79.8556 |  |  | 64.5756 |  |  | 55.5369 |  |  | 76.2518
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.74639 |  |  | 7.9754 |  |  | 21.5844 |  |  | 63.3039 |  |  | #NUM! |  |  | 153.3729 |  |  | 79.8556 |  |  | 64.5756 |  |  | 55.5369 |  |  | 76.2518
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.2536 | 172.5953 |  | 2.9754 | 1815.7908 |  | 11.5844 | 4490.6668 |  | 46.1039 | 8746.6726 |  | 7174 | 14385.0561 |  | 7174 | 20176.1487 |  | 7174 | 25618.3551 |  | 7174 | 30039.5361 |  | 7174 | 33514.1595 |  | 7174 | 37390.687
[13 empty] | Next iteration flow rate |  |  | 176.0472 | Abs Value of | Flow this | 1833.9487 | Abs Value of | Flow this | 4535.5734 | Abs Value of | Flow this | 8834.1394 | Abs Value of | Flow this | 14528.9067 | Abs Value of | Flow this | 20377.9102 | Abs Value of | Flow this | 25874.5386 | Abs Value of | Flow this | 30339.9314 | Abs Value of | Flow this | 33849.3011 | Abs Value of | Flow this | 37764.5938 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5104 |  |  | 99.1816 |  |  | 92.3197 |  |  | 69.4026 |  |  | 16.3485 |  |  | -65.0667 |  |  | -166.445 |  |  | -266.542 |  |  | -356.3686 |  |  | -468.1772
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48484 |  |  | 0.47843 |  |  | 0.44533 |  |  | 0.33479 |  |  | 0.078862 |  |  | -0.31387 |  |  | -0.8029 |  |  | -1.2858 |  |  | -1.7191 |  |  | -2.2584
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5104 |  |  | 49.1816 |  |  | 42.3197 |  |  | 19.4026 |  |  | -33.6515 |  |  | -115.0667 |  |  | -216.445 |  |  | -316.542 |  |  | -406.3686 |  |  | -518.1772
[13 empty] | Press drop ratio this iteration |  |  | 0.50254 |  |  | 0.49587 |  |  | 0.4584 |  |  | 0.27957 |  |  | -2.0584 |  |  | 1.7684 |  |  | 1.3004 |  |  | 1.1876 |  |  | 1.1403 |  |  | 1.1068
[13 empty] | Expansion factor | 12 |  | 0.73827 |  |  | 0.7418 |  |  | 0.75773 |  |  | 0.85022 |  |  | 2.133 |  |  | -0.028954 |  |  | 0.19116 |  |  | 0.19292 |  |  | 0.35959 |  |  | 0.056372
[13 empty] | C Non choked w/ reducers | 5 |  | 0.76132 |  |  | 8.0576 |  |  | 21.8466 |  |  | 64.9663 |  |  | #NUM! |  |  | -1929.2507 |  |  | 174.955 |  |  | 140.9838 |  |  | 73.1674 |  |  | 528.6317
[13 empty] | C Choked w/ reducers | 5 |  | 0.7467 |  |  | 7.8869 |  |  | 21.1584 |  |  | 55.5112 |  |  | 397.5257 |  |  | 147.1389 |  |  | 78.1052 |  |  | 63.4515 |  |  | 54.6752 |  |  | 75.1711
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.76132 |  |  | 8.0576 |  |  | 21.8466 |  |  | 64.9663 |  |  | #NUM! |  |  | 147.1389 |  |  | 78.1052 |  |  | 63.4515 |  |  | 54.6752 |  |  | 75.1711
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.2387 | 176.0472 |  | 3.0576 | 1833.9487 |  | 11.8466 | 4535.5734 |  | 47.7663 | 8834.1394 |  | 7174 | 14528.9067 |  | 7174 | 20377.9102 |  | 7174 | 25874.5386 |  | 7174 | 30339.9314 |  | 7174 | 33849.3011 |  | 7174 | 37764.5938
[13 empty] | Next iteration flow rate |  |  | 179.5682 | Abs Value of | Flow this | 1852.2882 | Abs Value of | Flow this | 4580.9292 | Abs Value of | Flow this | 8922.4807 | Abs Value of | Flow this | 14674.1958 | Abs Value of | Flow this | 20581.6893 | Abs Value of | Flow this | 26133.284 | Abs Value of | Flow this | 30643.3307 | Abs Value of | Flow this | 34187.7941 | Abs Value of | Flow this | 38142.2398 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5099 |  |  | 99.1546 |  |  | 92.1548 |  |  | 68.7771 |  |  | 14.6566 |  |  | -68.3951 |  |  | -171.811 |  |  | -273.92 |  |  | -365.5521 |  |  | -479.6081
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48484 |  |  | 0.4783 |  |  | 0.44454 |  |  | 0.33177 |  |  | 0.070701 |  |  | -0.32993 |  |  | -0.82879 |  |  | -1.3213 |  |  | -1.7634 |  |  | -2.3135
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5099 |  |  | 49.1546 |  |  | 42.1548 |  |  | 18.7771 |  |  | -35.3434 |  |  | -118.3951 |  |  | -221.811 |  |  | -323.92 |  |  | -415.5521 |  |  | -529.6081
[13 empty] | Press drop ratio this iteration |  |  | 0.50254 |  |  | 0.49574 |  |  | 0.45743 |  |  | 0.27301 |  |  | -2.4114 |  |  | 1.731 |  |  | 1.291 |  |  | 1.1825 |  |  | 1.1368 |  |  | 1.1043
[13 empty] | Expansion factor | 12 |  | 0.73827 |  |  | 0.74187 |  |  | 0.75824 |  |  | 0.85373 |  |  | 2.3274 |  |  | -0.0071958 |  |  | 0.19699 |  |  | 0.19636 |  |  | 0.36157 |  |  | 0.058542
[13 empty] | C Non choked w/ reducers | 5 |  | 0.77655 |  |  | 8.1407 |  |  | 22.1129 |  |  | 66.7271 |  |  | #NUM! |  |  | -7538.9975 |  |  | 166.7169 |  |  | 136.4258 |  |  | 71.7591 |  |  | 502.4504
[13 empty] | C Choked w/ reducers | 5 |  | 0.76164 |  |  | 7.9679 |  |  | 21.4082 |  |  | 56.5762 |  |  | 447.8487 |  |  | 141.3784 |  |  | 76.4225 |  |  | 62.3599 |  |  | 53.8347 |  |  | 74.1132
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.77655 |  |  | 8.1407 |  |  | 22.1129 |  |  | 66.7271 |  |  | #NUM! |  |  | 141.3784 |  |  | 76.4225 |  |  | 62.3599 |  |  | 53.8347 |  |  | 74.1132
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.2234 | 179.5682 |  | 3.1407 | 1852.2882 |  | 12.1129 | 4580.9292 |  | 49.5271 | 8922.4807 |  | 7174 | 14674.1958 |  | 7174 | 20581.6893 |  | 7174 | 26133.284 |  | 7174 | 30643.3307 |  | 7174 | 34187.7941 |  | 7174 | 38142.2398
[13 empty] | Next iteration flow rate |  |  | 183.1595 | Abs Value of | Flow this | 1870.8111 | Abs Value of | Flow this | 4626.7385 | Abs Value of | Flow this | 9011.7056 | Abs Value of | Flow this | 14820.9377 | Abs Value of | Flow this | 20787.5062 | Abs Value of | Flow this | 26394.6168 | Abs Value of | Flow this | 30949.764 | Abs Value of | Flow this | 34529.6721 | Abs Value of | Flow this | 38523.6622 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5094 |  |  | 99.1271 |  |  | 91.9866 |  |  | 68.139 |  |  | 12.9307 |  |  | -71.7903 |  |  | -177.2849 |  |  | -281.4463 |  |  | -374.9203 |  |  | -491.2687
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48484 |  |  | 0.47817 |  |  | 0.44373 |  |  | 0.32869 |  |  | 0.062375 |  |  | -0.3463 |  |  | -0.85519 |  |  | -1.3576 |  |  | -1.8085 |  |  | -2.3698
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5094 |  |  | 49.1271 |  |  | 41.9866 |  |  | 18.139 |  |  | -37.0693 |  |  | -121.7903 |  |  | -227.2849 |  |  | -331.4463 |  |  | -424.9203 |  |  | -541.2687
[13 empty] | Press drop ratio this iteration |  |  | 0.50253 |  |  | 0.4956 |  |  | 0.45644 |  |  | 0.26621 |  |  | -2.8668 |  |  | 1.6965 |  |  | 1.282 |  |  | 1.1777 |  |  | 1.1334 |  |  | 1.1018
[13 empty] | Expansion factor | 12 |  | 0.73827 |  |  | 0.74194 |  |  | 0.75877 |  |  | 0.85738 |  |  | 2.578 |  |  | 0.012921 |  |  | 0.20258 |  |  | 0.19967 |  |  | 0.36349 |  |  | 0.060652
[13 empty] | C Non choked w/ reducers | 5 |  | 0.79209 |  |  | 8.2248 |  |  | 22.3837 |  |  | 68.5968 |  |  | #NUM! |  |  | 4080.9401 |  |  | 159.238 |  |  | 132.1504 |  |  | 70.3985 |  |  | 478.7334
[13 empty] | C Choked w/ reducers | 5 |  | 0.77687 |  |  | 8.0498 |  |  | 21.6618 |  |  | 57.6771 |  |  | 512.7011 |  |  | 136.0389 |  |  | 74.8034 |  |  | 61.2992 |  |  | 53.0144 |  |  | 73.0776
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.79209 |  |  | 8.2248 |  |  | 22.3837 |  |  | 68.5968 |  |  | #NUM! |  |  | 136.0389 |  |  | 74.8034 |  |  | 61.2992 |  |  | 53.0144 |  |  | 73.0776
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.2079 | 183.1595 |  | 3.2248 | 1870.8111 |  | 12.3837 | 4626.7385 |  | 51.3968 | 9011.7056 |  | 7174 | 14820.9377 |  | 7174 | 20787.5062 |  | 7174 | 26394.6168 |  | 7174 | 30949.764 |  | 7174 | 34529.6721 |  | 7174 | 38523.6622
[13 empty] | Next iteration flow rate |  |  | 186.8227 | Abs Value of | Flow this | 1889.5192 | Abs Value of | Flow this | 4673.0058 | Abs Value of | Flow this | 9101.8226 | Abs Value of | Flow this | 14969.1471 | Abs Value of | Flow this | 20995.3812 | Abs Value of | Flow this | 26658.563 | Abs Value of | Flow this | 31259.2617 | Abs Value of | Flow this | 34874.9688 | Abs Value of | Flow this | 38908.8988 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5089 |  |  | 99.0991 |  |  | 91.815 |  |  | 67.4881 |  |  | 11.1701 |  |  | -75.2538 |  |  | -182.8689 |  |  | -289.1239 |  |  | -384.4767 |  |  | -503.1637
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48484 |  |  | 0.47804 |  |  | 0.4429 |  |  | 0.32555 |  |  | 0.053882 |  |  | -0.36301 |  |  | -0.88213 |  |  | -1.3947 |  |  | -1.8546 |  |  | -2.4272
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5089 |  |  | 49.0991 |  |  | 41.815 |  |  | 17.4881 |  |  | -38.8299 |  |  | -125.2538 |  |  | -232.8689 |  |  | -339.1239 |  |  | -434.4767 |  |  | -553.1637
[13 empty] | Press drop ratio this iteration |  |  | 0.50253 |  |  | 0.49545 |  |  | 0.45543 |  |  | 0.25913 |  |  | -3.4762 |  |  | 1.6644 |  |  | 1.2734 |  |  | 1.1729 |  |  | 1.13 |  |  | 1.0994
[13 empty] | Expansion factor | 12 |  | 0.73828 |  |  | 0.74202 |  |  | 0.7593 |  |  | 0.86117 |  |  | 2.9135 |  |  | 0.031572 |  |  | 0.20794 |  |  | 0.20288 |  |  | 0.36535 |  |  | 0.062703
[13 empty] | C Non choked w/ reducers | 5 |  | 0.80794 |  |  | 8.3097 |  |  | 22.659 |  |  | 70.5876 |  |  | #NUM! |  |  | 1624.6402 |  |  | 152.4156 |  |  | 128.1313 |  |  | 69.083 |  |  | 457.1449
[13 empty] | C Choked w/ reducers | 5 |  | 0.79241 |  |  | 8.1326 |  |  | 21.9193 |  |  | 58.8157 |  |  | 599.447 |  |  | 131.0756 |  |  | 73.2445 |  |  | 60.2682 |  |  | 52.2137 |  |  | 72.0636
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.80794 |  |  | 8.3097 |  |  | 22.659 |  |  | 70.5876 |  |  | #NUM! |  |  | 131.0756 |  |  | 73.2445 |  |  | 60.2682 |  |  | 52.2137 |  |  | 72.0636
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.1921 | 186.8227 |  | 3.3097 | 1889.5192 |  | 12.659 | 4673.0058 |  | 53.3876 | 9101.8226 |  | 7174 | 14969.1471 |  | 7174 | 20995.3812 |  | 7174 | 26658.563 |  | 7174 | 31259.2617 |  | 7174 | 34874.9688 |  | 7174 | 38908.8988
[13 empty] | Next iteration flow rate |  |  | 190.5592 | Abs Value of | Flow this | 1908.4144 | Abs Value of | Flow this | 4719.7359 | Abs Value of | Flow this | 9192.8408 | Abs Value of | Flow this | 15118.8386 | Abs Value of | Flow this | 21205.335 | Abs Value of | Flow this | 26925.1486 | Abs Value of | Flow this | 31571.8543 | Abs Value of | Flow this | 35223.7185 | Abs Value of | Flow this | 39297.9878 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5083 |  |  | 99.0705 |  |  | 91.64 |  |  | 66.8241 |  |  | 9.3741 |  |  | -78.7869 |  |  | -188.565 |  |  | -296.9558 |  |  | -394.2251 |  |  | -515.2978
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48483 |  |  | 0.4779 |  |  | 0.44206 |  |  | 0.32235 |  |  | 0.045219 |  |  | -0.38005 |  |  | -0.9096 |  |  | -1.4325 |  |  | -1.9017 |  |  | -2.4857
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5083 |  |  | 49.0705 |  |  | 41.64 |  |  | 16.8241 |  |  | -40.6259 |  |  | -128.7869 |  |  | -238.565 |  |  | -346.9558 |  |  | -444.2251 |  |  | -565.2978
[13 empty] | Press drop ratio this iteration |  |  | 0.50253 |  |  | 0.49531 |  |  | 0.45439 |  |  | 0.25177 |  |  | -4.3338 |  |  | 1.6346 |  |  | 1.2652 |  |  | 1.1684 |  |  | 1.1268 |  |  | 1.097
[13 empty] | Expansion factor | 12 |  | 0.73828 |  |  | 0.74209 |  |  | 0.75985 |  |  | 0.86511 |  |  | 3.3855 |  |  | 0.048908 |  |  | 0.21307 |  |  | 0.20598 |  |  | 0.36716 |  |  | 0.064698
[13 empty] | C Non choked w/ reducers | 5 |  | 0.8241 |  |  | 8.3956 |  |  | 22.939 |  |  | 72.714 |  |  | #NUM! |  |  | 1020.9284 |  |  | 146.1649 |  |  | 124.3454 |  |  | 67.8103 |  |  | 437.4077
[13 empty] | C Choked w/ reducers | 5 |  | 0.80827 |  |  | 8.2163 |  |  | 22.1808 |  |  | 59.9941 |  |  | 721.4384 |  |  | 126.4497 |  |  | 71.7422 |  |  | 59.2654 |  |  | 51.4317 |  |  | 71.0703
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.8241 |  |  | 8.3956 |  |  | 22.939 |  |  | 72.714 |  |  | #NUM! |  |  | 126.4497 |  |  | 71.7422 |  |  | 59.2654 |  |  | 51.4317 |  |  | 71.0703
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.1759 | 190.5592 |  | 3.3956 | 1908.4144 |  | 12.939 | 4719.7359 |  | 55.514 | 9192.8408 |  | 7174 | 15118.8386 |  | 7174 | 21205.335 |  | 7174 | 26925.1486 |  | 7174 | 31571.8543 |  | 7174 | 35223.7185 |  | 7174 | 39297.9878
[13 empty] | Next iteration flow rate |  |  | 194.3704 | Abs Value of | Flow this | 1927.4985 | Abs Value of | Flow this | 4766.9333 | Abs Value of | Flow this | 9284.7692 | Abs Value of | Flow this | 15270.027 | Abs Value of | Flow this | 21417.3884 | Abs Value of | Flow this | 27194.4001 | Abs Value of | Flow this | 31887.5728 | Abs Value of | Flow this | 35575.9557 | Abs Value of | Flow this | 39690.9677 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5077 |  |  | 99.0413 |  |  | 91.4615 |  |  | 66.1467 |  |  | 7.542 |  |  | -82.3911 |  |  | -194.3757 |  |  | -304.9451 |  |  | -404.1696 |  |  | -527.6758
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48483 |  |  | 0.47776 |  |  | 0.44119 |  |  | 0.31908 |  |  | 0.036381 |  |  | -0.39744 |  |  | -0.93763 |  |  | -1.471 |  |  | -1.9496 |  |  | -2.5454
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5077 |  |  | 49.0413 |  |  | 41.4615 |  |  | 16.1467 |  |  | -42.458 |  |  | -132.3911 |  |  | -244.3757 |  |  | -354.9451 |  |  | -454.1696 |  |  | -577.6758
[13 empty] | Press drop ratio this iteration |  |  | 0.50253 |  |  | 0.49516 |  |  | 0.45332 |  |  | 0.2441 |  |  | -5.6295 |  |  | 1.6069 |  |  | 1.2572 |  |  | 1.164 |  |  | 1.1237 |  |  | 1.0948
[13 empty] | Expansion factor | 12 |  | 0.73828 |  |  | 0.74217 |  |  | 0.76042 |  |  | 0.86922 |  |  | 4.0987 |  |  | 0.06506 |  |  | 0.218 |  |  | 0.20898 |  |  | 0.36891 |  |  | 0.066639
[13 empty] | C Non choked w/ reducers | 5 |  | 0.84059 |  |  | 8.4825 |  |  | 23.2236 |  |  | 74.9927 |  |  | #NUM! |  |  | 747.6041 |  |  | 140.415 |  |  | 120.7722 |  |  | 66.5781 |  |  | 419.2907
[13 empty] | C Choked w/ reducers | 5 |  | 0.82444 |  |  | 8.3009 |  |  | 22.4463 |  |  | 61.2145 |  |  | 905.6557 |  |  | 122.1274 |  |  | 70.2936 |  |  | 58.2899 |  |  | 50.6679 |  |  | 70.0972
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.84059 |  |  | 8.4825 |  |  | 23.2236 |  |  | 74.9927 |  |  | #NUM! |  |  | 122.1274 |  |  | 70.2936 |  |  | 58.2899 |  |  | 50.6679 |  |  | 70.0972
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.1594 | 194.3704 |  | 3.4825 | 1927.4985 |  | 13.2236 | 4766.9333 |  | 57.7927 | 9284.7692 |  | 7174 | 15270.027 |  | 7174 | 21417.3884 |  | 7174 | 27194.4001 |  | 7174 | 31887.5728 |  | 7174 | 35575.9557 |  | 7174 | 39690.9677
[13 empty] | Next iteration flow rate |  |  | 198.2578 | Abs Value of | Flow this | 1946.7735 | Abs Value of | Flow this | 4814.6026 | Abs Value of | Flow this | 9377.6169 | Abs Value of | Flow this | 15422.7272 | Abs Value of | Flow this | 21631.5623 | Abs Value of | Flow this | 27466.3441 | Abs Value of | Flow this | 32206.4486 | Abs Value of | Flow this | 35931.7152 | Abs Value of | Flow this | 40087.8773 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5071 |  |  | 99.0115 |  |  | 91.2793 |  |  | 65.4558 |  |  | 5.6731 |  |  | -86.0676 |  |  | -200.3032 |  |  | -313.0951 |  |  | -414.3139 |  |  | -540.3026
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48483 |  |  | 0.47761 |  |  | 0.44032 |  |  | 0.31575 |  |  | 0.027366 |  |  | -0.41517 |  |  | -0.96623 |  |  | -1.5103 |  |  | -1.9986 |  |  | -2.6063
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5071 |  |  | 49.0115 |  |  | 41.2793 |  |  | 15.4558 |  |  | -44.3269 |  |  | -136.0676 |  |  | -250.3032 |  |  | -363.0951 |  |  | -464.3139 |  |  | -590.3026
[13 empty] | Press drop ratio this iteration |  |  | 0.50252 |  |  | 0.49501 |  |  | 0.45223 |  |  | 0.23613 |  |  | -7.8135 |  |  | 1.5809 |  |  | 1.2496 |  |  | 1.1597 |  |  | 1.1207 |  |  | 1.0925
[13 empty] | Expansion factor | 12 |  | 0.73828 |  |  | 0.74225 |  |  | 0.76099 |  |  | 0.87349 |  |  | 5.3009 |  |  | 0.080143 |  |  | 0.22274 |  |  | 0.21188 |  |  | 0.37061 |  |  | 0.068527
[13 empty] | C Non choked w/ reducers | 5 |  | 0.85741 |  |  | 8.5703 |  |  | 23.5132 |  |  | 77.4438 |  |  | #NUM! |  |  | 591.5777 |  |  | 135.1066 |  |  | 117.3938 |  |  | 65.3846 |  |  | 402.5996
[13 empty] | C Choked w/ reducers | 5 |  | 0.84093 |  |  | 8.3865 |  |  | 22.716 |  |  | 62.4793 |  |  | 1216.0503 |  |  | 118.0796 |  |  | 68.8955 |  |  | 57.3403 |  |  | 49.9216 |  |  | 69.1436
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.85741 |  |  | 8.5703 |  |  | 23.5132 |  |  | 77.4438 |  |  | #NUM! |  |  | 118.0796 |  |  | 68.8955 |  |  | 57.3403 |  |  | 49.9216 |  |  | 69.1436
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.1426 | 198.2578 |  | 3.5703 | 1946.7735 |  | 13.5132 | 4814.6026 |  | 60.2438 | 9377.6169 |  | 7174 | 15422.7272 |  | 7174 | 21631.5623 |  | 7174 | 27466.3441 |  | 7174 | 32206.4486 |  | 7174 | 35931.7152 |  | 7174 | 40087.8773
[13 empty] | Next iteration flow rate |  |  | 202.2229 | Abs Value of | Flow this | 1966.2413 | Abs Value of | Flow this | 4862.7486 | Abs Value of | Flow this | 9471.3931 | Abs Value of | Flow this | 15576.9545 | Abs Value of | Flow this | 21847.8779 | Abs Value of | Flow this | 27741.0076 | Abs Value of | Flow this | 32528.5131 | Abs Value of | Flow this | 36291.0324 | Abs Value of | Flow this | 40488.7561 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5065 |  |  | 98.9811 |  |  | 91.0935 |  |  | 64.7509 |  |  | 3.7666 |  |  | -89.8181 |  |  | -206.3498 |  |  | -321.4088 |  |  | -424.6621 |  |  | -553.1832
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48483 |  |  | 0.47747 |  |  | 0.43942 |  |  | 0.31235 |  |  | 0.018169 |  |  | -0.43327 |  |  | -0.99539 |  |  | -1.5504 |  |  | -2.0485 |  |  | -2.6685
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5065 |  |  | 48.9811 |  |  | 41.0935 |  |  | 14.7509 |  |  | -46.2334 |  |  | -139.8181 |  |  | -256.3498 |  |  | -371.4088 |  |  | -474.6621 |  |  | -603.1832
[13 empty] | Press drop ratio this iteration |  |  | 0.50252 |  |  | 0.49485 |  |  | 0.45111 |  |  | 0.22781 |  |  | -12.2745 |  |  | 1.5567 |  |  | 1.2423 |  |  | 1.1556 |  |  | 1.1177 |  |  | 1.0904
[13 empty] | Expansion factor | 12 |  | 0.73828 |  |  | 0.74233 |  |  | 0.76158 |  |  | 0.87795 |  |  | 7.7564 |  |  | 0.094258 |  |  | 0.22729 |  |  | 0.21468 |  |  | 0.37226 |  |  | 0.070364
[13 empty] | C Non choked w/ reducers | 5 |  | 0.87456 |  |  | 8.6591 |  |  | 23.8077 |  |  | 80.0913 |  |  | #NUM! |  |  | 490.5895 |  |  | 130.1892 |  |  | 114.1941 |  |  | 64.2277 |  |  | 387.1703
[13 empty] | C Choked w/ reducers | 5 |  | 0.85776 |  |  | 8.4729 |  |  | 22.99 |  |  | 63.791 |  |  | 1849.8723 |  |  | 114.2805 |  |  | 67.5455 |  |  | 56.4157 |  |  | 49.1922 |  |  | 68.209
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.87456 |  |  | 8.6591 |  |  | 23.8077 |  |  | 80.0913 |  |  | #NUM! |  |  | 114.2805 |  |  | 67.5455 |  |  | 56.4157 |  |  | 49.1922 |  |  | 68.209
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.1254 | 202.2229 |  | 3.6591 | 1966.2413 |  | 13.8077 | 4862.7486 |  | 62.8913 | 9471.3931 |  | 7174 | 15576.9545 |  | 7174 | 21847.8779 |  | 7174 | 27741.0076 |  | 7174 | 32528.5131 |  | 7174 | 36291.0324 |  | 7174 | 40488.7561
[13 empty] | Next iteration flow rate |  |  | 206.2674 | Abs Value of | Flow this | 1985.9037 | Abs Value of | Flow this | 4911.3761 | Abs Value of | Flow this | 9566.107 | Abs Value of | Flow this | 15732.724 | Abs Value of | Flow this | 22066.3567 | Abs Value of | Flow this | 28018.4176 | Abs Value of | Flow this | 32853.7982 | Abs Value of | Flow this | 36653.9427 | Abs Value of | Flow this | 40893.6437 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5058 |  |  | 98.9501 |  |  | 90.904 |  |  | 64.0319 |  |  | 1.8218 |  |  | -93.644 |  |  | -212.5179 |  |  | -329.8896 |  |  | -435.2183 |  |  | -566.3227
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48482 |  |  | 0.47732 |  |  | 0.4385 |  |  | 0.30888 |  |  | 0.0087881 |  |  | -0.45172 |  |  | -1.0251 |  |  | -1.5913 |  |  | -2.0994 |  |  | -2.7318
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5058 |  |  | 48.9501 |  |  | 40.904 |  |  | 14.0319 |  |  | -48.1782 |  |  | -143.644 |  |  | -262.5179 |  |  | -379.8896 |  |  | -485.2183 |  |  | -616.3227
[13 empty] | Press drop ratio this iteration |  |  | 0.50252 |  |  | 0.4947 |  |  | 0.44997 |  |  | 0.21914 |  |  | -26.4452 |  |  | 1.5339 |  |  | 1.2353 |  |  | 1.1516 |  |  | 1.1149 |  |  | 1.0883
[13 empty] | Expansion factor | 12 |  | 0.73828 |  |  | 0.74241 |  |  | 0.76219 |  |  | 0.88259 |  |  | 15.5566 |  |  | 0.10749 |  |  | 0.23166 |  |  | 0.2174 |  |  | 0.37387 |  |  | 0.072152
[13 empty] | C Non choked w/ reducers | 5 |  | 0.89206 |  |  | 8.7488 |  |  | 24.1074 |  |  | 82.9642 |  |  | #NUM! |  |  | 419.8223 |  |  | 125.62 |  |  | 111.1587 |  |  | 63.1056 |  |  | 372.8627
[13 empty] | C Choked w/ reducers | 5 |  | 0.87492 |  |  | 8.5603 |  |  | 23.2683 |  |  | 65.1524 |  |  | 3862.8715 |  |  | 110.7077 |  |  | 66.2409 |  |  | 55.515 |  |  | 48.479 |  |  | 67.2927
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.89206 |  |  | 8.7488 |  |  | 24.1074 |  |  | 82.9642 |  |  | #NUM! |  |  | 110.7077 |  |  | 66.2409 |  |  | 55.515 |  |  | 48.479 |  |  | 67.2927
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.1079 | 206.2674 |  | 3.7488 | 1985.9037 |  | 14.1074 | 4911.3761 |  | 65.7642 | 9566.107 |  | 7174 | 15732.724 |  | 7174 | 22066.3567 |  | 7174 | 28018.4176 |  | 7174 | 32853.7982 |  | 7174 | 36653.9427 |  | 7174 | 40893.6437
[13 empty] | Next iteration flow rate |  |  | 210.3927 | Abs Value of | Flow this | 2005.7627 | Abs Value of | Flow this | 4960.4899 | Abs Value of | Flow this | 9661.7681 | Abs Value of | Flow this | 15890.0513 | Abs Value of | Flow this | 22287.0202 | Abs Value of | Flow this | 28298.6018 | Abs Value of | Flow this | 33182.3362 | Abs Value of | Flow this | 37020.4821 | Abs Value of | Flow this | 41302.5801 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5051 |  |  | 98.9185 |  |  | 90.7107 |  |  | 63.2985 |  |  | -0.16208 |  |  | -97.5467 |  |  | -218.81 |  |  | -338.5409 |  |  | -445.9867 |  |  | -579.7263
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48482 |  |  | 0.47717 |  |  | 0.43757 |  |  | 0.30534 |  |  | -0.00078183 |  |  | -0.47055 |  |  | -1.0555 |  |  | -1.6331 |  |  | -2.1514 |  |  | -2.7965
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5051 |  |  | 48.9185 |  |  | 40.7107 |  |  | 13.2985 |  |  | -50.1621 |  |  | -147.5467 |  |  | -268.81 |  |  | -388.5409 |  |  | -495.9867 |  |  | -629.7263
[13 empty] | Press drop ratio this iteration |  |  | 0.50251 |  |  | 0.49453 |  |  | 0.4488 |  |  | 0.21009 |  |  | 309.4959 |  |  | 1.5126 |  |  | 1.2285 |  |  | 1.1477 |  |  | 1.1121 |  |  | 1.0862
[13 empty] | Expansion factor | 12 |  | 0.73829 |  |  | 0.7425 |  |  | 0.76281 |  |  | 0.88744 |  |  | -169.3601 |  |  | 0.11992 |  |  | 0.23587 |  |  | 0.22003 |  |  | 0.37543 |  |  | 0.073892
[13 empty] | C Non choked w/ reducers | 5 |  | 0.90991 |  |  | 8.8396 |  |  | 24.4124 |  |  | 86.098 |  |  | -7.6399 |  |  | 367.4328 |  |  | 121.362 |  |  | 108.2747 |  |  | 62.0169 |  |  | 359.5571
[13 empty] | C Choked w/ reducers | 5 |  | 0.89242 |  |  | 8.6487 |  |  | 23.5511 |  |  | 66.5664 |  |  | 43854.556 |  |  | 107.3411 |  |  | 64.9794 |  |  | 54.6373 |  |  | 47.7816 |  |  | 66.3942
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.90991 |  |  | 8.8396 |  |  | 24.4124 |  |  | 86.098 |  |  | 43854.556 |  |  | 107.3411 |  |  | 64.9794 |  |  | 54.6373 |  |  | 47.7816 |  |  | 66.3942
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.0901 | 210.3927 |  | 3.8396 | 2005.7627 |  | 14.4124 | 4960.4899 |  | 68.898 | 9661.7681 |  | 7174 | 15890.0513 |  | 7174 | 22287.0202 |  | 7174 | 28298.6018 |  | 7174 | 33182.3362 |  | 7174 | 37020.4821 |  | 7174 | 41302.5801
[13 empty] | Next iteration flow rate |  |  | 214.6006 | Abs Value of | Flow this | 2025.8203 | Abs Value of | Flow this | 5010.0948 | Abs Value of | Flow this | 9758.3858 | Abs Value of | Flow this | 16048.9518 | Abs Value of | Flow this | 22509.8904 | Abs Value of | Flow this | 28581.5878 | Abs Value of | Flow this | 33514.1595 | Abs Value of | Flow this | 37390.687 | Abs Value of | Flow this | 41715.6059 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5044 |  |  | 98.8863 |  |  | 90.5134 |  |  | 62.5503 |  |  | -2.1858 |  |  | -101.5279 |  |  | -225.2286 |  |  | -347.3661 |  |  | -456.9716 |  |  | -593.3993
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48482 |  |  | 0.47701 |  |  | 0.43662 |  |  | 0.30173 |  |  | -0.010544 |  |  | -0.48975 |  |  | -1.0865 |  |  | -1.6756 |  |  | -2.2043 |  |  | -2.8625
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5044 |  |  | 48.8863 |  |  | 40.5134 |  |  | 12.5503 |  |  | -52.1858 |  |  | -151.5279 |  |  | -275.2286 |  |  | -397.3661 |  |  | -506.9716 |  |  | -643.3993
[13 empty] | Press drop ratio this iteration |  |  | 0.50251 |  |  | 0.49437 |  |  | 0.4476 |  |  | 0.20064 |  |  | 23.8745 |  |  | 1.4925 |  |  | 1.222 |  |  | 1.1439 |  |  | 1.1094 |  |  | 1.0843
[13 empty] | Expansion factor | 12 |  | 0.73829 |  |  | 0.74258 |  |  | 0.76344 |  |  | 0.8925 |  |  | -12.1416 |  |  | 0.13161 |  |  | 0.23992 |  |  | 0.22258 |  |  | 0.37694 |  |  | 0.075586
[13 empty] | C Non choked w/ reducers | 5 |  | 0.92811 |  |  | 8.9313 |  |  | 24.7228 |  |  | 89.5366 |  |  | -28.7346 |  |  | 327.0533 |  |  | 117.3836 |  |  | 105.5308 |  |  | 60.9598 |  |  | 347.1498
[13 empty] | C Choked w/ reducers | 5 |  | 0.91028 |  |  | 8.738 |  |  | 23.8384 |  |  | 68.0363 |  |  | 3284.2628 |  |  | 104.1633 |  |  | 63.7589 |  |  | 53.7817 |  |  | 47.0993 |  |  | 65.513
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.92811 |  |  | 8.9313 |  |  | 24.7228 |  |  | 89.5366 |  |  | 3284.2628 |  |  | 104.1633 |  |  | 63.7589 |  |  | 53.7817 |  |  | 47.0993 |  |  | 65.513
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.0719 | 214.6006 |  | 3.9313 | 2025.8203 |  | 14.7228 | 5010.0948 |  | 72.3366 | 9758.3858 |  | 7174 | 16048.9518 |  | 7174 | 22509.8904 |  | 7174 | 28581.5878 |  | 7174 | 33514.1595 |  | 7174 | 37390.687 |  | 7174 | 41715.6059
[13 empty] | Next iteration flow rate |  |  | 218.8926 | Abs Value of | Flow this | 2046.0785 | Abs Value of | Flow this | 5060.1957 | Abs Value of | Flow this | 9855.9696 | Abs Value of | Flow this | 16209.4413 | Abs Value of | Flow this | 22734.9894 | Abs Value of | Flow this | 28867.4037 | Abs Value of | Flow this | 33849.3011 | Abs Value of | Flow this | 37764.5938 | Abs Value of | Flow this | 42132.762 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5037 |  |  | 98.8534 |  |  | 90.3123 |  |  | 61.787 |  |  | -4.2503 |  |  | -105.5891 |  |  | -231.7762 |  |  | -356.3686 |  |  | -468.1772 |  |  | -607.3471
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48481 |  |  | 0.47685 |  |  | 0.43565 |  |  | 0.29805 |  |  | -0.020503 |  |  | -0.50934 |  |  | -1.118 |  |  | -1.7191 |  |  | -2.2584 |  |  | -2.9297
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5037 |  |  | 48.8534 |  |  | 40.3123 |  |  | 11.787 |  |  | -54.2503 |  |  | -155.5891 |  |  | -281.7762 |  |  | -406.3686 |  |  | -518.1772 |  |  | -657.3471
[13 empty] | Press drop ratio this iteration |  |  | 0.50251 |  |  | 0.4942 |  |  | 0.44637 |  |  | 0.19077 |  |  | 12.7639 |  |  | 1.4735 |  |  | 1.2157 |  |  | 1.1403 |  |  | 1.1068 |  |  | 1.0823
[13 empty] | Expansion factor | 12 |  | 0.73829 |  |  | 0.74267 |  |  | 0.76409 |  |  | 0.89779 |  |  | -6.0258 |  |  | 0.14264 |  |  | 0.24382 |  |  | 0.22505 |  |  | 0.37841 |  |  | 0.077236
[13 empty] | C Non choked w/ reducers | 5 |  | 0.94668 |  |  | 9.0241 |  |  | 25.0388 |  |  | 93.3353 |  |  | -41.1302 |  |  | 294.9548 |  |  | 113.6571 |  |  | 102.9164 |  |  | 59.933 |  |  | 335.5515
[13 empty] | C Choked w/ reducers | 5 |  | 0.92849 |  |  | 8.8284 |  |  | 24.1304 |  |  | 69.5655 |  |  | 1705.9252 |  |  | 101.1585 |  |  | 62.5773 |  |  | 52.9473 |  |  | 46.4317 |  |  | 64.6486
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.94668 |  |  | 9.0241 |  |  | 25.0388 |  |  | 93.3353 |  |  | 1705.9252 |  |  | 101.1585 |  |  | 62.5773 |  |  | 52.9473 |  |  | 46.4317 |  |  | 64.6486
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.0533 | 218.8926 |  | 4.0241 | 2046.0785 |  | 15.0388 | 5060.1957 |  | 76.1353 | 9855.9696 |  | 7174 | 16209.4413 |  | 7174 | 22734.9894 |  | 7174 | 28867.4037 |  | 7174 | 33849.3011 |  | 7174 | 37764.5938 |  | 7174 | 42132.762
[13 empty] | Next iteration flow rate |  |  | 223.2705 | Abs Value of | Flow this | 2066.5393 | Abs Value of | Flow this | 5110.7977 | Abs Value of | Flow this | 9954.5293 | Abs Value of | Flow this | 16371.5357 | Abs Value of | Flow this | 22962.3392 | Abs Value of | Flow this | 29156.0778 | Abs Value of | Flow this | 34187.7941 | Abs Value of | Flow this | 38142.2398 | Abs Value of | Flow this | 42554.0896 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5029 |  |  | 98.8198 |  |  | 90.107 |  |  | 61.0084 |  |  | -6.3562 |  |  | -109.732 |  |  | -238.4554 |  |  | -365.5521 |  |  | -479.6081 |  |  | -621.5753
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48481 |  |  | 0.47669 |  |  | 0.43466 |  |  | 0.29429 |  |  | -0.030661 |  |  | -0.52933 |  |  | -1.1503 |  |  | -1.7634 |  |  | -2.3135 |  |  | -2.9984
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5029 |  |  | 48.8198 |  |  | 40.107 |  |  | 11.0084 |  |  | -56.3562 |  |  | -159.732 |  |  | -288.4554 |  |  | -415.5521 |  |  | -529.6081 |  |  | -671.5753
[13 empty] | Press drop ratio this iteration |  |  | 0.5025 |  |  | 0.49403 |  |  | 0.4451 |  |  | 0.18044 |  |  | 8.8663 |  |  | 1.4557 |  |  | 1.2097 |  |  | 1.1368 |  |  | 1.1043 |  |  | 1.0804
[13 empty] | Expansion factor | 12 |  | 0.73829 |  |  | 0.74276 |  |  | 0.76476 |  |  | 0.90333 |  |  | -3.8804 |  |  | 0.15304 |  |  | 0.24758 |  |  | 0.22745 |  |  | 0.37984 |  |  | 0.078843
[13 empty] | C Non choked w/ reducers | 5 |  | 0.96562 |  |  | 9.1179 |  |  | 25.3605 |  |  | 97.5646 |  |  | -51.756 |  |  | 268.8086 |  |  | 110.1585 |  |  | 100.4223 |  |  | 58.935 |  |  | 324.6839
[13 empty] | C Choked w/ reducers | 5 |  | 0.94707 |  |  | 8.9197 |  |  | 24.4272 |  |  | 71.1579 |  |  | 1152.1268 |  |  | 98.3127 |  |  | 61.4327 |  |  | 52.1333 |  |  | 45.7783 |  |  | 63.8004
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.96562 |  |  | 9.1179 |  |  | 25.3605 |  |  | 97.5646 |  |  | 1152.1268 |  |  | 98.3127 |  |  | 61.4327 |  |  | 52.1333 |  |  | 45.7783 |  |  | 63.8004
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.0344 | 223.2705 |  | 4.1179 | 2066.5393 |  | 15.3605 | 5110.7977 |  | 80.3646 | 9954.5293 |  | 7174 | 16371.5357 |  | 7174 | 22962.3392 |  | 7174 | 29156.0778 |  | 7174 | 34187.7941 |  | 7174 | 38142.2398 |  | 7174 | 42554.0896
[13 empty] | Next iteration flow rate |  |  | 227.7359 | Abs Value of | Flow this | 2087.2047 | Abs Value of | Flow this | 5161.9056 | Abs Value of | Flow this | 10054.0746 | Abs Value of | Flow this | 16535.2511 | Abs Value of | Flow this | 23191.9626 | Abs Value of | Flow this | 29447.6385 | Abs Value of | Flow this | 34529.6721 | Abs Value of | Flow this | 38523.6622 | Abs Value of | Flow this | 42979.6305 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5021 |  |  | 98.7856 |  |  | 89.8977 |  |  | 60.2142 |  |  | -8.5045 |  |  | -113.9581 |  |  | -245.2689 |  |  | -374.9203 |  |  | -491.2687 |  |  | -636.0895
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4848 |  |  | 0.47652 |  |  | 0.43365 |  |  | 0.29046 |  |  | -0.041024 |  |  | -0.54971 |  |  | -1.1831 |  |  | -1.8085 |  |  | -2.3698 |  |  | -3.0684
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5021 |  |  | 48.7856 |  |  | 39.8977 |  |  | 10.2142 |  |  | -58.5045 |  |  | -163.9581 |  |  | -295.2689 |  |  | -424.9203 |  |  | -541.2687 |  |  | -686.0895
[13 empty] | Press drop ratio this iteration |  |  | 0.5025 |  |  | 0.49385 |  |  | 0.44381 |  |  | 0.16963 |  |  | 6.8792 |  |  | 1.4388 |  |  | 1.2039 |  |  | 1.1334 |  |  | 1.1018 |  |  | 1.0786
[13 empty] | Expansion factor | 12 |  | 0.73829 |  |  | 0.74285 |  |  | 0.76544 |  |  | 0.90912 |  |  | -2.7866 |  |  | 0.16287 |  |  | 0.2512 |  |  | 0.22977 |  |  | 0.38123 |  |  | 0.080408
[13 empty] | C Non choked w/ reducers | 5 |  | 0.98495 |  |  | 9.2128 |  |  | 25.6882 |  |  | 102.3161 |  |  | -61.7632 |  |  | 247.085 |  |  | 106.8669 |  |  | 98.0401 |  |  | 57.9646 |  |  | 314.4787
[13 empty] | C Choked w/ reducers | 5 |  | 0.96601 |  |  | 9.012 |  |  | 24.729 |  |  | 72.8174 |  |  | 869.706 |  |  | 95.6135 |  |  | 60.3234 |  |  | 51.3389 |  |  | 45.1387 |  |  | 62.9681
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 0.98495 |  |  | 9.2128 |  |  | 25.6882 |  |  | 102.3161 |  |  | 869.706 |  |  | 95.6135 |  |  | 60.3234 |  |  | 51.3389 |  |  | 45.1387 |  |  | 62.9681
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.0151 | 227.7359 |  | 4.2128 | 2087.2047 |  | 15.6882 | 5161.9056 |  | 85.1161 | 10054.0746 |  | 7174 | 16535.2511 |  | 7174 | 23191.9626 |  | 7174 | 29447.6385 |  | 7174 | 34529.6721 |  | 7174 | 38523.6622 |  | 7174 | 42979.6305
[13 empty] | Next iteration flow rate |  |  | 232.2906 | Abs Value of | Flow this | 2108.0768 | Abs Value of | Flow this | 5213.5247 | Abs Value of | Flow this | 10154.6154 | Abs Value of | Flow this | 16700.6036 | Abs Value of | Flow this | 23423.8823 | Abs Value of | Flow this | 29742.1149 | Abs Value of | Flow this | 34874.9688 | Abs Value of | Flow this | 38908.8988 | Abs Value of | Flow this | 43409.4268 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5013 |  |  | 98.7507 |  |  | 89.6841 |  |  | 59.404 |  |  | -10.6959 |  |  | -118.2692 |  |  | -252.2193 |  |  | -384.4767 |  |  | -503.1637 |  |  | -650.8954
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4848 |  |  | 0.47636 |  |  | 0.43262 |  |  | 0.28655 |  |  | -0.051595 |  |  | -0.57051 |  |  | -1.2167 |  |  | -1.8546 |  |  | -2.4272 |  |  | -3.1398
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5013 |  |  | 48.7507 |  |  | 39.6841 |  |  | 9.404 |  |  | -60.6959 |  |  | -168.2692 |  |  | -302.2193 |  |  | -434.4767 |  |  | -553.1637 |  |  | -700.8954
[13 empty] | Press drop ratio this iteration |  |  | 0.50249 |  |  | 0.49367 |  |  | 0.44249 |  |  | 0.15831 |  |  | 5.6747 |  |  | 1.4228 |  |  | 1.1982 |  |  | 1.13 |  |  | 1.0994 |  |  | 1.0768
[13 empty] | Expansion factor | 12 |  | 0.7383 |  |  | 0.74295 |  |  | 0.76614 |  |  | 0.91519 |  |  | -2.1236 |  |  | 0.17218 |  |  | 0.2547 |  |  | 0.23203 |  |  | 0.38258 |  |  | 0.081932
[13 empty] | C Non choked w/ reducers | 5 |  | 1.0047 |  |  | 9.3087 |  |  | 26.0219 |  |  | 107.712 |  |  | -71.6624 |  |  | 228.738 |  |  | 103.7636 |  |  | 95.7619 |  |  | 57.0207 |  |  | 304.876
[13 empty] | C Choked w/ reducers | 5 |  | 0.98534 |  |  | 9.1053 |  |  | 25.0357 |  |  | 74.5487 |  |  | 698.4306 |  |  | 93.0495 |  |  | 59.2477 |  |  | 50.5635 |  |  | 44.5123 |  |  | 62.1511
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.0047 |  |  | 9.3087 |  |  | 26.0219 |  |  | 107.712 |  |  | 698.4306 |  |  | 93.0495 |  |  | 59.2477 |  |  | 50.5635 |  |  | 44.5123 |  |  | 62.1511
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.99535 | 232.2906 |  | 4.3087 | 2108.0768 |  | 16.0219 | 5213.5247 |  | 90.512 | 10154.6154 |  | 7174 | 16700.6036 |  | 7174 | 23423.8823 |  | 7174 | 29742.1149 |  | 7174 | 34874.9688 |  | 7174 | 38908.8988 |  | 7174 | 43409.4268
[13 empty] | Next iteration flow rate |  |  | 236.9364 | Abs Value of | Flow this | 2129.1575 | Abs Value of | Flow this | 5265.6599 | Abs Value of | Flow this | 10256.1615 | Abs Value of | Flow this | 16867.6096 | Abs Value of | Flow this | 23658.1211 | Abs Value of | Flow this | 30039.5361 | Abs Value of | Flow this | 35223.7185 | Abs Value of | Flow this | 39297.9878 | Abs Value of | Flow this | 43843.521 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.5004 |  |  | 98.7151 |  |  | 89.4662 |  |  | 58.5775 |  |  | -12.9314 |  |  | -122.6669 |  |  | -259.3094 |  |  | -394.2251 |  |  | -515.2978 |  |  | -665.9989
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4848 |  |  | 0.47618 |  |  | 0.43157 |  |  | 0.28257 |  |  | -0.062379 |  |  | -0.59172 |  |  | -1.2509 |  |  | -1.9017 |  |  | -2.4857 |  |  | -3.2127
[13 empty] | Delta P at this iteration flow rate |  |  | 50.5004 |  |  | 48.7151 |  |  | 39.4662 |  |  | 8.5775 |  |  | -62.9314 |  |  | -172.6669 |  |  | -309.3094 |  |  | -444.2251 |  |  | -565.2978 |  |  | -715.9989
[13 empty] | Press drop ratio this iteration |  |  | 0.50249 |  |  | 0.49349 |  |  | 0.44113 |  |  | 0.14643 |  |  | 4.8665 |  |  | 1.4076 |  |  | 1.1928 |  |  | 1.1268 |  |  | 1.097 |  |  | 1.0751
[13 empty] | Expansion factor | 12 |  | 0.7383 |  |  | 0.74304 |  |  | 0.76686 |  |  | 0.92155 |  |  | -1.6788 |  |  | 0.18099 |  |  | 0.25807 |  |  | 0.23421 |  |  | 0.38389 |  |  | 0.083417
[13 empty] | C Non choked w/ reducers | 5 |  | 1.0248 |  |  | 9.4058 |  |  | 26.362 |  |  | 113.9186 |  |  | -81.7761 |  |  | 213.0278 |  |  | 100.8323 |  |  | 93.5809 |  |  | 56.102 |  |  | 295.8228
[13 empty] | C Choked w/ reducers | 5 |  | 1.0051 |  |  | 9.1997 |  |  | 25.3476 |  |  | 76.3565 |  |  | 583.4677 |  |  | 90.6108 |  |  | 58.204 |  |  | 49.8063 |  |  | 43.8988 |  |  | 61.3491
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.0248 |  |  | 9.4058 |  |  | 26.362 |  |  | 113.9186 |  |  | 583.4677 |  |  | 90.6108 |  |  | 58.204 |  |  | 49.8063 |  |  | 43.8988 |  |  | 61.3491
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.97524 | 236.9364 |  | 4.4058 | 2129.1575 |  | 16.362 | 5265.6599 |  | 96.7186 | 10256.1615 |  | 7174 | 16867.6096 |  | 7174 | 23658.1211 |  | 7174 | 30039.5361 |  | 7174 | 35223.7185 |  | 7174 | 39297.9878 |  | 7174 | 43843.521
[13 empty] | Next iteration flow rate |  |  | 241.6751 | Abs Value of | Flow this | 2150.4491 | Abs Value of | Flow this | 5318.3165 | Abs Value of | Flow this | 10358.7232 | Abs Value of | Flow this | 17036.2857 | Abs Value of | Flow this | 23894.7023 | Abs Value of | Flow this | 30339.9314 | Abs Value of | Flow this | 35575.9557 | Abs Value of | Flow this | 39690.9677 | Abs Value of | Flow this | 44281.9563 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4995 |  |  | 98.6787 |  |  | 89.244 |  |  | 57.7344 |  |  | -15.2119 |  |  | -127.153 |  |  | -266.542 |  |  | -404.1696 |  |  | -527.6758 |  |  | -681.406
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48479 |  |  | 0.47601 |  |  | 0.4305 |  |  | 0.2785 |  |  | -0.073379 |  |  | -0.61336 |  |  | -1.2858 |  |  | -1.9496 |  |  | -2.5454 |  |  | -3.287
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4995 |  |  | 48.6787 |  |  | 39.244 |  |  | 7.7344 |  |  | -65.2119 |  |  | -177.153 |  |  | -316.542 |  |  | -454.1696 |  |  | -577.6758 |  |  | -731.406
[13 empty] | Press drop ratio this iteration |  |  | 0.50249 |  |  | 0.49331 |  |  | 0.43974 |  |  | 0.13397 |  |  | 4.2869 |  |  | 1.3932 |  |  | 1.1876 |  |  | 1.1237 |  |  | 1.0948 |  |  | 1.0734
[13 empty] | Expansion factor | 12 |  | 0.7383 |  |  | 0.74314 |  |  | 0.76759 |  |  | 0.92823 |  |  | -1.3597 |  |  | 0.18936 |  |  | 0.26132 |  |  | 0.23633 |  |  | 0.38517 |  |  | 0.084864
[13 empty] | C Non choked w/ reducers | 5 |  | 1.0453 |  |  | 9.5039 |  |  | 26.7085 |  |  | 121.1701 |  |  | -92.3624 |  |  | 199.4165 |  |  | 98.0586 |  |  | 91.4906 |  |  | 55.2075 |  |  | 287.2722
[13 empty] | C Choked w/ reducers | 5 |  | 1.0252 |  |  | 9.2951 |  |  | 25.6649 |  |  | 78.2462 |  |  | 500.9593 |  |  | 88.288 |  |  | 57.1909 |  |  | 49.0666 |  |  | 43.2977 |  |  | 60.5615
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.0453 |  |  | 9.5039 |  |  | 26.7085 |  |  | 121.1701 |  |  | 500.9593 |  |  | 88.288 |  |  | 57.1909 |  |  | 49.0666 |  |  | 43.2977 |  |  | 60.5615
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.95474 | 241.6751 |  | 4.5039 | 2150.4491 |  | 16.7085 | 5318.3165 |  | 103.9701 | 10358.7232 |  | 7174 | 17036.2857 |  | 7174 | 23894.7023 |  | 7174 | 30339.9314 |  | 7174 | 35575.9557 |  | 7174 | 39690.9677 |  | 7174 | 44281.9563
[13 empty] | Next iteration flow rate |  |  | 246.5086 | Abs Value of | Flow this | 2171.9536 | Abs Value of | Flow this | 5371.4997 | Abs Value of | Flow this | 10462.3104 | Abs Value of | Flow this | 17206.6486 | Abs Value of | Flow this | 24133.6493 | Abs Value of | Flow this | 30643.3307 | Abs Value of | Flow this | 35931.7152 | Abs Value of | Flow this | 40087.8773 | Abs Value of | Flow this | 44724.7758 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4986 |  |  | 98.6417 |  |  | 89.0173 |  |  | 56.8743 |  |  | -17.5381 |  |  | -131.7293 |  |  | -273.92 |  |  | -414.3139 |  |  | -540.3026 |  |  | -697.1227
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48479 |  |  | 0.47583 |  |  | 0.4294 |  |  | 0.27435 |  |  | -0.084601 |  |  | -0.63544 |  |  | -1.3213 |  |  | -1.9986 |  |  | -2.6063 |  |  | -3.3628
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4986 |  |  | 48.6417 |  |  | 39.0173 |  |  | 6.8743 |  |  | -67.5381 |  |  | -181.7293 |  |  | -323.92 |  |  | -464.3139 |  |  | -590.3026 |  |  | -747.1227
[13 empty] | Press drop ratio this iteration |  |  | 0.50248 |  |  | 0.49311 |  |  | 0.43831 |  |  | 0.12087 |  |  | 3.8509 |  |  | 1.3796 |  |  | 1.1825 |  |  | 1.1207 |  |  | 1.0925 |  |  | 1.0717
[13 empty] | Expansion factor | 12 |  | 0.7383 |  |  | 0.74324 |  |  | 0.76835 |  |  | 0.93524 |  |  | -1.1197 |  |  | 0.19731 |  |  | 0.26447 |  |  | 0.23839 |  |  | 0.38642 |  |  | 0.086275
[13 empty] | C Non choked w/ reducers | 5 |  | 1.0662 |  |  | 9.6031 |  |  | 27.0617 |  |  | 129.8085 |  |  | -103.6666 |  |  | 187.5035 |  |  | 95.4296 |  |  | 89.4853 |  |  | 54.3362 |  |  | 279.1824
[13 empty] | C Choked w/ reducers | 5 |  | 1.0457 |  |  | 9.3916 |  |  | 25.9875 |  |  | 80.2238 |  |  | 438.857 |  |  | 86.0731 |  |  | 56.207 |  |  | 48.3439 |  |  | 42.7087 |  |  | 59.7881
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.0662 |  |  | 9.6031 |  |  | 27.0617 |  |  | 129.8085 |  |  | 438.857 |  |  | 86.0731 |  |  | 56.207 |  |  | 48.3439 |  |  | 42.7087 |  |  | 59.7881
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.93382 | 246.5086 |  | 4.6031 | 2171.9536 |  | 17.0617 | 5371.4997 |  | 112.6085 | 10462.3104 |  | 7174 | 17206.6486 |  | 7174 | 24133.6493 |  | 7174 | 30643.3307 |  | 7174 | 35931.7152 |  | 7174 | 40087.8773 |  | 7174 | 44724.7758
[13 empty] | Next iteration flow rate |  |  | 251.4388 | Abs Value of | Flow this | 2193.6731 | Abs Value of | Flow this | 5425.2147 | Abs Value of | Flow this | 10566.9335 | Abs Value of | Flow this | 17378.7151 | Abs Value of | Flow this | 24374.9858 | Abs Value of | Flow this | 30949.764 | Abs Value of | Flow this | 36291.0324 | Abs Value of | Flow this | 40488.7561 | Abs Value of | Flow this | 45172.0236 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4976 |  |  | 98.6039 |  |  | 88.786 |  |  | 55.997 |  |  | -19.9112 |  |  | -136.3975 |  |  | -281.4463 |  |  | -424.6621 |  |  | -553.1832 |  |  | -713.1554
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48478 |  |  | 0.47565 |  |  | 0.42829 |  |  | 0.27012 |  |  | -0.096048 |  |  | -0.65796 |  |  | -1.3576 |  |  | -2.0485 |  |  | -2.6685 |  |  | -3.4401
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4976 |  |  | 48.6039 |  |  | 38.786 |  |  | 5.997 |  |  | -69.9112 |  |  | -186.3975 |  |  | -331.4463 |  |  | -474.6621 |  |  | -603.1832 |  |  | -763.1554
[13 empty] | Press drop ratio this iteration |  |  | 0.50248 |  |  | 0.49292 |  |  | 0.43685 |  |  | 0.1071 |  |  | 3.5112 |  |  | 1.3666 |  |  | 1.1777 |  |  | 1.1177 |  |  | 1.0904 |  |  | 1.0701
[13 empty] | Expansion factor | 12 |  | 0.7383 |  |  | 0.74334 |  |  | 0.76912 |  |  | 0.94262 |  |  | -0.93269 |  |  | 0.20487 |  |  | 0.2675 |  |  | 0.24039 |  |  | 0.38763 |  |  | 0.08765
[13 empty] | C Non choked w/ reducers | 5 |  | 1.0875 |  |  | 9.7034 |  |  | 27.4217 |  |  | 140.3574 |  |  | -115.9514 |  |  | 176.9842 |  |  | 92.9338 |  |  | 87.5597 |  |  | 53.4871 |  |  | 271.5162
[13 empty] | C Choked w/ reducers | 5 |  | 1.0666 |  |  | 9.4891 |  |  | 26.3158 |  |  | 82.2955 |  |  | 390.4192 |  |  | 83.9585 |  |  | 55.251 |  |  | 47.6375 |  |  | 42.1314 |  |  | 59.0285
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.0875 |  |  | 9.7034 |  |  | 27.4217 |  |  | 140.3574 |  |  | 390.4192 |  |  | 83.9585 |  |  | 55.251 |  |  | 47.6375 |  |  | 42.1314 |  |  | 59.0285
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.91248 | 251.4388 |  | 4.7034 | 2193.6731 |  | 17.4217 | 5425.2147 |  | 123.1574 | 10566.9335 |  | 7174 | 17378.7151 |  | 7174 | 24374.9858 |  | 7174 | 30949.764 |  | 7174 | 36291.0324 |  | 7174 | 40488.7561 |  | 7174 | 45172.0236
[13 empty] | Next iteration flow rate |  |  | 256.4676 | Abs Value of | Flow this | 2215.6099 | Abs Value of | Flow this | 5479.4669 | Abs Value of | Flow this | 10672.6028 | Abs Value of | Flow this | 17552.5022 | Abs Value of | Flow this | 24618.7357 | Abs Value of | Flow this | 31259.2617 | Abs Value of | Flow this | 36653.9427 | Abs Value of | Flow this | 40893.6437 | Abs Value of | Flow this | 45623.7438 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4966 |  |  | 98.5653 |  |  | 88.5501 |  |  | 55.102 |  |  | -22.3319 |  |  | -141.1596 |  |  | -289.1239 |  |  | -435.2183 |  |  | -566.3227 |  |  | -729.5103
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48478 |  |  | 0.47546 |  |  | 0.42715 |  |  | 0.2658 |  |  | -0.10773 |  |  | -0.68093 |  |  | -1.3947 |  |  | -2.0994 |  |  | -2.7318 |  |  | -3.519
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4966 |  |  | 48.5653 |  |  | 38.5501 |  |  | 5.102 |  |  | -72.3319 |  |  | -191.1596 |  |  | -339.1239 |  |  | -485.2183 |  |  | -616.3227 |  |  | -779.5103
[13 empty] | Press drop ratio this iteration |  |  | 0.50247 |  |  | 0.49272 |  |  | 0.43535 |  |  | 0.092593 |  |  | 3.239 |  |  | 1.3542 |  |  | 1.1729 |  |  | 1.1149 |  |  | 1.0883 |  |  | 1.0685
[13 empty] | Expansion factor | 12 |  | 0.73831 |  |  | 0.74344 |  |  | 0.76991 |  |  | 0.95039 |  |  | -0.78286 |  |  | 0.21206 |  |  | 0.27044 |  |  | 0.24233 |  |  | 0.3888 |  |  | 0.08899
[13 empty] | C Non choked w/ reducers | 5 |  | 1.1093 |  |  | 9.8049 |  |  | 27.7889 |  |  | 153.6687 |  |  | -129.5226 |  |  | 167.6233 |  |  | 90.5608 |  |  | 85.7087 |  |  | 52.6595 |  |  | 264.2405
[13 empty] | C Choked w/ reducers | 5 |  | 1.0879 |  |  | 9.5878 |  |  | 26.6498 |  |  | 84.4685 |  |  | 351.5797 |  |  | 81.9374 |  |  | 54.3216 |  |  | 46.9469 |  |  | 41.5654 |  |  | 58.2821
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.1093 |  |  | 9.8049 |  |  | 27.7889 |  |  | 153.6687 |  |  | 351.5797 |  |  | 81.9374 |  |  | 54.3216 |  |  | 46.9469 |  |  | 41.5654 |  |  | 58.2821
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.89072 | 256.4676 |  | 4.8049 | 2215.6099 |  | 17.7889 | 5479.4669 |  | 136.4687 | 10672.6028 |  | 7174 | 17552.5022 |  | 7174 | 24618.7357 |  | 7174 | 31259.2617 |  | 7174 | 36653.9427 |  | 7174 | 40893.6437 |  | 7174 | 45623.7438
[13 empty] | Next iteration flow rate |  |  | 261.5969 | Abs Value of | Flow this | 2237.766 | Abs Value of | Flow this | 5534.2615 | Abs Value of | Flow this | 10779.3289 | Abs Value of | Flow this | 17728.0272 | Abs Value of | Flow this | 24864.923 | Abs Value of | Flow this | 31571.8543 | Abs Value of | Flow this | 37020.4821 | Abs Value of | Flow this | 41302.5801 | Abs Value of | Flow this | 46079.9813 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4955 |  |  | 98.5259 |  |  | 88.3095 |  |  | 54.1891 |  |  | -24.8013 |  |  | -146.0175 |  |  | -296.9558 |  |  | -445.9867 |  |  | -579.7263 |  |  | -746.194
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48477 |  |  | 0.47527 |  |  | 0.42599 |  |  | 0.2614 |  |  | -0.11964 |  |  | -0.70436 |  |  | -1.4325 |  |  | -2.1514 |  |  | -2.7965 |  |  | -3.5995
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4955 |  |  | 48.5259 |  |  | 38.3095 |  |  | 4.1891 |  |  | -74.8013 |  |  | -196.0175 |  |  | -346.9558 |  |  | -495.9867 |  |  | -629.7263 |  |  | -796.194
[13 empty] | Press drop ratio this iteration |  |  | 0.50247 |  |  | 0.49252 |  |  | 0.43381 |  |  | 0.077305 |  |  | 3.016 |  |  | 1.3424 |  |  | 1.1684 |  |  | 1.1121 |  |  | 1.0862 |  |  | 1.067
[13 empty] | Expansion factor | 12 |  | 0.73831 |  |  | 0.74355 |  |  | 0.77073 |  |  | 0.95858 |  |  | -0.66015 |  |  | 0.21892 |  |  | 0.27327 |  |  | 0.24421 |  |  | 0.38995 |  |  | 0.090296
[13 empty] | C Non choked w/ reducers | 5 |  | 1.1315 |  |  | 9.9075 |  |  | 28.1634 |  |  | 171.246 |  |  | -144.7581 |  |  | 159.2355 |  |  | 88.3014 |  |  | 83.9281 |  |  | 51.8523 |  |  | 257.3252
[13 empty] | C Choked w/ reducers | 5 |  | 1.1097 |  |  | 9.6875 |  |  | 26.9896 |  |  | 86.7505 |  |  | 319.7398 |  |  | 80.0035 |  |  | 53.4178 |  |  | 46.2715 |  |  | 41.0104 |  |  | 57.5488
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.1315 |  |  | 9.9075 |  |  | 28.1634 |  |  | 171.246 |  |  | 319.7398 |  |  | 80.0035 |  |  | 53.4178 |  |  | 46.2715 |  |  | 41.0104 |  |  | 57.5488
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.86852 | 261.5969 |  | 4.9075 | 2237.766 |  | 18.1634 | 5534.2615 |  | 154.046 | 10779.3289 |  | 7174 | 17728.0272 |  | 7174 | 24864.923 |  | 7174 | 31571.8543 |  | 7174 | 37020.4821 |  | 7174 | 41302.5801 |  | 7174 | 46079.9813
[13 empty] | Next iteration flow rate |  |  | 266.8289 | Abs Value of | Flow this | 2260.1436 | Abs Value of | Flow this | 5589.6041 | Abs Value of | Flow this | 10887.1221 | Abs Value of | Flow this | 17905.3075 | Abs Value of | Flow this | 25113.5723 | Abs Value of | Flow this | 31887.5728 | Abs Value of | Flow this | 37390.687 | Abs Value of | Flow this | 41715.6059 | Abs Value of | Flow this | 46540.7811 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4944 |  |  | 98.4858 |  |  | 88.064 |  |  | 53.2578 |  |  | -27.3203 |  |  | -150.9729 |  |  | -304.9451 |  |  | -456.9716 |  |  | -593.3993 |  |  | -763.213
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48477 |  |  | 0.47508 |  |  | 0.42481 |  |  | 0.25691 |  |  | -0.13179 |  |  | -0.72827 |  |  | -1.471 |  |  | -2.2043 |  |  | -2.8625 |  |  | -3.6816
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4944 |  |  | 48.4858 |  |  | 38.064 |  |  | 3.2578 |  |  | -77.3203 |  |  | -200.9729 |  |  | -354.9451 |  |  | -506.9716 |  |  | -643.3993 |  |  | -813.213
[13 empty] | Press drop ratio this iteration |  |  | 0.50246 |  |  | 0.49231 |  |  | 0.43223 |  |  | 0.06117 |  |  | 2.8301 |  |  | 1.3312 |  |  | 1.164 |  |  | 1.1094 |  |  | 1.0843 |  |  | 1.0655
[13 empty] | Expansion factor | 12 |  | 0.73831 |  |  | 0.74365 |  |  | 0.77156 |  |  | 0.96723 |  |  | -0.55783 |  |  | 0.22546 |  |  | 0.27602 |  |  | 0.24605 |  |  | 0.39107 |  |  | 0.09157
[13 empty] | C Non choked w/ reducers | 5 |  | 1.1541 |  |  | 10.0114 |  |  | 28.5455 |  |  | 196.0678 |  |  | -162.1458 |  |  | 151.6734 |  |  | 86.1473 |  |  | 82.2136 |  |  | 51.0648 |  |  | 250.7435
[13 empty] | C Choked w/ reducers | 5 |  | 1.1319 |  |  | 9.7884 |  |  | 27.3355 |  |  | 89.1501 |  |  | 293.1614 |  |  | 78.1513 |  |  | 52.5385 |  |  | 45.6108 |  |  | 40.4661 |  |  | 56.8282
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.1541 |  |  | 10.0114 |  |  | 28.5455 |  |  | 196.0678 |  |  | 293.1614 |  |  | 78.1513 |  |  | 52.5385 |  |  | 45.6108 |  |  | 40.4661 |  |  | 56.8282
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.84588 | 266.8289 |  | 5.0114 | 2260.1436 |  | 18.5455 | 5589.6041 |  | 178.8678 | 10887.1221 |  | 7174 | 17905.3075 |  | 7174 | 25113.5723 |  | 7174 | 31887.5728 |  | 7174 | 37390.687 |  | 7174 | 41715.6059 |  | 7174 | 46540.7811
[13 empty] | Next iteration flow rate |  |  | 272.1654 | Abs Value of | Flow this | 2282.7451 | Abs Value of | Flow this | 5645.5002 | Abs Value of | Flow this | 10995.9934 | Abs Value of | Flow this | 18084.3606 | Abs Value of | Flow this | 25364.708 | Abs Value of | Flow this | 32206.4486 | Abs Value of | Flow this | 37764.5938 | Abs Value of | Flow this | 42132.762 | Abs Value of | Flow this | 47006.1889 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4932 |  |  | 98.4449 |  |  | 87.8136 |  |  | 52.3077 |  |  | -29.8899 |  |  | -156.028 |  |  | -313.0951 |  |  | -468.1772 |  |  | -607.3471 |  |  | -780.5741
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48476 |  |  | 0.47488 |  |  | 0.4236 |  |  | 0.25232 |  |  | -0.14418 |  |  | -0.75265 |  |  | -1.5103 |  |  | -2.2584 |  |  | -2.9297 |  |  | -3.7654
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4932 |  |  | 48.4449 |  |  | 37.8136 |  |  | 2.3077 |  |  | -79.8899 |  |  | -206.028 |  |  | -363.0951 |  |  | -518.1772 |  |  | -657.3471 |  |  | -830.5741
[13 empty] | Press drop ratio this iteration |  |  | 0.50245 |  |  | 0.4921 |  |  | 0.43061 |  |  | 0.044119 |  |  | 2.6728 |  |  | 1.3205 |  |  | 1.1597 |  |  | 1.1068 |  |  | 1.0823 |  |  | 1.0641
[13 empty] | Expansion factor | 12 |  | 0.73832 |  |  | 0.74376 |  |  | 0.77242 |  |  | 0.97636 |  |  | -0.47123 |  |  | 0.2317 |  |  | 0.27867 |  |  | 0.24783 |  |  | 0.39215 |  |  | 0.092812
[13 empty] | C Non choked w/ reducers | 5 |  | 1.1772 |  |  | 10.1163 |  |  | 28.9354 |  |  | 235.1906 |  |  | -182.3398 |  |  | 144.818 |  |  | 84.091 |  |  | 80.5614 |  |  | 50.2962 |  |  | 244.4711
[13 empty] | C Choked w/ reducers | 5 |  | 1.1546 |  |  | 9.8904 |  |  | 27.6876 |  |  | 91.677 |  |  | 270.6378 |  |  | 76.3755 |  |  | 51.6826 |  |  | 44.9643 |  |  | 39.9322 |  |  | 56.1199
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.1772 |  |  | 10.1163 |  |  | 28.9354 |  |  | 235.1906 |  |  | 270.6378 |  |  | 76.3755 |  |  | 51.6826 |  |  | 44.9643 |  |  | 39.9322 |  |  | 56.1199
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.82278 | 272.1654 |  | 5.1163 | 2282.7451 |  | 18.9354 | 5645.5002 |  | 217.9906 | 10995.9934 |  | 7174 | 18084.3606 |  | 7174 | 25364.708 |  | 7174 | 32206.4486 |  | 7174 | 37764.5938 |  | 7174 | 42132.762 |  | 7174 | 47006.1889
[13 empty] | Next iteration flow rate |  |  | 277.6087 | Abs Value of | Flow this | 2305.5725 | Abs Value of | Flow this | 5701.9552 | Abs Value of | Flow this | 11105.9533 | Abs Value of | Flow this | 18265.2042 | Abs Value of | Flow this | 25618.3551 | Abs Value of | Flow this | 32528.5131 | Abs Value of | Flow this | 38142.2398 | Abs Value of | Flow this | 42554.0896 | Abs Value of | Flow this | 47476.2508 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4921 |  |  | 98.4031 |  |  | 87.5581 |  |  | 51.3386 |  |  | -32.5112 |  |  | -161.1847 |  |  | -321.4088 |  |  | -479.6081 |  |  | -621.5753 |  |  | -798.2842
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48476 |  |  | 0.47468 |  |  | 0.42236 |  |  | 0.24765 |  |  | -0.15683 |  |  | -0.77753 |  |  | -1.5504 |  |  | -2.3135 |  |  | -2.9984 |  |  | -3.8508
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4921 |  |  | 48.4031 |  |  | 37.5581 |  |  | 1.3386 |  |  | -82.5112 |  |  | -211.1847 |  |  | -371.4088 |  |  | -529.6081 |  |  | -671.5753 |  |  | -848.2842
[13 empty] | Press drop ratio this iteration |  |  | 0.50245 |  |  | 0.49189 |  |  | 0.42895 |  |  | 0.026074 |  |  | 2.5379 |  |  | 1.3102 |  |  | 1.1556 |  |  | 1.1043 |  |  | 1.0804 |  |  | 1.0626
[13 empty] | Expansion factor | 12 |  | 0.73832 |  |  | 0.74388 |  |  | 0.7733 |  |  | 0.98603 |  |  | -0.39699 |  |  | 0.23767 |  |  | 0.28124 |  |  | 0.24956 |  |  | 0.39321 |  |  | 0.094024
[13 empty] | C Non choked w/ reducers | 5 |  | 1.2008 |  |  | 10.2225 |  |  | 29.3333 |  |  | 311.7367 |  |  | -206.2492 |  |  | 138.5721 |  |  | 82.1256 |  |  | 78.968 |  |  | 49.5459 |  |  | 238.4862
[13 empty] | C Choked w/ reducers | 5 |  | 1.1777 |  |  | 9.9935 |  |  | 28.046 |  |  | 94.3416 |  |  | 251.3052 |  |  | 74.6714 |  |  | 50.8492 |  |  | 44.3315 |  |  | 39.4083 |  |  | 55.4236
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.2008 |  |  | 10.2225 |  |  | 29.3333 |  |  | 311.7367 |  |  | 251.3052 |  |  | 74.6714 |  |  | 50.8492 |  |  | 44.3315 |  |  | 39.4083 |  |  | 55.4236
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.79922 | 277.6087 |  | 5.2225 | 2305.5725 |  | 19.3333 | 5701.9552 |  | 294.5367 | 11105.9533 |  | 7174 | 18265.2042 |  | 7174 | 25618.3551 |  | 7174 | 32528.5131 |  | 7174 | 38142.2398 |  | 7174 | 42554.0896 |  | 7174 | 47476.2508
[13 empty] | Next iteration flow rate |  |  | 283.1609 | Abs Value of | Flow this | 2328.6282 | Abs Value of | Flow this | 5758.9747 | Abs Value of | Flow this | 11217.0128 | Abs Value of | Flow this | 18447.8562 | Abs Value of | Flow this | 25874.5386 | Abs Value of | Flow this | 32853.7982 | Abs Value of | Flow this | 38523.6622 | Abs Value of | Flow this | 42979.6305 | Abs Value of | Flow this | 47951.0133 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4908 |  |  | 98.3605 |  |  | 87.2975 |  |  | 50.35 |  |  | -35.1852 |  |  | -166.445 |  |  | -329.8896 |  |  | -491.2687 |  |  | -636.0895 |  |  | -816.3502
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48475 |  |  | 0.47447 |  |  | 0.42111 |  |  | 0.24288 |  |  | -0.16973 |  |  | -0.8029 |  |  | -1.5913 |  |  | -2.3698 |  |  | -3.0684 |  |  | -3.9379
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4908 |  |  | 48.3605 |  |  | 37.2975 |  |  | 0.35002 |  |  | -85.1852 |  |  | -216.445 |  |  | -379.8896 |  |  | -541.2687 |  |  | -686.0895 |  |  | -866.3502
[13 empty] | Press drop ratio this iteration |  |  | 0.50244 |  |  | 0.49167 |  |  | 0.42725 |  |  | 0.0069518 |  |  | 2.4211 |  |  | 1.3004 |  |  | 1.1516 |  |  | 1.1018 |  |  | 1.0786 |  |  | 1.0612
[13 empty] | Expansion factor | 12 |  | 0.73832 |  |  | 0.74399 |  |  | 0.7742 |  |  | 0.99628 |  |  | -0.33265 |  |  | 0.24337 |  |  | 0.28373 |  |  | 0.25124 |  |  | 0.39424 |  |  | 0.095206
[13 empty] | C Non choked w/ reducers | 5 |  | 1.2248 |  |  | 10.33 |  |  | 29.7397 |  |  | 615.3517 |  |  | -235.1856 |  |  | 132.8559 |  |  | 80.2449 |  |  | 77.4302 |  |  | 48.8132 |  |  | 232.7686
[13 empty] | C Choked w/ reducers | 5 |  | 1.2013 |  |  | 10.0978 |  |  | 28.4111 |  |  | 97.1559 |  |  | 234.5287 |  |  | 73.0346 |  |  | 50.0374 |  |  | 43.7121 |  |  | 38.8942 |  |  | 54.7391
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.2248 |  |  | 10.33 |  |  | 29.7397 |  |  | 615.3517 |  |  | 234.5287 |  |  | 73.0346 |  |  | 50.0374 |  |  | 43.7121 |  |  | 38.8942 |  |  | 54.7391
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.77519 | 283.1609 |  | 5.33 | 2328.6282 |  | 19.7397 | 5758.9747 |  | 598.1517 | 11217.0128 |  | 7174 | 18447.8562 |  | 7174 | 25874.5386 |  | 7174 | 32853.7982 |  | 7174 | 38523.6622 |  | 7174 | 42979.6305 |  | 7174 | 47951.0133
[13 empty] | Next iteration flow rate |  |  | 288.8241 | Abs Value of | Flow this | 2351.9145 | Abs Value of | Flow this | 5816.5645 | Abs Value of | Flow this | 11329.183 | Abs Value of | Flow this | 18632.3348 | Abs Value of | Flow this | 26133.284 | Abs Value of | Flow this | 33182.3362 | Abs Value of | Flow this | 38908.8988 | Abs Value of | Flow this | 43409.4268 | Abs Value of | Flow this | 48430.5234 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4895 |  |  | 98.317 |  |  | 87.0317 |  |  | 49.3416 |  |  | -37.9129 |  |  | -171.811 |  |  | -338.5409 |  |  | -503.1637 |  |  | -650.8954 |  |  | -834.7793
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48474 |  |  | 0.47426 |  |  | 0.41983 |  |  | 0.23801 |  |  | -0.18289 |  |  | -0.82879 |  |  | -1.6331 |  |  | -2.4272 |  |  | -3.1398 |  |  | -4.0268
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4895 |  |  | 48.317 |  |  | 37.0317 |  |  | -0.65845 |  |  | -87.9129 |  |  | -221.811 |  |  | -388.5409 |  |  | -553.1637 |  |  | -700.8954 |  |  | -884.7793
[13 empty] | Press drop ratio this iteration |  |  | 0.50244 |  |  | 0.49144 |  |  | 0.4255 |  |  | -0.013345 |  |  | 2.3188 |  |  | 1.291 |  |  | 1.1477 |  |  | 1.0994 |  |  | 1.0768 |  |  | 1.0599
[13 empty] | Expansion factor | 12 |  | 0.73833 |  |  | 0.74411 |  |  | 0.77512 |  |  | 1.0071 |  |  | -0.27638 |  |  | 0.24883 |  |  | 0.28614 |  |  | 0.25287 |  |  | 0.39525 |  |  | 0.096359
[13 empty] | C Non choked w/ reducers | 5 |  | 1.2493 |  |  | 10.4386 |  |  | 30.1547 |  |  | #NUM! |  |  | -271.123 |  |  | 127.6029 |  |  | 78.4433 |  |  | 75.9449 |  |  | 48.0973 |  |  | 227.3005
[13 empty] | C Choked w/ reducers | 5 |  | 1.2253 |  |  | 10.2033 |  |  | 28.7828 |  |  | 100.1331 |  |  | 219.8316 |  |  | 71.4611 |  |  | 49.2463 |  |  | 43.1055 |  |  | 38.3896 |  |  | 54.0659
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.2493 |  |  | 10.4386 |  |  | 30.1547 |  |  | #NUM! |  |  | 219.8316 |  |  | 71.4611 |  |  | 49.2463 |  |  | 43.1055 |  |  | 38.3896 |  |  | 54.0659
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.75067 | 288.8241 |  | 5.4386 | 2351.9145 |  | 20.1547 | 5816.5645 |  | 7174 | 11329.183 |  | 7174 | 18632.3348 |  | 7174 | 26133.284 |  | 7174 | 33182.3362 |  | 7174 | 38908.8988 |  | 7174 | 43409.4268 |  | 7174 | 48430.5234
[13 empty] | Next iteration flow rate |  |  | 294.6006 | Abs Value of | Flow this | 2375.4337 | Abs Value of | Flow this | 5874.7301 | Abs Value of | Flow this | 11442.4748 | Abs Value of | Flow this | 18818.6582 | Abs Value of | Flow this | 26394.6168 | Abs Value of | Flow this | 33514.1595 | Abs Value of | Flow this | 39297.9878 | Abs Value of | Flow this | 43843.521 | Abs Value of | Flow this | 48914.8286 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4882 |  |  | 98.2727 |  |  | 86.7605 |  |  | 48.3128 |  |  | -40.6955 |  |  | -177.2849 |  |  | -347.3661 |  |  | -515.2978 |  |  | -665.9989 |  |  | -853.5789
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48474 |  |  | 0.47405 |  |  | 0.41852 |  |  | 0.23305 |  |  | -0.19631 |  |  | -0.85519 |  |  | -1.6756 |  |  | -2.4857 |  |  | -3.2127 |  |  | -4.1175
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4882 |  |  | 48.2727 |  |  | 36.7605 |  |  | -1.6872 |  |  | -90.6955 |  |  | -227.2849 |  |  | -397.3661 |  |  | -565.2978 |  |  | -715.9989 |  |  | -903.5789
[13 empty] | Press drop ratio this iteration |  |  | 0.50243 |  |  | 0.49121 |  |  | 0.4237 |  |  | -0.034922 |  |  | 2.2286 |  |  | 1.282 |  |  | 1.1439 |  |  | 1.097 |  |  | 1.0751 |  |  | 1.0586
[13 empty] | Expansion factor | 12 |  | 0.73833 |  |  | 0.74423 |  |  | 0.77607 |  |  | 1.0187 |  |  | -0.22674 |  |  | 0.25406 |  |  | 0.28847 |  |  | 0.25446 |  |  | 0.39623 |  |  | 0.097483
[13 empty] | C Non choked w/ reducers | 5 |  | 1.2743 |  |  | 10.5485 |  |  | 30.5786 |  |  | #NUM! |  |  | -317.1856 |  |  | 122.7573 |  |  | 76.7157 |  |  | 74.5094 |  |  | 47.3978 |  |  | 222.0652
[13 empty] | C Choked w/ reducers | 5 |  | 1.2498 |  |  | 10.31 |  |  | 29.1615 |  |  | 103.2879 |  |  | 206.8486 |  |  | 69.9472 |  |  | 48.4751 |  |  | 42.5114 |  |  | 37.8942 |  |  | 53.4039
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.2743 |  |  | 10.5485 |  |  | 30.5786 |  |  | #NUM! |  |  | 206.8486 |  |  | 69.9472 |  |  | 48.4751 |  |  | 42.5114 |  |  | 37.8942 |  |  | 53.4039
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.72567 | 294.6006 |  | 5.5485 | 2375.4337 |  | 20.5786 | 5874.7301 |  | 7174 | 11442.4748 |  | 7174 | 18818.6582 |  | 7174 | 26394.6168 |  | 7174 | 33514.1595 |  | 7174 | 39297.9878 |  | 7174 | 43843.521 |  | 7174 | 48914.8286
[13 empty] | Next iteration flow rate |  |  | 300.4926 | Abs Value of | Flow this | 2399.188 | Abs Value of | Flow this | 5933.4774 | Abs Value of | Flow this | 11556.8995 | Abs Value of | Flow this | 19006.8447 | Abs Value of | Flow this | 26658.563 | Abs Value of | Flow this | 33849.3011 | Abs Value of | Flow this | 39690.9677 | Abs Value of | Flow this | 44281.9563 | Abs Value of | Flow this | 49403.9769 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4868 |  |  | 98.2275 |  |  | 86.4839 |  |  | 47.2634 |  |  | -43.534 |  |  | -182.8689 |  |  | -356.3686 |  |  | -527.6758 |  |  | -681.406 |  |  | -872.7563
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48473 |  |  | 0.47383 |  |  | 0.41718 |  |  | 0.22799 |  |  | -0.21 |  |  | -0.88213 |  |  | -1.7191 |  |  | -2.5454 |  |  | -3.287 |  |  | -4.21
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4868 |  |  | 48.2275 |  |  | 36.4839 |  |  | -2.7366 |  |  | -93.534 |  |  | -232.8689 |  |  | -406.3686 |  |  | -577.6758 |  |  | -731.406 |  |  | -922.7563
[13 empty] | Press drop ratio this iteration |  |  | 0.50242 |  |  | 0.49098 |  |  | 0.42186 |  |  | -0.057901 |  |  | 2.1485 |  |  | 1.2734 |  |  | 1.1403 |  |  | 1.0948 |  |  | 1.0734 |  |  | 1.0573
[13 empty] | Expansion factor | 12 |  | 0.73833 |  |  | 0.74435 |  |  | 0.77704 |  |  | 1.031 |  |  | -0.18264 |  |  | 0.25907 |  |  | 0.29073 |  |  | 0.25601 |  |  | 0.39718 |  |  | 0.098581
[13 empty] | C Non choked w/ reducers | 5 |  | 1.2998 |  |  | 10.6597 |  |  | 31.0119 |  |  | #NUM! |  |  | -378.6377 |  |  | 118.2721 |  |  | 75.0573 |  |  | 73.1211 |  |  | 46.7139 |  |  | 217.0476
[13 empty] | C Choked w/ reducers | 5 |  | 1.2748 |  |  | 10.4179 |  |  | 29.5473 |  |  | 106.6371 |  |  | 195.2953 |  |  | 68.4895 |  |  | 47.7231 |  |  | 41.9293 |  |  | 37.4077 |  |  | 52.7527
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.2998 |  |  | 10.6597 |  |  | 31.0119 |  |  | #NUM! |  |  | 195.2953 |  |  | 68.4895 |  |  | 47.7231 |  |  | 41.9293 |  |  | 37.4077 |  |  | 52.7527
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.70016 | 300.4926 |  | 5.6597 | 2399.188 |  | 21.0119 | 5933.4774 |  | 7174 | 11556.8995 |  | 7174 | 19006.8447 |  | 7174 | 26658.563 |  | 7174 | 33849.3011 |  | 7174 | 39690.9677 |  | 7174 | 44281.9563 |  | 7174 | 49403.9769
[13 empty] | Next iteration flow rate |  |  | 306.5025 | Abs Value of | Flow this | 2423.1799 | Abs Value of | Flow this | 5992.8122 | Abs Value of | Flow this | 11672.4685 | Abs Value of | Flow this | 19196.9132 | Abs Value of | Flow this | 26925.1486 | Abs Value of | Flow this | 34187.7941 | Abs Value of | Flow this | 40087.8773 | Abs Value of | Flow this | 44724.7758 | Abs Value of | Flow this | 49898.0167 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4853 |  |  | 98.1813 |  |  | 86.2017 |  |  | 46.1929 |  |  | -46.4295 |  |  | -188.565 |  |  | -365.5521 |  |  | -540.3026 |  |  | -697.1227 |  |  | -892.3192
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48472 |  |  | 0.47361 |  |  | 0.41582 |  |  | 0.22283 |  |  | -0.22397 |  |  | -0.9096 |  |  | -1.7634 |  |  | -2.6063 |  |  | -3.3628 |  |  | -4.3044
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4853 |  |  | 48.1813 |  |  | 36.2017 |  |  | -3.8071 |  |  | -96.4295 |  |  | -238.565 |  |  | -415.5521 |  |  | -590.3026 |  |  | -747.1227 |  |  | -942.3192
[13 empty] | Press drop ratio this iteration |  |  | 0.50241 |  |  | 0.49074 |  |  | 0.41997 |  |  | -0.082418 |  |  | 2.0769 |  |  | 1.2652 |  |  | 1.1368 |  |  | 1.0925 |  |  | 1.0717 |  |  | 1.056
[13 empty] | Expansion factor | 12 |  | 0.73834 |  |  | 0.74447 |  |  | 0.77804 |  |  | 1.0442 |  |  | -0.14322 |  |  | 0.26388 |  |  | 0.29293 |  |  | 0.25751 |  |  | 0.39811 |  |  | 0.099651
[13 empty] | C Non choked w/ reducers | 5 |  | 1.3259 |  |  | 10.7722 |  |  | 31.4548 |  |  | #NUM! |  |  | -465.1057 |  |  | 114.1072 |  |  | 73.4639 |  |  | 71.7775 |  |  | 46.0452 |  |  | 212.2341
[13 empty] | C Choked w/ reducers | 5 |  | 1.3003 |  |  | 10.527 |  |  | 29.9405 |  |  | 110.1995 |  |  | 184.947 |  |  | 67.0847 |  |  | 46.9894 |  |  | 41.3589 |  |  | 36.93 |  |  | 52.1122
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.3259 |  |  | 10.7722 |  |  | 31.4548 |  |  | #NUM! |  |  | 184.947 |  |  | 67.0847 |  |  | 46.9894 |  |  | 41.3589 |  |  | 36.93 |  |  | 52.1122
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.67414 | 306.5025 |  | 5.7722 | 2423.1799 |  | 21.4548 | 5992.8122 |  | 7174 | 11672.4685 |  | 7174 | 19196.9132 |  | 7174 | 26925.1486 |  | 7174 | 34187.7941 |  | 7174 | 40087.8773 |  | 7174 | 44724.7758 |  | 7174 | 49898.0167
[13 empty] | Next iteration flow rate |  |  | 312.6325 | Abs Value of | Flow this | 2447.4117 | Abs Value of | Flow this | 6052.7403 | Abs Value of | Flow this | 11789.1932 | Abs Value of | Flow this | 19388.8823 | Abs Value of | Flow this | 27194.4001 | Abs Value of | Flow this | 34529.6721 | Abs Value of | Flow this | 40488.7561 | Abs Value of | Flow this | 45172.0236 | Abs Value of | Flow this | 50396.9969 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4838 |  |  | 98.1343 |  |  | 85.9139 |  |  | 45.1008 |  |  | -49.3833 |  |  | -194.3757 |  |  | -374.9203 |  |  | -553.1832 |  |  | -713.1554 |  |  | -912.2754
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48472 |  |  | 0.47338 |  |  | 0.41443 |  |  | 0.21756 |  |  | -0.23822 |  |  | -0.93763 |  |  | -1.8085 |  |  | -2.6685 |  |  | -3.4401 |  |  | -4.4007
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4838 |  |  | 48.1343 |  |  | 35.9139 |  |  | -4.8992 |  |  | -99.3833 |  |  | -244.3757 |  |  | -424.9203 |  |  | -603.1832 |  |  | -763.1554 |  |  | -962.2754
[13 empty] | Press drop ratio this iteration |  |  | 0.50241 |  |  | 0.49049 |  |  | 0.41802 |  |  | -0.10863 |  |  | 2.0125 |  |  | 1.2572 |  |  | 1.1334 |  |  | 1.0904 |  |  | 1.0701 |  |  | 1.0548
[13 empty] | Expansion factor | 12 |  | 0.73834 |  |  | 0.7446 |  |  | 0.77907 |  |  | 1.0582 |  |  | -0.10776 |  |  | 0.26849 |  |  | 0.29505 |  |  | 0.25898 |  |  | 0.39901 |  |  | 0.1007
[13 empty] | C Non choked w/ reducers | 5 |  | 1.3524 |  |  | 10.886 |  |  | 31.9077 |  |  | #NUM! |  |  | -596.2911 |  |  | 110.2284 |  |  | 71.9315 |  |  | 70.4764 |  |  | 45.3912 |  |  | 207.612
[13 empty] | C Choked w/ reducers | 5 |  | 1.3264 |  |  | 10.6374 |  |  | 30.3412 |  |  | 113.9964 |  |  | 175.6237 |  |  | 65.7301 |  |  | 46.2734 |  |  | 40.7999 |  |  | 36.4608 |  |  | 51.4819
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.3524 |  |  | 10.886 |  |  | 31.9077 |  |  | #NUM! |  |  | 175.6237 |  |  | 65.7301 |  |  | 46.2734 |  |  | 40.7999 |  |  | 36.4608 |  |  | 51.4819
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.6476 | 312.6325 |  | 5.886 | 2447.4117 |  | 21.9077 | 6052.7403 |  | 7174 | 11789.1932 |  | 7174 | 19388.8823 |  | 7174 | 27194.4001 |  | 7174 | 34529.6721 |  | 7174 | 40488.7561 |  | 7174 | 45172.0236 |  | 7174 | 50396.9969
[13 empty] | Next iteration flow rate |  |  | 318.8852 | Abs Value of | Flow this | 2471.8858 | Abs Value of | Flow this | 6113.2677 | Abs Value of | Flow this | 11907.0851 | Abs Value of | Flow this | 19582.7711 | Abs Value of | Flow this | 27466.3441 | Abs Value of | Flow this | 34874.9688 | Abs Value of | Flow this | 40893.6437 | Abs Value of | Flow this | 45623.7438 | Abs Value of | Flow this | 50900.9668 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4822 |  |  | 98.0863 |  |  | 85.6202 |  |  | 43.9869 |  |  | -52.3964 |  |  | -200.3032 |  |  | -384.4767 |  |  | -566.3227 |  |  | -729.5103 |  |  | -932.6326
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48471 |  |  | 0.47315 |  |  | 0.41302 |  |  | 0.21218 |  |  | -0.25275 |  |  | -0.96623 |  |  | -1.8546 |  |  | -2.7318 |  |  | -3.519 |  |  | -4.4989
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4822 |  |  | 48.0863 |  |  | 35.6202 |  |  | -6.0131 |  |  | -102.3964 |  |  | -250.3032 |  |  | -434.4767 |  |  | -616.3227 |  |  | -779.5103 |  |  | -982.6326
[13 empty] | Press drop ratio this iteration |  |  | 0.5024 |  |  | 0.49024 |  |  | 0.41603 |  |  | -0.1367 |  |  | 1.9543 |  |  | 1.2496 |  |  | 1.13 |  |  | 1.0883 |  |  | 1.0685 |  |  | 1.0536
[13 empty] | Expansion factor | 12 |  | 0.73834 |  |  | 0.74473 |  |  | 0.78013 |  |  | 1.0732 |  |  | -0.075713 |  |  | 0.27292 |  |  | 0.29711 |  |  | 0.2604 |  |  | 0.3999 |  |  | 0.10172
[13 empty] | C Non choked w/ reducers | 5 |  | 1.3795 |  |  | 11.0011 |  |  | 32.3709 |  |  | #NUM! |  |  | -819.8403 |  |  | 106.606 |  |  | 70.4566 |  |  | 69.2158 |  |  | 44.7512 |  |  | 203.1696
[13 empty] | C Choked w/ reducers | 5 |  | 1.3529 |  |  | 10.749 |  |  | 30.7497 |  |  | 118.0523 |  |  | 167.1795 |  |  | 64.4228 |  |  | 45.5745 |  |  | 40.2518 |  |  | 35.9998 |  |  | 50.8618
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.3795 |  |  | 11.0011 |  |  | 32.3709 |  |  | #NUM! |  |  | 167.1795 |  |  | 64.4228 |  |  | 45.5745 |  |  | 40.2518 |  |  | 35.9998 |  |  | 50.8618
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.62053 | 318.8852 |  | 6.0011 | 2471.8858 |  | 22.3709 | 6113.2677 |  | 7174 | 11907.0851 |  | 7174 | 19582.7711 |  | 7174 | 27466.3441 |  | 7174 | 34874.9688 |  | 7174 | 40893.6437 |  | 7174 | 45623.7438 |  | 7174 | 50900.9668
[13 empty] | Next iteration flow rate |  |  | 325.2629 | Abs Value of | Flow this | 2496.6047 | Abs Value of | Flow this | 6174.4004 | Abs Value of | Flow this | 12026.156 | Abs Value of | Flow this | 19778.5989 | Abs Value of | Flow this | 27741.0076 | Abs Value of | Flow this | 35223.7185 | Abs Value of | Flow this | 41302.5801 | Abs Value of | Flow this | 46079.9813 | Abs Value of | Flow this | 51409.9765 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4806 |  |  | 98.0373 |  |  | 85.3207 |  |  | 42.8505 |  |  | -55.47 |  |  | -206.3498 |  |  | -394.2251 |  |  | -579.7263 |  |  | -746.194 |  |  | -953.399
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4847 |  |  | 0.47291 |  |  | 0.41157 |  |  | 0.2067 |  |  | -0.26758 |  |  | -0.99539 |  |  | -1.9017 |  |  | -2.7965 |  |  | -3.5995 |  |  | -4.599
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4806 |  |  | 48.0373 |  |  | 35.3207 |  |  | -7.1495 |  |  | -105.47 |  |  | -256.3498 |  |  | -444.2251 |  |  | -629.7263 |  |  | -796.194 |  |  | -1003.399
[13 empty] | Press drop ratio this iteration |  |  | 0.50239 |  |  | 0.48999 |  |  | 0.41398 |  |  | -0.16685 |  |  | 1.9014 |  |  | 1.2423 |  |  | 1.1268 |  |  | 1.0862 |  |  | 1.067 |  |  | 1.0524
[13 empty] | Expansion factor | 12 |  | 0.73835 |  |  | 0.74486 |  |  | 0.78121 |  |  | 1.0894 |  |  | -0.046607 |  |  | 0.27717 |  |  | 0.29911 |  |  | 0.26179 |  |  | 0.40076 |  |  | 0.10271
[13 empty] | C Non choked w/ reducers | 5 |  | 1.4071 |  |  | 11.1176 |  |  | 32.8449 |  |  | #NUM! |  |  | -1288.1547 |  |  | 103.2147 |  |  | 69.0356 |  |  | 67.9935 |  |  | 44.1249 |  |  | 198.8962
[13 empty] | C Choked w/ reducers | 5 |  | 1.38 |  |  | 10.8619 |  |  | 31.1662 |  |  | 122.3948 |  |  | 159.495 |  |  | 63.1604 |  |  | 44.892 |  |  | 39.7143 |  |  | 35.5468 |  |  | 50.2515
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.4071 |  |  | 11.1176 |  |  | 32.8449 |  |  | #NUM! |  |  | 159.495 |  |  | 63.1604 |  |  | 44.892 |  |  | 39.7143 |  |  | 35.5468 |  |  | 50.2515
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.59291 | 325.2629 |  | 6.1176 | 2496.6047 |  | 22.8449 | 6174.4004 |  | 7174 | 12026.156 |  | 7174 | 19778.5989 |  | 7174 | 27741.0076 |  | 7174 | 35223.7185 |  | 7174 | 41302.5801 |  | 7174 | 46079.9813 |  | 7174 | 51409.9765
[13 empty] | Next iteration flow rate |  |  | 331.7681 | Abs Value of | Flow this | 2521.5707 | Abs Value of | Flow this | 6236.1444 | Abs Value of | Flow this | 12146.4176 | Abs Value of | Flow this | 19976.3848 | Abs Value of | Flow this | 28018.4176 | Abs Value of | Flow this | 35575.9557 | Abs Value of | Flow this | 41715.6059 | Abs Value of | Flow this | 46540.7811 | Abs Value of | Flow this | 51924.0763 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4789 |  |  | 97.9873 |  |  | 85.0151 |  |  | 41.6913 |  |  | -58.6055 |  |  | -212.5179 |  |  | -404.1696 |  |  | -593.3993 |  |  | -763.213 |  |  | -974.5829
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48469 |  |  | 0.47267 |  |  | 0.4101 |  |  | 0.20111 |  |  | -0.2827 |  |  | -1.0251 |  |  | -1.9496 |  |  | -2.8625 |  |  | -3.6816 |  |  | -4.7012
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4789 |  |  | 47.9873 |  |  | 35.0151 |  |  | -8.3087 |  |  | -108.6055 |  |  | -262.5179 |  |  | -454.1696 |  |  | -643.3993 |  |  | -813.213 |  |  | -1024.5829
[13 empty] | Press drop ratio this iteration |  |  | 0.50238 |  |  | 0.48973 |  |  | 0.41187 |  |  | -0.19929 |  |  | 1.8532 |  |  | 1.2353 |  |  | 1.1237 |  |  | 1.0843 |  |  | 1.0655 |  |  | 1.0513
[13 empty] | Expansion factor | 12 |  | 0.73835 |  |  | 0.745 |  |  | 0.78232 |  |  | 1.1068 |  |  | -0.020062 |  |  | 0.28127 |  |  | 0.30106 |  |  | 0.26314 |  |  | 0.4016 |  |  | 0.10368
[13 empty] | C Non choked w/ reducers | 5 |  | 1.4353 |  |  | 11.2354 |  |  | 33.3301 |  |  | #NUM! |  |  | -2897.803 |  |  | 100.0321 |  |  | 67.6657 |  |  | 66.8079 |  |  | 43.5118 |  |  | 194.7821
[13 empty] | C Choked w/ reducers | 5 |  | 1.4076 |  |  | 10.9762 |  |  | 31.591 |  |  | 127.0559 |  |  | 152.4715 |  |  | 61.9405 |  |  | 44.2253 |  |  | 39.1872 |  |  | 35.1017 |  |  | 49.6508
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.4353 |  |  | 11.2354 |  |  | 33.3301 |  |  | #NUM! |  |  | 152.4715 |  |  | 61.9405 |  |  | 44.2253 |  |  | 39.1872 |  |  | 35.1017 |  |  | 49.6508
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.56474 | 331.7681 |  | 6.2354 | 2521.5707 |  | 23.3301 | 6236.1444 |  | 7174 | 12146.4176 |  | 7174 | 19976.3848 |  | 7174 | 28018.4176 |  | 7174 | 35575.9557 |  | 7174 | 41715.6059 |  | 7174 | 46540.7811 |  | 7174 | 51924.0763
[13 empty] | Next iteration flow rate |  |  | 338.4035 | Abs Value of | Flow this | 2546.7864 | Abs Value of | Flow this | 6298.5059 | Abs Value of | Flow this | 12267.8817 | Abs Value of | Flow this | 20176.1487 | Abs Value of | Flow this | 28298.6018 | Abs Value of | Flow this | 35931.7152 | Abs Value of | Flow this | 42132.762 | Abs Value of | Flow this | 47006.1889 | Abs Value of | Flow this | 52443.317 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4771 |  |  | 97.9364 |  |  | 84.7034 |  |  | 40.5088 |  |  | -61.804 |  |  | -218.81 |  |  | -414.3139 |  |  | -607.3471 |  |  | -780.5741 |  |  | -996.1925
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48468 |  |  | 0.47243 |  |  | 0.40859 |  |  | 0.19541 |  |  | -0.29813 |  |  | -1.0555 |  |  | -1.9986 |  |  | -2.9297 |  |  | -3.7654 |  |  | -4.8055
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4771 |  |  | 47.9364 |  |  | 34.7034 |  |  | -9.4912 |  |  | -111.804 |  |  | -268.81 |  |  | -464.3139 |  |  | -657.3471 |  |  | -830.5741 |  |  | -1046.1925
[13 empty] | Press drop ratio this iteration |  |  | 0.50237 |  |  | 0.48946 |  |  | 0.40971 |  |  | -0.2343 |  |  | 1.809 |  |  | 1.2285 |  |  | 1.1207 |  |  | 1.0823 |  |  | 1.0641 |  |  | 1.0502
[13 empty] | Expansion factor | 12 |  | 0.73836 |  |  | 0.74514 |  |  | 0.78347 |  |  | 1.1255 |  |  | 0.0042418 |  |  | 0.2852 |  |  | 0.30294 |  |  | 0.26446 |  |  | 0.40241 |  |  | 0.10463
[13 empty] | C Non choked w/ reducers | 5 |  | 1.464 |  |  | 11.3546 |  |  | 33.827 |  |  | #NUM! |  |  | 13285.3236 |  |  | 97.0389 |  |  | 66.3438 |  |  | 65.6572 |  |  | 42.9115 |  |  | 190.8182
[13 empty] | C Choked w/ reducers | 5 |  | 1.4358 |  |  | 11.0917 |  |  | 32.0244 |  |  | 132.0725 |  |  | 146.0266 |  |  | 60.761 |  |  | 43.5739 |  |  | 38.6702 |  |  | 34.6642 |  |  | 49.0595
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.464 |  |  | 11.3546 |  |  | 33.827 |  |  | #NUM! |  |  | 146.0266 |  |  | 60.761 |  |  | 43.5739 |  |  | 38.6702 |  |  | 34.6642 |  |  | 49.0595
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.53601 | 338.4035 |  | 6.3546 | 2546.7864 |  | 23.827 | 6298.5059 |  | 7174 | 12267.8817 |  | 7174 | 20176.1487 |  | 7174 | 28298.6018 |  | 7174 | 35931.7152 |  | 7174 | 42132.762 |  | 7174 | 47006.1889 |  | 7174 | 52443.317
[13 empty] | Next iteration flow rate |  |  | 345.1716 | Abs Value of | Flow this | 2572.2543 | Abs Value of | Flow this | 6361.4909 | Abs Value of | Flow this | 12390.5606 | Abs Value of | Flow this | 20377.9102 | Abs Value of | Flow this | 28581.5878 | Abs Value of | Flow this | 36291.0324 | Abs Value of | Flow this | 42554.0896 | Abs Value of | Flow this | 47476.2508 | Abs Value of | Flow this | 52967.7502 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4753 |  |  | 97.8844 |  |  | 84.3855 |  |  | 39.3025 |  |  | -65.0667 |  |  | -225.2286 |  |  | -424.6621 |  |  | -621.5753 |  |  | -798.2842 |  |  | -1018.2365
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48467 |  |  | 0.47218 |  |  | 0.40706 |  |  | 0.18959 |  |  | -0.31387 |  |  | -1.0865 |  |  | -2.0485 |  |  | -2.9984 |  |  | -3.8508 |  |  | -4.9118
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4753 |  |  | 47.8844 |  |  | 34.3855 |  |  | -10.6975 |  |  | -115.0667 |  |  | -275.2286 |  |  | -474.6621 |  |  | -671.5753 |  |  | -848.2842 |  |  | -1068.2365
[13 empty] | Press drop ratio this iteration |  |  | 0.50237 |  |  | 0.48919 |  |  | 0.40748 |  |  | -0.27218 |  |  | 1.7684 |  |  | 1.222 |  |  | 1.1177 |  |  | 1.0804 |  |  | 1.0626 |  |  | 1.0491
[13 empty] | Expansion factor | 12 |  | 0.73836 |  |  | 0.74528 |  |  | 0.78464 |  |  | 1.1458 |  |  | 0.026572 |  |  | 0.28899 |  |  | 0.30477 |  |  | 0.26574 |  |  | 0.40321 |  |  | 0.10556
[13 empty] | C Non choked w/ reducers | 5 |  | 1.4933 |  |  | 11.4753 |  |  | 34.3359 |  |  | #NUM! |  |  | 2057.7807 |  |  | 94.2178 |  |  | 65.0675 |  |  | 64.5397 |  |  | 42.3234 |  |  | 186.996
[13 empty] | C Choked w/ reducers | 5 |  | 1.4645 |  |  | 11.2086 |  |  | 32.4665 |  |  | 137.4874 |  |  | 140.0911 |  |  | 59.6197 |  |  | 42.9372 |  |  | 38.1628 |  |  | 34.2341 |  |  | 48.4774
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.4933 |  |  | 11.4753 |  |  | 34.3359 |  |  | #NUM! |  |  | 140.0911 |  |  | 59.6197 |  |  | 42.9372 |  |  | 38.1628 |  |  | 34.2341 |  |  | 48.4774
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.50669 | 345.1716 |  | 6.4753 | 2572.2543 |  | 24.3359 | 6361.4909 |  | 7174 | 12390.5606 |  | 7174 | 20377.9102 |  | 7174 | 28581.5878 |  | 7174 | 36291.0324 |  | 7174 | 42554.0896 |  | 7174 | 47476.2508 |  | 7174 | 52967.7502
[13 empty] | Next iteration flow rate |  |  | 352.075 | Abs Value of | Flow this | 2597.9768 | Abs Value of | Flow this | 6425.1058 | Abs Value of | Flow this | 12514.4662 | Abs Value of | Flow this | 20581.6893 | Abs Value of | Flow this | 28867.4037 | Abs Value of | Flow this | 36653.9427 | Abs Value of | Flow this | 42979.6305 | Abs Value of | Flow this | 47951.0133 | Abs Value of | Flow this | 53497.4277 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4734 |  |  | 97.8314 |  |  | 84.0611 |  |  | 38.072 |  |  | -68.3951 |  |  | -231.7762 |  |  | -435.2183 |  |  | -636.0895 |  |  | -816.3502 |  |  | -1040.7235
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48467 |  |  | 0.47192 |  |  | 0.4055 |  |  | 0.18365 |  |  | -0.32993 |  |  | -1.118 |  |  | -2.0994 |  |  | -3.0684 |  |  | -3.9379 |  |  | -5.0203
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4734 |  |  | 47.8314 |  |  | 34.0611 |  |  | -11.928 |  |  | -118.3951 |  |  | -281.7762 |  |  | -485.2183 |  |  | -686.0895 |  |  | -866.3502 |  |  | -1090.7235
[13 empty] | Press drop ratio this iteration |  |  | 0.50236 |  |  | 0.48892 |  |  | 0.40519 |  |  | -0.3133 |  |  | 1.731 |  |  | 1.2157 |  |  | 1.1149 |  |  | 1.0786 |  |  | 1.0612 |  |  | 1.048
[13 empty] | Expansion factor | 12 |  | 0.73837 |  |  | 0.74542 |  |  | 0.78585 |  |  | 1.1679 |  |  | 0.047156 |  |  | 0.29264 |  |  | 0.30654 |  |  | 0.26699 |  |  | 0.40399 |  |  | 0.10646
[13 empty] | C Non choked w/ reducers | 5 |  | 1.5232 |  |  | 11.5974 |  |  | 34.8575 |  |  | #NUM! |  |  | 1126.1181 |  |  | 91.554 |  |  | 63.8342 |  |  | 63.4541 |  |  | 41.7474 |  |  | 183.3078
[13 empty] | C Choked w/ reducers | 5 |  | 1.4939 |  |  | 11.3268 |  |  | 32.9177 |  |  | 143.3504 |  |  | 134.6065 |  |  | 58.5148 |  |  | 42.3147 |  |  | 37.665 |  |  | 33.8113 |  |  | 47.9042
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.5232 |  |  | 11.5974 |  |  | 34.8575 |  |  | #NUM! |  |  | 134.6065 |  |  | 58.5148 |  |  | 42.3147 |  |  | 37.665 |  |  | 33.8113 |  |  | 47.9042
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.4768 | 352.075 |  | 6.5974 | 2597.9768 |  | 24.8575 | 6425.1058 |  | 7174 | 12514.4662 |  | 7174 | 20581.6893 |  | 7174 | 28867.4037 |  | 7174 | 36653.9427 |  | 7174 | 42979.6305 |  | 7174 | 47951.0133 |  | 7174 | 53497.4277
[13 empty] | Next iteration flow rate |  |  | 359.1165 | Abs Value of | Flow this | 2623.9566 | Abs Value of | Flow this | 6489.3569 | Abs Value of | Flow this | 12639.6108 | Abs Value of | Flow this | 20787.5062 | Abs Value of | Flow this | 29156.0778 | Abs Value of | Flow this | 37020.4821 | Abs Value of | Flow this | 43409.4268 | Abs Value of | Flow this | 48430.5234 | Abs Value of | Flow this | 54032.402 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4714 |  |  | 97.7773 |  |  | 83.7302 |  |  | 36.8167 |  |  | -71.7903 |  |  | -238.4554 |  |  | -445.9867 |  |  | -650.8954 |  |  | -834.7793 |  |  | -1063.6626
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48466 |  |  | 0.47166 |  |  | 0.4039 |  |  | 0.1776 |  |  | -0.3463 |  |  | -1.1503 |  |  | -2.1514 |  |  | -3.1398 |  |  | -4.0268 |  |  | -5.1309
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4714 |  |  | 47.7773 |  |  | 33.7302 |  |  | -13.1833 |  |  | -121.7903 |  |  | -288.4554 |  |  | -495.9867 |  |  | -700.8954 |  |  | -884.7793 |  |  | -1113.6626
[13 empty] | Press drop ratio this iteration |  |  | 0.50235 |  |  | 0.48863 |  |  | 0.40284 |  |  | -0.35808 |  |  | 1.6965 |  |  | 1.2097 |  |  | 1.1121 |  |  | 1.0768 |  |  | 1.0599 |  |  | 1.047
[13 empty] | Expansion factor | 12 |  | 0.73837 |  |  | 0.74557 |  |  | 0.78709 |  |  | 1.1918 |  |  | 0.066187 |  |  | 0.29616 |  |  | 0.30827 |  |  | 0.2682 |  |  | 0.40475 |  |  | 0.10735
[13 empty] | C Non choked w/ reducers | 5 |  | 1.5537 |  |  | 11.7209 |  |  | 35.3922 |  |  | #NUM! |  |  | 779.8457 |  |  | 89.0339 |  |  | 62.6417 |  |  | 62.3988 |  |  | 41.1829 |  |  | 179.7463
[13 empty] | C Choked w/ reducers | 5 |  | 1.5238 |  |  | 11.4464 |  |  | 33.3782 |  |  | 149.7203 |  |  | 129.5229 |  |  | 57.4445 |  |  | 41.706 |  |  | 37.1763 |  |  | 33.3955 |  |  | 47.3398
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.5537 |  |  | 11.7209 |  |  | 35.3922 |  |  | #NUM! |  |  | 129.5229 |  |  | 57.4445 |  |  | 41.706 |  |  | 37.1763 |  |  | 33.3955 |  |  | 47.3398
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.4463 | 359.1165 |  | 6.7209 | 2623.9566 |  | 25.3922 | 6489.3569 |  | 7174 | 12639.6108 |  | 7174 | 20787.5062 |  | 7174 | 29156.0778 |  | 7174 | 37020.4821 |  | 7174 | 43409.4268 |  | 7174 | 48430.5234 |  | 7174 | 54032.402
[13 empty] | Next iteration flow rate |  |  | 366.2988 | Abs Value of | Flow this | 2650.1961 | Abs Value of | Flow this | 6554.2504 | Abs Value of | Flow this | 12766.0069 | Abs Value of | Flow this | 20995.3812 | Abs Value of | Flow this | 29447.6385 | Abs Value of | Flow this | 37390.687 | Abs Value of | Flow this | 43843.521 | Abs Value of | Flow this | 48914.8286 | Abs Value of | Flow this | 54572.726 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4693 |  |  | 97.7221 |  |  | 83.3927 |  |  | 35.5362 |  |  | -75.2538 |  |  | -245.2689 |  |  | -456.9716 |  |  | -665.9989 |  |  | -853.5789 |  |  | -1087.0627
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48465 |  |  | 0.47139 |  |  | 0.40227 |  |  | 0.17142 |  |  | -0.36301 |  |  | -1.1831 |  |  | -2.2043 |  |  | -3.2127 |  |  | -4.1175 |  |  | -5.2438
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4693 |  |  | 47.7221 |  |  | 33.3927 |  |  | -14.4638 |  |  | -125.2538 |  |  | -295.2689 |  |  | -506.9716 |  |  | -715.9989 |  |  | -903.5789 |  |  | -1137.0627
[13 empty] | Press drop ratio this iteration |  |  | 0.50234 |  |  | 0.48834 |  |  | 0.40043 |  |  | -0.40702 |  |  | 1.6644 |  |  | 1.2039 |  |  | 1.1094 |  |  | 1.0751 |  |  | 1.0586 |  |  | 1.046
[13 empty] | Expansion factor | 12 |  | 0.73838 |  |  | 0.74572 |  |  | 0.78837 |  |  | 1.2181 |  |  | 0.083831 |  |  | 0.29954 |  |  | 0.30995 |  |  | 0.26938 |  |  | 0.40549 |  |  | 0.10821
[13 empty] | C Non choked w/ reducers | 5 |  | 1.5848 |  |  | 11.8459 |  |  | 35.9407 |  |  | #NUM! |  |  | 598.9307 |  |  | 86.6459 |  |  | 61.4879 |  |  | 61.3725 |  |  | 40.6296 |  |  | 176.3048
[13 empty] | C Choked w/ reducers | 5 |  | 1.5543 |  |  | 11.5674 |  |  | 33.8485 |  |  | 156.6664 |  |  | 124.7973 |  |  | 56.4072 |  |  | 41.1105 |  |  | 36.6965 |  |  | 32.9866 |  |  | 46.784
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.5848 |  |  | 11.8459 |  |  | 35.9407 |  |  | #NUM! |  |  | 124.7973 |  |  | 56.4072 |  |  | 41.1105 |  |  | 36.6965 |  |  | 32.9866 |  |  | 46.784
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.41518 | 366.2988 |  | 6.8459 | 2650.1961 |  | 25.9407 | 6554.2504 |  | 7174 | 12766.0069 |  | 7174 | 20995.3812 |  | 7174 | 29447.6385 |  | 7174 | 37390.687 |  | 7174 | 43843.521 |  | 7174 | 48914.8286 |  | 7174 | 54572.726
[13 empty] | Next iteration flow rate |  |  | 373.6248 | Abs Value of | Flow this | 2676.6981 | Abs Value of | Flow this | 6619.793 | Abs Value of | Flow this | 12893.667 | Abs Value of | Flow this | 21205.335 | Abs Value of | Flow this | 29742.1149 | Abs Value of | Flow this | 37764.5938 | Abs Value of | Flow this | 44281.9563 | Abs Value of | Flow this | 49403.9769 | Abs Value of | Flow this | 55118.4533 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4671 |  |  | 97.6658 |  |  | 83.0484 |  |  | 34.23 |  |  | -78.7869 |  |  | -252.2193 |  |  | -468.1772 |  |  | -681.406 |  |  | -872.7563 |  |  | -1110.9332
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48464 |  |  | 0.47112 |  |  | 0.40061 |  |  | 0.16512 |  |  | -0.38005 |  |  | -1.2167 |  |  | -2.2584 |  |  | -3.287 |  |  | -4.21 |  |  | -5.3589
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4671 |  |  | 47.6658 |  |  | 33.0484 |  |  | -15.77 |  |  | -128.7869 |  |  | -302.2193 |  |  | -518.1772 |  |  | -731.406 |  |  | -922.7563 |  |  | -1160.9332
[13 empty] | Press drop ratio this iteration |  |  | 0.50232 |  |  | 0.48805 |  |  | 0.39794 |  |  | -0.46071 |  |  | 1.6346 |  |  | 1.1982 |  |  | 1.1068 |  |  | 1.0734 |  |  | 1.0573 |  |  | 1.045
[13 empty] | Expansion factor | 12 |  | 0.73838 |  |  | 0.74587 |  |  | 0.78968 |  |  | 1.2468 |  |  | 0.10023 |  |  | 0.30281 |  |  | 0.31158 |  |  | 0.27054 |  |  | 0.40621 |  |  | 0.10905
[13 empty] | C Non choked w/ reducers | 5 |  | 1.6166 |  |  | 11.9724 |  |  | 36.5034 |  |  | #NUM! |  |  | 487.6355 |  |  | 84.3793 |  |  | 60.3707 |  |  | 60.374 |  |  | 40.0871 |  |  | 172.9772
[13 empty] | C Choked w/ reducers | 5 |  | 1.5854 |  |  | 11.6898 |  |  | 34.3287 |  |  | 164.2713 |  |  | 120.3929 |  |  | 55.4014 |  |  | 40.5278 |  |  | 36.2255 |  |  | 32.5844 |  |  | 46.2365
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.6166 |  |  | 11.9724 |  |  | 36.5034 |  |  | #NUM! |  |  | 120.3929 |  |  | 55.4014 |  |  | 40.5278 |  |  | 36.2255 |  |  | 32.5844 |  |  | 46.2365
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.38345 | 373.6248 |  | 6.9724 | 2676.6981 |  | 26.5034 | 6619.793 |  | 7174 | 12893.667 |  | 7174 | 21205.335 |  | 7174 | 29742.1149 |  | 7174 | 37764.5938 |  | 7174 | 44281.9563 |  | 7174 | 49403.9769 |  | 7174 | 55118.4533
[13 empty] | Next iteration flow rate |  |  | 381.0973 | Abs Value of | Flow this | 2703.4651 | Abs Value of | Flow this | 6685.9909 | Abs Value of | Flow this | 13022.6037 | Abs Value of | Flow this | 21417.3884 | Abs Value of | Flow this | 30039.5361 | Abs Value of | Flow this | 38142.2398 | Abs Value of | Flow this | 44724.7758 | Abs Value of | Flow this | 49898.0167 | Abs Value of | Flow this | 55669.6378 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4649 |  |  | 97.6083 |  |  | 82.6971 |  |  | 32.8975 |  |  | -82.3911 |  |  | -259.3094 |  |  | -479.6081 |  |  | -697.1227 |  |  | -892.3192 |  |  | -1135.2834
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48462 |  |  | 0.47085 |  |  | 0.39892 |  |  | 0.15869 |  |  | -0.39744 |  |  | -1.2509 |  |  | -2.3135 |  |  | -3.3628 |  |  | -4.3044 |  |  | -5.4764
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4649 |  |  | 47.6083 |  |  | 32.6971 |  |  | -17.1025 |  |  | -132.3911 |  |  | -309.3094 |  |  | -529.6081 |  |  | -747.1227 |  |  | -942.3192 |  |  | -1185.2834
[13 empty] | Press drop ratio this iteration |  |  | 0.50231 |  |  | 0.48775 |  |  | 0.39538 |  |  | -0.51987 |  |  | 1.6069 |  |  | 1.1928 |  |  | 1.1043 |  |  | 1.0717 |  |  | 1.056 |  |  | 1.044
[13 empty] | Expansion factor | 12 |  | 0.73839 |  |  | 0.74603 |  |  | 0.79104 |  |  | 1.2785 |  |  | 0.11551 |  |  | 0.30597 |  |  | 0.31316 |  |  | 0.27166 |  |  | 0.40692 |  |  | 0.10988
[13 empty] | C Non choked w/ reducers | 5 |  | 1.6489 |  |  | 12.1004 |  |  | 37.0811 |  |  | #NUM! |  |  | 412.1793 |  |  | 82.2247 |  |  | 59.2885 |  |  | 59.4021 |  |  | 39.5552 |  |  | 169.7576
[13 empty] | C Choked w/ reducers | 5 |  | 1.6171 |  |  | 11.8136 |  |  | 34.8192 |  |  | 172.6343 |  |  | 116.2777 |  |  | 54.4254 |  |  | 39.9574 |  |  | 35.7629 |  |  | 32.1887 |  |  | 45.6973
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.6489 |  |  | 12.1004 |  |  | 37.0811 |  |  | #NUM! |  |  | 116.2777 |  |  | 54.4254 |  |  | 39.9574 |  |  | 35.7629 |  |  | 32.1887 |  |  | 45.6973
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.35108 | 381.0973 |  | 7.1004 | 2703.4651 |  | 27.0811 | 6685.9909 |  | 7174 | 13022.6037 |  | 7174 | 21417.3884 |  | 7174 | 30039.5361 |  | 7174 | 38142.2398 |  | 7174 | 44724.7758 |  | 7174 | 49898.0167 |  | 7174 | 55669.6378
[13 empty] | Next iteration flow rate |  |  | 388.7193 | Abs Value of | Flow this | 2730.4997 | Abs Value of | Flow this | 6752.8508 | Abs Value of | Flow this | 13152.8297 | Abs Value of | Flow this | 21631.5623 | Abs Value of | Flow this | 30339.9314 | Abs Value of | Flow this | 38523.6622 | Abs Value of | Flow this | 45172.0236 | Abs Value of | Flow this | 50396.9969 | Abs Value of | Flow this | 56226.3342 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4625 |  |  | 97.5498 |  |  | 82.3389 |  |  | 31.5382 |  |  | -86.0676 |  |  | -266.542 |  |  | -491.2687 |  |  | -713.1554 |  |  | -912.2754 |  |  | -1160.1231
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48461 |  |  | 0.47056 |  |  | 0.39719 |  |  | 0.15213 |  |  | -0.41517 |  |  | -1.2858 |  |  | -2.3698 |  |  | -3.4401 |  |  | -4.4007 |  |  | -5.5962
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4625 |  |  | 47.5498 |  |  | 32.3389 |  |  | -18.4618 |  |  | -136.0676 |  |  | -316.542 |  |  | -541.2687 |  |  | -763.1554 |  |  | -962.2754 |  |  | -1210.1231
[13 empty] | Press drop ratio this iteration |  |  | 0.5023 |  |  | 0.48744 |  |  | 0.39275 |  |  | -0.58538 |  |  | 1.5809 |  |  | 1.1876 |  |  | 1.1018 |  |  | 1.0701 |  |  | 1.0548 |  |  | 1.0431
[13 empty] | Expansion factor | 12 |  | 0.7384 |  |  | 0.74619 |  |  | 0.79243 |  |  | 1.3136 |  |  | 0.12978 |  |  | 0.30901 |  |  | 0.3147 |  |  | 0.27276 |  |  | 0.40761 |  |  | 0.11068
[13 empty] | C Non choked w/ reducers | 5 |  | 1.6819 |  |  | 12.23 |  |  | 37.6744 |  |  | #NUM! |  |  | 357.5976 |  |  | 80.1735 |  |  | 58.2394 |  |  | 58.4557 |  |  | 39.0335 |  |  | 166.6406
[13 empty] | C Choked w/ reducers | 5 |  | 1.6495 |  |  | 11.9389 |  |  | 35.3205 |  |  | 181.8754 |  |  | 112.4238 |  |  | 53.4781 |  |  | 39.3991 |  |  | 35.3084 |  |  | 31.7994 |  |  | 45.166
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.6819 |  |  | 12.23 |  |  | 37.6744 |  |  | #NUM! |  |  | 112.4238 |  |  | 53.4781 |  |  | 39.3991 |  |  | 35.3084 |  |  | 31.7994 |  |  | 45.166
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.31805 | 388.7193 |  | 7.23 | 2730.4997 |  | 27.6744 | 6752.8508 |  | 7174 | 13152.8297 |  | 7174 | 21631.5623 |  | 7174 | 30339.9314 |  | 7174 | 38523.6622 |  | 7174 | 45172.0236 |  | 7174 | 50396.9969 |  | 7174 | 56226.3342
[13 empty] | Next iteration flow rate |  |  | 396.4936 | Abs Value of | Flow this | 2757.8047 | Abs Value of | Flow this | 6820.3793 | Abs Value of | Flow this | 13284.358 | Abs Value of | Flow this | 21847.8779 | Abs Value of | Flow this | 30643.3307 | Abs Value of | Flow this | 38908.8988 | Abs Value of | Flow this | 45623.7438 | Abs Value of | Flow this | 50900.9668 | Abs Value of | Flow this | 56788.5975 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4601 |  |  | 97.49 |  |  | 81.9734 |  |  | 30.1516 |  |  | -89.8181 |  |  | -273.92 |  |  | -503.1637 |  |  | -729.5103 |  |  | -932.6326 |  |  | -1185.4621
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4846 |  |  | 0.47027 |  |  | 0.39542 |  |  | 0.14545 |  |  | -0.43327 |  |  | -1.3213 |  |  | -2.4272 |  |  | -3.519 |  |  | -4.4989 |  |  | -5.7185
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4601 |  |  | 47.49 |  |  | 31.9734 |  |  | -19.8484 |  |  | -139.8181 |  |  | -323.92 |  |  | -553.1637 |  |  | -779.5103 |  |  | -982.6326 |  |  | -1235.4621
[13 empty] | Press drop ratio this iteration |  |  | 0.50229 |  |  | 0.48713 |  |  | 0.39005 |  |  | -0.65829 |  |  | 1.5567 |  |  | 1.1825 |  |  | 1.0994 |  |  | 1.0685 |  |  | 1.0536 |  |  | 1.0422
[13 empty] | Expansion factor | 12 |  | 0.7384 |  |  | 0.74635 |  |  | 0.79386 |  |  | 1.3527 |  |  | 0.14313 |  |  | 0.31195 |  |  | 0.31619 |  |  | 0.27383 |  |  | 0.40828 |  |  | 0.11146
[13 empty] | C Non choked w/ reducers | 5 |  | 1.7156 |  |  | 12.3612 |  |  | 38.2841 |  |  | #NUM! |  |  | 316.242 |  |  | 78.2182 |  |  | 57.2219 |  |  | 57.5338 |  |  | 38.5217 |  |  | 163.6212
[13 empty] | C Choked w/ reducers | 5 |  | 1.6826 |  |  | 12.0657 |  |  | 35.8327 |  |  | 192.1417 |  |  | 108.8067 |  |  | 52.558 |  |  | 38.8524 |  |  | 34.862 |  |  | 31.4164 |  |  | 44.6426
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.7156 |  |  | 12.3612 |  |  | 38.2841 |  |  | #NUM! |  |  | 108.8067 |  |  | 52.558 |  |  | 38.8524 |  |  | 34.862 |  |  | 31.4164 |  |  | 44.6426
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.28437 | 396.4936 |  | 7.3612 | 2757.8047 |  | 28.2841 | 6820.3793 |  | 7174 | 13284.358 |  | 7174 | 21847.8779 |  | 7174 | 30643.3307 |  | 7174 | 38908.8988 |  | 7174 | 45623.7438 |  | 7174 | 50900.9668 |  | 7174 | 56788.5975
[13 empty] | Next iteration flow rate |  |  | 404.4235 | Abs Value of | Flow this | 2785.3828 | Abs Value of | Flow this | 6888.5831 | Abs Value of | Flow this | 13417.2016 | Abs Value of | Flow this | 22066.3567 | Abs Value of | Flow this | 30949.764 | Abs Value of | Flow this | 39297.9878 | Abs Value of | Flow this | 46079.9813 | Abs Value of | Flow this | 51409.9765 | Abs Value of | Flow this | 57356.4835 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4576 |  |  | 97.429 |  |  | 81.6005 |  |  | 28.7372 |  |  | -93.644 |  |  | -281.4463 |  |  | -515.2978 |  |  | -746.194 |  |  | -953.399 |  |  | -1211.3104
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48459 |  |  | 0.46998 |  |  | 0.39363 |  |  | 0.13862 |  |  | -0.45172 |  |  | -1.3576 |  |  | -2.4857 |  |  | -3.5995 |  |  | -4.599 |  |  | -5.8431
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4576 |  |  | 47.429 |  |  | 31.6005 |  |  | -21.2628 |  |  | -143.644 |  |  | -331.4463 |  |  | -565.2978 |  |  | -796.194 |  |  | -1003.399 |  |  | -1261.3104
[13 empty] | Press drop ratio this iteration |  |  | 0.50228 |  |  | 0.48681 |  |  | 0.38726 |  |  | -0.73991 |  |  | 1.5339 |  |  | 1.1777 |  |  | 1.097 |  |  | 1.067 |  |  | 1.0524 |  |  | 1.0413
[13 empty] | Expansion factor | 12 |  | 0.73841 |  |  | 0.74652 |  |  | 0.79533 |  |  | 1.3964 |  |  | 0.15565 |  |  | 0.31479 |  |  | 0.31765 |  |  | 0.27487 |  |  | 0.40894 |  |  | 0.11223
[13 empty] | C Non choked w/ reducers | 5 |  | 1.75 |  |  | 12.4939 |  |  | 38.911 |  |  | #NUM! |  |  | 283.7963 |  |  | 76.3518 |  |  | 56.2345 |  |  | 56.6353 |  |  | 38.0195 |  |  | 160.6945
[13 empty] | C Choked w/ reducers | 5 |  | 1.7163 |  |  | 12.194 |  |  | 36.3564 |  |  | 203.6151 |  |  | 105.4049 |  |  | 51.6641 |  |  | 38.3169 |  |  | 34.4234 |  |  | 31.0394 |  |  | 44.1269
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.75 |  |  | 12.4939 |  |  | 38.911 |  |  | #NUM! |  |  | 105.4049 |  |  | 51.6641 |  |  | 38.3169 |  |  | 34.4234 |  |  | 31.0394 |  |  | 44.1269
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.25 | 404.4235 |  | 7.4939 | 2785.3828 |  | 28.911 | 6888.5831 |  | 7174 | 13417.2016 |  | 7174 | 22066.3567 |  | 7174 | 30949.764 |  | 7174 | 39297.9878 |  | 7174 | 46079.9813 |  | 7174 | 51409.9765 |  | 7174 | 57356.4835
[13 empty] | Next iteration flow rate |  |  | 412.512 | Abs Value of | Flow this | 2813.2366 | Abs Value of | Flow this | 6957.4689 | Abs Value of | Flow this | 13551.3736 | Abs Value of | Flow this | 22287.0202 | Abs Value of | Flow this | 31259.2617 | Abs Value of | Flow this | 39690.9677 | Abs Value of | Flow this | 46540.7811 | Abs Value of | Flow this | 51924.0763 | Abs Value of | Flow this | 57930.0483 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4549 |  |  | 97.3669 |  |  | 81.2202 |  |  | 27.2943 |  |  | -97.5467 |  |  | -289.1239 |  |  | -527.6758 |  |  | -763.213 |  |  | -974.5829 |  |  | -1237.6783
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48458 |  |  | 0.46968 |  |  | 0.39179 |  |  | 0.13166 |  |  | -0.47055 |  |  | -1.3947 |  |  | -2.5454 |  |  | -3.6816 |  |  | -4.7012 |  |  | -5.9703
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4549 |  |  | 47.3669 |  |  | 31.2202 |  |  | -22.7057 |  |  | -147.5467 |  |  | -339.1239 |  |  | -577.6758 |  |  | -813.213 |  |  | -1024.5829 |  |  | -1287.6783
[13 empty] | Press drop ratio this iteration |  |  | 0.50226 |  |  | 0.48648 |  |  | 0.38439 |  |  | -0.83189 |  |  | 1.5126 |  |  | 1.1729 |  |  | 1.0948 |  |  | 1.0655 |  |  | 1.0513 |  |  | 1.0404
[13 empty] | Expansion factor | 12 |  | 0.73841 |  |  | 0.74669 |  |  | 0.79685 |  |  | 1.4457 |  |  | 0.16741 |  |  | 0.31754 |  |  | 0.31907 |  |  | 0.27588 |  |  | 0.40958 |  |  | 0.11298
[13 empty] | C Non choked w/ reducers | 5 |  | 1.7851 |  |  | 12.6283 |  |  | 39.5558 |  |  | #NUM! |  |  | 257.6394 |  |  | 74.5682 |  |  | 55.2758 |  |  | 55.7593 |  |  | 37.5266 |  |  | 157.8564
[13 empty] | C Choked w/ reducers | 5 |  | 1.7506 |  |  | 12.3238 |  |  | 36.8919 |  |  | 216.5228 |  |  | 102.1997 |  |  | 50.7951 |  |  | 37.7922 |  |  | 33.9923 |  |  | 30.6683 |  |  | 43.6186
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.7851 |  |  | 12.6283 |  |  | 39.5558 |  |  | #NUM! |  |  | 102.1997 |  |  | 50.7951 |  |  | 37.7922 |  |  | 33.9923 |  |  | 30.6683 |  |  | 43.6186
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.21495 | 412.512 |  | 7.6283 | 2813.2366 |  | 29.5558 | 6957.4689 |  | 7174 | 13551.3736 |  | 7174 | 22287.0202 |  | 7174 | 31259.2617 |  | 7174 | 39690.9677 |  | 7174 | 46540.7811 |  | 7174 | 51924.0763 |  | 7174 | 57930.0483
[13 empty] | Next iteration flow rate |  |  | 420.7622 | Abs Value of | Flow this | 2841.369 | Abs Value of | Flow this | 7027.0436 | Abs Value of | Flow this | 13686.8873 | Abs Value of | Flow this | 22509.8904 | Abs Value of | Flow this | 31571.8543 | Abs Value of | Flow this | 40087.8773 | Abs Value of | Flow this | 47006.1889 | Abs Value of | Flow this | 52443.317 | Abs Value of | Flow this | 58509.3488 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4522 |  |  | 97.3034 |  |  | 80.8322 |  |  | 25.8224 |  |  | -101.5279 |  |  | -296.9558 |  |  | -540.3026 |  |  | -780.5741 |  |  | -996.1925 |  |  | -1264.5761
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48456 |  |  | 0.46937 |  |  | 0.38992 |  |  | 0.12456 |  |  | -0.48975 |  |  | -1.4325 |  |  | -2.6063 |  |  | -3.7654 |  |  | -4.8055 |  |  | -6.1001
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4522 |  |  | 47.3034 |  |  | 30.8322 |  |  | -24.1776 |  |  | -151.5279 |  |  | -346.9558 |  |  | -590.3026 |  |  | -830.5741 |  |  | -1046.1925 |  |  | -1314.5761
[13 empty] | Press drop ratio this iteration |  |  | 0.50225 |  |  | 0.48614 |  |  | 0.38143 |  |  | -0.9363 |  |  | 1.4925 |  |  | 1.1684 |  |  | 1.0925 |  |  | 1.0641 |  |  | 1.0502 |  |  | 1.0395
[13 empty] | Expansion factor | 12 |  | 0.73842 |  |  | 0.74687 |  |  | 0.79841 |  |  | 1.5016 |  |  | 0.17848 |  |  | 0.32019 |  |  | 0.32044 |  |  | 0.27687 |  |  | 0.4102 |  |  | 0.11371
[13 empty] | C Non choked w/ reducers | 5 |  | 1.8208 |  |  | 12.7643 |  |  | 40.2195 |  |  | #NUM! |  |  | 236.0877 |  |  | 72.8616 |  |  | 54.3445 |  |  | 54.9049 |  |  | 37.0428 |  |  | 155.1025
[13 empty] | C Choked w/ reducers | 5 |  | 1.7857 |  |  | 12.4551 |  |  | 37.4397 |  |  | 231.1534 |  |  | 99.174 |  |  | 49.95 |  |  | 37.2781 |  |  | 33.5687 |  |  | 30.3031 |  |  | 43.1178
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.8208 |  |  | 12.7643 |  |  | 40.2195 |  |  | #NUM! |  |  | 99.174 |  |  | 49.95 |  |  | 37.2781 |  |  | 33.5687 |  |  | 30.3031 |  |  | 43.1178
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.17919 | 420.7622 |  | 7.7643 | 2841.369 |  | 30.2195 | 7027.0436 |  | 7174 | 13686.8873 |  | 7174 | 22509.8904 |  | 7174 | 31571.8543 |  | 7174 | 40087.8773 |  | 7174 | 47006.1889 |  | 7174 | 52443.317 |  | 7174 | 58509.3488
[13 empty] | Next iteration flow rate |  |  | 429.1775 | Abs Value of | Flow this | 2869.7827 | Abs Value of | Flow this | 7097.314 | Abs Value of | Flow this | 13823.7562 | Abs Value of | Flow this | 22734.9894 | Abs Value of | Flow this | 31887.5728 | Abs Value of | Flow this | 40488.7561 | Abs Value of | Flow this | 47476.2508 | Abs Value of | Flow this | 52967.7502 | Abs Value of | Flow this | 59094.4423 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4493 |  |  | 97.2387 |  |  | 80.4364 |  |  | 24.3209 |  |  | -105.5891 |  |  | -304.9451 |  |  | -553.1832 |  |  | -798.2842 |  |  | -1018.2365 |  |  | -1292.0146
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48455 |  |  | 0.46906 |  |  | 0.38801 |  |  | 0.11732 |  |  | -0.50934 |  |  | -1.471 |  |  | -2.6685 |  |  | -3.8508 |  |  | -4.9118 |  |  | -6.2324
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4493 |  |  | 47.2387 |  |  | 30.4364 |  |  | -25.6791 |  |  | -155.5891 |  |  | -354.9451 |  |  | -603.1832 |  |  | -848.2842 |  |  | -1068.2365 |  |  | -1342.0146
[13 empty] | Press drop ratio this iteration |  |  | 0.50224 |  |  | 0.4858 |  |  | 0.37839 |  |  | -1.0558 |  |  | 1.4735 |  |  | 1.164 |  |  | 1.0904 |  |  | 1.0626 |  |  | 1.0491 |  |  | 1.0387
[13 empty] | Expansion factor | 12 |  | 0.73843 |  |  | 0.74704 |  |  | 0.80002 |  |  | 1.5657 |  |  | 0.1889 |  |  | 0.32276 |  |  | 0.32178 |  |  | 0.27784 |  |  | 0.41081 |  |  | 0.11443
[13 empty] | C Non choked w/ reducers | 5 |  | 1.8573 |  |  | 12.902 |  |  | 40.903 |  |  | #NUM! |  |  | 218.0102 |  |  | 71.2269 |  |  | 53.4393 |  |  | 54.0713 |  |  | 36.5678 |  |  | 152.429
[13 empty] | C Choked w/ reducers | 5 |  | 1.8214 |  |  | 12.5881 |  |  | 38.0002 |  |  | 247.8782 |  |  | 96.3132 |  |  | 49.1277 |  |  | 36.7742 |  |  | 33.1522 |  |  | 29.9435 |  |  | 42.6241
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.8573 |  |  | 12.902 |  |  | 40.903 |  |  | #NUM! |  |  | 96.3132 |  |  | 49.1277 |  |  | 36.7742 |  |  | 33.1522 |  |  | 29.9435 |  |  | 42.6241
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.14271 | 429.1775 |  | 7.902 | 2869.7827 |  | 30.903 | 7097.314 |  | 7174 | 13823.7562 |  | 7174 | 22734.9894 |  | 7174 | 31887.5728 |  | 7174 | 40488.7561 |  | 7174 | 47476.2508 |  | 7174 | 52967.7502 |  | 7174 | 59094.4423
[13 empty] | Next iteration flow rate |  |  | 437.761 | Abs Value of | Flow this | 2898.4805 | Abs Value of | Flow this | 7168.2872 | Abs Value of | Flow this | 13961.9938 | Abs Value of | Flow this | 22962.3392 | Abs Value of | Flow this | 32206.4486 | Abs Value of | Flow this | 40893.6437 | Abs Value of | Flow this | 47951.0133 | Abs Value of | Flow this | 53497.4277 | Abs Value of | Flow this | 59685.3867 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4464 |  |  | 97.1727 |  |  | 80.0327 |  |  | 22.7892 |  |  | -109.732 |  |  | -313.0951 |  |  | -566.3227 |  |  | -816.3502 |  |  | -1040.7235 |  |  | -1320.0046
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48454 |  |  | 0.46874 |  |  | 0.38606 |  |  | 0.10993 |  |  | -0.52933 |  |  | -1.5103 |  |  | -2.7318 |  |  | -3.9379 |  |  | -5.0203 |  |  | -6.3675
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4464 |  |  | 47.1727 |  |  | 30.0327 |  |  | -27.2108 |  |  | -159.732 |  |  | -363.0951 |  |  | -616.3227 |  |  | -866.3502 |  |  | -1090.7235 |  |  | -1370.0046
[13 empty] | Press drop ratio this iteration |  |  | 0.50222 |  |  | 0.48545 |  |  | 0.37526 |  |  | -1.194 |  |  | 1.4557 |  |  | 1.1597 |  |  | 1.0883 |  |  | 1.0612 |  |  | 1.048 |  |  | 1.0379
[13 empty] | Expansion factor | 12 |  | 0.73844 |  |  | 0.74723 |  |  | 0.80167 |  |  | 1.6397 |  |  | 0.19874 |  |  | 0.32524 |  |  | 0.32309 |  |  | 0.27878 |  |  | 0.41141 |  |  | 0.11513
[13 empty] | C Non choked w/ reducers | 5 |  | 1.8945 |  |  | 13.0414 |  |  | 41.6074 |  |  | #NUM! |  |  | 202.619 |  |  | 69.6594 |  |  | 52.5592 |  |  | 53.2578 |  |  | 36.1014 |  |  | 149.8323
[13 empty] | C Choked w/ reducers | 5 |  | 1.8579 |  |  | 12.7226 |  |  | 38.5738 |  |  | 267.1834 |  |  | 93.6037 |  |  | 48.3274 |  |  | 36.2802 |  |  | 32.7427 |  |  | 29.5895 |  |  | 42.1375
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.8945 |  |  | 13.0414 |  |  | 41.6074 |  |  | #NUM! |  |  | 93.6037 |  |  | 48.3274 |  |  | 36.2802 |  |  | 32.7427 |  |  | 29.5895 |  |  | 42.1375
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.1055 | 437.761 |  | 8.0414 | 2898.4805 |  | 31.6074 | 7168.2872 |  | 7174 | 13961.9938 |  | 7174 | 22962.3392 |  | 7174 | 32206.4486 |  | 7174 | 40893.6437 |  | 7174 | 47951.0133 |  | 7174 | 53497.4277 |  | 7174 | 59685.3867
[13 empty] | Next iteration flow rate |  |  | 446.5162 | Abs Value of | Flow this | 2927.4653 | Abs Value of | Flow this | 7239.9701 | Abs Value of | Flow this | 14101.6137 | Abs Value of | Flow this | 23191.9626 | Abs Value of | Flow this | 32528.5131 | Abs Value of | Flow this | 41302.5801 | Abs Value of | Flow this | 48430.5234 | Abs Value of | Flow this | 54032.402 | Abs Value of | Flow this | 60282.2406 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4433 |  |  | 97.1054 |  |  | 79.6208 |  |  | 21.2268 |  |  | -113.9581 |  |  | -321.4088 |  |  | -579.7263 |  |  | -834.7793 |  |  | -1063.6626 |  |  | -1348.5572
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48452 |  |  | 0.46842 |  |  | 0.38408 |  |  | 0.10239 |  |  | -0.54971 |  |  | -1.5504 |  |  | -2.7965 |  |  | -4.0268 |  |  | -5.1309 |  |  | -6.5052
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4433 |  |  | 47.1054 |  |  | 29.6208 |  |  | -28.7732 |  |  | -163.9581 |  |  | -371.4088 |  |  | -629.7263 |  |  | -884.7793 |  |  | -1113.6626 |  |  | -1398.5572
[13 empty] | Press drop ratio this iteration |  |  | 0.50221 |  |  | 0.4851 |  |  | 0.37202 |  |  | -1.3555 |  |  | 1.4388 |  |  | 1.1556 |  |  | 1.0862 |  |  | 1.0599 |  |  | 1.047 |  |  | 1.0371
[13 empty] | Expansion factor | 12 |  | 0.73845 |  |  | 0.74741 |  |  | 0.80338 |  |  | 1.7262 |  |  | 0.20804 |  |  | 0.32764 |  |  | 0.32436 |  |  | 0.2797 |  |  | 0.41199 |  |  | 0.11581
[13 empty] | C Non choked w/ reducers | 5 |  | 1.9325 |  |  | 13.1825 |  |  | 42.3337 |  |  | #NUM! |  |  | 189.3481 |  |  | 68.1549 |  |  | 51.703 |  |  | 52.4635 |  |  | 35.6433 |  |  | 147.3089
[13 empty] | C Choked w/ reducers | 5 |  | 1.8951 |  |  | 12.8587 |  |  | 39.161 |  |  | 289.7185 |  |  | 91.0337 |  |  | 47.5481 |  |  | 35.7958 |  |  | 32.3401 |  |  | 29.2409 |  |  | 41.6578
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.9325 |  |  | 13.1825 |  |  | 42.3337 |  |  | #NUM! |  |  | 91.0337 |  |  | 47.5481 |  |  | 35.7958 |  |  | 32.3401 |  |  | 29.2409 |  |  | 41.6578
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.067546 | 446.5162 |  | 8.1825 | 2927.4653 |  | 32.3337 | 7239.9701 |  | 7174 | 14101.6137 |  | 7174 | 23191.9626 |  | 7174 | 32528.5131 |  | 7174 | 41302.5801 |  | 7174 | 48430.5234 |  | 7174 | 54032.402 |  | 7174 | 60282.2406
[13 empty] | Next iteration flow rate |  |  | 455.4466 | Abs Value of | Flow this | 2956.74 | Abs Value of | Flow this | 7312.3698 | Abs Value of | Flow this | 14242.6298 | Abs Value of | Flow this | 23423.8823 | Abs Value of | Flow this | 32853.7982 | Abs Value of | Flow this | 41715.6059 | Abs Value of | Flow this | 48914.8286 | Abs Value of | Flow this | 54572.726 | Abs Value of | Flow this | 60885.063 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4401 |  |  | 97.0367 |  |  | 79.2007 |  |  | 19.6329 |  |  | -118.2692 |  |  | -329.8896 |  |  | -593.3993 |  |  | -853.5789 |  |  | -1087.0627 |  |  | -1377.6837
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48451 |  |  | 0.46809 |  |  | 0.38205 |  |  | 0.094706 |  |  | -0.57051 |  |  | -1.5913 |  |  | -2.8625 |  |  | -4.1175 |  |  | -5.2438 |  |  | -6.6457
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4401 |  |  | 47.0367 |  |  | 29.2007 |  |  | -30.3671 |  |  | -168.2692 |  |  | -379.8896 |  |  | -643.3993 |  |  | -903.5789 |  |  | -1137.0627 |  |  | -1427.6837
[13 empty] | Press drop ratio this iteration |  |  | 0.50219 |  |  | 0.48473 |  |  | 0.36869 |  |  | -1.5467 |  |  | 1.4228 |  |  | 1.1516 |  |  | 1.0843 |  |  | 1.0586 |  |  | 1.046 |  |  | 1.0363
[13 empty] | Expansion factor | 12 |  | 0.73845 |  |  | 0.7476 |  |  | 0.80514 |  |  | 1.8287 |  |  | 0.21685 |  |  | 0.32997 |  |  | 0.32559 |  |  | 0.2806 |  |  | 0.41256 |  |  | 0.11648
[13 empty] | C Non choked w/ reducers | 5 |  | 1.9712 |  |  | 13.3253 |  |  | 43.0832 |  |  | #NUM! |  |  | 177.7805 |  |  | 66.7094 |  |  | 50.8696 |  |  | 51.6877 |  |  | 35.1933 |  |  | 144.8557
[13 empty] | C Choked w/ reducers | 5 |  | 1.9331 |  |  | 12.9965 |  |  | 39.7625 |  |  | 316.3709 |  |  | 88.5926 |  |  | 46.789 |  |  | 35.3207 |  |  | 31.9441 |  |  | 28.8976 |  |  | 41.1848
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1.9712 |  |  | 13.3253 |  |  | 43.0832 |  |  | #NUM! |  |  | 88.5926 |  |  | 46.789 |  |  | 35.3207 |  |  | 31.9441 |  |  | 28.8976 |  |  | 41.1848
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.028825 | 455.4466 |  | 8.3253 | 2956.74 |  | 33.0832 | 7312.3698 |  | 7174 | 14242.6298 |  | 7174 | 23423.8823 |  | 7174 | 32853.7982 |  | 7174 | 41715.6059 |  | 7174 | 48914.8286 |  | 7174 | 54572.726 |  | 7174 | 60885.063
[13 empty] | Next iteration flow rate |  |  | 464.5555 | Abs Value of | Flow this | 2986.3074 | Abs Value of | Flow this | 7385.4935 | Abs Value of | Flow this | 14385.0561 | Abs Value of | Flow this | 23658.1211 | Abs Value of | Flow this | 33182.3362 | Abs Value of | Flow this | 42132.762 | Abs Value of | Flow this | 49403.9769 | Abs Value of | Flow this | 55118.4533 | Abs Value of | Flow this | 61493.9136 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4367 |  |  | 96.9666 |  |  | 78.7721 |  |  | 18.0071 |  |  | -122.6669 |  |  | -338.5409 |  |  | -607.3471 |  |  | -872.7563 |  |  | -1110.9332 |  |  | -1407.3957
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48449 |  |  | 0.46775 |  |  | 0.37998 |  |  | 0.086863 |  |  | -0.59172 |  |  | -1.6331 |  |  | -2.9297 |  |  | -4.21 |  |  | -5.3589 |  |  | -6.789
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4367 |  |  | 46.9666 |  |  | 28.7721 |  |  | -31.9929 |  |  | -172.6669 |  |  | -388.5409 |  |  | -657.3471 |  |  | -922.7563 |  |  | -1160.9332 |  |  | -1457.3957
[13 empty] | Press drop ratio this iteration |  |  | 0.50217 |  |  | 0.48436 |  |  | 0.36526 |  |  | -1.7767 |  |  | 1.4076 |  |  | 1.1477 |  |  | 1.0823 |  |  | 1.0573 |  |  | 1.045 |  |  | 1.0355
[13 empty] | Expansion factor | 12 |  | 0.73846 |  |  | 0.7478 |  |  | 0.80696 |  |  | 1.9519 |  |  | 0.22519 |  |  | 0.33222 |  |  | 0.3268 |  |  | 0.28147 |  |  | 0.41311 |  |  | 0.11714
[13 empty] | C Non choked w/ reducers | 5 |  | 2.0107 |  |  | 13.47 |  |  | 43.8571 |  |  | #NUM! |  |  | 167.6024 |  |  | 65.3193 |  |  | 50.0582 |  |  | 50.9297 |  |  | 34.7512 |  |  | 142.4696
[13 empty] | C Choked w/ reducers | 5 |  | 1.9718 |  |  | 13.136 |  |  | 40.3786 |  |  | 348.3859 |  |  | 86.2706 |  |  | 46.0493 |  |  | 34.8547 |  |  | 31.5546 |  |  | 28.5594 |  |  | 40.7185
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.0107 |  |  | 13.47 |  |  | 43.8571 |  |  | #NUM! |  |  | 86.2706 |  |  | 46.0493 |  |  | 34.8547 |  |  | 31.5546 |  |  | 28.5594 |  |  | 40.7185
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.010675 | 464.5555 |  | 8.47 | 2986.3074 |  | 33.8571 | 7385.4935 |  | 7174 | 14385.0561 |  | 7174 | 23658.1211 |  | 7174 | 33182.3362 |  | 7174 | 42132.762 |  | 7174 | 49403.9769 |  | 7174 | 55118.4533 |  | 7174 | 61493.9136
[13 empty] | Next iteration flow rate |  |  | 473.8466 | Abs Value of | Flow this | 3016.1704 | Abs Value of | Flow this | 7459.3484 | Abs Value of | Flow this | 14528.9067 | Abs Value of | Flow this | 23894.7023 | Abs Value of | Flow this | 33514.1595 | Abs Value of | Flow this | 42554.0896 | Abs Value of | Flow this | 49898.0167 | Abs Value of | Flow this | 55669.6378 | Abs Value of | Flow this | 62108.8528 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4333 |  |  | 96.8951 |  |  | 78.3349 |  |  | 16.3485 |  |  | -127.153 |  |  | -347.3661 |  |  | -621.5753 |  |  | -892.3192 |  |  | -1135.2834 |  |  | -1437.7048
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48447 |  |  | 0.4674 |  |  | 0.37787 |  |  | 0.078862 |  |  | -0.61336 |  |  | -1.6756 |  |  | -2.9984 |  |  | -4.3044 |  |  | -5.4764 |  |  | -6.9352
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4333 |  |  | 46.8951 |  |  | 28.3349 |  |  | -33.6515 |  |  | -177.153 |  |  | -397.3661 |  |  | -671.5753 |  |  | -942.3192 |  |  | -1185.2834 |  |  | -1487.7048
[13 empty] | Press drop ratio this iteration |  |  | 0.50216 |  |  | 0.48398 |  |  | 0.36172 |  |  | -2.0584 |  |  | 1.3932 |  |  | 1.1439 |  |  | 1.0804 |  |  | 1.056 |  |  | 1.044 |  |  | 1.0348
[13 empty] | Expansion factor | 12 |  | 0.73847 |  |  | 0.74799 |  |  | 0.80883 |  |  | 2.1028 |  |  | 0.23311 |  |  | 0.33441 |  |  | 0.32797 |  |  | 0.28232 |  |  | 0.41365 |  |  | 0.11777
[13 empty] | C Non choked w/ reducers | 5 |  | 2.051 |  |  | 13.6165 |  |  | 44.6568 |  |  | #NUM! |  |  | 158.5726 |  |  | 63.9813 |  |  | 49.2678 |  |  | 50.189 |  |  | 34.3167 |  |  | 140.1477
[13 empty] | C Choked w/ reducers | 5 |  | 2.0113 |  |  | 13.2771 |  |  | 41.01 |  |  | 387.5671 |  |  | 84.0592 |  |  | 45.3281 |  |  | 34.3974 |  |  | 31.1714 |  |  | 28.2263 |  |  | 40.2587
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.051 |  |  | 13.6165 |  |  | 44.6568 |  |  | #NUM! |  |  | 84.0592 |  |  | 45.3281 |  |  | 34.3974 |  |  | 31.1714 |  |  | 28.2263 |  |  | 40.2587
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.05097 | 473.8466 |  | 8.6165 | 3016.1704 |  | 34.6568 | 7459.3484 |  | 7174 | 14528.9067 |  | 7174 | 23894.7023 |  | 7174 | 33514.1595 |  | 7174 | 42554.0896 |  | 7174 | 49898.0167 |  | 7174 | 55669.6378 |  | 7174 | 62108.8528
[13 empty] | Next iteration flow rate |  |  | 483.3235 | Abs Value of | Flow this | 3046.3321 | Abs Value of | Flow this | 7533.9419 | Abs Value of | Flow this | 14674.1958 | Abs Value of | Flow this | 24133.6493 | Abs Value of | Flow this | 33849.3011 | Abs Value of | Flow this | 42979.6305 | Abs Value of | Flow this | 50396.9969 | Abs Value of | Flow this | 56226.3342 | Abs Value of | Flow this | 62729.9413 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4296 |  |  | 96.8222 |  |  | 77.889 |  |  | 14.6566 |  |  | -131.7293 |  |  | -356.3686 |  |  | -636.0895 |  |  | -912.2754 |  |  | -1160.1231 |  |  | -1468.6232
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48445 |  |  | 0.46705 |  |  | 0.37572 |  |  | 0.070701 |  |  | -0.63544 |  |  | -1.7191 |  |  | -3.0684 |  |  | -4.4007 |  |  | -5.5962 |  |  | -7.0844
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4296 |  |  | 46.8222 |  |  | 27.889 |  |  | -35.3434 |  |  | -181.7293 |  |  | -406.3686 |  |  | -686.0895 |  |  | -962.2754 |  |  | -1210.1231 |  |  | -1518.6232
[13 empty] | Press drop ratio this iteration |  |  | 0.50214 |  |  | 0.48359 |  |  | 0.35806 |  |  | -2.4114 |  |  | 1.3796 |  |  | 1.1403 |  |  | 1.0786 |  |  | 1.0548 |  |  | 1.0431 |  |  | 1.034
[13 empty] | Expansion factor | 12 |  | 0.73848 |  |  | 0.7482 |  |  | 0.81076 |  |  | 2.2919 |  |  | 0.24063 |  |  | 0.33652 |  |  | 0.32911 |  |  | 0.28316 |  |  | 0.41418 |  |  | 0.1184
[13 empty] | C Non choked w/ reducers | 5 |  | 2.0921 |  |  | 13.7648 |  |  | 45.484 |  |  | #NUM! |  |  | 150.5031 |  |  | 62.6924 |  |  | 48.4976 |  |  | 49.4649 |  |  | 33.8897 |  |  | 137.8874
[13 empty] | C Choked w/ reducers | 5 |  | 2.0516 |  |  | 13.42 |  |  | 41.6572 |  |  | 436.6295 |  |  | 81.9503 |  |  | 44.6249 |  |  | 33.9486 |  |  | 30.7944 |  |  | 27.8982 |  |  | 39.8053
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.0921 |  |  | 13.7648 |  |  | 45.484 |  |  | #NUM! |  |  | 81.9503 |  |  | 44.6249 |  |  | 33.9486 |  |  | 30.7944 |  |  | 27.8982 |  |  | 39.8053
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.092075 | 483.3235 |  | 8.7648 | 3046.3321 |  | 35.484 | 7533.9419 |  | 7174 | 14674.1958 |  | 7174 | 24133.6493 |  | 7174 | 33849.3011 |  | 7174 | 42979.6305 |  | 7174 | 50396.9969 |  | 7174 | 56226.3342 |  | 7174 | 62729.9413
[13 empty] | Next iteration flow rate |  |  | 492.99 | Abs Value of | Flow this | 3076.7955 | Abs Value of | Flow this | 7609.2813 | Abs Value of | Flow this | 14820.9377 | Abs Value of | Flow this | 24374.9858 | Abs Value of | Flow this | 34187.7941 | Abs Value of | Flow this | 43409.4268 | Abs Value of | Flow this | 50900.9668 | Abs Value of | Flow this | 56788.5975 | Abs Value of | Flow this | 63357.2407 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4259 |  |  | 96.7478 |  |  | 77.434 |  |  | 12.9307 |  |  | -136.3975 |  |  | -365.5521 |  |  | -650.8954 |  |  | -932.6326 |  |  | -1185.4621 |  |  | -1500.163
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48444 |  |  | 0.46669 |  |  | 0.37353 |  |  | 0.062375 |  |  | -0.65796 |  |  | -1.7634 |  |  | -3.1398 |  |  | -4.4989 |  |  | -5.7185 |  |  | -7.2365
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4259 |  |  | 46.7478 |  |  | 27.434 |  |  | -37.0693 |  |  | -186.3975 |  |  | -415.5521 |  |  | -700.8954 |  |  | -982.6326 |  |  | -1235.4621 |  |  | -1550.163
[13 empty] | Press drop ratio this iteration |  |  | 0.50212 |  |  | 0.48319 |  |  | 0.35429 |  |  | -2.8668 |  |  | 1.3666 |  |  | 1.1368 |  |  | 1.0768 |  |  | 1.0536 |  |  | 1.0422 |  |  | 1.0333
[13 empty] | Expansion factor | 12 |  | 0.73849 |  |  | 0.7484 |  |  | 0.81276 |  |  | 2.5359 |  |  | 0.24778 |  |  | 0.33857 |  |  | 0.33022 |  |  | 0.28397 |  |  | 0.4147 |  |  | 0.11901
[13 empty] | C Non choked w/ reducers | 5 |  | 2.134 |  |  | 13.915 |  |  | 46.3401 |  |  | #NUM! |  |  | 143.2449 |  |  | 61.4497 |  |  | 47.7468 |  |  | 48.7568 |  |  | 33.47 |  |  | 135.6862
[13 empty] | C Choked w/ reducers | 5 |  | 2.0928 |  |  | 13.5646 |  |  | 42.321 |  |  | 499.8573 |  |  | 79.937 |  |  | 43.9388 |  |  | 33.5082 |  |  | 30.4235 |  |  | 27.5749 |  |  | 39.3581
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.134 |  |  | 13.915 |  |  | 46.3401 |  |  | #NUM! |  |  | 79.937 |  |  | 43.9388 |  |  | 33.5082 |  |  | 30.4235 |  |  | 27.5749 |  |  | 39.3581
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.13401 | 492.99 |  | 8.915 | 3076.7955 |  | 36.3401 | 7609.2813 |  | 7174 | 14820.9377 |  | 7174 | 24374.9858 |  | 7174 | 34187.7941 |  | 7174 | 43409.4268 |  | 7174 | 50900.9668 |  | 7174 | 56788.5975 |  | 7174 | 63357.2407
[13 empty] | Next iteration flow rate |  |  | 502.8498 | Abs Value of | Flow this | 3107.5634 | Abs Value of | Flow this | 7685.3741 | Abs Value of | Flow this | 14969.1471 | Abs Value of | Flow this | 24618.7357 | Abs Value of | Flow this | 34529.6721 | Abs Value of | Flow this | 43843.521 | Abs Value of | Flow this | 51409.9765 | Abs Value of | Flow this | 57356.4835 | Abs Value of | Flow this | 63990.8131 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.422 |  |  | 96.672 |  |  | 76.9699 |  |  | 11.1701 |  |  | -141.1596 |  |  | -374.9203 |  |  | -665.9989 |  |  | -953.399 |  |  | -1211.3104 |  |  | -1532.3368
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48442 |  |  | 0.46633 |  |  | 0.37129 |  |  | 0.053882 |  |  | -0.68093 |  |  | -1.8085 |  |  | -3.2127 |  |  | -4.599 |  |  | -5.8431 |  |  | -7.3917
[13 empty] | Delta P at this iteration flow rate |  |  | 50.422 |  |  | 46.672 |  |  | 26.9699 |  |  | -38.8299 |  |  | -191.1596 |  |  | -424.9203 |  |  | -715.9989 |  |  | -1003.399 |  |  | -1261.3104 |  |  | -1582.3368
[13 empty] | Press drop ratio this iteration |  |  | 0.5021 |  |  | 0.48279 |  |  | 0.3504 |  |  | -3.4762 |  |  | 1.3542 |  |  | 1.1334 |  |  | 1.0751 |  |  | 1.0524 |  |  | 1.0413 |  |  | 1.0326
[13 empty] | Expansion factor | 12 |  | 0.7385 |  |  | 0.74861 |  |  | 0.81481 |  |  | 2.8624 |  |  | 0.25458 |  |  | 0.34056 |  |  | 0.33131 |  |  | 0.28476 |  |  | 0.41521 |  |  | 0.11961
[13 empty] | C Non choked w/ reducers | 5 |  | 2.1768 |  |  | 14.0671 |  |  | 47.227 |  |  | #NUM! |  |  | 136.6785 |  |  | 60.2507 |  |  | 47.0145 |  |  | 48.0641 |  |  | 33.0573 |  |  | 133.5416
[13 empty] | C Choked w/ reducers | 5 |  | 2.1347 |  |  | 13.711 |  |  | 43.0019 |  |  | 584.43 |  |  | 78.0127 |  |  | 43.2694 |  |  | 33.0758 |  |  | 30.0584 |  |  | 27.2563 |  |  | 38.917
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.1768 |  |  | 14.0671 |  |  | 47.227 |  |  | #NUM! |  |  | 78.0127 |  |  | 43.2694 |  |  | 33.0758 |  |  | 30.0584 |  |  | 27.2563 |  |  | 38.917
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.17679 | 502.8498 |  | 9.0671 | 3107.5634 |  | 37.227 | 7685.3741 |  | 7174 | 14969.1471 |  | 7174 | 24618.7357 |  | 7174 | 34529.6721 |  | 7174 | 43843.521 |  | 7174 | 51409.9765 |  | 7174 | 57356.4835 |  | 7174 | 63990.8131
[13 empty] | Next iteration flow rate |  |  | 512.9068 | Abs Value of | Flow this | 3138.639 | Abs Value of | Flow this | 7762.2278 | Abs Value of | Flow this | 15118.8386 | Abs Value of | Flow this | 24864.923 | Abs Value of | Flow this | 34874.9688 | Abs Value of | Flow this | 44281.9563 | Abs Value of | Flow this | 51924.0763 | Abs Value of | Flow this | 57930.0483 | Abs Value of | Flow this | 64630.7212 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4179 |  |  | 96.5946 |  |  | 76.4965 |  |  | 9.3741 |  |  | -146.0175 |  |  | -384.4767 |  |  | -681.406 |  |  | -974.5829 |  |  | -1237.6783 |  |  | -1565.1573
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4844 |  |  | 0.46595 |  |  | 0.36901 |  |  | 0.045219 |  |  | -0.70436 |  |  | -1.8546 |  |  | -3.287 |  |  | -4.7012 |  |  | -5.9703 |  |  | -7.55
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4179 |  |  | 46.5946 |  |  | 26.4965 |  |  | -40.6259 |  |  | -196.0175 |  |  | -434.4767 |  |  | -731.406 |  |  | -1024.5829 |  |  | -1287.6783 |  |  | -1615.1573
[13 empty] | Press drop ratio this iteration |  |  | 0.50208 |  |  | 0.48237 |  |  | 0.34638 |  |  | -4.3338 |  |  | 1.3424 |  |  | 1.13 |  |  | 1.0734 |  |  | 1.0513 |  |  | 1.0404 |  |  | 1.0319
[13 empty] | Expansion factor | 12 |  | 0.73851 |  |  | 0.74883 |  |  | 0.81694 |  |  | 3.3219 |  |  | 0.26107 |  |  | 0.34249 |  |  | 0.33236 |  |  | 0.28554 |  |  | 0.4157 |  |  | 0.12019
[13 empty] | C Non choked w/ reducers | 5 |  | 2.2204 |  |  | 14.2212 |  |  | 48.1466 |  |  | #NUM! |  |  | 130.7069 |  |  | 59.093 |  |  | 46.3001 |  |  | 47.3864 |  |  | 32.6515 |  |  | 131.4513
[13 empty] | C Choked w/ reducers | 5 |  | 2.1775 |  |  | 13.8592 |  |  | 43.7007 |  |  | 703.3654 |  |  | 76.1715 |  |  | 42.6158 |  |  | 32.6512 |  |  | 29.6991 |  |  | 26.9424 |  |  | 38.482
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.2204 |  |  | 14.2212 |  |  | 48.1466 |  |  | #NUM! |  |  | 76.1715 |  |  | 42.6158 |  |  | 32.6512 |  |  | 29.6991 |  |  | 26.9424 |  |  | 38.482
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.22042 | 512.9068 |  | 9.2212 | 3138.639 |  | 38.1466 | 7762.2278 |  | 7174 | 15118.8386 |  | 7174 | 24864.923 |  | 7174 | 34874.9688 |  | 7174 | 44281.9563 |  | 7174 | 51924.0763 |  | 7174 | 57930.0483 |  | 7174 | 64630.7212
[13 empty] | Next iteration flow rate |  |  | 523.1649 | Abs Value of | Flow this | 3170.0254 | Abs Value of | Flow this | 7839.8501 | Abs Value of | Flow this | 15270.027 | Abs Value of | Flow this | 25113.5723 | Abs Value of | Flow this | 35223.7185 | Abs Value of | Flow this | 44724.7758 | Abs Value of | Flow this | 52443.317 | Abs Value of | Flow this | 58509.3488 | Abs Value of | Flow this | 65277.0284 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4136 |  |  | 96.5156 |  |  | 76.0136 |  |  | 7.542 |  |  | -150.9729 |  |  | -394.2251 |  |  | -697.1227 |  |  | -996.1925 |  |  | -1264.5761 |  |  | -1598.6375
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48438 |  |  | 0.46557 |  |  | 0.36668 |  |  | 0.036381 |  |  | -0.72827 |  |  | -1.9017 |  |  | -3.3628 |  |  | -4.8055 |  |  | -6.1001 |  |  | -7.7115
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4136 |  |  | 46.5156 |  |  | 26.0136 |  |  | -42.458 |  |  | -200.9729 |  |  | -444.2251 |  |  | -747.1227 |  |  | -1046.1925 |  |  | -1314.5761 |  |  | -1648.6375
[13 empty] | Press drop ratio this iteration |  |  | 0.50206 |  |  | 0.48195 |  |  | 0.34222 |  |  | -5.6295 |  |  | 1.3312 |  |  | 1.1268 |  |  | 1.0717 |  |  | 1.0502 |  |  | 1.0395 |  |  | 1.0313
[13 empty] | Expansion factor | 12 |  | 0.73852 |  |  | 0.74905 |  |  | 0.81913 |  |  | 4.0161 |  |  | 0.26726 |  |  | 0.34436 |  |  | 0.33339 |  |  | 0.2863 |  |  | 0.41618 |  |  | 0.12076
[13 empty] | C Non choked w/ reducers | 5 |  | 2.2649 |  |  | 14.3772 |  |  | 49.1011 |  |  | #NUM! |  |  | 125.2505 |  |  | 57.9743 |  |  | 45.6029 |  |  | 46.7231 |  |  | 32.2525 |  |  | 129.4133
[13 empty] | C Choked w/ reducers | 5 |  | 2.2211 |  |  | 14.0092 |  |  | 44.4182 |  |  | 882.9678 |  |  | 74.408 |  |  | 41.9776 |  |  | 32.2342 |  |  | 29.3454 |  |  | 26.633 |  |  | 38.0528
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.2649 |  |  | 14.3772 |  |  | 49.1011 |  |  | #NUM! |  |  | 74.408 |  |  | 41.9776 |  |  | 32.2342 |  |  | 29.3454 |  |  | 26.633 |  |  | 38.0528
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.26494 | 523.1649 |  | 9.3772 | 3170.0254 |  | 39.1011 | 7839.8501 |  | 7174 | 15270.027 |  | 7174 | 25113.5723 |  | 7174 | 35223.7185 |  | 7174 | 44724.7758 |  | 7174 | 52443.317 |  | 7174 | 58509.3488 |  | 7174 | 65277.0284
[13 empty] | Next iteration flow rate |  |  | 533.6282 | Abs Value of | Flow this | 3201.7257 | Abs Value of | Flow this | 7918.2486 | Abs Value of | Flow this | 15422.7272 | Abs Value of | Flow this | 25364.708 | Abs Value of | Flow this | 35575.9557 | Abs Value of | Flow this | 45172.0236 | Abs Value of | Flow this | 52967.7502 | Abs Value of | Flow this | 59094.4423 | Abs Value of | Flow this | 65929.7987 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4092 |  |  | 96.4351 |  |  | 75.521 |  |  | 5.6731 |  |  | -156.028 |  |  | -404.1696 |  |  | -713.1554 |  |  | -1018.2365 |  |  | -1292.0146 |  |  | -1632.7906
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48436 |  |  | 0.46519 |  |  | 0.3643 |  |  | 0.027366 |  |  | -0.75265 |  |  | -1.9496 |  |  | -3.4401 |  |  | -4.9118 |  |  | -6.2324 |  |  | -7.8763
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4092 |  |  | 46.4351 |  |  | 25.521 |  |  | -44.3269 |  |  | -206.028 |  |  | -454.1696 |  |  | -763.1554 |  |  | -1068.2365 |  |  | -1342.0146 |  |  | -1682.7906
[13 empty] | Press drop ratio this iteration |  |  | 0.50204 |  |  | 0.48152 |  |  | 0.33793 |  |  | -7.8135 |  |  | 1.3205 |  |  | 1.1237 |  |  | 1.0701 |  |  | 1.0491 |  |  | 1.0387 |  |  | 1.0306
[13 empty] | Expansion factor | 12 |  | 0.73853 |  |  | 0.74928 |  |  | 0.8214 |  |  | 5.1861 |  |  | 0.27316 |  |  | 0.34618 |  |  | 0.33439 |  |  | 0.28703 |  |  | 0.41665 |  |  | 0.12132
[13 empty] | C Non choked w/ reducers | 5 |  | 2.3104 |  |  | 14.5353 |  |  | 50.0928 |  |  | #NUM! |  |  | 120.2435 |  |  | 56.8926 |  |  | 44.9222 |  |  | 46.0738 |  |  | 31.86 |  |  | 127.4255
[13 empty] | C Choked w/ reducers | 5 |  | 2.2656 |  |  | 14.1611 |  |  | 45.155 |  |  | 1185.5866 |  |  | 72.7173 |  |  | 41.3542 |  |  | 31.8246 |  |  | 28.9972 |  |  | 26.3281 |  |  | 37.6294
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.3104 |  |  | 14.5353 |  |  | 50.0928 |  |  | #NUM! |  |  | 72.7173 |  |  | 41.3542 |  |  | 31.8246 |  |  | 28.9972 |  |  | 26.3281 |  |  | 37.6294
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.31036 | 533.6282 |  | 9.5353 | 3201.7257 |  | 40.0928 | 7918.2486 |  | 7174 | 15422.7272 |  | 7174 | 25364.708 |  | 7174 | 35575.9557 |  | 7174 | 45172.0236 |  | 7174 | 52967.7502 |  | 7174 | 59094.4423 |  | 7174 | 65929.7987
[13 empty] | Next iteration flow rate |  |  | 544.3008 | Abs Value of | Flow this | 3233.7429 | Abs Value of | Flow this | 7997.4311 | Abs Value of | Flow this | 15576.9545 | Abs Value of | Flow this | 25618.3551 | Abs Value of | Flow this | 35931.7152 | Abs Value of | Flow this | 45623.7438 | Abs Value of | Flow this | 53497.4277 | Abs Value of | Flow this | 59685.3867 | Abs Value of | Flow this | 66589.0967 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.4046 |  |  | 96.3529 |  |  | 75.0184 |  |  | 3.7666 |  |  | -161.1847 |  |  | -414.3139 |  |  | -729.5103 |  |  | -1040.7235 |  |  | -1320.0046 |  |  | -1667.6302
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48433 |  |  | 0.46479 |  |  | 0.36188 |  |  | 0.018169 |  |  | -0.77753 |  |  | -1.9986 |  |  | -3.519 |  |  | -5.0203 |  |  | -6.3675 |  |  | -8.0444
[13 empty] | Delta P at this iteration flow rate |  |  | 50.4046 |  |  | 46.3529 |  |  | 25.0184 |  |  | -46.2334 |  |  | -211.1847 |  |  | -464.3139 |  |  | -779.5103 |  |  | -1090.7235 |  |  | -1370.0046 |  |  | -1717.6302
[13 empty] | Press drop ratio this iteration |  |  | 0.50202 |  |  | 0.48107 |  |  | 0.3335 |  |  | -12.2745 |  |  | 1.3102 |  |  | 1.1207 |  |  | 1.0685 |  |  | 1.048 |  |  | 1.0379 |  |  | 1.03
[13 empty] | Expansion factor | 12 |  | 0.73854 |  |  | 0.74951 |  |  | 0.82374 |  |  | 7.5761 |  |  | 0.27881 |  |  | 0.34794 |  |  | 0.33537 |  |  | 0.28775 |  |  | 0.41712 |  |  | 0.12186
[13 empty] | C Non choked w/ reducers | 5 |  | 2.3567 |  |  | 14.6954 |  |  | 51.1244 |  |  | #NUM! |  |  | 115.6309 |  |  | 55.846 |  |  | 44.2575 |  |  | 45.4379 |  |  | 31.4739 |  |  | 125.4859
[13 empty] | C Choked w/ reducers | 5 |  | 2.3111 |  |  | 14.315 |  |  | 45.9121 |  |  | 1803.5306 |  |  | 71.0948 |  |  | 40.7451 |  |  | 31.4223 |  |  | 28.6544 |  |  | 26.0275 |  |  | 37.2117
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.3567 |  |  | 14.6954 |  |  | 51.1244 |  |  | #NUM! |  |  | 71.0948 |  |  | 40.7451 |  |  | 31.4223 |  |  | 28.6544 |  |  | 26.0275 |  |  | 37.2117
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.35669 | 544.3008 |  | 9.6954 | 3233.7429 |  | 41.1244 | 7997.4311 |  | 7174 | 15576.9545 |  | 7174 | 25618.3551 |  | 7174 | 35931.7152 |  | 7174 | 45623.7438 |  | 7174 | 53497.4277 |  | 7174 | 59685.3867 |  | 7174 | 66589.0967
[13 empty] | Next iteration flow rate |  |  | 555.1868 | Abs Value of | Flow this | 3266.0804 | Abs Value of | Flow this | 8077.4054 | Abs Value of | Flow this | 15732.724 | Abs Value of | Flow this | 25874.5386 | Abs Value of | Flow this | 36291.0324 | Abs Value of | Flow this | 46079.9813 | Abs Value of | Flow this | 54032.402 | Abs Value of | Flow this | 60282.2406 | Abs Value of | Flow this | 67254.9877 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3999 |  |  | 96.2691 |  |  | 74.5058 |  |  | 1.8218 |  |  | -166.445 |  |  | -424.6621 |  |  | -746.194 |  |  | -1063.6626 |  |  | -1348.5572 |  |  | -1703.1701
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48431 |  |  | 0.46438 |  |  | 0.3594 |  |  | 0.0087881 |  |  | -0.8029 |  |  | -2.0485 |  |  | -3.5995 |  |  | -5.1309 |  |  | -6.5052 |  |  | -8.2158
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3999 |  |  | 46.2691 |  |  | 24.5058 |  |  | -48.1782 |  |  | -216.445 |  |  | -474.6621 |  |  | -796.194 |  |  | -1113.6626 |  |  | -1398.5572 |  |  | -1753.1701
[13 empty] | Press drop ratio this iteration |  |  | 0.50199 |  |  | 0.48062 |  |  | 0.32891 |  |  | -26.4452 |  |  | 1.3004 |  |  | 1.1177 |  |  | 1.067 |  |  | 1.047 |  |  | 1.0371 |  |  | 1.0294
[13 empty] | Expansion factor | 12 |  | 0.73856 |  |  | 0.74974 |  |  | 0.82617 |  |  | 15.1681 |  |  | 0.2842 |  |  | 0.34965 |  |  | 0.33632 |  |  | 0.28846 |  |  | 0.41757 |  |  | 0.1224
[13 empty] | C Non choked w/ reducers | 5 |  | 2.404 |  |  | 14.8576 |  |  | 52.1985 |  |  | #NUM! |  |  | 111.3663 |  |  | 54.8327 |  |  | 43.6081 |  |  | 44.8151 |  |  | 31.0941 |  |  | 123.5928
[13 empty] | C Choked w/ reducers | 5 |  | 2.3574 |  |  | 14.4707 |  |  | 46.6902 |  |  | 3766.1015 |  |  | 69.5364 |  |  | 40.1497 |  |  | 31.0269 |  |  | 28.3168 |  |  | 25.7312 |  |  | 36.7996
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.404 |  |  | 14.8576 |  |  | 52.1985 |  |  | #NUM! |  |  | 69.5364 |  |  | 40.1497 |  |  | 31.0269 |  |  | 28.3168 |  |  | 25.7312 |  |  | 36.7996
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.40395 | 555.1868 |  | 9.8576 | 3266.0804 |  | 42.1985 | 8077.4054 |  | 7174 | 15732.724 |  | 7174 | 25874.5386 |  | 7174 | 36291.0324 |  | 7174 | 46079.9813 |  | 7174 | 54032.402 |  | 7174 | 60282.2406 |  | 7174 | 67254.9877
[13 empty] | Next iteration flow rate |  |  | 566.2906 | Abs Value of | Flow this | 3298.7412 | Abs Value of | Flow this | 8158.1795 | Abs Value of | Flow this | 15890.0513 | Abs Value of | Flow this | 26133.284 | Abs Value of | Flow this | 36653.9427 | Abs Value of | Flow this | 46540.7811 | Abs Value of | Flow this | 54572.726 | Abs Value of | Flow this | 60885.063 | Abs Value of | Flow this | 67927.5376 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3949 |  |  | 96.1836 |  |  | 73.9828 |  |  | -0.16208 |  |  | -171.811 |  |  | -435.2183 |  |  | -763.213 |  |  | -1087.0627 |  |  | -1377.6837 |  |  | -1739.4243
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48429 |  |  | 0.46397 |  |  | 0.35688 |  |  | -0.00078183 |  |  | -0.82879 |  |  | -2.0994 |  |  | -3.6816 |  |  | -5.2438 |  |  | -6.6457 |  |  | -8.3907
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3949 |  |  | 46.1836 |  |  | 23.9828 |  |  | -50.1621 |  |  | -221.811 |  |  | -485.2183 |  |  | -813.213 |  |  | -1137.0627 |  |  | -1427.6837 |  |  | -1789.4243
[13 empty] | Press drop ratio this iteration |  |  | 0.50197 |  |  | 0.48016 |  |  | 0.32417 |  |  | 309.4959 |  |  | 1.291 |  |  | 1.1149 |  |  | 1.0655 |  |  | 1.046 |  |  | 1.0363 |  |  | 1.0287
[13 empty] | Expansion factor | 12 |  | 0.73857 |  |  | 0.74998 |  |  | 0.82867 |  |  | -164.8138 |  |  | 0.28937 |  |  | 0.35131 |  |  | 0.33725 |  |  | 0.28915 |  |  | 0.41801 |  |  | 0.12292
[13 empty] | C Non choked w/ reducers | 5 |  | 2.4522 |  |  | 15.0219 |  |  | 53.3184 |  |  | -7.7581 |  |  | 107.4104 |  |  | 53.851 |  |  | 42.9734 |  |  | 44.205 |  |  | 30.7203 |  |  | 121.7444
[13 empty] | C Choked w/ reducers | 5 |  | 2.4047 |  |  | 14.6284 |  |  | 47.4905 |  |  | 42755.9421 |  |  | 68.0382 |  |  | 39.5677 |  |  | 30.6384 |  |  | 27.9843 |  |  | 25.4391 |  |  | 36.3929
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.4522 |  |  | 15.0219 |  |  | 53.3184 |  |  | 42755.9421 |  |  | 68.0382 |  |  | 39.5677 |  |  | 30.6384 |  |  | 27.9843 |  |  | 25.4391 |  |  | 36.3929
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.45217 | 566.2906 |  | 10.0219 | 3298.7412 |  | 43.3184 | 8158.1795 |  | 7174 | 15890.0513 |  | 7174 | 26133.284 |  | 7174 | 36653.9427 |  | 7174 | 46540.7811 |  | 7174 | 54572.726 |  | 7174 | 60885.063 |  | 7174 | 67927.5376
[13 empty] | Next iteration flow rate |  |  | 577.6164 | Abs Value of | Flow this | 3331.7286 | Abs Value of | Flow this | 8239.7613 | Abs Value of | Flow this | 16048.9518 | Abs Value of | Flow this | 26394.6168 | Abs Value of | Flow this | 37020.4821 | Abs Value of | Flow this | 47006.1889 | Abs Value of | Flow this | 55118.4533 | Abs Value of | Flow this | 61493.9136 | Abs Value of | Flow this | 68606.8129 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3897 |  |  | 96.0964 |  |  | 73.4494 |  |  | -2.1858 |  |  | -177.2849 |  |  | -445.9867 |  |  | -780.5741 |  |  | -1110.9332 |  |  | -1407.3957 |  |  | -1776.4072
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48426 |  |  | 0.46355 |  |  | 0.35431 |  |  | -0.010544 |  |  | -0.85519 |  |  | -2.1514 |  |  | -3.7654 |  |  | -5.3589 |  |  | -6.789 |  |  | -8.5691
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3897 |  |  | 46.0964 |  |  | 23.4494 |  |  | -52.1858 |  |  | -227.2849 |  |  | -495.9867 |  |  | -830.5741 |  |  | -1160.9332 |  |  | -1457.3957 |  |  | -1826.4072
[13 empty] | Press drop ratio this iteration |  |  | 0.50194 |  |  | 0.47969 |  |  | 0.31926 |  |  | 23.8745 |  |  | 1.282 |  |  | 1.1121 |  |  | 1.0641 |  |  | 1.045 |  |  | 1.0355 |  |  | 1.0281
[13 empty] | Expansion factor | 12 |  | 0.73858 |  |  | 0.75023 |  |  | 0.83127 |  |  | -11.7909 |  |  | 0.29431 |  |  | 0.35293 |  |  | 0.33816 |  |  | 0.28982 |  |  | 0.41844 |  |  | 0.12343
[13 empty] | C Non choked w/ reducers | 5 |  | 2.5014 |  |  | 15.1884 |  |  | 54.4875 |  |  | -29.2408 |  |  | 103.7296 |  |  | 52.8994 |  |  | 42.3531 |  |  | 43.6071 |  |  | 30.3524 |  |  | 119.9391
[13 empty] | C Choked w/ reducers | 5 |  | 2.4529 |  |  | 14.7881 |  |  | 48.3137 |  |  | 3201.9877 |  |  | 66.5968 |  |  | 38.9984 |  |  | 30.2565 |  |  | 27.6568 |  |  | 25.1511 |  |  | 35.9916
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.5014 |  |  | 15.1884 |  |  | 54.4875 |  |  | 3201.9877 |  |  | 66.5968 |  |  | 38.9984 |  |  | 30.2565 |  |  | 27.6568 |  |  | 25.1511 |  |  | 35.9916
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.50136 | 577.6164 |  | 10.1884 | 3331.7286 |  | 44.4875 | 8239.7613 |  | 7174 | 16048.9518 |  | 7174 | 26394.6168 |  | 7174 | 37020.4821 |  | 7174 | 47006.1889 |  | 7174 | 55118.4533 |  | 7174 | 61493.9136 |  | 7174 | 68606.8129
[13 empty] | Next iteration flow rate |  |  | 589.1687 | Abs Value of | Flow this | 3365.0459 | Abs Value of | Flow this | 8322.1589 | Abs Value of | Flow this | 16209.4413 | Abs Value of | Flow this | 26658.563 | Abs Value of | Flow this | 37390.687 | Abs Value of | Flow this | 47476.2508 | Abs Value of | Flow this | 55669.6378 | Abs Value of | Flow this | 62108.8528 | Abs Value of | Flow this | 69292.8811 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3844 |  |  | 96.0074 |  |  | 72.9052 |  |  | -4.2503 |  |  | -182.8689 |  |  | -456.9716 |  |  | -798.2842 |  |  | -1135.2834 |  |  | -1437.7048 |  |  | -1814.1335
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48424 |  |  | 0.46312 |  |  | 0.35168 |  |  | -0.020503 |  |  | -0.88213 |  |  | -2.2043 |  |  | -3.8508 |  |  | -5.4764 |  |  | -6.9352 |  |  | -8.7511
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3844 |  |  | 46.0074 |  |  | 22.9052 |  |  | -54.2503 |  |  | -232.8689 |  |  | -506.9716 |  |  | -848.2842 |  |  | -1185.2834 |  |  | -1487.7048 |  |  | -1864.1335
[13 empty] | Press drop ratio this iteration |  |  | 0.50191 |  |  | 0.47921 |  |  | 0.31418 |  |  | 12.7639 |  |  | 1.2734 |  |  | 1.1094 |  |  | 1.0626 |  |  | 1.044 |  |  | 1.0348 |  |  | 1.0276
[13 empty] | Expansion factor | 12 |  | 0.7386 |  |  | 0.75048 |  |  | 0.83395 |  |  | -5.8383 |  |  | 0.29905 |  |  | 0.3545 |  |  | 0.33904 |  |  | 0.29047 |  |  | 0.41886 |  |  | 0.12393
[13 empty] | C Non choked w/ reducers | 5 |  | 2.5515 |  |  | 15.3571 |  |  | 55.7097 |  |  | -41.9511 |  |  | 100.2953 |  |  | 51.9764 |  |  | 41.7464 |  |  | 43.021 |  |  | 29.9904 |  |  | 118.1753
[13 empty] | C Choked w/ reducers | 5 |  | 2.5021 |  |  | 14.9498 |  |  | 49.1611 |  |  | 1663.1896 |  |  | 65.2089 |  |  | 38.4416 |  |  | 29.8811 |  |  | 27.3343 |  |  | 24.867 |  |  | 35.5955
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.5515 |  |  | 15.3571 |  |  | 55.7097 |  |  | 1663.1896 |  |  | 65.2089 |  |  | 38.4416 |  |  | 29.8811 |  |  | 27.3343 |  |  | 24.867 |  |  | 35.5955
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.55154 | 589.1687 |  | 10.3571 | 3365.0459 |  | 45.7097 | 8322.1589 |  | 7174 | 16209.4413 |  | 7174 | 26658.563 |  | 7174 | 37390.687 |  | 7174 | 47476.2508 |  | 7174 | 55669.6378 |  | 7174 | 62108.8528 |  | 7174 | 69292.8811
[13 empty] | Next iteration flow rate |  |  | 600.9521 | Abs Value of | Flow this | 3398.6963 | Abs Value of | Flow this | 8405.3805 | Abs Value of | Flow this | 16371.5357 | Abs Value of | Flow this | 26925.1486 | Abs Value of | Flow this | 37764.5938 | Abs Value of | Flow this | 47951.0133 | Abs Value of | Flow this | 56226.3342 | Abs Value of | Flow this | 62729.9413 | Abs Value of | Flow this | 69985.8099 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3788 |  |  | 95.9166 |  |  | 72.3501 |  |  | -6.3562 |  |  | -188.565 |  |  | -468.1772 |  |  | -816.3502 |  |  | -1160.1231 |  |  | -1468.6232 |  |  | -1852.6181
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48421 |  |  | 0.46268 |  |  | 0.349 |  |  | -0.030661 |  |  | -0.9096 |  |  | -2.2584 |  |  | -3.9379 |  |  | -5.5962 |  |  | -7.0844 |  |  | -8.9367
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3788 |  |  | 45.9166 |  |  | 22.3501 |  |  | -56.3562 |  |  | -238.565 |  |  | -518.1772 |  |  | -866.3502 |  |  | -1210.1231 |  |  | -1518.6232 |  |  | -1902.6181
[13 empty] | Press drop ratio this iteration |  |  | 0.50189 |  |  | 0.47871 |  |  | 0.30892 |  |  | 8.8663 |  |  | 1.2652 |  |  | 1.1068 |  |  | 1.0612 |  |  | 1.0431 |  |  | 1.034 |  |  | 1.027
[13 empty] | Expansion factor | 12 |  | 0.73861 |  |  | 0.75074 |  |  | 0.83674 |  |  | -3.7502 |  |  | 0.3036 |  |  | 0.35602 |  |  | 0.33991 |  |  | 0.29112 |  |  | 0.41927 |  |  | 0.12441
[13 empty] | C Non choked w/ reducers | 5 |  | 2.6027 |  |  | 15.528 |  |  | 56.9893 |  |  | -52.9228 |  |  | 97.0825 |  |  | 51.0807 |  |  | 41.1531 |  |  | 42.4465 |  |  | 29.634 |  |  | 116.4515
[13 empty] | C Choked w/ reducers | 5 |  | 2.5523 |  |  | 15.1136 |  |  | 50.0337 |  |  | 1123.2645 |  |  | 63.8715 |  |  | 37.8967 |  |  | 29.512 |  |  | 27.0165 |  |  | 24.587 |  |  | 35.2047
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.6027 |  |  | 15.528 |  |  | 56.9893 |  |  | 1123.2645 |  |  | 63.8715 |  |  | 37.8967 |  |  | 29.512 |  |  | 27.0165 |  |  | 24.587 |  |  | 35.2047
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.60274 | 600.9521 |  | 10.528 | 3398.6963 |  | 46.9893 | 8405.3805 |  | 7174 | 16371.5357 |  | 7174 | 26925.1486 |  | 7174 | 37764.5938 |  | 7174 | 47951.0133 |  | 7174 | 56226.3342 |  | 7174 | 62729.9413 |  | 7174 | 69985.8099
[13 empty] | Next iteration flow rate |  |  | 612.9711 | Abs Value of | Flow this | 3432.6833 | Abs Value of | Flow this | 8489.4343 | Abs Value of | Flow this | 16535.2511 | Abs Value of | Flow this | 27194.4001 | Abs Value of | Flow this | 38142.2398 | Abs Value of | Flow this | 48430.5234 | Abs Value of | Flow this | 56788.5975 | Abs Value of | Flow this | 63357.2407 | Abs Value of | Flow this | 70685.668 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.373 |  |  | 95.8241 |  |  | 71.7838 |  |  | -8.5045 |  |  | -194.3757 |  |  | -479.6081 |  |  | -834.7793 |  |  | -1185.4621 |  |  | -1500.163 |  |  | -1891.8762
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48418 |  |  | 0.46224 |  |  | 0.34627 |  |  | -0.041024 |  |  | -0.93763 |  |  | -2.3135 |  |  | -4.0268 |  |  | -5.7185 |  |  | -7.2365 |  |  | -9.1261
[13 empty] | Delta P at this iteration flow rate |  |  | 50.373 |  |  | 45.8241 |  |  | 21.7838 |  |  | -58.5045 |  |  | -244.3757 |  |  | -529.6081 |  |  | -884.7793 |  |  | -1235.4621 |  |  | -1550.163 |  |  | -1941.8762
[13 empty] | Press drop ratio this iteration |  |  | 0.50186 |  |  | 0.47821 |  |  | 0.30346 |  |  | 6.8792 |  |  | 1.2572 |  |  | 1.1043 |  |  | 1.0599 |  |  | 1.0422 |  |  | 1.0333 |  |  | 1.0264
[13 empty] | Expansion factor | 12 |  | 0.73863 |  |  | 0.751 |  |  | 0.83962 |  |  | -2.6856 |  |  | 0.30796 |  |  | 0.3575 |  |  | 0.34075 |  |  | 0.29174 |  |  | 0.41967 |  |  | 0.12489
[13 empty] | C Non choked w/ reducers | 5 |  | 2.655 |  |  | 15.7012 |  |  | 58.3312 |  |  | -63.3325 |  |  | 94.0696 |  |  | 50.211 |  |  | 40.5725 |  |  | 41.883 |  |  | 29.2832 |  |  | 114.7664
[13 empty] | C Choked w/ reducers | 5 |  | 2.6035 |  |  | 15.2795 |  |  | 50.9326 |  |  | 847.9187 |  |  | 62.5817 |  |  | 37.3634 |  |  | 29.1491 |  |  | 26.7034 |  |  | 24.3107 |  |  | 34.8189
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.655 |  |  | 15.7012 |  |  | 58.3312 |  |  | 847.9187 |  |  | 62.5817 |  |  | 37.3634 |  |  | 29.1491 |  |  | 26.7034 |  |  | 24.3107 |  |  | 34.8189
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.65497 | 612.9711 |  | 10.7012 | 3432.6833 |  | 48.3312 | 8489.4343 |  | 7174 | 16535.2511 |  | 7174 | 27194.4001 |  | 7174 | 38142.2398 |  | 7174 | 48430.5234 |  | 7174 | 56788.5975 |  | 7174 | 63357.2407 |  | 7174 | 70685.668
[13 empty] | Next iteration flow rate |  |  | 625.2305 | Abs Value of | Flow this | 3467.0101 | Abs Value of | Flow this | 8574.3286 | Abs Value of | Flow this | 16700.6036 | Abs Value of | Flow this | 27466.3441 | Abs Value of | Flow this | 38523.6622 | Abs Value of | Flow this | 48914.8286 | Abs Value of | Flow this | 57356.4835 | Abs Value of | Flow this | 63990.8131 | Abs Value of | Flow this | 71392.5247 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3669 |  |  | 95.7296 |  |  | 71.2062 |  |  | -10.6959 |  |  | -200.3032 |  |  | -491.2687 |  |  | -853.5789 |  |  | -1211.3104 |  |  | -1532.3368 |  |  | -1931.9235
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48415 |  |  | 0.46178 |  |  | 0.34349 |  |  | -0.051595 |  |  | -0.96623 |  |  | -2.3698 |  |  | -4.1175 |  |  | -5.8431 |  |  | -7.3917 |  |  | -9.3193
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3669 |  |  | 45.7296 |  |  | 21.2062 |  |  | -60.6959 |  |  | -250.3032 |  |  | -541.2687 |  |  | -903.5789 |  |  | -1261.3104 |  |  | -1582.3368 |  |  | -1981.9235
[13 empty] | Press drop ratio this iteration |  |  | 0.50183 |  |  | 0.4777 |  |  | 0.29781 |  |  | 5.6747 |  |  | 1.2496 |  |  | 1.1018 |  |  | 1.0586 |  |  | 1.0413 |  |  | 1.0326 |  |  | 1.0259
[13 empty] | Expansion factor | 12 |  | 0.73864 |  |  | 0.75127 |  |  | 0.8426 |  |  | -2.0402 |  |  | 0.31215 |  |  | 0.35894 |  |  | 0.34157 |  |  | 0.29235 |  |  | 0.42006 |  |  | 0.12536
[13 empty] | C Non choked w/ reducers | 5 |  | 2.7083 |  |  | 15.8768 |  |  | 59.7407 |  |  | -73.7119 |  |  | 91.2377 |  |  | 49.3662 |  |  | 40.0044 |  |  | 41.3304 |  |  | 28.9377 |  |  | 113.1185
[13 empty] | C Choked w/ reducers | 5 |  | 2.6557 |  |  | 15.4475 |  |  | 51.8593 |  |  | 680.934 |  |  | 61.3371 |  |  | 36.8413 |  |  | 28.7922 |  |  | 26.3949 |  |  | 24.0383 |  |  | 34.4381
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.7083 |  |  | 15.8768 |  |  | 59.7407 |  |  | 680.934 |  |  | 61.3371 |  |  | 36.8413 |  |  | 28.7922 |  |  | 26.3949 |  |  | 24.0383 |  |  | 34.4381
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.70826 | 625.2305 |  | 10.8768 | 3467.0101 |  | 49.7407 | 8574.3286 |  | 7174 | 16700.6036 |  | 7174 | 27466.3441 |  | 7174 | 38523.6622 |  | 7174 | 48914.8286 |  | 7174 | 57356.4835 |  | 7174 | 63990.8131 |  | 7174 | 71392.5247
[13 empty] | Next iteration flow rate |  |  | 637.7351 | Abs Value of | Flow this | 3501.6802 | Abs Value of | Flow this | 8660.0719 | Abs Value of | Flow this | 16867.6096 | Abs Value of | Flow this | 27741.0076 | Abs Value of | Flow this | 38908.8988 | Abs Value of | Flow this | 49403.9769 | Abs Value of | Flow this | 57930.0483 | Abs Value of | Flow this | 64630.7212 | Abs Value of | Flow this | 72106.4499 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3606 |  |  | 95.6333 |  |  | 70.6169 |  |  | -12.9314 |  |  | -206.3498 |  |  | -503.1637 |  |  | -872.7563 |  |  | -1237.6783 |  |  | -1565.1573 |  |  | -1972.7756
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48412 |  |  | 0.46132 |  |  | 0.34064 |  |  | -0.062379 |  |  | -0.99539 |  |  | -2.4272 |  |  | -4.21 |  |  | -5.9703 |  |  | -7.55 |  |  | -9.5163
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3606 |  |  | 45.6333 |  |  | 20.6169 |  |  | -62.9314 |  |  | -256.3498 |  |  | -553.1637 |  |  | -922.7563 |  |  | -1287.6783 |  |  | -1615.1573 |  |  | -2022.7756
[13 empty] | Press drop ratio this iteration |  |  | 0.5018 |  |  | 0.47717 |  |  | 0.29195 |  |  | 4.8665 |  |  | 1.2423 |  |  | 1.0994 |  |  | 1.0573 |  |  | 1.0404 |  |  | 1.0319 |  |  | 1.0253
[13 empty] | Expansion factor | 12 |  | 0.73866 |  |  | 0.75154 |  |  | 0.8457 |  |  | -1.6073 |  |  | 0.31618 |  |  | 0.36034 |  |  | 0.34237 |  |  | 0.29295 |  |  | 0.42045 |  |  | 0.12582
[13 empty] | C Non choked w/ reducers | 5 |  | 2.7626 |  |  | 16.0547 |  |  | 61.2241 |  |  | -84.4074 |  |  | 88.5704 |  |  | 48.5451 |  |  | 39.4482 |  |  | 40.7883 |  |  | 28.5975 |  |  | 111.5066
[13 empty] | C Choked w/ reducers | 5 |  | 2.709 |  |  | 15.6177 |  |  | 52.815 |  |  | 568.8511 |  |  | 60.1351 |  |  | 36.3301 |  |  | 28.4411 |  |  | 26.0909 |  |  | 23.7696 |  |  | 34.0622
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.7626 |  |  | 16.0547 |  |  | 61.2241 |  |  | 568.8511 |  |  | 60.1351 |  |  | 36.3301 |  |  | 28.4411 |  |  | 26.0909 |  |  | 23.7696 |  |  | 34.0622
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.76262 | 637.7351 |  | 11.0547 | 3501.6802 |  | 51.2241 | 8660.0719 |  | 7174 | 16867.6096 |  | 7174 | 27741.0076 |  | 7174 | 38908.8988 |  | 7174 | 49403.9769 |  | 7174 | 57930.0483 |  | 7174 | 64630.7212 |  | 7174 | 72106.4499
[13 empty] | Next iteration flow rate |  |  | 650.4899 | Abs Value of | Flow this | 3536.697 | Abs Value of | Flow this | 8746.6726 | Abs Value of | Flow this | 17036.2857 | Abs Value of | Flow this | 28018.4176 | Abs Value of | Flow this | 39297.9878 | Abs Value of | Flow this | 49898.0167 | Abs Value of | Flow this | 58509.3488 | Abs Value of | Flow this | 65277.0284 | Abs Value of | Flow this | 72827.5144 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3541 |  |  | 95.535 |  |  | 70.0158 |  |  | -15.2119 |  |  | -212.5179 |  |  | -515.2978 |  |  | -892.3192 |  |  | -1264.5761 |  |  | -1598.6375 |  |  | -2014.4489
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48409 |  |  | 0.46084 |  |  | 0.33774 |  |  | -0.073379 |  |  | -1.0251 |  |  | -2.4857 |  |  | -4.3044 |  |  | -6.1001 |  |  | -7.7115 |  |  | -9.7173
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3541 |  |  | 45.535 |  |  | 20.0158 |  |  | -65.2119 |  |  | -262.5179 |  |  | -565.2978 |  |  | -942.3192 |  |  | -1314.5761 |  |  | -1648.6375 |  |  | -2064.4489
[13 empty] | Press drop ratio this iteration |  |  | 0.50176 |  |  | 0.47663 |  |  | 0.28588 |  |  | 4.2869 |  |  | 1.2353 |  |  | 1.097 |  |  | 1.056 |  |  | 1.0395 |  |  | 1.0313 |  |  | 1.0248
[13 empty] | Expansion factor | 12 |  | 0.73868 |  |  | 0.75182 |  |  | 0.84891 |  |  | -1.2967 |  |  | 0.32005 |  |  | 0.3617 |  |  | 0.34315 |  |  | 0.29353 |  |  | 0.42082 |  |  | 0.12626
[13 empty] | C Non choked w/ reducers | 5 |  | 2.8181 |  |  | 16.235 |  |  | 62.7883 |  |  | -95.7072 |  |  | 86.053 |  |  | 47.7466 |  |  | 38.9035 |  |  | 40.2563 |  |  | 28.2625 |  |  | 109.9295
[13 empty] | C Choked w/ reducers | 5 |  | 2.7633 |  |  | 15.7901 |  |  | 53.8011 |  |  | 488.4096 |  |  | 58.9737 |  |  | 35.8293 |  |  | 28.0958 |  |  | 25.7913 |  |  | 23.5045 |  |  | 33.6911
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.8181 |  |  | 16.235 |  |  | 62.7883 |  |  | 488.4096 |  |  | 58.9737 |  |  | 35.8293 |  |  | 28.0958 |  |  | 25.7913 |  |  | 23.5045 |  |  | 33.6911
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.81809 | 650.4899 |  | 11.235 | 3536.697 |  | 52.7883 | 8746.6726 |  | 7174 | 17036.2857 |  | 7174 | 28018.4176 |  | 7174 | 39297.9878 |  | 7174 | 49898.0167 |  | 7174 | 58509.3488 |  | 7174 | 65277.0284 |  | 7174 | 72827.5144
[13 empty] | Next iteration flow rate |  |  | 663.4996 | Abs Value of | Flow this | 3572.064 | Abs Value of | Flow this | 8834.1394 | Abs Value of | Flow this | 17206.6486 | Abs Value of | Flow this | 28298.6018 | Abs Value of | Flow this | 39690.9677 | Abs Value of | Flow this | 50396.9969 | Abs Value of | Flow this | 59094.4423 | Abs Value of | Flow this | 65929.7987 | Abs Value of | Flow this | 73555.7895 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3472 |  |  | 95.4347 |  |  | 69.4026 |  |  | -17.5381 |  |  | -218.81 |  |  | -527.6758 |  |  | -912.2754 |  |  | -1292.0146 |  |  | -1632.7906 |  |  | -2056.9599
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48406 |  |  | 0.46036 |  |  | 0.33479 |  |  | -0.084601 |  |  | -1.0555 |  |  | -2.5454 |  |  | -4.4007 |  |  | -6.2324 |  |  | -7.8763 |  |  | -9.9224
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3472 |  |  | 45.4347 |  |  | 19.4026 |  |  | -67.5381 |  |  | -268.81 |  |  | -577.6758 |  |  | -962.2754 |  |  | -1342.0146 |  |  | -1682.7906 |  |  | -2106.9599
[13 empty] | Press drop ratio this iteration |  |  | 0.50173 |  |  | 0.47608 |  |  | 0.27957 |  |  | 3.8509 |  |  | 1.2285 |  |  | 1.0948 |  |  | 1.0548 |  |  | 1.0387 |  |  | 1.0306 |  |  | 1.0243
[13 empty] | Expansion factor | 12 |  | 0.73869 |  |  | 0.75211 |  |  | 0.85225 |  |  | -1.0632 |  |  | 0.32377 |  |  | 0.36303 |  |  | 0.34391 |  |  | 0.29411 |  |  | 0.42119 |  |  | 0.1267
[13 empty] | C Non choked w/ reducers | 5 |  | 2.8747 |  |  | 16.4178 |  |  | 64.4413 |  |  | -107.8967 |  |  | 83.6728 |  |  | 46.9698 |  |  | 38.3701 |  |  | 39.7343 |  |  | 27.9325 |  |  | 108.3859
[13 empty] | C Choked w/ reducers | 5 |  | 2.8188 |  |  | 15.9647 |  |  | 54.8192 |  |  | 427.863 |  |  | 57.8506 |  |  | 35.3388 |  |  | 27.756 |  |  | 25.496 |  |  | 23.243 |  |  | 33.3248
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.8747 |  |  | 16.4178 |  |  | 64.4413 |  |  | 427.863 |  |  | 57.8506 |  |  | 35.3388 |  |  | 27.756 |  |  | 25.496 |  |  | 23.243 |  |  | 33.3248
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.87467 | 663.4996 |  | 11.4178 | 3572.064 |  | 54.4413 | 8834.1394 |  | 7174 | 17206.6486 |  | 7174 | 28298.6018 |  | 7174 | 39690.9677 |  | 7174 | 50396.9969 |  | 7174 | 59094.4423 |  | 7174 | 65929.7987 |  | 7174 | 73555.7895
[13 empty] | Next iteration flow rate |  |  | 676.7696 | Abs Value of | Flow this | 3607.7846 | Abs Value of | Flow this | 8922.4807 | Abs Value of | Flow this | 17378.7151 | Abs Value of | Flow this | 28581.5878 | Abs Value of | Flow this | 40087.8773 | Abs Value of | Flow this | 50900.9668 | Abs Value of | Flow this | 59685.3867 | Abs Value of | Flow this | 66589.0967 | Abs Value of | Flow this | 74291.3474 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3401 |  |  | 95.3325 |  |  | 68.7771 |  |  | -19.9112 |  |  | -225.2286 |  |  | -540.3026 |  |  | -932.6326 |  |  | -1320.0046 |  |  | -1667.6302 |  |  | -2100.3253
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48402 |  |  | 0.45987 |  |  | 0.33177 |  |  | -0.096048 |  |  | -1.0865 |  |  | -2.6063 |  |  | -4.4989 |  |  | -6.3675 |  |  | -8.0444 |  |  | -10.1316
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3401 |  |  | 45.3325 |  |  | 18.7771 |  |  | -69.9112 |  |  | -275.2286 |  |  | -590.3026 |  |  | -982.6326 |  |  | -1370.0046 |  |  | -1717.6302 |  |  | -2150.3253
[13 empty] | Press drop ratio this iteration |  |  | 0.50169 |  |  | 0.47552 |  |  | 0.27301 |  |  | 3.5112 |  |  | 1.222 |  |  | 1.0925 |  |  | 1.0536 |  |  | 1.0379 |  |  | 1.03 |  |  | 1.0238
[13 empty] | Expansion factor | 12 |  | 0.73871 |  |  | 0.7524 |  |  | 0.85571 |  |  | -0.88112 |  |  | 0.32736 |  |  | 0.36431 |  |  | 0.34466 |  |  | 0.29466 |  |  | 0.42155 |  |  | 0.12713
[13 empty] | C Non choked w/ reducers | 5 |  | 2.9324 |  |  | 16.6031 |  |  | 66.1921 |  |  | -121.2932 |  |  | 81.4182 |  |  | 46.2137 |  |  | 37.8475 |  |  | 39.2218 |  |  | 27.6075 |  |  | 106.8749
[13 empty] | C Choked w/ reducers | 5 |  | 2.8754 |  |  | 16.1417 |  |  | 55.8709 |  |  | 380.6387 |  |  | 56.764 |  |  | 34.858 |  |  | 27.4216 |  |  | 25.2049 |  |  | 22.985 |  |  | 32.9631
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.9324 |  |  | 16.6031 |  |  | 66.1921 |  |  | 380.6387 |  |  | 56.764 |  |  | 34.858 |  |  | 27.4216 |  |  | 25.2049 |  |  | 22.985 |  |  | 32.9631
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.9324 | 676.7696 |  | 11.6031 | 3607.7846 |  | 56.1921 | 8922.4807 |  | 7174 | 17378.7151 |  | 7174 | 28581.5878 |  | 7174 | 40087.8773 |  | 7174 | 50900.9668 |  | 7174 | 59685.3867 |  | 7174 | 66589.0967 |  | 7174 | 74291.3474
[13 empty] | Next iteration flow rate |  |  | 690.305 | Abs Value of | Flow this | 3643.8625 | Abs Value of | Flow this | 9011.7056 | Abs Value of | Flow this | 17552.5022 | Abs Value of | Flow this | 28867.4037 | Abs Value of | Flow this | 40488.7561 | Abs Value of | Flow this | 51409.9765 | Abs Value of | Flow this | 60282.2406 | Abs Value of | Flow this | 67254.9877 | Abs Value of | Flow this | 75034.2609 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3328 |  |  | 95.2281 |  |  | 68.139 |  |  | -22.3319 |  |  | -231.7762 |  |  | -553.1832 |  |  | -953.399 |  |  | -1348.5572 |  |  | -1703.1701 |  |  | -2144.5623
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48399 |  |  | 0.45936 |  |  | 0.32869 |  |  | -0.10773 |  |  | -1.118 |  |  | -2.6685 |  |  | -4.599 |  |  | -6.5052 |  |  | -8.2158 |  |  | -10.345
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3328 |  |  | 45.2281 |  |  | 18.139 |  |  | -72.3319 |  |  | -281.7762 |  |  | -603.1832 |  |  | -1003.399 |  |  | -1398.5572 |  |  | -1753.1701 |  |  | -2194.5623
[13 empty] | Press drop ratio this iteration |  |  | 0.50166 |  |  | 0.47495 |  |  | 0.26621 |  |  | 3.239 |  |  | 1.2157 |  |  | 1.0904 |  |  | 1.0524 |  |  | 1.0371 |  |  | 1.0294 |  |  | 1.0233
[13 empty] | Expansion factor | 12 |  | 0.73873 |  |  | 0.7527 |  |  | 0.85931 |  |  | -0.73528 |  |  | 0.33081 |  |  | 0.36557 |  |  | 0.34538 |  |  | 0.29521 |  |  | 0.4219 |  |  | 0.12755
[13 empty] | C Non choked w/ reducers | 5 |  | 2.9913 |  |  | 16.791 |  |  | 68.0514 |  |  | -136.2796 |  |  | 79.2792 |  |  | 45.4776 |  |  | 37.3355 |  |  | 38.7186 |  |  | 27.2873 |  |  | 105.3953
[13 empty] | C Choked w/ reducers | 5 |  | 2.9331 |  |  | 16.321 |  |  | 56.9581 |  |  | 342.7722 |  |  | 55.712 |  |  | 34.3868 |  |  | 27.0926 |  |  | 24.918 |  |  | 22.7304 |  |  | 32.606
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2.9913 |  |  | 16.791 |  |  | 68.0514 |  |  | 342.7722 |  |  | 55.712 |  |  | 34.3868 |  |  | 27.0926 |  |  | 24.918 |  |  | 22.7304 |  |  | 32.606
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.9913 | 690.305 |  | 11.791 | 3643.8625 |  | 58.0514 | 9011.7056 |  | 7174 | 17552.5022 |  | 7174 | 28867.4037 |  | 7174 | 40488.7561 |  | 7174 | 51409.9765 |  | 7174 | 60282.2406 |  | 7174 | 67254.9877 |  | 7174 | 75034.2609
[13 empty] | Next iteration flow rate |  |  | 704.1111 | Abs Value of | Flow this | 3680.3011 | Abs Value of | Flow this | 9101.8226 | Abs Value of | Flow this | 17728.0272 | Abs Value of | Flow this | 29156.0778 | Abs Value of | Flow this | 40893.6437 | Abs Value of | Flow this | 51924.0763 | Abs Value of | Flow this | 60885.063 | Abs Value of | Flow this | 67927.5376 | Abs Value of | Flow this | 75784.6035 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3251 |  |  | 95.1217 |  |  | 67.4881 |  |  | -24.8013 |  |  | -238.4554 |  |  | -566.3227 |  |  | -974.5829 |  |  | -1377.6837 |  |  | -1739.4243 |  |  | -2189.6885
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48395 |  |  | 0.45885 |  |  | 0.32555 |  |  | -0.11964 |  |  | -1.1503 |  |  | -2.7318 |  |  | -4.7012 |  |  | -6.6457 |  |  | -8.3907 |  |  | -10.5627
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3251 |  |  | 45.1217 |  |  | 17.4881 |  |  | -74.8013 |  |  | -288.4554 |  |  | -616.3227 |  |  | -1024.5829 |  |  | -1427.6837 |  |  | -1789.4243 |  |  | -2239.6885
[13 empty] | Press drop ratio this iteration |  |  | 0.50162 |  |  | 0.47436 |  |  | 0.25913 |  |  | 3.016 |  |  | 1.2097 |  |  | 1.0883 |  |  | 1.0513 |  |  | 1.0363 |  |  | 1.0287 |  |  | 1.0228
[13 empty] | Expansion factor | 12 |  | 0.73875 |  |  | 0.753 |  |  | 0.86305 |  |  | -0.61585 |  |  | 0.33414 |  |  | 0.36679 |  |  | 0.34609 |  |  | 0.29574 |  |  | 0.42224 |  |  | 0.12796
[13 empty] | C Non choked w/ reducers | 5 |  | 3.0514 |  |  | 16.9815 |  |  | 70.0313 |  |  | -153.3444 |  |  | 77.2467 |  |  | 44.7605 |  |  | 36.8335 |  |  | 38.2246 |  |  | 26.9718 |  |  | 103.9462
[13 empty] | C Choked w/ reducers | 5 |  | 2.992 |  |  | 16.5026 |  |  | 58.0825 |  |  | 311.7299 |  |  | 54.693 |  |  | 33.9249 |  |  | 26.7687 |  |  | 24.6351 |  |  | 22.4792 |  |  | 32.2533
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.0514 |  |  | 16.9815 |  |  | 70.0313 |  |  | 311.7299 |  |  | 54.693 |  |  | 33.9249 |  |  | 26.7687 |  |  | 24.6351 |  |  | 22.4792 |  |  | 32.2533
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.0514 | 704.1111 |  | 11.9815 | 3680.3011 |  | 60.0313 | 9101.8226 |  | 7174 | 17728.0272 |  | 7174 | 29156.0778 |  | 7174 | 40893.6437 |  | 7174 | 51924.0763 |  | 7174 | 60885.063 |  | 7174 | 67927.5376 |  | 7174 | 75784.6035
[13 empty] | Next iteration flow rate |  |  | 718.1934 | Abs Value of | Flow this | 3717.1041 | Abs Value of | Flow this | 9192.8408 | Abs Value of | Flow this | 17905.3075 | Abs Value of | Flow this | 29447.6385 | Abs Value of | Flow this | 41302.5801 | Abs Value of | Flow this | 52443.317 | Abs Value of | Flow this | 61493.9136 | Abs Value of | Flow this | 68606.8129 | Abs Value of | Flow this | 76542.4496 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3171 |  |  | 95.0131 |  |  | 66.8241 |  |  | -27.3203 |  |  | -245.2689 |  |  | -579.7263 |  |  | -996.1925 |  |  | -1407.3957 |  |  | -1776.4072 |  |  | -2235.7218
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48391 |  |  | 0.45833 |  |  | 0.32235 |  |  | -0.13179 |  |  | -1.1831 |  |  | -2.7965 |  |  | -4.8055 |  |  | -6.789 |  |  | -8.5691 |  |  | -10.7847
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3171 |  |  | 45.0131 |  |  | 16.8241 |  |  | -77.3203 |  |  | -295.2689 |  |  | -629.7263 |  |  | -1046.1925 |  |  | -1457.3957 |  |  | -1826.4072 |  |  | -2285.7218
[13 empty] | Press drop ratio this iteration |  |  | 0.50158 |  |  | 0.47376 |  |  | 0.25177 |  |  | 2.8301 |  |  | 1.2039 |  |  | 1.0862 |  |  | 1.0502 |  |  | 1.0355 |  |  | 1.0281 |  |  | 1.0224
[13 empty] | Expansion factor | 12 |  | 0.73877 |  |  | 0.75332 |  |  | 0.86694 |  |  | -0.51626 |  |  | 0.33734 |  |  | 0.36798 |  |  | 0.34678 |  |  | 0.29626 |  |  | 0.42258 |  |  | 0.12836
[13 empty] | C Non choked w/ reducers | 5 |  | 3.1127 |  |  | 17.1747 |  |  | 72.146 |  |  | -173.1396 |  |  | 75.3124 |  |  | 44.0616 |  |  | 36.3415 |  |  | 37.7393 |  |  | 26.6609 |  |  | 102.5264
[13 empty] | C Choked w/ reducers | 5 |  | 3.0521 |  |  | 16.6867 |  |  | 59.2462 |  |  | 285.8174 |  |  | 53.7054 |  |  | 33.472 |  |  | 26.45 |  |  | 24.3562 |  |  | 22.2313 |  |  | 31.9051
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.1127 |  |  | 17.1747 |  |  | 72.146 |  |  | 285.8174 |  |  | 53.7054 |  |  | 33.472 |  |  | 26.45 |  |  | 24.3562 |  |  | 22.2313 |  |  | 31.9051
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.1127 | 718.1934 |  | 12.1747 | 3717.1041 |  | 62.146 | 9192.8408 |  | 7174 | 17905.3075 |  | 7174 | 29447.6385 |  | 7174 | 41302.5801 |  | 7174 | 52443.317 |  | 7174 | 61493.9136 |  | 7174 | 68606.8129 |  | 7174 | 76542.4496
[13 empty] | Next iteration flow rate |  |  | 732.5572 | Abs Value of | Flow this | 3754.2752 | Abs Value of | Flow this | 9284.7692 | Abs Value of | Flow this | 18084.3606 | Abs Value of | Flow this | 29742.1149 | Abs Value of | Flow this | 41715.6059 | Abs Value of | Flow this | 52967.7502 | Abs Value of | Flow this | 62108.8528 | Abs Value of | Flow this | 69292.8811 | Abs Value of | Flow this | 77307.8741 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3088 |  |  | 94.9024 |  |  | 66.1467 |  |  | -29.8899 |  |  | -252.2193 |  |  | -593.3993 |  |  | -1018.2365 |  |  | -1437.7048 |  |  | -1814.1335 |  |  | -2282.6803
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48387 |  |  | 0.45779 |  |  | 0.31908 |  |  | -0.14418 |  |  | -1.2167 |  |  | -2.8625 |  |  | -4.9118 |  |  | -6.9352 |  |  | -8.7511 |  |  | -11.0112
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3088 |  |  | 44.9024 |  |  | 16.1467 |  |  | -79.8899 |  |  | -302.2193 |  |  | -643.3993 |  |  | -1068.2365 |  |  | -1487.7048 |  |  | -1864.1335 |  |  | -2332.6803
[13 empty] | Press drop ratio this iteration |  |  | 0.50154 |  |  | 0.47314 |  |  | 0.2441 |  |  | 2.6728 |  |  | 1.1982 |  |  | 1.0843 |  |  | 1.0491 |  |  | 1.0348 |  |  | 1.0276 |  |  | 1.0219
[13 empty] | Expansion factor | 12 |  | 0.73879 |  |  | 0.75364 |  |  | 0.87099 |  |  | -0.43197 |  |  | 0.34044 |  |  | 0.36913 |  |  | 0.34746 |  |  | 0.29677 |  |  | 0.42291 |  |  | 0.12875
[13 empty] | C Non choked w/ reducers | 5 |  | 3.1753 |  |  | 17.3705 |  |  | 74.4124 |  |  | -196.5702 |  |  | 73.4691 |  |  | 43.3803 |  |  | 35.859 |  |  | 37.2626 |  |  | 26.3545 |  |  | 101.1352
[13 empty] | C Choked w/ reducers | 5 |  | 3.1134 |  |  | 16.8732 |  |  | 60.4514 |  |  | 263.858 |  |  | 52.7477 |  |  | 33.0277 |  |  | 26.1361 |  |  | 24.0811 |  |  | 21.9867 |  |  | 31.5613
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.1753 |  |  | 17.3705 |  |  | 74.4124 |  |  | 263.858 |  |  | 52.7477 |  |  | 33.0277 |  |  | 26.1361 |  |  | 24.0811 |  |  | 21.9867 |  |  | 31.5613
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.1753 | 732.5572 |  | 12.3705 | 3754.2752 |  | 64.4124 | 9284.7692 |  | 7174 | 18084.3606 |  | 7174 | 29742.1149 |  | 7174 | 41715.6059 |  | 7174 | 52967.7502 |  | 7174 | 62108.8528 |  | 7174 | 69292.8811 |  | 7174 | 77307.8741
[13 empty] | Next iteration flow rate |  |  | 747.2084 | Abs Value of | Flow this | 3791.8179 | Abs Value of | Flow this | 9377.6169 | Abs Value of | Flow this | 18265.2042 | Abs Value of | Flow this | 30039.5361 | Abs Value of | Flow this | 42132.762 | Abs Value of | Flow this | 53497.4277 | Abs Value of | Flow this | 62729.9413 | Abs Value of | Flow this | 69985.8099 | Abs Value of | Flow this | 78080.9528 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.3001 |  |  | 94.7894 |  |  | 65.4558 |  |  | -32.5112 |  |  | -259.3094 |  |  | -607.3471 |  |  | -1040.7235 |  |  | -1468.6232 |  |  | -1852.6181 |  |  | -2330.5827
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48383 |  |  | 0.45725 |  |  | 0.31575 |  |  | -0.15683 |  |  | -1.2509 |  |  | -2.9297 |  |  | -5.0203 |  |  | -7.0844 |  |  | -8.9367 |  |  | -11.2423
[13 empty] | Delta P at this iteration flow rate |  |  | 50.3001 |  |  | 44.7894 |  |  | 15.4558 |  |  | -82.5112 |  |  | -309.3094 |  |  | -657.3471 |  |  | -1090.7235 |  |  | -1518.6232 |  |  | -1902.6181 |  |  | -2380.5827
[13 empty] | Press drop ratio this iteration |  |  | 0.5015 |  |  | 0.47252 |  |  | 0.23613 |  |  | 2.5379 |  |  | 1.1928 |  |  | 1.0823 |  |  | 1.048 |  |  | 1.034 |  |  | 1.027 |  |  | 1.0215
[13 empty] | Expansion factor | 12 |  | 0.73882 |  |  | 0.75396 |  |  | 0.87521 |  |  | -0.35971 |  |  | 0.34342 |  |  | 0.37026 |  |  | 0.34812 |  |  | 0.29727 |  |  | 0.42323 |  |  | 0.12913
[13 empty] | C Non choked w/ reducers | 5 |  | 3.2391 |  |  | 17.5692 |  |  | 76.8504 |  |  | -224.9444 |  |  | 71.7102 |  |  | 42.7159 |  |  | 35.3857 |  |  | 36.7943 |  |  | 26.0526 |  |  | 99.7717
[13 empty] | C Choked w/ reducers | 5 |  | 3.1759 |  |  | 17.0623 |  |  | 61.7005 |  |  | 245.0097 |  |  | 51.8185 |  |  | 32.5919 |  |  | 25.8271 |  |  | 23.8099 |  |  | 21.7453 |  |  | 31.2217
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.2391 |  |  | 17.5692 |  |  | 76.8504 |  |  | 245.0097 |  |  | 51.8185 |  |  | 32.5919 |  |  | 25.8271 |  |  | 23.8099 |  |  | 21.7453 |  |  | 31.2217
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.2391 | 747.2084 |  | 12.5692 | 3791.8179 |  | 66.8504 | 9377.6169 |  | 7174 | 18265.2042 |  | 7174 | 30039.5361 |  | 7174 | 42132.762 |  | 7174 | 53497.4277 |  | 7174 | 62729.9413 |  | 7174 | 69985.8099 |  | 7174 | 78080.9528
[13 empty] | Next iteration flow rate |  |  | 762.1525 | Abs Value of | Flow this | 3829.7361 | Abs Value of | Flow this | 9471.3931 | Abs Value of | Flow this | 18447.8562 | Abs Value of | Flow this | 30339.9314 | Abs Value of | Flow this | 42554.0896 | Abs Value of | Flow this | 54032.402 | Abs Value of | Flow this | 63357.2407 | Abs Value of | Flow this | 70685.668 | Abs Value of | Flow this | 78861.7623 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.2912 |  |  | 94.6742 |  |  | 64.7509 |  |  | -35.1852 |  |  | -266.542 |  |  | -621.5753 |  |  | -1063.6626 |  |  | -1500.163 |  |  | -1891.8762 |  |  | -2379.4479
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48379 |  |  | 0.45669 |  |  | 0.31235 |  |  | -0.16973 |  |  | -1.2858 |  |  | -2.9984 |  |  | -5.1309 |  |  | -7.2365 |  |  | -9.1261 |  |  | -11.478
[13 empty] | Delta P at this iteration flow rate |  |  | 50.2912 |  |  | 44.6742 |  |  | 14.7509 |  |  | -85.1852 |  |  | -316.542 |  |  | -671.5753 |  |  | -1113.6626 |  |  | -1550.163 |  |  | -1941.8762 |  |  | -2429.4479
[13 empty] | Press drop ratio this iteration |  |  | 0.50145 |  |  | 0.47187 |  |  | 0.22781 |  |  | 2.4211 |  |  | 1.1876 |  |  | 1.0804 |  |  | 1.047 |  |  | 1.0333 |  |  | 1.0264 |  |  | 1.021
[13 empty] | Expansion factor | 12 |  | 0.73884 |  |  | 0.7543 |  |  | 0.8796 |  |  | -0.29709 |  |  | 0.3463 |  |  | 0.37135 |  |  | 0.34876 |  |  | 0.29775 |  |  | 0.42355 |  |  | 0.12951
[13 empty] | C Non choked w/ reducers | 5 |  | 3.3042 |  |  | 17.7707 |  |  | 79.4839 |  |  | -260.2376 |  |  | 70.0298 |  |  | 42.0677 |  |  | 34.9215 |  |  | 36.334 |  |  | 25.755 |  |  | 98.4349
[13 empty] | C Choked w/ reducers | 5 |  | 3.2397 |  |  | 17.2539 |  |  | 62.9958 |  |  | 228.6535 |  |  | 50.9165 |  |  | 32.1643 |  |  | 25.5228 |  |  | 23.5424 |  |  | 21.507 |  |  | 30.8863
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.3042 |  |  | 17.7707 |  |  | 79.4839 |  |  | 228.6535 |  |  | 50.9165 |  |  | 32.1643 |  |  | 25.5228 |  |  | 23.5424 |  |  | 21.507 |  |  | 30.8863
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.3042 | 762.1525 |  | 12.7707 | 3829.7361 |  | 69.4839 | 9471.3931 |  | 7174 | 18447.8562 |  | 7174 | 30339.9314 |  | 7174 | 42554.0896 |  | 7174 | 54032.402 |  | 7174 | 63357.2407 |  | 7174 | 70685.668 |  | 7174 | 78861.7623
[13 empty] | Next iteration flow rate |  |  | 777.3956 | Abs Value of | Flow this | 3868.0335 | Abs Value of | Flow this | 9566.107 | Abs Value of | Flow this | 18632.3348 | Abs Value of | Flow this | 30643.3307 | Abs Value of | Flow this | 42979.6305 | Abs Value of | Flow this | 54572.726 | Abs Value of | Flow this | 63990.8131 | Abs Value of | Flow this | 71392.5247 | Abs Value of | Flow this | 79650.3799 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.2818 |  |  | 94.5566 |  |  | 64.0319 |  |  | -37.9129 |  |  | -273.92 |  |  | -636.0895 |  |  | -1087.0627 |  |  | -1532.3368 |  |  | -1931.9235 |  |  | -2429.2953
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48374 |  |  | 0.45612 |  |  | 0.30888 |  |  | -0.18289 |  |  | -1.3213 |  |  | -3.0684 |  |  | -5.2438 |  |  | -7.3917 |  |  | -9.3193 |  |  | -11.7185
[13 empty] | Delta P at this iteration flow rate |  |  | 50.2818 |  |  | 44.5566 |  |  | 14.0319 |  |  | -87.9129 |  |  | -323.92 |  |  | -686.0895 |  |  | -1137.0627 |  |  | -1582.3368 |  |  | -1981.9235 |  |  | -2479.2953
[13 empty] | Press drop ratio this iteration |  |  | 0.50141 |  |  | 0.47122 |  |  | 0.21914 |  |  | 2.3188 |  |  | 1.1825 |  |  | 1.0786 |  |  | 1.046 |  |  | 1.0326 |  |  | 1.0259 |  |  | 1.0206
[13 empty] | Expansion factor | 12 |  | 0.73886 |  |  | 0.75464 |  |  | 0.88418 |  |  | -0.24231 |  |  | 0.34908 |  |  | 0.37242 |  |  | 0.34939 |  |  | 0.29823 |  |  | 0.42385 |  |  | 0.12988
[13 empty] | C Non choked w/ reducers | 5 |  | 3.3707 |  |  | 17.9751 |  |  | 82.3417 |  |  | -305.5926 |  |  | 68.4223 |  |  | 41.435 |  |  | 34.4659 |  |  | 35.8817 |  |  | 25.4616 |  |  | 97.1241
[13 empty] | C Choked w/ reducers | 5 |  | 3.3048 |  |  | 17.4481 |  |  | 64.3403 |  |  | 214.3245 |  |  | 50.0406 |  |  | 31.7447 |  |  | 25.2231 |  |  | 23.2786 |  |  | 21.2717 |  |  | 30.5551
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.3707 |  |  | 17.9751 |  |  | 82.3417 |  |  | 214.3245 |  |  | 50.0406 |  |  | 31.7447 |  |  | 25.2231 |  |  | 23.2786 |  |  | 21.2717 |  |  | 30.5551
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.3707 | 777.3956 |  | 12.9751 | 3868.0335 |  | 72.3417 | 9566.107 |  | 7174 | 18632.3348 |  | 7174 | 30643.3307 |  | 7174 | 42979.6305 |  | 7174 | 54572.726 |  | 7174 | 63990.8131 |  | 7174 | 71392.5247 |  | 7174 | 79650.3799
[13 empty] | Next iteration flow rate |  |  | 792.9435 | Abs Value of | Flow this | 3906.7138 | Abs Value of | Flow this | 9661.7681 | Abs Value of | Flow this | 18818.6582 | Abs Value of | Flow this | 30949.764 | Abs Value of | Flow this | 43409.4268 | Abs Value of | Flow this | 55118.4533 | Abs Value of | Flow this | 64630.7212 | Abs Value of | Flow this | 72106.4499 | Abs Value of | Flow this | 80446.8837 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.2721 |  |  | 94.4367 |  |  | 63.2985 |  |  | -40.6955 |  |  | -281.4463 |  |  | -650.8954 |  |  | -1110.9332 |  |  | -1565.1573 |  |  | -1972.7756 |  |  | -2480.1446
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48369 |  |  | 0.45555 |  |  | 0.30534 |  |  | -0.19631 |  |  | -1.3576 |  |  | -3.1398 |  |  | -5.3589 |  |  | -7.55 |  |  | -9.5163 |  |  | -11.9638
[13 empty] | Delta P at this iteration flow rate |  |  | 50.2721 |  |  | 44.4367 |  |  | 13.2985 |  |  | -90.6955 |  |  | -331.4463 |  |  | -700.8954 |  |  | -1160.9332 |  |  | -1615.1573 |  |  | -2022.7756 |  |  | -2530.1446
[13 empty] | Press drop ratio this iteration |  |  | 0.50136 |  |  | 0.47054 |  |  | 0.21009 |  |  | 2.2286 |  |  | 1.1777 |  |  | 1.0768 |  |  | 1.045 |  |  | 1.0319 |  |  | 1.0253 |  |  | 1.0202
[13 empty] | Expansion factor | 12 |  | 0.73889 |  |  | 0.75499 |  |  | 0.88896 |  |  | -0.194 |  |  | 0.35177 |  |  | 0.37346 |  |  | 0.35001 |  |  | 0.29869 |  |  | 0.42415 |  |  | 0.13024
[13 empty] | C Non choked w/ reducers | 5 |  | 3.4384 |  |  | 18.1824 |  |  | 85.4591 |  |  | -366.3435 |  |  | 66.883 |  |  | 40.8173 |  |  | 34.0189 |  |  | 35.4371 |  |  | 25.1724 |  |  | 95.8386
[13 empty] | C Choked w/ reducers | 5 |  | 3.3712 |  |  | 17.6449 |  |  | 65.7366 |  |  | 201.6667 |  |  | 49.1894 |  |  | 31.3328 |  |  | 24.928 |  |  | 23.0184 |  |  | 21.0396 |  |  | 30.2279
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.4384 |  |  | 18.1824 |  |  | 85.4591 |  |  | 201.6667 |  |  | 49.1894 |  |  | 31.3328 |  |  | 24.928 |  |  | 23.0184 |  |  | 21.0396 |  |  | 30.2279
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.4384 | 792.9435 |  | 13.1824 | 3906.7138 |  | 75.4591 | 9661.7681 |  | 7174 | 18818.6582 |  | 7174 | 30949.764 |  | 7174 | 43409.4268 |  | 7174 | 55118.4533 |  | 7174 | 64630.7212 |  | 7174 | 72106.4499 |  | 7174 | 80446.8837
[13 empty] | Next iteration flow rate |  |  | 808.8024 | Abs Value of | Flow this | 3945.7809 | Abs Value of | Flow this | 9758.3858 | Abs Value of | Flow this | 19006.8447 | Abs Value of | Flow this | 31259.2617 | Abs Value of | Flow this | 43843.521 | Abs Value of | Flow this | 55669.6378 | Abs Value of | Flow this | 65277.0284 | Abs Value of | Flow this | 72827.5144 | Abs Value of | Flow this | 81251.3526 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.2619 |  |  | 94.3144 |  |  | 62.5503 |  |  | -43.534 |  |  | -289.1239 |  |  | -665.9989 |  |  | -1135.2834 |  |  | -1598.6375 |  |  | -2014.4489 |  |  | -2532.016
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48365 |  |  | 0.45496 |  |  | 0.30173 |  |  | -0.21 |  |  | -1.3947 |  |  | -3.2127 |  |  | -5.4764 |  |  | -7.7115 |  |  | -9.7173 |  |  | -12.214
[13 empty] | Delta P at this iteration flow rate |  |  | 50.2619 |  |  | 44.3144 |  |  | 12.5503 |  |  | -93.534 |  |  | -339.1239 |  |  | -715.9989 |  |  | -1185.2834 |  |  | -1648.6375 |  |  | -2064.4489 |  |  | -2582.016
[13 empty] | Press drop ratio this iteration |  |  | 0.50131 |  |  | 0.46986 |  |  | 0.20064 |  |  | 2.1485 |  |  | 1.1729 |  |  | 1.0751 |  |  | 1.044 |  |  | 1.0313 |  |  | 1.0248 |  |  | 1.0197
[13 empty] | Expansion factor | 12 |  | 0.73891 |  |  | 0.75535 |  |  | 0.89396 |  |  | -0.15108 |  |  | 0.35436 |  |  | 0.37448 |  |  | 0.35061 |  |  | 0.29915 |  |  | 0.42445 |  |  | 0.13059
[13 empty] | C Non choked w/ reducers | 5 |  | 3.5076 |  |  | 18.3928 |  |  | 88.8798 |  |  | -452.3418 |  |  | 65.4073 |  |  | 40.2141 |  |  | 33.58 |  |  | 35 |  |  | 24.8873 |  |  | 94.5774
[13 empty] | C Choked w/ reducers | 5 |  | 3.439 |  |  | 17.8445 |  |  | 67.1882 |  |  | 190.4029 |  |  | 48.3621 |  |  | 30.9285 |  |  | 24.6372 |  |  | 22.7616 |  |  | 20.8104 |  |  | 29.9048
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.5076 |  |  | 18.3928 |  |  | 88.8798 |  |  | 190.4029 |  |  | 48.3621 |  |  | 30.9285 |  |  | 24.6372 |  |  | 22.7616 |  |  | 20.8104 |  |  | 29.9048
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5076 | 808.8024 |  | 13.3928 | 3945.7809 |  | 78.8798 | 9758.3858 |  | 7174 | 19006.8447 |  | 7174 | 31259.2617 |  | 7174 | 43843.521 |  | 7174 | 55669.6378 |  | 7174 | 65277.0284 |  | 7174 | 72827.5144 |  | 7174 | 81251.3526
[13 empty] | Next iteration flow rate |  |  | 824.9784 | Abs Value of | Flow this | 3985.2387 | Abs Value of | Flow this | 9855.9696 | Abs Value of | Flow this | 19196.9132 | Abs Value of | Flow this | 31571.8543 | Abs Value of | Flow this | 44281.9563 | Abs Value of | Flow this | 56226.3342 | Abs Value of | Flow this | 65929.7987 | Abs Value of | Flow this | 73555.7895 | Abs Value of | Flow this | 82063.8661 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.2514 |  |  | 94.1896 |  |  | 61.787 |  |  | -46.4295 |  |  | -296.9558 |  |  | -681.406 |  |  | -1160.1231 |  |  | -1632.7906 |  |  | -2056.9599 |  |  | -2584.9301
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48359 |  |  | 0.45435 |  |  | 0.29805 |  |  | -0.22397 |  |  | -1.4325 |  |  | -3.287 |  |  | -5.5962 |  |  | -7.8763 |  |  | -9.9224 |  |  | -12.4692
[13 empty] | Delta P at this iteration flow rate |  |  | 50.2514 |  |  | 44.1896 |  |  | 11.787 |  |  | -96.4295 |  |  | -346.9558 |  |  | -731.406 |  |  | -1210.1231 |  |  | -1682.7906 |  |  | -2106.9599 |  |  | -2634.9301
[13 empty] | Press drop ratio this iteration |  |  | 0.50125 |  |  | 0.46916 |  |  | 0.19077 |  |  | 2.0769 |  |  | 1.1684 |  |  | 1.0734 |  |  | 1.0431 |  |  | 1.0306 |  |  | 1.0243 |  |  | 1.0193
[13 empty] | Expansion factor | 12 |  | 0.73894 |  |  | 0.75571 |  |  | 0.89918 |  |  | -0.11271 |  |  | 0.35687 |  |  | 0.37546 |  |  | 0.3512 |  |  | 0.29959 |  |  | 0.42474 |  |  | 0.13093
[13 empty] | C Non choked w/ reducers | 5 |  | 3.5782 |  |  | 18.6062 |  |  | 92.6589 |  |  | -584.0405 |  |  | 63.9911 |  |  | 39.6247 |  |  | 33.1492 |  |  | 34.5702 |  |  | 24.6061 |  |  | 93.34
[13 empty] | C Choked w/ reducers | 5 |  | 3.5082 |  |  | 18.0468 |  |  | 68.6983 |  |  | 180.3139 |  |  | 47.5574 |  |  | 30.5315 |  |  | 24.3508 |  |  | 22.5084 |  |  | 20.5841 |  |  | 29.5855
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.5782 |  |  | 18.6062 |  |  | 92.6589 |  |  | 180.3139 |  |  | 47.5574 |  |  | 30.5315 |  |  | 24.3508 |  |  | 22.5084 |  |  | 20.5841 |  |  | 29.5855
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5782 | 824.9784 |  | 13.6062 | 3985.2387 |  | 82.6589 | 9855.9696 |  | 7174 | 19196.9132 |  | 7174 | 31571.8543 |  | 7174 | 44281.9563 |  | 7174 | 56226.3342 |  | 7174 | 65929.7987 |  | 7174 | 73555.7895 |  | 7174 | 82063.8661
[13 empty] | Next iteration flow rate |  |  | 841.478 | Abs Value of | Flow this | 4025.0911 | Abs Value of | Flow this | 9954.5293 | Abs Value of | Flow this | 19388.8823 | Abs Value of | Flow this | 31887.5728 | Abs Value of | Flow this | 44724.7758 | Abs Value of | Flow this | 56788.5975 | Abs Value of | Flow this | 66589.0967 | Abs Value of | Flow this | 74291.3474 | Abs Value of | Flow this | 82884.5048 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.2404 |  |  | 94.0623 |  |  | 61.0084 |  |  | -49.3833 |  |  | -304.9451 |  |  | -697.1227 |  |  | -1185.4621 |  |  | -1667.6302 |  |  | -2100.3253 |  |  | -2638.9077
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48354 |  |  | 0.45374 |  |  | 0.29429 |  |  | -0.23822 |  |  | -1.471 |  |  | -3.3628 |  |  | -5.7185 |  |  | -8.0444 |  |  | -10.1316 |  |  | -12.7296
[13 empty] | Delta P at this iteration flow rate |  |  | 50.2404 |  |  | 44.0623 |  |  | 11.0084 |  |  | -99.3833 |  |  | -354.9451 |  |  | -747.1227 |  |  | -1235.4621 |  |  | -1717.6302 |  |  | -2150.3253 |  |  | -2688.9077
[13 empty] | Press drop ratio this iteration |  |  | 0.5012 |  |  | 0.46844 |  |  | 0.18044 |  |  | 2.0125 |  |  | 1.164 |  |  | 1.0717 |  |  | 1.0422 |  |  | 1.03 |  |  | 1.0238 |  |  | 1.0189
[13 empty] | Expansion factor | 12 |  | 0.73897 |  |  | 0.75609 |  |  | 0.90464 |  |  | -0.0782 |  |  | 0.3593 |  |  | 0.37643 |  |  | 0.35177 |  |  | 0.30003 |  |  | 0.42502 |  |  | 0.13127
[13 empty] | C Non choked w/ reducers | 5 |  | 3.6502 |  |  | 18.8228 |  |  | 96.8664 |  |  | -812.0297 |  |  | 62.6308 |  |  | 39.0488 |  |  | 32.7261 |  |  | 34.1475 |  |  | 24.3289 |  |  | 92.1257
[13 empty] | C Choked w/ reducers | 5 |  | 3.5787 |  |  | 18.252 |  |  | 70.2708 |  |  | 171.2241 |  |  | 46.7746 |  |  | 30.1416 |  |  | 24.0686 |  |  | 22.2585 |  |  | 20.3607 |  |  | 29.2702
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.6502 |  |  | 18.8228 |  |  | 96.8664 |  |  | 171.2241 |  |  | 46.7746 |  |  | 30.1416 |  |  | 24.0686 |  |  | 22.2585 |  |  | 20.3607 |  |  | 29.2702
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6502 | 841.478 |  | 13.8228 | 4025.0911 |  | 86.8664 | 9954.5293 |  | 7174 | 19388.8823 |  | 7174 | 31887.5728 |  | 7174 | 44724.7758 |  | 7174 | 56788.5975 |  | 7174 | 66589.0967 |  | 7174 | 74291.3474 |  | 7174 | 82884.5048
[13 empty] | Next iteration flow rate |  |  | 858.3075 | Abs Value of | Flow this | 4065.342 | Abs Value of | Flow this | 10054.0746 | Abs Value of | Flow this | 19582.7711 | Abs Value of | Flow this | 32206.4486 | Abs Value of | Flow this | 45172.0236 | Abs Value of | Flow this | 57356.4835 | Abs Value of | Flow this | 67254.9877 | Abs Value of | Flow this | 75034.2609 | Abs Value of | Flow this | 83713.3498 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.229 |  |  | 93.9324 |  |  | 60.2142 |  |  | -52.3964 |  |  | -313.0951 |  |  | -713.1554 |  |  | -1211.3104 |  |  | -1703.1701 |  |  | -2144.5623 |  |  | -2693.9702
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48349 |  |  | 0.45311 |  |  | 0.29046 |  |  | -0.25275 |  |  | -1.5103 |  |  | -3.4401 |  |  | -5.8431 |  |  | -8.2158 |  |  | -10.345 |  |  | -12.9952
[13 empty] | Delta P at this iteration flow rate |  |  | 50.229 |  |  | 43.9324 |  |  | 10.2142 |  |  | -102.3964 |  |  | -363.0951 |  |  | -763.1554 |  |  | -1261.3104 |  |  | -1753.1701 |  |  | -2194.5623 |  |  | -2743.9702
[13 empty] | Press drop ratio this iteration |  |  | 0.50114 |  |  | 0.4677 |  |  | 0.16963 |  |  | 1.9543 |  |  | 1.1597 |  |  | 1.0701 |  |  | 1.0413 |  |  | 1.0294 |  |  | 1.0233 |  |  | 1.0186
[13 empty] | Expansion factor | 12 |  | 0.739 |  |  | 0.75647 |  |  | 0.91035 |  |  | -0.047006 |  |  | 0.36165 |  |  | 0.37736 |  |  | 0.35233 |  |  | 0.30045 |  |  | 0.42529 |  |  | 0.1316
[13 empty] | C Non choked w/ reducers | 5 |  | 3.7237 |  |  | 19.0427 |  |  | 101.5937 |  |  | -1304.9643 |  |  | 61.3228 |  |  | 38.4857 |  |  | 32.3106 |  |  | 33.7317 |  |  | 24.0555 |  |  | 90.9338
[13 empty] | C Choked w/ reducers | 5 |  | 3.6507 |  |  | 18.46 |  |  | 71.9097 |  |  | 162.9915 |  |  | 46.0126 |  |  | 29.7586 |  |  | 23.7906 |  |  | 22.012 |  |  | 20.1401 |  |  | 28.9586
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.7237 |  |  | 19.0427 |  |  | 101.5937 |  |  | 162.9915 |  |  | 46.0126 |  |  | 29.7586 |  |  | 23.7906 |  |  | 22.012 |  |  | 20.1401 |  |  | 28.9586
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7237 | 858.3075 |  | 14.0427 | 4065.342 |  | 91.5937 | 10054.0746 |  | 7174 | 19582.7711 |  | 7174 | 32206.4486 |  | 7174 | 45172.0236 |  | 7174 | 57356.4835 |  | 7174 | 67254.9877 |  | 7174 | 75034.2609 |  | 7174 | 83713.3498
[13 empty] | Next iteration flow rate |  |  | 875.4737 | Abs Value of | Flow this | 4105.9955 | Abs Value of | Flow this | 10154.6154 | Abs Value of | Flow this | 19778.5989 | Abs Value of | Flow this | 32528.5131 | Abs Value of | Flow this | 45623.7438 | Abs Value of | Flow this | 57930.0483 | Abs Value of | Flow this | 67927.5376 | Abs Value of | Flow this | 75784.6035 | Abs Value of | Flow this | 84550.4833 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.2172 |  |  | 93.8 |  |  | 59.404 |  |  | -55.47 |  |  | -321.4088 |  |  | -729.5103 |  |  | -1237.6783 |  |  | -1739.4243 |  |  | -2189.6885 |  |  | -2750.1395
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48343 |  |  | 0.45247 |  |  | 0.28655 |  |  | -0.26758 |  |  | -1.5504 |  |  | -3.519 |  |  | -5.9703 |  |  | -8.3907 |  |  | -10.5627 |  |  | -13.2662
[13 empty] | Delta P at this iteration flow rate |  |  | 50.2172 |  |  | 43.8 |  |  | 9.404 |  |  | -105.47 |  |  | -371.4088 |  |  | -779.5103 |  |  | -1287.6783 |  |  | -1789.4243 |  |  | -2239.6885 |  |  | -2800.1395
[13 empty] | Press drop ratio this iteration |  |  | 0.50108 |  |  | 0.46695 |  |  | 0.15831 |  |  | 1.9014 |  |  | 1.1556 |  |  | 1.0685 |  |  | 1.0404 |  |  | 1.0287 |  |  | 1.0228 |  |  | 1.0182
[13 empty] | Expansion factor | 12 |  | 0.73903 |  |  | 0.75686 |  |  | 0.91633 |  |  | -0.018677 |  |  | 0.36393 |  |  | 0.37828 |  |  | 0.35288 |  |  | 0.30087 |  |  | 0.42556 |  |  | 0.13192
[13 empty] | C Non choked w/ reducers | 5 |  | 3.7987 |  |  | 19.2658 |  |  | 106.962 |  |  | -3176.6148 |  |  | 60.0641 |  |  | 37.9351 |  |  | 31.9025 |  |  | 33.3228 |  |  | 23.7858 |  |  | 89.7636
[13 empty] | C Choked w/ reducers | 5 |  | 3.7242 |  |  | 18.6709 |  |  | 73.6194 |  |  | 155.4995 |  |  | 45.2706 |  |  | 29.3823 |  |  | 23.5166 |  |  | 21.7688 |  |  | 19.9223 |  |  | 28.6508
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.7987 |  |  | 19.2658 |  |  | 106.962 |  |  | 155.4995 |  |  | 45.2706 |  |  | 29.3823 |  |  | 23.5166 |  |  | 21.7688 |  |  | 19.9223 |  |  | 28.6508
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7987 | 875.4737 |  | 14.2658 | 4105.9955 |  | 96.962 | 10154.6154 |  | 7174 | 19778.5989 |  | 7174 | 32528.5131 |  | 7174 | 45623.7438 |  | 7174 | 57930.0483 |  | 7174 | 67927.5376 |  | 7174 | 75784.6035 |  | 7174 | 84550.4833
[13 empty] | Next iteration flow rate |  |  | 892.9832 | Abs Value of | Flow this | 4147.0554 | Abs Value of | Flow this | 10256.1615 | Abs Value of | Flow this | 19976.3848 | Abs Value of | Flow this | 32853.7982 | Abs Value of | Flow this | 46079.9813 | Abs Value of | Flow this | 58509.3488 | Abs Value of | Flow this | 68606.8129 | Abs Value of | Flow this | 76542.4496 | Abs Value of | Flow this | 85395.9881 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.2048 |  |  | 93.6649 |  |  | 58.5775 |  |  | -58.6055 |  |  | -329.8896 |  |  | -746.194 |  |  | -1264.5761 |  |  | -1776.4072 |  |  | -2235.7218 |  |  | -2807.4379
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48337 |  |  | 0.45182 |  |  | 0.28257 |  |  | -0.2827 |  |  | -1.5913 |  |  | -3.5995 |  |  | -6.1001 |  |  | -8.5691 |  |  | -10.7847 |  |  | -13.5426
[13 empty] | Delta P at this iteration flow rate |  |  | 50.2048 |  |  | 43.6649 |  |  | 8.5775 |  |  | -108.6055 |  |  | -379.8896 |  |  | -796.194 |  |  | -1314.5761 |  |  | -1826.4072 |  |  | -2285.7218 |  |  | -2857.4379
[13 empty] | Press drop ratio this iteration |  |  | 0.50102 |  |  | 0.46618 |  |  | 0.14643 |  |  | 1.8532 |  |  | 1.1516 |  |  | 1.067 |  |  | 1.0395 |  |  | 1.0281 |  |  | 1.0224 |  |  | 1.0178
[13 empty] | Expansion factor | 12 |  | 0.73906 |  |  | 0.75726 |  |  | 0.92261 |  |  | 0.0071597 |  |  | 0.36613 |  |  | 0.37917 |  |  | 0.35341 |  |  | 0.30128 |  |  | 0.42583 |  |  | 0.13224
[13 empty] | C Non choked w/ reducers | 5 |  | 3.8752 |  |  | 19.4923 |  |  | 113.1369 |  |  | 8024.203 |  |  | 58.8517 |  |  | 37.3966 |  |  | 31.5014 |  |  | 32.9204 |  |  | 23.5199 |  |  | 88.6146
[13 empty] | C Choked w/ reducers | 5 |  | 3.7991 |  |  | 18.8848 |  |  | 75.4047 |  |  | 148.6519 |  |  | 44.5479 |  |  | 29.0126 |  |  | 23.2465 |  |  | 21.5287 |  |  | 19.7072 |  |  | 28.3468
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.8752 |  |  | 19.4923 |  |  | 113.1369 |  |  | 148.6519 |  |  | 44.5479 |  |  | 29.0126 |  |  | 23.2465 |  |  | 21.5287 |  |  | 19.7072 |  |  | 28.3468
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8752 | 892.9832 |  | 14.4923 | 4147.0554 |  | 103.1369 | 10256.1615 |  | 7174 | 19976.3848 |  | 7174 | 32853.7982 |  | 7174 | 46079.9813 |  | 7174 | 58509.3488 |  | 7174 | 68606.8129 |  | 7174 | 76542.4496 |  | 7174 | 85395.9881
[13 empty] | Next iteration flow rate |  |  | 910.8428 | Abs Value of | Flow this | 4188.526 | Abs Value of | Flow this | 10358.7232 | Abs Value of | Flow this | 20176.1487 | Abs Value of | Flow this | 33182.3362 | Abs Value of | Flow this | 46540.7811 | Abs Value of | Flow this | 59094.4423 | Abs Value of | Flow this | 69292.8811 | Abs Value of | Flow this | 77307.8741 | Abs Value of | Flow this | 86249.948 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.192 |  |  | 93.527 |  |  | 57.7344 |  |  | -61.804 |  |  | -338.5409 |  |  | -763.213 |  |  | -1292.0146 |  |  | -1814.1335 |  |  | -2282.6803 |  |  | -2865.8879
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48331 |  |  | 0.45116 |  |  | 0.2785 |  |  | -0.29813 |  |  | -1.6331 |  |  | -3.6816 |  |  | -6.2324 |  |  | -8.7511 |  |  | -11.0112 |  |  | -13.8245
[13 empty] | Delta P at this iteration flow rate |  |  | 50.192 |  |  | 43.527 |  |  | 7.7344 |  |  | -111.804 |  |  | -388.5409 |  |  | -813.213 |  |  | -1342.0146 |  |  | -1864.1335 |  |  | -2332.6803 |  |  | -2915.8879
[13 empty] | Press drop ratio this iteration |  |  | 0.50096 |  |  | 0.4654 |  |  | 0.13397 |  |  | 1.809 |  |  | 1.1477 |  |  | 1.0655 |  |  | 1.0387 |  |  | 1.0276 |  |  | 1.0219 |  |  | 1.0174
[13 empty] | Expansion factor | 12 |  | 0.7391 |  |  | 0.75767 |  |  | 0.9292 |  |  | 0.030815 |  |  | 0.36826 |  |  | 0.38004 |  |  | 0.35393 |  |  | 0.30167 |  |  | 0.42609 |  |  | 0.13255
[13 empty] | C Non choked w/ reducers | 5 |  | 3.9533 |  |  | 19.7222 |  |  | 120.3514 |  |  | 1807.2427 |  |  | 57.683 |  |  | 36.8696 |  |  | 31.1074 |  |  | 32.5245 |  |  | 23.2575 |  |  | 87.4861
[13 empty] | C Choked w/ reducers | 5 |  | 3.8756 |  |  | 19.1018 |  |  | 77.2709 |  |  | 142.3684 |  |  | 43.8436 |  |  | 28.6493 |  |  | 22.9804 |  |  | 21.2918 |  |  | 19.4948 |  |  | 28.0463
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 3.9533 |  |  | 19.7222 |  |  | 120.3514 |  |  | 142.3684 |  |  | 43.8436 |  |  | 28.6493 |  |  | 22.9804 |  |  | 21.2918 |  |  | 19.4948 |  |  | 28.0463
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9533 | 910.8428 |  | 14.7222 | 4188.526 |  | 110.3514 | 10358.7232 |  | 7174 | 20176.1487 |  | 7174 | 33182.3362 |  | 7174 | 46540.7811 |  | 7174 | 59094.4423 |  | 7174 | 69292.8811 |  | 7174 | 77307.8741 |  | 7174 | 86249.948
[13 empty] | Next iteration flow rate |  |  | 929.0597 | Abs Value of | Flow this | 4230.4112 | Abs Value of | Flow this | 10462.3104 | Abs Value of | Flow this | 20377.9102 | Abs Value of | Flow this | 33514.1595 | Abs Value of | Flow this | 47006.1889 | Abs Value of | Flow this | 59685.3867 | Abs Value of | Flow this | 69985.8099 | Abs Value of | Flow this | 78080.9528 | Abs Value of | Flow this | 87112.4475 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.1786 |  |  | 93.3864 |  |  | 56.8743 |  |  | -65.0667 |  |  | -347.3661 |  |  | -780.5741 |  |  | -1320.0046 |  |  | -1852.6181 |  |  | -2330.5827 |  |  | -2925.5127
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48324 |  |  | 0.45048 |  |  | 0.27435 |  |  | -0.31387 |  |  | -1.6756 |  |  | -3.7654 |  |  | -6.3675 |  |  | -8.9367 |  |  | -11.2423 |  |  | -14.1122
[13 empty] | Delta P at this iteration flow rate |  |  | 50.1786 |  |  | 43.3864 |  |  | 6.8743 |  |  | -115.0667 |  |  | -397.3661 |  |  | -830.5741 |  |  | -1370.0046 |  |  | -1902.6181 |  |  | -2380.5827 |  |  | -2975.5127
[13 empty] | Press drop ratio this iteration |  |  | 0.50089 |  |  | 0.46459 |  |  | 0.12087 |  |  | 1.7684 |  |  | 1.1439 |  |  | 1.0641 |  |  | 1.0379 |  |  | 1.027 |  |  | 1.0215 |  |  | 1.0171
[13 empty] | Expansion factor | 12 |  | 0.73913 |  |  | 0.75809 |  |  | 0.93612 |  |  | 0.052549 |  |  | 0.37032 |  |  | 0.38089 |  |  | 0.35444 |  |  | 0.30206 |  |  | 0.42634 |  |  | 0.13285
[13 empty] | C Non choked w/ reducers | 5 |  | 4.033 |  |  | 19.9556 |  |  | 128.9454 |  |  | 1028.2856 |  |  | 56.5555 |  |  | 36.3539 |  |  | 30.7201 |  |  | 32.1349 |  |  | 22.9987 |  |  | 86.3777
[13 empty] | C Choked w/ reducers | 5 |  | 3.9536 |  |  | 19.3218 |  |  | 79.2237 |  |  | 136.5817 |  |  | 43.157 |  |  | 28.2923 |  |  | 22.718 |  |  | 21.058 |  |  | 19.2851 |  |  | 27.7494
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 4.033 |  |  | 19.9556 |  |  | 128.9454 |  |  | 136.5817 |  |  | 43.157 |  |  | 28.2923 |  |  | 22.718 |  |  | 21.058 |  |  | 19.2851 |  |  | 27.7494
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.033 | 929.0597 |  | 14.9556 | 4230.4112 |  | 118.9454 | 10462.3104 |  | 7174 | 20377.9102 |  | 7174 | 33514.1595 |  | 7174 | 47006.1889 |  | 7174 | 59685.3867 |  | 7174 | 69985.8099 |  | 7174 | 78080.9528 |  | 7174 | 87112.4475
[13 empty] | Next iteration flow rate |  |  | 947.6409 | Abs Value of | Flow this | 4272.7153 | Abs Value of | Flow this | 10566.9335 | Abs Value of | Flow this | 20581.6893 | Abs Value of | Flow this | 33849.3011 | Abs Value of | Flow this | 47476.2508 | Abs Value of | Flow this | 60282.2406 | Abs Value of | Flow this | 70685.668 | Abs Value of | Flow this | 78861.7623 | Abs Value of | Flow this | 87983.572 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.1647 |  |  | 93.243 |  |  | 55.997 |  |  | -68.3951 |  |  | -356.3686 |  |  | -798.2842 |  |  | -1348.5572 |  |  | -1891.8762 |  |  | -2379.4479 |  |  | -2986.336
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48318 |  |  | 0.44979 |  |  | 0.27012 |  |  | -0.32993 |  |  | -1.7191 |  |  | -3.8508 |  |  | -6.5052 |  |  | -9.1261 |  |  | -11.478 |  |  | -14.4056
[13 empty] | Delta P at this iteration flow rate |  |  | 50.1647 |  |  | 43.243 |  |  | 5.997 |  |  | -118.3951 |  |  | -406.3686 |  |  | -848.2842 |  |  | -1398.5572 |  |  | -1941.8762 |  |  | -2429.4479 |  |  | -3036.336
[13 empty] | Press drop ratio this iteration |  |  | 0.50082 |  |  | 0.46377 |  |  | 0.1071 |  |  | 1.731 |  |  | 1.1403 |  |  | 1.0626 |  |  | 1.0371 |  |  | 1.0264 |  |  | 1.021 |  |  | 1.0167
[13 empty] | Expansion factor | 12 |  | 0.73917 |  |  | 0.75852 |  |  | 0.9434 |  |  | 0.072584 |  |  | 0.37233 |  |  | 0.38171 |  |  | 0.35494 |  |  | 0.30244 |  |  | 0.42659 |  |  | 0.13315
[13 empty] | C Non choked w/ reducers | 5 |  | 4.1143 |  |  | 20.1927 |  |  | 139.44 |  |  | 722.9969 |  |  | 55.467 |  |  | 35.8491 |  |  | 30.3394 |  |  | 31.7514 |  |  | 22.7434 |  |  | 85.2887
[13 empty] | C Choked w/ reducers | 5 |  | 4.0333 |  |  | 19.5451 |  |  | 81.2696 |  |  | 131.2345 |  |  | 42.4874 |  |  | 27.9412 |  |  | 22.4594 |  |  | 20.8272 |  |  | 19.0779 |  |  | 27.4561
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 4.1143 |  |  | 20.1927 |  |  | 139.44 |  |  | 131.2345 |  |  | 42.4874 |  |  | 27.9412 |  |  | 22.4594 |  |  | 20.8272 |  |  | 19.0779 |  |  | 27.4561
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.1143 | 947.6409 |  | 15.1927 | 4272.7153 |  | 129.44 | 10566.9335 |  | 7174 | 20581.6893 |  | 7174 | 33849.3011 |  | 7174 | 47476.2508 |  | 7174 | 60282.2406 |  | 7174 | 70685.668 |  | 7174 | 78861.7623 |  | 7174 | 87983.572
[13 empty] | Next iteration flow rate |  |  | 966.5937 | Abs Value of | Flow this | 4315.4425 | Abs Value of | Flow this | 10672.6028 | Abs Value of | Flow this | 20787.5062 | Abs Value of | Flow this | 34187.7941 | Abs Value of | Flow this | 47951.0133 | Abs Value of | Flow this | 60885.063 | Abs Value of | Flow this | 71392.5247 | Abs Value of | Flow this | 79650.3799 | Abs Value of | Flow this | 88863.4077 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.1502 |  |  | 93.0966 |  |  | 55.102 |  |  | -71.7903 |  |  | -365.5521 |  |  | -816.3502 |  |  | -1377.6837 |  |  | -1931.9235 |  |  | -2429.2953 |  |  | -3048.3819
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48311 |  |  | 0.44908 |  |  | 0.2658 |  |  | -0.3463 |  |  | -1.7634 |  |  | -3.9379 |  |  | -6.6457 |  |  | -9.3193 |  |  | -11.7185 |  |  | -14.7049
[13 empty] | Delta P at this iteration flow rate |  |  | 50.1502 |  |  | 43.0966 |  |  | 5.102 |  |  | -121.7903 |  |  | -415.5521 |  |  | -866.3502 |  |  | -1427.6837 |  |  | -1981.9235 |  |  | -2479.2953 |  |  | -3098.3819
[13 empty] | Press drop ratio this iteration |  |  | 0.50075 |  |  | 0.46292 |  |  | 0.092593 |  |  | 1.6965 |  |  | 1.1368 |  |  | 1.0612 |  |  | 1.0363 |  |  | 1.0259 |  |  | 1.0206 |  |  | 1.0164
[13 empty] | Expansion factor | 12 |  | 0.7392 |  |  | 0.75896 |  |  | 0.95106 |  |  | 0.091107 |  |  | 0.37427 |  |  | 0.38252 |  |  | 0.35543 |  |  | 0.30282 |  |  | 0.42683 |  |  | 0.13344
[13 empty] | C Non choked w/ reducers | 5 |  | 4.1973 |  |  | 20.4334 |  |  | 152.6822 |  |  | 559.8678 |  |  | 54.4153 |  |  | 35.3547 |  |  | 29.9651 |  |  | 31.3739 |  |  | 22.4914 |  |  | 84.2186
[13 empty] | C Choked w/ reducers | 5 |  | 4.1145 |  |  | 19.7715 |  |  | 83.4155 |  |  | 126.2782 |  |  | 41.8342 |  |  | 27.5961 |  |  | 22.2044 |  |  | 20.5995 |  |  | 18.8733 |  |  | 27.1662
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 4.1973 |  |  | 20.4334 |  |  | 152.6822 |  |  | 126.2782 |  |  | 41.8342 |  |  | 27.5961 |  |  | 22.2044 |  |  | 20.5995 |  |  | 18.8733 |  |  | 27.1662
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.1973 | 966.5937 |  | 15.4334 | 4315.4425 |  | 142.6822 | 10672.6028 |  | 7174 | 20787.5062 |  | 7174 | 34187.7941 |  | 7174 | 47951.0133 |  | 7174 | 60885.063 |  | 7174 | 71392.5247 |  | 7174 | 79650.3799 |  | 7174 | 88863.4077
[13 empty] | Next iteration flow rate |  |  | 985.9256 | Abs Value of | Flow this | 4358.5969 | Abs Value of | Flow this | 10779.3289 | Abs Value of | Flow this | 20995.3812 | Abs Value of | Flow this | 34529.6721 | Abs Value of | Flow this | 48430.5234 | Abs Value of | Flow this | 61493.9136 | Abs Value of | Flow this | 72106.4499 | Abs Value of | Flow this | 80446.8837 | Abs Value of | Flow this | 89752.0418 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.1352 |  |  | 92.9474 |  |  | 54.1891 |  |  | -75.2538 |  |  | -374.9203 |  |  | -834.7793 |  |  | -1407.3957 |  |  | -1972.7756 |  |  | -2480.1446 |  |  | -3111.6749
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48303 |  |  | 0.44836 |  |  | 0.2614 |  |  | -0.36301 |  |  | -1.8085 |  |  | -4.0268 |  |  | -6.789 |  |  | -9.5163 |  |  | -11.9638 |  |  | -15.0102
[13 empty] | Delta P at this iteration flow rate |  |  | 50.1352 |  |  | 42.9474 |  |  | 4.1891 |  |  | -125.2538 |  |  | -424.9203 |  |  | -884.7793 |  |  | -1457.3957 |  |  | -2022.7756 |  |  | -2530.1446 |  |  | -3161.6749
[13 empty] | Press drop ratio this iteration |  |  | 0.50067 |  |  | 0.46206 |  |  | 0.077305 |  |  | 1.6644 |  |  | 1.1334 |  |  | 1.0599 |  |  | 1.0355 |  |  | 1.0253 |  |  | 1.0202 |  |  | 1.0161
[13 empty] | Expansion factor | 12 |  | 0.73924 |  |  | 0.75941 |  |  | 0.95914 |  |  | 0.10828 |  |  | 0.37615 |  |  | 0.38331 |  |  | 0.35591 |  |  | 0.30318 |  |  | 0.42707 |  |  | 0.13372
[13 empty] | C Non choked w/ reducers | 5 |  | 4.282 |  |  | 20.678 |  |  | 170.1673 |  |  | 458.2351 |  |  | 53.3985 |  |  | 34.8705 |  |  | 29.5971 |  |  | 31.0023 |  |  | 22.2429 |  |  | 83.1671
[13 empty] | C Choked w/ reducers | 5 |  | 4.1974 |  |  | 20.0013 |  |  | 85.6691 |  |  | 121.671 |  |  | 41.1968 |  |  | 27.2568 |  |  | 21.953 |  |  | 20.3746 |  |  | 18.6712 |  |  | 26.8798
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 4.282 |  |  | 20.678 |  |  | 170.1673 |  |  | 121.671 |  |  | 41.1968 |  |  | 27.2568 |  |  | 21.953 |  |  | 20.3746 |  |  | 18.6712 |  |  | 26.8798
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.282 | 985.9256 |  | 15.678 | 4358.5969 |  | 160.1673 | 10779.3289 |  | 7174 | 20995.3812 |  | 7174 | 34529.6721 |  | 7174 | 48430.5234 |  | 7174 | 61493.9136 |  | 7174 | 72106.4499 |  | 7174 | 80446.8837 |  | 7174 | 89752.0418
[13 empty] | Next iteration flow rate |  |  | 1005.6441 | Abs Value of | Flow this | 4402.1829 | Abs Value of | Flow this | 10887.1221 | Abs Value of | Flow this | 21205.335 | Abs Value of | Flow this | 34874.9688 | Abs Value of | Flow this | 48914.8286 | Abs Value of | Flow this | 62108.8528 | Abs Value of | Flow this | 72827.5144 | Abs Value of | Flow this | 81251.3526 | Abs Value of | Flow this | 90649.5622 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.1195 |  |  | 92.7951 |  |  | 53.2578 |  |  | -78.7869 |  |  | -384.4767 |  |  | -853.5789 |  |  | -1437.7048 |  |  | -2014.4489 |  |  | -2532.016 |  |  | -3176.24
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48296 |  |  | 0.44763 |  |  | 0.25691 |  |  | -0.38005 |  |  | -1.8546 |  |  | -4.1175 |  |  | -6.9352 |  |  | -9.7173 |  |  | -12.214 |  |  | -15.3216
[13 empty] | Delta P at this iteration flow rate |  |  | 50.1195 |  |  | 42.7951 |  |  | 3.2578 |  |  | -128.7869 |  |  | -434.4767 |  |  | -903.5789 |  |  | -1487.7048 |  |  | -2064.4489 |  |  | -2582.016 |  |  | -3226.24
[13 empty] | Press drop ratio this iteration |  |  | 0.5006 |  |  | 0.46118 |  |  | 0.06117 |  |  | 1.6346 |  |  | 1.13 |  |  | 1.0586 |  |  | 1.0348 |  |  | 1.0248 |  |  | 1.0197 |  |  | 1.0157
[13 empty] | Expansion factor | 12 |  | 0.73928 |  |  | 0.75987 |  |  | 0.96767 |  |  | 0.12424 |  |  | 0.37797 |  |  | 0.38408 |  |  | 0.35637 |  |  | 0.30354 |  |  | 0.4273 |  |  | 0.134
[13 empty] | C Non choked w/ reducers | 5 |  | 4.3684 |  |  | 20.9264 |  |  | 194.8573 |  |  | 388.7618 |  |  | 52.4148 |  |  | 34.3961 |  |  | 29.2352 |  |  | 30.6364 |  |  | 21.9976 |  |  | 82.1334
[13 empty] | C Choked w/ reducers | 5 |  | 4.2821 |  |  | 20.2345 |  |  | 88.0388 |  |  | 117.3769 |  |  | 40.5746 |  |  | 26.923 |  |  | 21.7051 |  |  | 20.1527 |  |  | 18.4716 |  |  | 26.5967
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 4.3684 |  |  | 20.9264 |  |  | 194.8573 |  |  | 117.3769 |  |  | 40.5746 |  |  | 26.923 |  |  | 21.7051 |  |  | 20.1527 |  |  | 18.4716 |  |  | 26.5967
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.3684 | 1005.6441 |  | 15.9264 | 4402.1829 |  | 184.8573 | 10887.1221 |  | 7174 | 21205.335 |  | 7174 | 34874.9688 |  | 7174 | 48914.8286 |  | 7174 | 62108.8528 |  | 7174 | 72827.5144 |  | 7174 | 81251.3526 |  | 7174 | 90649.5622
[13 empty] | Next iteration flow rate |  |  | 1025.757 | Abs Value of | Flow this | 4446.2047 | Abs Value of | Flow this | 10995.9934 | Abs Value of | Flow this | 21417.3884 | Abs Value of | Flow this | 35223.7185 | Abs Value of | Flow this | 49403.9769 | Abs Value of | Flow this | 62729.9413 | Abs Value of | Flow this | 73555.7895 | Abs Value of | Flow this | 82063.8661 | Abs Value of | Flow this | 91556.0578 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.1032 |  |  | 92.6398 |  |  | 52.3077 |  |  | -82.3911 |  |  | -394.2251 |  |  | -872.7563 |  |  | -1468.6232 |  |  | -2056.9599 |  |  | -2584.9301 |  |  | -3242.103
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48288 |  |  | 0.44688 |  |  | 0.25232 |  |  | -0.39744 |  |  | -1.9017 |  |  | -4.21 |  |  | -7.0844 |  |  | -9.9224 |  |  | -12.4692 |  |  | -15.6393
[13 empty] | Delta P at this iteration flow rate |  |  | 50.1032 |  |  | 42.6398 |  |  | 2.3077 |  |  | -132.3911 |  |  | -444.2251 |  |  | -922.7563 |  |  | -1518.6232 |  |  | -2106.9599 |  |  | -2634.9301 |  |  | -3292.103
[13 empty] | Press drop ratio this iteration |  |  | 0.50052 |  |  | 0.46027 |  |  | 0.044119 |  |  | 1.6069 |  |  | 1.1268 |  |  | 1.0573 |  |  | 1.034 |  |  | 1.0243 |  |  | 1.0193 |  |  | 1.0154
[13 empty] | Expansion factor | 12 |  | 0.73933 |  |  | 0.76034 |  |  | 0.97668 |  |  | 0.13912 |  |  | 0.37974 |  |  | 0.38482 |  |  | 0.35683 |  |  | 0.30389 |  |  | 0.42753 |  |  | 0.13428
[13 empty] | C Non choked w/ reducers | 5 |  | 4.4566 |  |  | 21.1787 |  |  | 233.7692 |  |  | 338.2153 |  |  | 51.4625 |  |  | 33.9312 |  |  | 28.8793 |  |  | 30.276 |  |  | 21.7555 |  |  | 81.1173
[13 empty] | C Choked w/ reducers | 5 |  | 4.3684 |  |  | 20.4711 |  |  | 90.5342 |  |  | 113.3648 |  |  | 39.9669 |  |  | 26.5947 |  |  | 21.4606 |  |  | 19.9335 |  |  | 18.2744 |  |  | 26.317
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 4.4566 |  |  | 21.1787 |  |  | 233.7692 |  |  | 113.3648 |  |  | 39.9669 |  |  | 26.5947 |  |  | 21.4606 |  |  | 19.9335 |  |  | 18.2744 |  |  | 26.317
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.4566 | 1025.757 |  | 16.1787 | 4446.2047 |  | 223.7692 | 10995.9934 |  | 7174 | 21417.3884 |  | 7174 | 35223.7185 |  | 7174 | 49403.9769 |  | 7174 | 62729.9413 |  | 7174 | 73555.7895 |  | 7174 | 82063.8661 |  | 7174 | 91556.0578
[13 empty] | Next iteration flow rate |  |  | 1046.2721 | Abs Value of | Flow this | 4490.6668 | Abs Value of | Flow this | 11105.9533 | Abs Value of | Flow this | 21631.5623 | Abs Value of | Flow this | 35575.9557 | Abs Value of | Flow this | 49898.0167 | Abs Value of | Flow this | 63357.2407 | Abs Value of | Flow this | 74291.3474 | Abs Value of | Flow this | 82884.5048 | Abs Value of | Flow this | 92471.6184 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.0863 |  |  | 92.4813 |  |  | 51.3386 |  |  | -86.0676 |  |  | -404.1696 |  |  | -892.3192 |  |  | -1500.163 |  |  | -2100.3253 |  |  | -2638.9077 |  |  | -3309.2898
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4828 |  |  | 0.44611 |  |  | 0.24765 |  |  | -0.41517 |  |  | -1.9496 |  |  | -4.3044 |  |  | -7.2365 |  |  | -10.1316 |  |  | -12.7296 |  |  | -15.9634
[13 empty] | Delta P at this iteration flow rate |  |  | 50.0863 |  |  | 42.4813 |  |  | 1.3386 |  |  | -136.0676 |  |  | -454.1696 |  |  | -942.3192 |  |  | -1550.163 |  |  | -2150.3253 |  |  | -2688.9077 |  |  | -3359.2898
[13 empty] | Press drop ratio this iteration |  |  | 0.50043 |  |  | 0.45935 |  |  | 0.026074 |  |  | 1.5809 |  |  | 1.1237 |  |  | 1.056 |  |  | 1.0333 |  |  | 1.0238 |  |  | 1.0189 |  |  | 1.0151
[13 empty] | Expansion factor | 12 |  | 0.73937 |  |  | 0.76082 |  |  | 0.98622 |  |  | 0.153 |  |  | 0.38146 |  |  | 0.38556 |  |  | 0.35727 |  |  | 0.30423 |  |  | 0.42775 |  |  | 0.13454
[13 empty] | C Non choked w/ reducers | 5 |  | 4.5466 |  |  | 21.4351 |  |  | 309.8947 |  |  | 299.7501 |  |  | 50.54 |  |  | 33.4755 |  |  | 28.5291 |  |  | 29.9212 |  |  | 21.5166 |  |  | 80.1182
[13 empty] | C Choked w/ reducers | 5 |  | 4.4565 |  |  | 20.7112 |  |  | 93.1656 |  |  | 109.6074 |  |  | 39.3734 |  |  | 26.2718 |  |  | 21.2195 |  |  | 19.7172 |  |  | 18.0796 |  |  | 26.0405
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 4.5466 |  |  | 21.4351 |  |  | 309.8947 |  |  | 109.6074 |  |  | 39.3734 |  |  | 26.2718 |  |  | 21.2195 |  |  | 19.7172 |  |  | 18.0796 |  |  | 26.0405
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.5466 | 1046.2721 |  | 16.4351 | 4490.6668 |  | 299.8947 | 11105.9533 |  | 7174 | 21631.5623 |  | 7174 | 35575.9557 |  | 7174 | 49898.0167 |  | 7174 | 63357.2407 |  | 7174 | 74291.3474 |  | 7174 | 82884.5048 |  | 7174 | 92471.6184
[13 empty] | Next iteration flow rate |  |  | 1067.1976 | Abs Value of | Flow this | 4535.5734 | Abs Value of | Flow this | 11217.0128 | Abs Value of | Flow this | 21847.8779 | Abs Value of | Flow this | 35931.7152 | Abs Value of | Flow this | 50396.9969 | Abs Value of | Flow this | 63990.8131 | Abs Value of | Flow this | 75034.2609 | Abs Value of | Flow this | 83713.3498 | Abs Value of | Flow this | 93396.3346 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.0686 |  |  | 92.3197 |  |  | 50.35 |  |  | -89.8181 |  |  | -414.3139 |  |  | -912.2754 |  |  | -1532.3368 |  |  | -2144.5623 |  |  | -2693.9702 |  |  | -3377.827
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48271 |  |  | 0.44533 |  |  | 0.24288 |  |  | -0.43327 |  |  | -1.9986 |  |  | -4.4007 |  |  | -7.3917 |  |  | -10.345 |  |  | -12.9952 |  |  | -16.294
[13 empty] | Delta P at this iteration flow rate |  |  | 50.0686 |  |  | 42.3197 |  |  | 0.35002 |  |  | -139.8181 |  |  | -464.3139 |  |  | -962.2754 |  |  | -1582.3368 |  |  | -2194.5623 |  |  | -2743.9702 |  |  | -3427.827
[13 empty] | Press drop ratio this iteration |  |  | 0.50034 |  |  | 0.4584 |  |  | 0.0069518 |  |  | 1.5567 |  |  | 1.1207 |  |  | 1.0548 |  |  | 1.0326 |  |  | 1.0233 |  |  | 1.0186 |  |  | 1.0148
[13 empty] | Expansion factor | 12 |  | 0.73942 |  |  | 0.76131 |  |  | 0.99633 |  |  | 0.166 |  |  | 0.38313 |  |  | 0.38627 |  |  | 0.35771 |  |  | 0.30456 |  |  | 0.42796 |  |  | 0.1348
[13 empty] | C Non choked w/ reducers | 5 |  | 4.6385 |  |  | 21.6957 |  |  | 611.802 |  |  | 269.4689 |  |  | 49.6458 |  |  | 33.0288 |  |  | 28.1846 |  |  | 29.5717 |  |  | 21.2808 |  |  | 79.1358
[13 empty] | C Choked w/ reducers | 5 |  | 4.5465 |  |  | 20.955 |  |  | 95.9448 |  |  | 106.0809 |  |  | 38.7935 |  |  | 25.9541 |  |  | 20.9817 |  |  | 19.5036 |  |  | 17.8872 |  |  | 25.7673
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 4.6385 |  |  | 21.6957 |  |  | 611.802 |  |  | 106.0809 |  |  | 38.7935 |  |  | 25.9541 |  |  | 20.9817 |  |  | 19.5036 |  |  | 17.8872 |  |  | 25.7673
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.6385 | 1067.1976 |  | 16.6957 | 4535.5734 |  | 601.802 | 11217.0128 |  | 7174 | 21847.8779 |  | 7174 | 35931.7152 |  | 7174 | 50396.9969 |  | 7174 | 63990.8131 |  | 7174 | 75034.2609 |  | 7174 | 83713.3498 |  | 7174 | 93396.3346
[13 empty] | Next iteration flow rate |  |  | 1088.5415 | Abs Value of | Flow this | 4580.9292 | Abs Value of | Flow this | 11329.183 | Abs Value of | Flow this | 22066.3567 | Abs Value of | Flow this | 36291.0324 | Abs Value of | Flow this | 50900.9668 | Abs Value of | Flow this | 64630.7212 | Abs Value of | Flow this | 75784.6035 | Abs Value of | Flow this | 84550.4833 | Abs Value of | Flow this | 94330.2979 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.0503 |  |  | 92.1548 |  |  | 49.3416 |  |  | -93.644 |  |  | -424.6621 |  |  | -932.6326 |  |  | -1565.1573 |  |  | -2189.6885 |  |  | -2750.1395 |  |  | -3447.7418
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48262 |  |  | 0.44454 |  |  | 0.23801 |  |  | -0.45172 |  |  | -2.0485 |  |  | -4.4989 |  |  | -7.55 |  |  | -10.5627 |  |  | -13.2662 |  |  | -16.6313
[13 empty] | Delta P at this iteration flow rate |  |  | 50.0503 |  |  | 42.1548 |  |  | -0.65845 |  |  | -143.644 |  |  | -474.6621 |  |  | -982.6326 |  |  | -1615.1573 |  |  | -2239.6885 |  |  | -2800.1395 |  |  | -3497.7418
[13 empty] | Press drop ratio this iteration |  |  | 0.50025 |  |  | 0.45743 |  |  | -0.013345 |  |  | 1.5339 |  |  | 1.1177 |  |  | 1.0536 |  |  | 1.0319 |  |  | 1.0228 |  |  | 1.0182 |  |  | 1.0145
[13 empty] | Expansion factor | 12 |  | 0.73946 |  |  | 0.76182 |  |  | 1.0071 |  |  | 0.17819 |  |  | 0.38475 |  |  | 0.38696 |  |  | 0.35813 |  |  | 0.30489 |  |  | 0.42818 |  |  | 0.13506
[13 empty] | C Non choked w/ reducers | 5 |  | 4.7323 |  |  | 21.9606 |  |  | #NUM! |  |  | 244.9896 |  |  | 48.7786 |  |  | 32.5907 |  |  | 27.8457 |  |  | 29.2274 |  |  | 21.0481 |  |  | 78.1695
[13 empty] | C Choked w/ reducers | 5 |  | 4.6382 |  |  | 21.2024 |  |  | 98.8849 |  |  | 102.7644 |  |  | 38.2266 |  |  | 25.6414 |  |  | 20.7472 |  |  | 19.2926 |  |  | 17.6971 |  |  | 25.4972
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 4.7323 |  |  | 21.9606 |  |  | #NUM! |  |  | 102.7644 |  |  | 38.2266 |  |  | 25.6414 |  |  | 20.7472 |  |  | 19.2926 |  |  | 17.6971 |  |  | 25.4972
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.7323 | 1088.5415 |  | 16.9606 | 4580.9292 |  | 7174 | 11329.183 |  | 7174 | 22066.3567 |  | 7174 | 36291.0324 |  | 7174 | 50900.9668 |  | 7174 | 64630.7212 |  | 7174 | 75784.6035 |  | 7174 | 84550.4833 |  | 7174 | 94330.2979
[13 empty] | Next iteration flow rate |  |  | 1110.3123 | Abs Value of | Flow this | 4626.7385 | Abs Value of | Flow this | 11442.4748 | Abs Value of | Flow this | 22287.0202 | Abs Value of | Flow this | 36653.9427 | Abs Value of | Flow this | 51409.9765 | Abs Value of | Flow this | 65277.0284 | Abs Value of | Flow this | 76542.4496 | Abs Value of | Flow this | 85395.9881 | Abs Value of | Flow this | 95273.6009 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.0312 |  |  | 91.9866 |  |  | 48.3128 |  |  | -97.5467 |  |  | -435.2183 |  |  | -953.399 |  |  | -1598.6375 |  |  | -2235.7218 |  |  | -2807.4379 |  |  | -3519.0619
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48253 |  |  | 0.44373 |  |  | 0.23305 |  |  | -0.47055 |  |  | -2.0994 |  |  | -4.599 |  |  | -7.7115 |  |  | -10.7847 |  |  | -13.5426 |  |  | -16.9753
[13 empty] | Delta P at this iteration flow rate |  |  | 50.0312 |  |  | 41.9866 |  |  | -1.6872 |  |  | -147.5467 |  |  | -485.2183 |  |  | -1003.399 |  |  | -1648.6375 |  |  | -2285.7218 |  |  | -2857.4379 |  |  | -3569.0619
[13 empty] | Press drop ratio this iteration |  |  | 0.50016 |  |  | 0.45644 |  |  | -0.034922 |  |  | 1.5126 |  |  | 1.1149 |  |  | 1.0524 |  |  | 1.0313 |  |  | 1.0224 |  |  | 1.0178 |  |  | 1.0142
[13 empty] | Expansion factor | 12 |  | 0.73951 |  |  | 0.76233 |  |  | 1.0185 |  |  | 0.18963 |  |  | 0.38632 |  |  | 0.38764 |  |  | 0.35855 |  |  | 0.30521 |  |  | 0.42839 |  |  | 0.13531
[13 empty] | C Non choked w/ reducers | 5 |  | 4.828 |  |  | 22.2298 |  |  | #NUM! |  |  | 224.7739 |  |  | 47.9371 |  |  | 32.161 |  |  | 27.5121 |  |  | 28.8883 |  |  | 20.8183 |  |  | 77.219
[13 empty] | C Choked w/ reducers | 5 |  | 4.7319 |  |  | 21.4536 |  |  | 102.0004 |  |  | 99.6394 |  |  | 37.6724 |  |  | 25.3338 |  |  | 20.5158 |  |  | 19.0844 |  |  | 17.5093 |  |  | 25.2303
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 4.828 |  |  | 22.2298 |  |  | #NUM! |  |  | 99.6394 |  |  | 37.6724 |  |  | 25.3338 |  |  | 20.5158 |  |  | 19.0844 |  |  | 17.5093 |  |  | 25.2303
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.828 | 1110.3123 |  | 17.2298 | 4626.7385 |  | 7174 | 11442.4748 |  | 7174 | 22287.0202 |  | 7174 | 36653.9427 |  | 7174 | 51409.9765 |  | 7174 | 65277.0284 |  | 7174 | 76542.4496 |  | 7174 | 85395.9881 |  | 7174 | 95273.6009
[13 empty] | Next iteration flow rate |  |  | 1132.5186 | Abs Value of | Flow this | 4673.0058 | Abs Value of | Flow this | 11556.8995 | Abs Value of | Flow this | 22509.8904 | Abs Value of | Flow this | 37020.4821 | Abs Value of | Flow this | 51924.0763 | Abs Value of | Flow this | 65929.7987 | Abs Value of | Flow this | 77307.8741 | Abs Value of | Flow this | 86249.948 | Abs Value of | Flow this | 96226.3369 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 100.0113 |  |  | 91.815 |  |  | 47.2634 |  |  | -101.5279 |  |  | -445.9867 |  |  | -974.5829 |  |  | -1632.7906 |  |  | -2282.6803 |  |  | -2865.8879 |  |  | -3591.8156
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48244 |  |  | 0.4429 |  |  | 0.22799 |  |  | -0.48975 |  |  | -2.1514 |  |  | -4.7012 |  |  | -7.8763 |  |  | -11.0112 |  |  | -13.8245 |  |  | -17.3263
[13 empty] | Delta P at this iteration flow rate |  |  | 50.0113 |  |  | 41.815 |  |  | -2.7366 |  |  | -151.5279 |  |  | -495.9867 |  |  | -1024.5829 |  |  | -1682.7906 |  |  | -2332.6803 |  |  | -2915.8879 |  |  | -3641.8156
[13 empty] | Press drop ratio this iteration |  |  | 0.50006 |  |  | 0.45543 |  |  | -0.057901 |  |  | 1.4925 |  |  | 1.1121 |  |  | 1.0513 |  |  | 1.0306 |  |  | 1.0219 |  |  | 1.0174 |  |  | 1.0139
[13 empty] | Expansion factor | 12 |  | 0.73956 |  |  | 0.76286 |  |  | 1.0306 |  |  | 0.2004 |  |  | 0.38785 |  |  | 0.38831 |  |  | 0.35896 |  |  | 0.30552 |  |  | 0.42859 |  |  | 0.13556
[13 empty] | C Non choked w/ reducers | 5 |  | 4.9256 |  |  | 22.5035 |  |  | #NUM! |  |  | 207.784 |  |  | 47.1201 |  |  | 31.7395 |  |  | 27.1838 |  |  | 28.5541 |  |  | 20.5916 |  |  | 76.284
[13 empty] | C Choked w/ reducers | 5 |  | 4.8275 |  |  | 21.7086 |  |  | 105.3078 |  |  | 96.6896 |  |  | 37.1305 |  |  | 25.0309 |  |  | 20.2875 |  |  | 18.8787 |  |  | 17.3237 |  |  | 24.9664
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 4.9256 |  |  | 22.5035 |  |  | #NUM! |  |  | 96.6896 |  |  | 37.1305 |  |  | 25.0309 |  |  | 20.2875 |  |  | 18.8787 |  |  | 17.3237 |  |  | 24.9664
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.9256 | 1132.5186 |  | 17.5035 | 4673.0058 |  | 7174 | 11556.8995 |  | 7174 | 22509.8904 |  | 7174 | 37020.4821 |  | 7174 | 51924.0763 |  | 7174 | 65929.7987 |  | 7174 | 77307.8741 |  | 7174 | 86249.948 |  | 7174 | 96226.3369
[13 empty] | Next iteration flow rate |  |  | 1155.169 | Abs Value of | Flow this | 4719.7359 | Abs Value of | Flow this | 11672.4685 | Abs Value of | Flow this | 22734.9894 | Abs Value of | Flow this | 37390.687 | Abs Value of | Flow this | 52443.317 | Abs Value of | Flow this | 66589.0967 | Abs Value of | Flow this | 78080.9528 | Abs Value of | Flow this | 87112.4475 | Abs Value of | Flow this | 97188.6003 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.9907 |  |  | 91.64 |  |  | 46.1929 |  |  | -105.5891 |  |  | -456.9716 |  |  | -996.1925 |  |  | -1667.6302 |  |  | -2330.5827 |  |  | -2925.5127 |  |  | -3666.0316
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48234 |  |  | 0.44206 |  |  | 0.22283 |  |  | -0.50934 |  |  | -2.2043 |  |  | -4.8055 |  |  | -8.0444 |  |  | -11.2423 |  |  | -14.1122 |  |  | -17.6843
[13 empty] | Delta P at this iteration flow rate |  |  | 49.9907 |  |  | 41.64 |  |  | -3.8071 |  |  | -155.5891 |  |  | -506.9716 |  |  | -1046.1925 |  |  | -1717.6302 |  |  | -2380.5827 |  |  | -2975.5127 |  |  | -3716.0316
[13 empty] | Press drop ratio this iteration |  |  | 0.49995 |  |  | 0.45439 |  |  | -0.082418 |  |  | 1.4735 |  |  | 1.1094 |  |  | 1.0502 |  |  | 1.03 |  |  | 1.0215 |  |  | 1.0171 |  |  | 1.0136
[13 empty] | Expansion factor | 12 |  | 0.73962 |  |  | 0.7634 |  |  | 1.0436 |  |  | 0.21055 |  |  | 0.38933 |  |  | 0.38895 |  |  | 0.35935 |  |  | 0.30582 |  |  | 0.42879 |  |  | 0.1358
[13 empty] | C Non choked w/ reducers | 5 |  | 5.0253 |  |  | 22.7818 |  |  | #NUM! |  |  | 193.2945 |  |  | 46.3265 |  |  | 31.3259 |  |  | 26.8606 |  |  | 28.2248 |  |  | 20.3677 |  |  | 75.364
[13 empty] | C Choked w/ reducers | 5 |  | 4.9251 |  |  | 21.9676 |  |  | 108.8258 |  |  | 93.9004 |  |  | 36.6003 |  |  | 24.7328 |  |  | 20.0623 |  |  | 18.6756 |  |  | 17.1403 |  |  | 24.7056
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 5.0253 |  |  | 22.7818 |  |  | #NUM! |  |  | 93.9004 |  |  | 36.6003 |  |  | 24.7328 |  |  | 20.0623 |  |  | 18.6756 |  |  | 17.1403 |  |  | 24.7056
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.0253 | 1155.169 |  | 17.7818 | 4719.7359 |  | 7174 | 11672.4685 |  | 7174 | 22734.9894 |  | 7174 | 37390.687 |  | 7174 | 52443.317 |  | 7174 | 66589.0967 |  | 7174 | 78080.9528 |  | 7174 | 87112.4475 |  | 7174 | 97188.6003
[13 empty] | Next iteration flow rate |  |  | 1178.2723 | Abs Value of | Flow this | 4766.9333 | Abs Value of | Flow this | 11789.1932 | Abs Value of | Flow this | 22962.3392 | Abs Value of | Flow this | 37764.5938 | Abs Value of | Flow this | 52967.7502 | Abs Value of | Flow this | 67254.9877 | Abs Value of | Flow this | 78861.7623 | Abs Value of | Flow this | 87983.572 | Abs Value of | Flow this | 98160.4863 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.9692 |  |  | 91.4615 |  |  | 45.1008 |  |  | -109.732 |  |  | -468.1772 |  |  | -1018.2365 |  |  | -1703.1701 |  |  | -2379.4479 |  |  | -2986.336 |  |  | -3741.7393
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48223 |  |  | 0.44119 |  |  | 0.21756 |  |  | -0.52933 |  |  | -2.2584 |  |  | -4.9118 |  |  | -8.2158 |  |  | -11.478 |  |  | -14.4056 |  |  | -18.0495
[13 empty] | Delta P at this iteration flow rate |  |  | 49.9692 |  |  | 41.4615 |  |  | -4.8992 |  |  | -159.732 |  |  | -518.1772 |  |  | -1068.2365 |  |  | -1753.1701 |  |  | -2429.4479 |  |  | -3036.336 |  |  | -3791.7393
[13 empty] | Press drop ratio this iteration |  |  | 0.49985 |  |  | 0.45332 |  |  | -0.10863 |  |  | 1.4557 |  |  | 1.1068 |  |  | 1.0491 |  |  | 1.0294 |  |  | 1.021 |  |  | 1.0167 |  |  | 1.0134
[13 empty] | Expansion factor | 12 |  | 0.73967 |  |  | 0.76396 |  |  | 1.0574 |  |  | 0.22013 |  |  | 0.39077 |  |  | 0.38959 |  |  | 0.35974 |  |  | 0.30612 |  |  | 0.42899 |  |  | 0.13603
[13 empty] | C Non choked w/ reducers | 5 |  | 5.1271 |  |  | 23.0649 |  |  | #NUM! |  |  | 180.7827 |  |  | 45.5552 |  |  | 30.9199 |  |  | 26.5424 |  |  | 27.9004 |  |  | 20.1466 |  |  | 74.4587
[13 empty] | C Choked w/ reducers | 5 |  | 5.0247 |  |  | 22.2306 |  |  | 112.5754 |  |  | 91.2588 |  |  | 36.0815 |  |  | 24.4394 |  |  | 19.8401 |  |  | 18.475 |  |  | 16.9591 |  |  | 24.4478
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 5.1271 |  |  | 23.0649 |  |  | #NUM! |  |  | 91.2588 |  |  | 36.0815 |  |  | 24.4394 |  |  | 19.8401 |  |  | 18.475 |  |  | 16.9591 |  |  | 24.4478
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.1271 | 1178.2723 |  | 18.0649 | 4766.9333 |  | 7174 | 11789.1932 |  | 7174 | 22962.3392 |  | 7174 | 37764.5938 |  | 7174 | 52967.7502 |  | 7174 | 67254.9877 |  | 7174 | 78861.7623 |  | 7174 | 87983.572 |  | 7174 | 98160.4863
[13 empty] | Next iteration flow rate |  |  | 1201.8378 | Abs Value of | Flow this | 4814.6026 | Abs Value of | Flow this | 11907.0851 | Abs Value of | Flow this | 23191.9626 | Abs Value of | Flow this | 38142.2398 | Abs Value of | Flow this | 53497.4277 | Abs Value of | Flow this | 67927.5376 | Abs Value of | Flow this | 79650.3799 | Abs Value of | Flow this | 88863.4077 | Abs Value of | Flow this | 99142.0911 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.9468 |  |  | 91.2793 |  |  | 43.9869 |  |  | -113.9581 |  |  | -479.6081 |  |  | -1040.7235 |  |  | -1739.4243 |  |  | -2429.2953 |  |  | -3048.3819 |  |  | -3818.9688
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48213 |  |  | 0.44032 |  |  | 0.21218 |  |  | -0.54971 |  |  | -2.3135 |  |  | -5.0203 |  |  | -8.3907 |  |  | -11.7185 |  |  | -14.7049 |  |  | -18.422
[13 empty] | Delta P at this iteration flow rate |  |  | 49.9468 |  |  | 41.2793 |  |  | -6.0131 |  |  | -163.9581 |  |  | -529.6081 |  |  | -1090.7235 |  |  | -1789.4243 |  |  | -2479.2953 |  |  | -3098.3819 |  |  | -3868.9688
[13 empty] | Press drop ratio this iteration |  |  | 0.49973 |  |  | 0.45223 |  |  | -0.1367 |  |  | 1.4388 |  |  | 1.1043 |  |  | 1.048 |  |  | 1.0287 |  |  | 1.0206 |  |  | 1.0164 |  |  | 1.0131
[13 empty] | Expansion factor | 12 |  | 0.73973 |  |  | 0.76452 |  |  | 1.0722 |  |  | 0.22918 |  |  | 0.39217 |  |  | 0.3902 |  |  | 0.36012 |  |  | 0.30642 |  |  | 0.42918 |  |  | 0.13626
[13 empty] | C Non choked w/ reducers | 5 |  | 5.231 |  |  | 23.3528 |  |  | #NUM! |  |  | 169.8627 |  |  | 44.8052 |  |  | 30.5215 |  |  | 26.2291 |  |  | 27.5806 |  |  | 19.9284 |  |  | 73.5677
[13 empty] | C Choked w/ reducers | 5 |  | 5.1263 |  |  | 22.4977 |  |  | 116.5807 |  |  | 88.7532 |  |  | 35.5738 |  |  | 24.1504 |  |  | 19.6209 |  |  | 18.2768 |  |  | 16.7801 |  |  | 24.1929
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 5.231 |  |  | 23.3528 |  |  | #NUM! |  |  | 88.7532 |  |  | 35.5738 |  |  | 24.1504 |  |  | 19.6209 |  |  | 18.2768 |  |  | 16.7801 |  |  | 24.1929
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.231 | 1201.8378 |  | 18.3528 | 4814.6026 |  | 7174 | 11907.0851 |  | 7174 | 23191.9626 |  | 7174 | 38142.2398 |  | 7174 | 53497.4277 |  | 7174 | 67927.5376 |  | 7174 | 79650.3799 |  | 7174 | 88863.4077 |  | 7174 | 99142.0911
[13 empty] | Next iteration flow rate |  |  | 1225.8745 | Abs Value of | Flow this | 4862.7486 | Abs Value of | Flow this | 12026.156 | Abs Value of | Flow this | 23423.8823 | Abs Value of | Flow this | 38523.6622 | Abs Value of | Flow this | 54032.402 | Abs Value of | Flow this | 68606.8129 | Abs Value of | Flow this | 80446.8837 | Abs Value of | Flow this | 89752.0418 | Abs Value of | Flow this | 100133.5121 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.9235 |  |  | 91.0935 |  |  | 42.8505 |  |  | -118.2692 |  |  | -491.2687 |  |  | -1063.6626 |  |  | -1776.4072 |  |  | -2480.1446 |  |  | -3111.6749 |  |  | -3897.7506
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48201 |  |  | 0.43942 |  |  | 0.2067 |  |  | -0.57051 |  |  | -2.3698 |  |  | -5.1309 |  |  | -8.5691 |  |  | -11.9638 |  |  | -15.0102 |  |  | -18.8021
[13 empty] | Delta P at this iteration flow rate |  |  | 49.9235 |  |  | 41.0935 |  |  | -7.1495 |  |  | -168.2692 |  |  | -541.2687 |  |  | -1113.6626 |  |  | -1826.4072 |  |  | -2530.1446 |  |  | -3161.6749 |  |  | -3947.7506
[13 empty] | Press drop ratio this iteration |  |  | 0.49962 |  |  | 0.45111 |  |  | -0.16685 |  |  | 1.4228 |  |  | 1.1018 |  |  | 1.047 |  |  | 1.0281 |  |  | 1.0202 |  |  | 1.0161 |  |  | 1.0128
[13 empty] | Expansion factor | 12 |  | 0.73979 |  |  | 0.76511 |  |  | 1.0882 |  |  | 0.23775 |  |  | 0.39353 |  |  | 0.39081 |  |  | 0.3605 |  |  | 0.3067 |  |  | 0.42936 |  |  | 0.13649
[13 empty] | C Non choked w/ reducers | 5 |  | 5.337 |  |  | 23.6457 |  |  | #NUM! |  |  | 160.2431 |  |  | 44.0756 |  |  | 30.1302 |  |  | 25.9207 |  |  | 27.2654 |  |  | 19.7129 |  |  | 72.6907
[13 empty] | C Choked w/ reducers | 5 |  | 5.23 |  |  | 22.769 |  |  | 120.8691 |  |  | 86.3732 |  |  | 35.0767 |  |  | 23.8659 |  |  | 19.4045 |  |  | 18.0811 |  |  | 16.6031 |  |  | 23.941
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 5.337 |  |  | 23.6457 |  |  | #NUM! |  |  | 86.3732 |  |  | 35.0767 |  |  | 23.8659 |  |  | 19.4045 |  |  | 18.0811 |  |  | 16.6031 |  |  | 23.941
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.337 | 1225.8745 |  | 18.6457 | 4862.7486 |  | 7174 | 12026.156 |  | 7174 | 23423.8823 |  | 7174 | 38523.6622 |  | 7174 | 54032.402 |  | 7174 | 68606.8129 |  | 7174 | 80446.8837 |  | 7174 | 89752.0418 |  | 7174 | 100133.5121
[13 empty] | Next iteration flow rate |  |  | 1250.392 | Abs Value of | Flow this | 4911.3761 | Abs Value of | Flow this | 12146.4176 | Abs Value of | Flow this | 23658.1211 | Abs Value of | Flow this | 38908.8988 | Abs Value of | Flow this | 54572.726 | Abs Value of | Flow this | 69292.8811 | Abs Value of | Flow this | 81251.3526 | Abs Value of | Flow this | 90649.5622 | Abs Value of | Flow this | 101134.8472 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.8993 |  |  | 90.904 |  |  | 41.6913 |  |  | -122.6669 |  |  | -503.1637 |  |  | -1087.0627 |  |  | -1814.1335 |  |  | -2532.016 |  |  | -3176.24 |  |  | -3978.1159
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4819 |  |  | 0.4385 |  |  | 0.20111 |  |  | -0.59172 |  |  | -2.4272 |  |  | -5.2438 |  |  | -8.7511 |  |  | -12.214 |  |  | -15.3216 |  |  | -19.1897
[13 empty] | Delta P at this iteration flow rate |  |  | 49.8993 |  |  | 40.904 |  |  | -8.3087 |  |  | -172.6669 |  |  | -553.1637 |  |  | -1137.0627 |  |  | -1864.1335 |  |  | -2582.016 |  |  | -3226.24 |  |  | -4028.1159
[13 empty] | Press drop ratio this iteration |  |  | 0.4995 |  |  | 0.44997 |  |  | -0.19929 |  |  | 1.4076 |  |  | 1.0994 |  |  | 1.046 |  |  | 1.0276 |  |  | 1.0197 |  |  | 1.0157 |  |  | 1.0126
[13 empty] | Expansion factor | 12 |  | 0.73986 |  |  | 0.7657 |  |  | 1.1053 |  |  | 0.24587 |  |  | 0.39486 |  |  | 0.3914 |  |  | 0.36086 |  |  | 0.30698 |  |  | 0.42955 |  |  | 0.13671
[13 empty] | C Non choked w/ reducers | 5 |  | 5.4453 |  |  | 23.9437 |  |  | #NUM! |  |  | 151.6998 |  |  | 43.3656 |  |  | 29.7461 |  |  | 25.6169 |  |  | 26.9547 |  |  | 19.5001 |  |  | 71.8274
[13 empty] | C Choked w/ reducers | 5 |  | 5.3359 |  |  | 23.0446 |  |  | 125.4721 |  |  | 84.1094 |  |  | 34.5899 |  |  | 23.5857 |  |  | 19.191 |  |  | 17.8878 |  |  | 16.4283 |  |  | 23.6919
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 5.4453 |  |  | 23.9437 |  |  | #NUM! |  |  | 84.1094 |  |  | 34.5899 |  |  | 23.5857 |  |  | 19.191 |  |  | 17.8878 |  |  | 16.4283 |  |  | 23.6919
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.4453 | 1250.392 |  | 18.9437 | 4911.3761 |  | 7174 | 12146.4176 |  | 7174 | 23658.1211 |  | 7174 | 38908.8988 |  | 7174 | 54572.726 |  | 7174 | 69292.8811 |  | 7174 | 81251.3526 |  | 7174 | 90649.5622 |  | 7174 | 101134.8472
[13 empty] | Next iteration flow rate |  |  | 1275.3999 | Abs Value of | Flow this | 4960.4899 | Abs Value of | Flow this | 12267.8817 | Abs Value of | Flow this | 23894.7023 | Abs Value of | Flow this | 39297.9878 | Abs Value of | Flow this | 55118.4533 | Abs Value of | Flow this | 69985.8099 | Abs Value of | Flow this | 82063.8661 | Abs Value of | Flow this | 91556.0578 | Abs Value of | Flow this | 102146.1957 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.8741 |  |  | 90.7107 |  |  | 40.5088 |  |  | -127.153 |  |  | -515.2978 |  |  | -1110.9332 |  |  | -1852.6181 |  |  | -2584.9301 |  |  | -3242.103 |  |  | -4060.0965
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48178 |  |  | 0.43757 |  |  | 0.19541 |  |  | -0.61336 |  |  | -2.4857 |  |  | -5.3589 |  |  | -8.9367 |  |  | -12.4692 |  |  | -15.6393 |  |  | -19.5852
[13 empty] | Delta P at this iteration flow rate |  |  | 49.8741 |  |  | 40.7107 |  |  | -9.4912 |  |  | -177.153 |  |  | -565.2978 |  |  | -1160.9332 |  |  | -1902.6181 |  |  | -2634.9301 |  |  | -3292.103 |  |  | -4110.0965
[13 empty] | Press drop ratio this iteration |  |  | 0.49937 |  |  | 0.4488 |  |  | -0.2343 |  |  | 1.3932 |  |  | 1.097 |  |  | 1.045 |  |  | 1.027 |  |  | 1.0193 |  |  | 1.0154 |  |  | 1.0123
[13 empty] | Expansion factor | 12 |  | 0.73992 |  |  | 0.76631 |  |  | 1.1238 |  |  | 0.25357 |  |  | 0.39615 |  |  | 0.39197 |  |  | 0.36122 |  |  | 0.30726 |  |  | 0.42973 |  |  | 0.13693
[13 empty] | C Non choked w/ reducers | 5 |  | 5.5558 |  |  | 24.247 |  |  | #NUM! |  |  | 144.0578 |  |  | 42.6743 |  |  | 29.3687 |  |  | 25.3176 |  |  | 26.6484 |  |  | 19.29 |  |  | 70.9774
[13 empty] | C Choked w/ reducers | 5 |  | 5.444 |  |  | 23.3247 |  |  | 130.4262 |  |  | 81.9534 |  |  | 34.1132 |  |  | 23.3097 |  |  | 18.9803 |  |  | 17.6969 |  |  | 16.2555 |  |  | 23.4456
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 5.5558 |  |  | 24.247 |  |  | #NUM! |  |  | 81.9534 |  |  | 34.1132 |  |  | 23.3097 |  |  | 18.9803 |  |  | 17.6969 |  |  | 16.2555 |  |  | 23.4456
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.5558 | 1275.3999 |  | 19.247 | 4960.4899 |  | 7174 | 12267.8817 |  | 7174 | 23894.7023 |  | 7174 | 39297.9878 |  | 7174 | 55118.4533 |  | 7174 | 69985.8099 |  | 7174 | 82063.8661 |  | 7174 | 91556.0578 |  | 7174 | 102146.1957
[13 empty] | Next iteration flow rate |  |  | 1300.9079 | Abs Value of | Flow this | 5010.0948 | Abs Value of | Flow this | 12390.5606 | Abs Value of | Flow this | 24133.6493 | Abs Value of | Flow this | 39690.9677 | Abs Value of | Flow this | 55669.6378 | Abs Value of | Flow this | 70685.668 | Abs Value of | Flow this | 82884.5048 | Abs Value of | Flow this | 92471.6184 | Abs Value of | Flow this | 103167.6576 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.8479 |  |  | 90.5134 |  |  | 39.3025 |  |  | -131.7293 |  |  | -527.6758 |  |  | -1135.2834 |  |  | -1891.8762 |  |  | -2638.9077 |  |  | -3309.2898 |  |  | -4143.725
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48165 |  |  | 0.43662 |  |  | 0.18959 |  |  | -0.63544 |  |  | -2.5454 |  |  | -5.4764 |  |  | -9.1261 |  |  | -12.7296 |  |  | -15.9634 |  |  | -19.9886
[13 empty] | Delta P at this iteration flow rate |  |  | 49.8479 |  |  | 40.5134 |  |  | -10.6975 |  |  | -181.7293 |  |  | -577.6758 |  |  | -1185.2834 |  |  | -1941.8762 |  |  | -2688.9077 |  |  | -3359.2898 |  |  | -4193.725
[13 empty] | Press drop ratio this iteration |  |  | 0.49924 |  |  | 0.4476 |  |  | -0.27218 |  |  | 1.3796 |  |  | 1.0948 |  |  | 1.044 |  |  | 1.0264 |  |  | 1.0189 |  |  | 1.0151 |  |  | 1.0121
[13 empty] | Expansion factor | 12 |  | 0.73999 |  |  | 0.76694 |  |  | 1.1439 |  |  | 0.26089 |  |  | 0.3974 |  |  | 0.39253 |  |  | 0.36156 |  |  | 0.30753 |  |  | 0.4299 |  |  | 0.13714
[13 empty] | C Non choked w/ reducers | 5 |  | 5.6686 |  |  | 24.5557 |  |  | #NUM! |  |  | 137.178 |  |  | 42.0009 |  |  | 28.9981 |  |  | 25.0229 |  |  | 26.3464 |  |  | 19.0825 |  |  | 70.1404
[13 empty] | C Choked w/ reducers | 5 |  | 5.5544 |  |  | 23.6092 |  |  | 135.7735 |  |  | 79.8974 |  |  | 33.6461 |  |  | 23.0378 |  |  | 18.7723 |  |  | 17.5082 |  |  | 16.0847 |  |  | 23.2022
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 5.6686 |  |  | 24.5557 |  |  | #NUM! |  |  | 79.8974 |  |  | 33.6461 |  |  | 23.0378 |  |  | 18.7723 |  |  | 17.5082 |  |  | 16.0847 |  |  | 23.2022
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.6686 | 1300.9079 |  | 19.5557 | 5010.0948 |  | 7174 | 12390.5606 |  | 7174 | 24133.6493 |  | 7174 | 39690.9677 |  | 7174 | 55669.6378 |  | 7174 | 70685.668 |  | 7174 | 82884.5048 |  | 7174 | 92471.6184 |  | 7174 | 103167.6576
[13 empty] | Next iteration flow rate |  |  | 1326.926 | Abs Value of | Flow this | 5060.1957 | Abs Value of | Flow this | 12514.4662 | Abs Value of | Flow this | 24374.9858 | Abs Value of | Flow this | 40087.8773 | Abs Value of | Flow this | 56226.3342 | Abs Value of | Flow this | 71392.5247 | Abs Value of | Flow this | 83713.3498 | Abs Value of | Flow this | 93396.3346 | Abs Value of | Flow this | 104199.3342 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.8207 |  |  | 90.3123 |  |  | 38.072 |  |  | -136.3975 |  |  | -540.3026 |  |  | -1160.1231 |  |  | -1931.9235 |  |  | -2693.9702 |  |  | -3377.827 |  |  | -4229.0343
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48152 |  |  | 0.43565 |  |  | 0.18365 |  |  | -0.65796 |  |  | -2.6063 |  |  | -5.5962 |  |  | -9.3193 |  |  | -12.9952 |  |  | -16.294 |  |  | -20.4001
[13 empty] | Delta P at this iteration flow rate |  |  | 49.8207 |  |  | 40.3123 |  |  | -11.928 |  |  | -186.3975 |  |  | -590.3026 |  |  | -1210.1231 |  |  | -1981.9235 |  |  | -2743.9702 |  |  | -3427.827 |  |  | -4279.0343
[13 empty] | Press drop ratio this iteration |  |  | 0.4991 |  |  | 0.44637 |  |  | -0.3133 |  |  | 1.3666 |  |  | 1.0925 |  |  | 1.0431 |  |  | 1.0259 |  |  | 1.0186 |  |  | 1.0148 |  |  | 1.0118
[13 empty] | Expansion factor | 12 |  | 0.74006 |  |  | 0.76758 |  |  | 1.1656 |  |  | 0.26785 |  |  | 0.39862 |  |  | 0.39308 |  |  | 0.36191 |  |  | 0.30779 |  |  | 0.43007 |  |  | 0.13734
[13 empty] | C Non choked w/ reducers | 5 |  | 5.7838 |  |  | 24.8699 |  |  | #NUM! |  |  | 130.949 |  |  | 41.3447 |  |  | 28.6339 |  |  | 24.7325 |  |  | 26.0486 |  |  | 18.8775 |  |  | 69.3163
[13 empty] | C Choked w/ reducers | 5 |  | 5.667 |  |  | 23.8985 |  |  | 141.5635 |  |  | 77.9345 |  |  | 33.1884 |  |  | 22.77 |  |  | 18.567 |  |  | 17.3219 |  |  | 15.916 |  |  | 22.9615
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 5.7838 |  |  | 24.8699 |  |  | #NUM! |  |  | 77.9345 |  |  | 33.1884 |  |  | 22.77 |  |  | 18.567 |  |  | 17.3219 |  |  | 15.916 |  |  | 22.9615
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.7838 | 1326.926 |  | 19.8699 | 5060.1957 |  | 7174 | 12514.4662 |  | 7174 | 24374.9858 |  | 7174 | 40087.8773 |  | 7174 | 56226.3342 |  | 7174 | 71392.5247 |  | 7174 | 83713.3498 |  | 7174 | 93396.3346 |  | 7174 | 104199.3342
[13 empty] | Next iteration flow rate |  |  | 1353.4645 | Abs Value of | Flow this | 5110.7977 | Abs Value of | Flow this | 12639.6108 | Abs Value of | Flow this | 24618.7357 | Abs Value of | Flow this | 40488.7561 | Abs Value of | Flow this | 56788.5975 | Abs Value of | Flow this | 72106.4499 | Abs Value of | Flow this | 84550.4833 | Abs Value of | Flow this | 94330.2979 | Abs Value of | Flow this | 105241.3275 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.7923 |  |  | 90.107 |  |  | 36.8167 |  |  | -141.1596 |  |  | -553.1832 |  |  | -1185.4621 |  |  | -1972.7756 |  |  | -2750.1395 |  |  | -3447.7418 |  |  | -4316.0584
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48138 |  |  | 0.43466 |  |  | 0.1776 |  |  | -0.68093 |  |  | -2.6685 |  |  | -5.7185 |  |  | -9.5163 |  |  | -13.2662 |  |  | -16.6313 |  |  | -20.8199
[13 empty] | Delta P at this iteration flow rate |  |  | 49.7923 |  |  | 40.107 |  |  | -13.1833 |  |  | -191.1596 |  |  | -603.1832 |  |  | -1235.4621 |  |  | -2022.7756 |  |  | -2800.1395 |  |  | -3497.7418 |  |  | -4366.0584
[13 empty] | Press drop ratio this iteration |  |  | 0.49896 |  |  | 0.4451 |  |  | -0.35808 |  |  | 1.3542 |  |  | 1.0904 |  |  | 1.0422 |  |  | 1.0253 |  |  | 1.0182 |  |  | 1.0145 |  |  | 1.0116
[13 empty] | Expansion factor | 12 |  | 0.74014 |  |  | 0.76824 |  |  | 1.1892 |  |  | 0.27448 |  |  | 0.3998 |  |  | 0.39362 |  |  | 0.36224 |  |  | 0.30805 |  |  | 0.43024 |  |  | 0.13755
[13 empty] | C Non choked w/ reducers | 5 |  | 5.9014 |  |  | 25.1899 |  |  | #NUM! |  |  | 125.28 |  |  | 40.705 |  |  | 28.276 |  |  | 24.4465 |  |  | 25.755 |  |  | 18.6751 |  |  | 68.5045
[13 empty] | C Choked w/ reducers | 5 |  | 5.782 |  |  | 24.1924 |  |  | 147.854 |  |  | 76.0584 |  |  | 32.7398 |  |  | 22.5061 |  |  | 18.3643 |  |  | 17.1378 |  |  | 15.7491 |  |  | 22.7235
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 5.9014 |  |  | 25.1899 |  |  | #NUM! |  |  | 76.0584 |  |  | 32.7398 |  |  | 22.5061 |  |  | 18.3643 |  |  | 17.1378 |  |  | 15.7491 |  |  | 22.7235
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.9014 | 1353.4645 |  | 20.1899 | 5110.7977 |  | 7174 | 12639.6108 |  | 7174 | 24618.7357 |  | 7174 | 40488.7561 |  | 7174 | 56788.5975 |  | 7174 | 72106.4499 |  | 7174 | 84550.4833 |  | 7174 | 94330.2979 |  | 7174 | 105241.3275
[13 empty] | Next iteration flow rate |  |  | 1380.5338 | Abs Value of | Flow this | 5161.9056 | Abs Value of | Flow this | 12766.0069 | Abs Value of | Flow this | 24864.923 | Abs Value of | Flow this | 40893.6437 | Abs Value of | Flow this | 57356.4835 | Abs Value of | Flow this | 72827.5144 | Abs Value of | Flow this | 85395.9881 | Abs Value of | Flow this | 95273.6009 | Abs Value of | Flow this | 106293.7408 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.7628 |  |  | 89.8977 |  |  | 35.5362 |  |  | -146.0175 |  |  | -566.3227 |  |  | -1211.3104 |  |  | -2014.4489 |  |  | -2807.4379 |  |  | -3519.0619 |  |  | -4404.8317
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48124 |  |  | 0.43365 |  |  | 0.17142 |  |  | -0.70436 |  |  | -2.7318 |  |  | -5.8431 |  |  | -9.7173 |  |  | -13.5426 |  |  | -16.9753 |  |  | -21.2481
[13 empty] | Delta P at this iteration flow rate |  |  | 49.7628 |  |  | 39.8977 |  |  | -14.4638 |  |  | -196.0175 |  |  | -616.3227 |  |  | -1261.3104 |  |  | -2064.4489 |  |  | -2857.4379 |  |  | -3569.0619 |  |  | -4454.8317
[13 empty] | Press drop ratio this iteration |  |  | 0.49881 |  |  | 0.44381 |  |  | -0.40702 |  |  | 1.3424 |  |  | 1.0883 |  |  | 1.0413 |  |  | 1.0248 |  |  | 1.0178 |  |  | 1.0142 |  |  | 1.0114
[13 empty] | Expansion factor | 12 |  | 0.74021 |  |  | 0.76891 |  |  | 1.2151 |  |  | 0.28079 |  |  | 0.40096 |  |  | 0.39414 |  |  | 0.36256 |  |  | 0.3083 |  |  | 0.43041 |  |  | 0.13775
[13 empty] | C Non choked w/ reducers | 5 |  | 6.0215 |  |  | 25.5158 |  |  | #NUM! |  |  | 120.0965 |  |  | 40.0811 |  |  | 27.9243 |  |  | 24.1646 |  |  | 25.4655 |  |  | 18.4752 |  |  | 67.705
[13 empty] | C Choked w/ reducers | 5 |  | 5.8994 |  |  | 24.4912 |  |  | 154.7135 |  |  | 74.2633 |  |  | 32.3 |  |  | 22.2461 |  |  | 18.1642 |  |  | 16.9559 |  |  | 15.5843 |  |  | 22.4882
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 6.0215 |  |  | 25.5158 |  |  | #NUM! |  |  | 74.2633 |  |  | 32.3 |  |  | 22.2461 |  |  | 18.1642 |  |  | 16.9559 |  |  | 15.5843 |  |  | 22.4882
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0215 | 1380.5338 |  | 20.5158 | 5161.9056 |  | 7174 | 12766.0069 |  | 7174 | 24864.923 |  | 7174 | 40893.6437 |  | 7174 | 57356.4835 |  | 7174 | 72827.5144 |  | 7174 | 85395.9881 |  | 7174 | 95273.6009 |  | 7174 | 106293.7408
[13 empty] | Next iteration flow rate |  |  | 1408.1445 | Abs Value of | Flow this | 5213.5247 | Abs Value of | Flow this | 12893.667 | Abs Value of | Flow this | 25113.5723 | Abs Value of | Flow this | 41302.5801 | Abs Value of | Flow this | 57930.0483 | Abs Value of | Flow this | 73555.7895 | Abs Value of | Flow this | 86249.948 | Abs Value of | Flow this | 96226.3369 | Abs Value of | Flow this | 107356.6782 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.7321 |  |  | 89.6841 |  |  | 34.23 |  |  | -150.9729 |  |  | -579.7263 |  |  | -1237.6783 |  |  | -2056.9599 |  |  | -2865.8879 |  |  | -3591.8156 |  |  | -4495.3894
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48109 |  |  | 0.43262 |  |  | 0.16512 |  |  | -0.72827 |  |  | -2.7965 |  |  | -5.9703 |  |  | -9.9224 |  |  | -13.8245 |  |  | -17.3263 |  |  | -21.685
[13 empty] | Delta P at this iteration flow rate |  |  | 49.7321 |  |  | 39.6841 |  |  | -15.77 |  |  | -200.9729 |  |  | -629.7263 |  |  | -1287.6783 |  |  | -2106.9599 |  |  | -2915.8879 |  |  | -3641.8156 |  |  | -4545.3894
[13 empty] | Press drop ratio this iteration |  |  | 0.49866 |  |  | 0.44249 |  |  | -0.46071 |  |  | 1.3312 |  |  | 1.0862 |  |  | 1.0404 |  |  | 1.0243 |  |  | 1.0174 |  |  | 1.0139 |  |  | 1.0111
[13 empty] | Expansion factor | 12 |  | 0.74029 |  |  | 0.7696 |  |  | 1.2435 |  |  | 0.28681 |  |  | 0.40208 |  |  | 0.39465 |  |  | 0.36288 |  |  | 0.30855 |  |  | 0.43057 |  |  | 0.13794
[13 empty] | C Non choked w/ reducers | 5 |  | 6.1441 |  |  | 25.8478 |  |  | #NUM! |  |  | 115.3368 |  |  | 39.4725 |  |  | 27.5785 |  |  | 23.8868 |  |  | 25.1799 |  |  | 18.2777 |  |  | 66.9174
[13 empty] | C Choked w/ reducers | 5 |  | 6.0192 |  |  | 24.7951 |  |  | 162.2236 |  |  | 72.544 |  |  | 31.8687 |  |  | 21.9899 |  |  | 17.9667 |  |  | 16.7762 |  |  | 15.4213 |  |  | 22.2555
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 6.1441 |  |  | 25.8478 |  |  | #NUM! |  |  | 72.544 |  |  | 31.8687 |  |  | 21.9899 |  |  | 17.9667 |  |  | 16.7762 |  |  | 15.4213 |  |  | 22.2555
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1441 | 1408.1445 |  | 20.8478 | 5213.5247 |  | 7174 | 12893.667 |  | 7174 | 25113.5723 |  | 7174 | 41302.5801 |  | 7174 | 57930.0483 |  | 7174 | 73555.7895 |  | 7174 | 86249.948 |  | 7174 | 96226.3369 |  | 7174 | 107356.6782
[13 empty] | Next iteration flow rate |  |  | 1436.3074 | Abs Value of | Flow this | 5265.6599 | Abs Value of | Flow this | 13022.6037 | Abs Value of | Flow this | 25364.708 | Abs Value of | Flow this | 41715.6059 | Abs Value of | Flow this | 58509.3488 | Abs Value of | Flow this | 74291.3474 | Abs Value of | Flow this | 87112.4475 | Abs Value of | Flow this | 97188.6003 | Abs Value of | Flow this | 108430.245 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.7001 |  |  | 89.4662 |  |  | 32.8975 |  |  | -156.028 |  |  | -593.3993 |  |  | -1264.5761 |  |  | -2100.3253 |  |  | -2925.5127 |  |  | -3666.0316 |  |  | -4587.7672
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48094 |  |  | 0.43157 |  |  | 0.15869 |  |  | -0.75265 |  |  | -2.8625 |  |  | -6.1001 |  |  | -10.1316 |  |  | -14.1122 |  |  | -17.6843 |  |  | -22.1306
[13 empty] | Delta P at this iteration flow rate |  |  | 49.7001 |  |  | 39.4662 |  |  | -17.1025 |  |  | -206.028 |  |  | -643.3993 |  |  | -1314.5761 |  |  | -2150.3253 |  |  | -2975.5127 |  |  | -3716.0316 |  |  | -4637.7672
[13 empty] | Press drop ratio this iteration |  |  | 0.4985 |  |  | 0.44113 |  |  | -0.51987 |  |  | 1.3205 |  |  | 1.0843 |  |  | 1.0395 |  |  | 1.0238 |  |  | 1.0171 |  |  | 1.0136 |  |  | 1.0109
[13 empty] | Expansion factor | 12 |  | 0.74038 |  |  | 0.77031 |  |  | 1.2748 |  |  | 0.29256 |  |  | 0.40318 |  |  | 0.39515 |  |  | 0.3632 |  |  | 0.30879 |  |  | 0.43073 |  |  | 0.13813
[13 empty] | C Non choked w/ reducers | 5 |  | 6.2693 |  |  | 26.186 |  |  | #NUM! |  |  | 110.9494 |  |  | 38.8785 |  |  | 27.2386 |  |  | 23.613 |  |  | 24.8982 |  |  | 18.0826 |  |  | 66.1415
[13 empty] | C Choked w/ reducers | 5 |  | 6.1416 |  |  | 25.104 |  |  | 170.4823 |  |  | 70.8956 |  |  | 31.4457 |  |  | 21.7374 |  |  | 17.7717 |  |  | 16.5986 |  |  | 15.2602 |  |  | 22.0255
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 6.2693 |  |  | 26.186 |  |  | #NUM! |  |  | 70.8956 |  |  | 31.4457 |  |  | 21.7374 |  |  | 17.7717 |  |  | 16.5986 |  |  | 15.2602 |  |  | 22.0255
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2693 | 1436.3074 |  | 21.186 | 5265.6599 |  | 7174 | 13022.6037 |  | 7174 | 25364.708 |  | 7174 | 41715.6059 |  | 7174 | 58509.3488 |  | 7174 | 74291.3474 |  | 7174 | 87112.4475 |  | 7174 | 97188.6003 |  | 7174 | 108430.245
[13 empty] | Next iteration flow rate |  |  | 1465.0335 | Abs Value of | Flow this | 5318.3165 | Abs Value of | Flow this | 13152.8297 | Abs Value of | Flow this | 25618.3551 | Abs Value of | Flow this | 42132.762 | Abs Value of | Flow this | 59094.4423 | Abs Value of | Flow this | 75034.2609 | Abs Value of | Flow this | 87983.572 | Abs Value of | Flow this | 98160.4863 | Abs Value of | Flow this | 109514.5474 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.6669 |  |  | 89.244 |  |  | 31.5382 |  |  | -161.1847 |  |  | -607.3471 |  |  | -1292.0146 |  |  | -2144.5623 |  |  | -2986.336 |  |  | -3741.7393 |  |  | -4682.0018
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48078 |  |  | 0.4305 |  |  | 0.15213 |  |  | -0.77753 |  |  | -2.9297 |  |  | -6.2324 |  |  | -10.345 |  |  | -14.4056 |  |  | -18.0495 |  |  | -22.5851
[13 empty] | Delta P at this iteration flow rate |  |  | 49.6669 |  |  | 39.244 |  |  | -18.4618 |  |  | -211.1847 |  |  | -657.3471 |  |  | -1342.0146 |  |  | -2194.5623 |  |  | -3036.336 |  |  | -3791.7393 |  |  | -4732.0018
[13 empty] | Press drop ratio this iteration |  |  | 0.49833 |  |  | 0.43974 |  |  | -0.58538 |  |  | 1.3102 |  |  | 1.0823 |  |  | 1.0387 |  |  | 1.0233 |  |  | 1.0167 |  |  | 1.0134 |  |  | 1.0107
[13 empty] | Expansion factor | 12 |  | 0.74046 |  |  | 0.77103 |  |  | 1.3094 |  |  | 0.29805 |  |  | 0.40424 |  |  | 0.39564 |  |  | 0.3635 |  |  | 0.30903 |  |  | 0.43088 |  |  | 0.13832
[13 empty] | C Non choked w/ reducers | 5 |  | 6.3971 |  |  | 26.5307 |  |  | #NUM! |  |  | 106.8906 |  |  | 38.2986 |  |  | 26.9043 |  |  | 23.3432 |  |  | 24.6204 |  |  | 17.8899 |  |  | 65.3769
[13 empty] | C Choked w/ reducers | 5 |  | 6.2665 |  |  | 25.4182 |  |  | 179.6082 |  |  | 69.3138 |  |  | 31.0308 |  |  | 21.4885 |  |  | 17.5792 |  |  | 16.4231 |  |  | 15.1009 |  |  | 21.798
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 6.3971 |  |  | 26.5307 |  |  | #NUM! |  |  | 69.3138 |  |  | 31.0308 |  |  | 21.4885 |  |  | 17.5792 |  |  | 16.4231 |  |  | 15.1009 |  |  | 21.798
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3971 | 1465.0335 |  | 21.5307 | 5318.3165 |  | 7174 | 13152.8297 |  | 7174 | 25618.3551 |  | 7174 | 42132.762 |  | 7174 | 59094.4423 |  | 7174 | 75034.2609 |  | 7174 | 87983.572 |  | 7174 | 98160.4863 |  | 7174 | 109514.5474
[13 empty] | Next iteration flow rate |  |  | 1494.3342 | Abs Value of | Flow this | 5371.4997 | Abs Value of | Flow this | 13284.358 | Abs Value of | Flow this | 25874.5386 | Abs Value of | Flow this | 42554.0896 | Abs Value of | Flow this | 59685.3867 | Abs Value of | Flow this | 75784.6035 | Abs Value of | Flow this | 88863.4077 | Abs Value of | Flow this | 99142.0911 | Abs Value of | Flow this | 110609.6929 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.6323 |  |  | 89.0173 |  |  | 30.1516 |  |  | -166.445 |  |  | -621.5753 |  |  | -1320.0046 |  |  | -2189.6885 |  |  | -3048.3819 |  |  | -3818.9688 |  |  | -4778.1306
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48061 |  |  | 0.4294 |  |  | 0.14545 |  |  | -0.8029 |  |  | -2.9984 |  |  | -6.3675 |  |  | -10.5627 |  |  | -14.7049 |  |  | -18.422 |  |  | -23.0489
[13 empty] | Delta P at this iteration flow rate |  |  | 49.6323 |  |  | 39.0173 |  |  | -19.8484 |  |  | -216.445 |  |  | -671.5753 |  |  | -1370.0046 |  |  | -2239.6885 |  |  | -3098.3819 |  |  | -3868.9688 |  |  | -4828.1306
[13 empty] | Press drop ratio this iteration |  |  | 0.49815 |  |  | 0.43831 |  |  | -0.65829 |  |  | 1.3004 |  |  | 1.0804 |  |  | 1.0379 |  |  | 1.0228 |  |  | 1.0164 |  |  | 1.0131 |  |  | 1.0105
[13 empty] | Expansion factor | 12 |  | 0.74056 |  |  | 0.77177 |  |  | 1.3479 |  |  | 0.3033 |  |  | 0.40528 |  |  | 0.39612 |  |  | 0.3638 |  |  | 0.30926 |  |  | 0.43104 |  |  | 0.1385
[13 empty] | C Non choked w/ reducers | 5 |  | 6.5277 |  |  | 26.8821 |  |  | #NUM! |  |  | 103.1236 |  |  | 37.7323 |  |  | 26.5756 |  |  | 23.0772 |  |  | 24.3463 |  |  | 17.6995 |  |  | 64.6236
[13 empty] | C Choked w/ reducers | 5 |  | 6.394 |  |  | 25.7377 |  |  | 189.7466 |  |  | 67.7944 |  |  | 30.6237 |  |  | 21.2432 |  |  | 17.3891 |  |  | 16.2498 |  |  | 14.9435 |  |  | 21.573
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 6.5277 |  |  | 26.8821 |  |  | #NUM! |  |  | 67.7944 |  |  | 30.6237 |  |  | 21.2432 |  |  | 17.3891 |  |  | 16.2498 |  |  | 14.9435 |  |  | 21.573
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5277 | 1494.3342 |  | 21.8821 | 5371.4997 |  | 7174 | 13284.358 |  | 7174 | 25874.5386 |  | 7174 | 42554.0896 |  | 7174 | 59685.3867 |  | 7174 | 75784.6035 |  | 7174 | 88863.4077 |  | 7174 | 99142.0911 |  | 7174 | 110609.6929
[13 empty] | Next iteration flow rate |  |  | 1524.2209 | Abs Value of | Flow this | 5425.2147 | Abs Value of | Flow this | 13417.2016 | Abs Value of | Flow this | 26133.284 | Abs Value of | Flow this | 42979.6305 | Abs Value of | Flow this | 60282.2406 | Abs Value of | Flow this | 76542.4496 | Abs Value of | Flow this | 89752.0418 | Abs Value of | Flow this | 100133.5121 | Abs Value of | Flow this | 111715.7898 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.5964 |  |  | 88.786 |  |  | 28.7372 |  |  | -171.811 |  |  | -636.0895 |  |  | -1348.5572 |  |  | -2235.7218 |  |  | -3111.6749 |  |  | -3897.7506 |  |  | -4876.1915
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48044 |  |  | 0.42829 |  |  | 0.13862 |  |  | -0.82879 |  |  | -3.0684 |  |  | -6.5052 |  |  | -10.7847 |  |  | -15.0102 |  |  | -18.8021 |  |  | -23.5219
[13 empty] | Delta P at this iteration flow rate |  |  | 49.5964 |  |  | 38.786 |  |  | -21.2628 |  |  | -221.811 |  |  | -686.0895 |  |  | -1398.5572 |  |  | -2285.7218 |  |  | -3161.6749 |  |  | -3947.7506 |  |  | -4926.1915
[13 empty] | Press drop ratio this iteration |  |  | 0.49797 |  |  | 0.43685 |  |  | -0.73991 |  |  | 1.291 |  |  | 1.0786 |  |  | 1.0371 |  |  | 1.0224 |  |  | 1.0161 |  |  | 1.0128 |  |  | 1.0103
[13 empty] | Expansion factor | 12 |  | 0.74065 |  |  | 0.77253 |  |  | 1.391 |  |  | 0.30833 |  |  | 0.40629 |  |  | 0.39659 |  |  | 0.36409 |  |  | 0.30948 |  |  | 0.43118 |  |  | 0.13868
[13 empty] | C Non choked w/ reducers | 5 |  | 6.661 |  |  | 27.2402 |  |  | #NUM! |  |  | 99.6169 |  |  | 37.179 |  |  | 26.2523 |  |  | 22.8149 |  |  | 24.0759 |  |  | 17.5115 |  |  | 63.8811
[13 empty] | C Choked w/ reducers | 5 |  | 6.5243 |  |  | 26.0628 |  |  | 201.0769 |  |  | 66.3338 |  |  | 30.2242 |  |  | 21.0013 |  |  | 17.2014 |  |  | 16.0784 |  |  | 14.7879 |  |  | 21.3506
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 6.661 |  |  | 27.2402 |  |  | #NUM! |  |  | 66.3338 |  |  | 30.2242 |  |  | 21.0013 |  |  | 17.2014 |  |  | 16.0784 |  |  | 14.7879 |  |  | 21.3506
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.661 | 1524.2209 |  | 22.2402 | 5425.2147 |  | 7174 | 13417.2016 |  | 7174 | 26133.284 |  | 7174 | 42979.6305 |  | 7174 | 60282.2406 |  | 7174 | 76542.4496 |  | 7174 | 89752.0418 |  | 7174 | 100133.5121 |  | 7174 | 111715.7898
[13 empty] | Next iteration flow rate |  |  | 1554.7053 | Abs Value of | Flow this | 5479.4669 | Abs Value of | Flow this | 13551.3736 | Abs Value of | Flow this | 26394.6168 | Abs Value of | Flow this | 43409.4268 | Abs Value of | Flow this | 60885.063 | Abs Value of | Flow this | 77307.8741 | Abs Value of | Flow this | 90649.5622 | Abs Value of | Flow this | 101134.8472 | Abs Value of | Flow this | 112832.9477 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.5589 |  |  | 88.5501 |  |  | 27.2943 |  |  | -177.2849 |  |  | -650.8954 |  |  | -1377.6837 |  |  | -2282.6803 |  |  | -3176.24 |  |  | -3978.1159 |  |  | -4976.2235
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48025 |  |  | 0.42715 |  |  | 0.13166 |  |  | -0.85519 |  |  | -3.1398 |  |  | -6.6457 |  |  | -11.0112 |  |  | -15.3216 |  |  | -19.1897 |  |  | -24.0044
[13 empty] | Delta P at this iteration flow rate |  |  | 49.5589 |  |  | 38.5501 |  |  | -22.7057 |  |  | -227.2849 |  |  | -700.8954 |  |  | -1427.6837 |  |  | -2332.6803 |  |  | -3226.24 |  |  | -4028.1159 |  |  | -5026.2235
[13 empty] | Press drop ratio this iteration |  |  | 0.49778 |  |  | 0.43535 |  |  | -0.83189 |  |  | 1.282 |  |  | 1.0768 |  |  | 1.0363 |  |  | 1.0219 |  |  | 1.0157 |  |  | 1.0126 |  |  | 1.01
[13 empty] | Expansion factor | 12 |  | 0.74075 |  |  | 0.77332 |  |  | 1.4397 |  |  | 0.31315 |  |  | 0.40727 |  |  | 0.39704 |  |  | 0.36438 |  |  | 0.30971 |  |  | 0.43133 |  |  | 0.13886
[13 empty] | C Non choked w/ reducers | 5 |  | 6.7972 |  |  | 27.6055 |  |  | #NUM! |  |  | 96.3434 |  |  | 36.6383 |  |  | 25.9343 |  |  | 22.5564 |  |  | 23.8091 |  |  | 17.3256 |  |  | 63.1494
[13 empty] | C Choked w/ reducers | 5 |  | 6.6573 |  |  | 26.3936 |  |  | 213.8237 |  |  | 64.9285 |  |  | 29.832 |  |  | 20.7629 |  |  | 17.016 |  |  | 15.9091 |  |  | 14.634 |  |  | 21.1306
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 6.7972 |  |  | 27.6055 |  |  | #NUM! |  |  | 64.9285 |  |  | 29.832 |  |  | 20.7629 |  |  | 17.016 |  |  | 15.9091 |  |  | 14.634 |  |  | 21.1306
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.7972 | 1554.7053 |  | 22.6055 | 5479.4669 |  | 7174 | 13551.3736 |  | 7174 | 26394.6168 |  | 7174 | 43409.4268 |  | 7174 | 60885.063 |  | 7174 | 77307.8741 |  | 7174 | 90649.5622 |  | 7174 | 101134.8472 |  | 7174 | 112832.9477
[13 empty] | Next iteration flow rate |  |  | 1585.7994 | Abs Value of | Flow this | 5534.2615 | Abs Value of | Flow this | 13686.8873 | Abs Value of | Flow this | 26658.563 | Abs Value of | Flow this | 43843.521 | Abs Value of | Flow this | 61493.9136 | Abs Value of | Flow this | 78080.9528 | Abs Value of | Flow this | 91556.0578 | Abs Value of | Flow this | 102146.1957 | Abs Value of | Flow this | 113961.2772 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.52 |  |  | 88.3095 |  |  | 25.8224 |  |  | -182.8689 |  |  | -665.9989 |  |  | -1407.3957 |  |  | -2330.5827 |  |  | -3242.103 |  |  | -4060.0965 |  |  | -5078.2661
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.48007 |  |  | 0.42599 |  |  | 0.12456 |  |  | -0.88213 |  |  | -3.2127 |  |  | -6.789 |  |  | -11.2423 |  |  | -15.6393 |  |  | -19.5852 |  |  | -24.4967
[13 empty] | Delta P at this iteration flow rate |  |  | 49.52 |  |  | 38.3095 |  |  | -24.1776 |  |  | -232.8689 |  |  | -715.9989 |  |  | -1457.3957 |  |  | -2380.5827 |  |  | -3292.103 |  |  | -4110.0965 |  |  | -5128.2661
[13 empty] | Press drop ratio this iteration |  |  | 0.49759 |  |  | 0.43381 |  |  | -0.9363 |  |  | 1.2734 |  |  | 1.0751 |  |  | 1.0355 |  |  | 1.0215 |  |  | 1.0154 |  |  | 1.0123 |  |  | 1.0098
[13 empty] | Expansion factor | 12 |  | 0.74085 |  |  | 0.77412 |  |  | 1.4948 |  |  | 0.31776 |  |  | 0.40823 |  |  | 0.39749 |  |  | 0.36466 |  |  | 0.30992 |  |  | 0.43147 |  |  | 0.13903
[13 empty] | C Non choked w/ reducers | 5 |  | 6.9362 |  |  | 27.9781 |  |  | #NUM! |  |  | 93.2796 |  |  | 36.1098 |  |  | 25.6213 |  |  | 22.3015 |  |  | 23.5459 |  |  | 17.1421 |  |  | 62.4281
[13 empty] | C Choked w/ reducers | 5 |  | 6.7931 |  |  | 26.7302 |  |  | 228.2719 |  |  | 63.5754 |  |  | 29.4471 |  |  | 20.5278 |  |  | 16.8329 |  |  | 15.7418 |  |  | 14.4819 |  |  | 20.9131
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 6.9362 |  |  | 27.9781 |  |  | #NUM! |  |  | 63.5754 |  |  | 29.4471 |  |  | 20.5278 |  |  | 16.8329 |  |  | 15.7418 |  |  | 14.4819 |  |  | 20.9131
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.9362 | 1585.7994 |  | 22.9781 | 5534.2615 |  | 7174 | 13686.8873 |  | 7174 | 26658.563 |  | 7174 | 43843.521 |  | 7174 | 61493.9136 |  | 7174 | 78080.9528 |  | 7174 | 91556.0578 |  | 7174 | 102146.1957 |  | 7174 | 113961.2772
[13 empty] | Next iteration flow rate |  |  | 1617.5154 | Abs Value of | Flow this | 5589.6041 | Abs Value of | Flow this | 13823.7562 | Abs Value of | Flow this | 26925.1486 | Abs Value of | Flow this | 44281.9563 | Abs Value of | Flow this | 62108.8528 | Abs Value of | Flow this | 78861.7623 | Abs Value of | Flow this | 92471.6184 | Abs Value of | Flow this | 103167.6576 | Abs Value of | Flow this | 115100.89 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.4795 |  |  | 88.064 |  |  | 24.3209 |  |  | -188.565 |  |  | -681.406 |  |  | -1437.7048 |  |  | -2379.4479 |  |  | -3309.2898 |  |  | -4143.725 |  |  | -5182.3597
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47987 |  |  | 0.42481 |  |  | 0.11732 |  |  | -0.9096 |  |  | -3.287 |  |  | -6.9352 |  |  | -11.478 |  |  | -15.9634 |  |  | -19.9886 |  |  | -24.9988
[13 empty] | Delta P at this iteration flow rate |  |  | 49.4795 |  |  | 38.064 |  |  | -25.6791 |  |  | -238.565 |  |  | -731.406 |  |  | -1487.7048 |  |  | -2429.4479 |  |  | -3359.2898 |  |  | -4193.725 |  |  | -5232.3597
[13 empty] | Press drop ratio this iteration |  |  | 0.49738 |  |  | 0.43223 |  |  | -1.0558 |  |  | 1.2652 |  |  | 1.0734 |  |  | 1.0348 |  |  | 1.021 |  |  | 1.0151 |  |  | 1.0121 |  |  | 1.0096
[13 empty] | Expansion factor | 12 |  | 0.74096 |  |  | 0.77494 |  |  | 1.558 |  |  | 0.32218 |  |  | 0.40917 |  |  | 0.39792 |  |  | 0.36493 |  |  | 0.31014 |  |  | 0.43161 |  |  | 0.1392
[13 empty] | C Non choked w/ reducers | 5 |  | 7.0783 |  |  | 28.3582 |  |  | #NUM! |  |  | 90.4053 |  |  | 35.593 |  |  | 25.3134 |  |  | 22.0501 |  |  | 23.2861 |  |  | 16.9607 |  |  | 61.7171
[13 empty] | C Choked w/ reducers | 5 |  | 6.9317 |  |  | 27.0727 |  |  | 244.7882 |  |  | 62.2714 |  |  | 29.0691 |  |  | 20.296 |  |  | 16.6521 |  |  | 15.5764 |  |  | 14.3315 |  |  | 20.6979
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 7.0783 |  |  | 28.3582 |  |  | #NUM! |  |  | 62.2714 |  |  | 29.0691 |  |  | 20.296 |  |  | 16.6521 |  |  | 15.5764 |  |  | 14.3315 |  |  | 20.6979
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.0783 | 1617.5154 |  | 23.3582 | 5589.6041 |  | 7174 | 13823.7562 |  | 7174 | 26925.1486 |  | 7174 | 44281.9563 |  | 7174 | 62108.8528 |  | 7174 | 78861.7623 |  | 7174 | 92471.6184 |  | 7174 | 103167.6576 |  | 7174 | 115100.89
[13 empty] | Next iteration flow rate |  |  | 1649.8657 | Abs Value of | Flow this | 5645.5002 | Abs Value of | Flow this | 13961.9938 | Abs Value of | Flow this | 27194.4001 | Abs Value of | Flow this | 44724.7758 | Abs Value of | Flow this | 62729.9413 | Abs Value of | Flow this | 79650.3799 | Abs Value of | Flow this | 93396.3346 | Abs Value of | Flow this | 104199.3342 | Abs Value of | Flow this | 116251.8989 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.4373 |  |  | 87.8136 |  |  | 22.7892 |  |  | -194.3757 |  |  | -697.1227 |  |  | -1468.6232 |  |  | -2429.2953 |  |  | -3377.827 |  |  | -4229.0343 |  |  | -5288.5456
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47967 |  |  | 0.4236 |  |  | 0.10993 |  |  | -0.93763 |  |  | -3.3628 |  |  | -7.0844 |  |  | -11.7185 |  |  | -16.294 |  |  | -20.4001 |  |  | -25.511
[13 empty] | Delta P at this iteration flow rate |  |  | 49.4373 |  |  | 37.8136 |  |  | -27.2108 |  |  | -244.3757 |  |  | -747.1227 |  |  | -1518.6232 |  |  | -2479.2953 |  |  | -3427.827 |  |  | -4279.0343 |  |  | -5338.5456
[13 empty] | Press drop ratio this iteration |  |  | 0.49717 |  |  | 0.43061 |  |  | -1.194 |  |  | 1.2572 |  |  | 1.0717 |  |  | 1.034 |  |  | 1.0206 |  |  | 1.0148 |  |  | 1.0118 |  |  | 1.0095
[13 empty] | Expansion factor | 12 |  | 0.74107 |  |  | 0.77578 |  |  | 1.631 |  |  | 0.32643 |  |  | 0.41008 |  |  | 0.39835 |  |  | 0.3652 |  |  | 0.31035 |  |  | 0.43175 |  |  | 0.13936
[13 empty] | C Non choked w/ reducers | 5 |  | 7.2234 |  |  | 28.7462 |  |  | #NUM! |  |  | 87.7025 |  |  | 35.0874 |  |  | 25.0104 |  |  | 21.8022 |  |  | 23.0298 |  |  | 16.7814 |  |  | 61.0162
[13 empty] | C Choked w/ reducers | 5 |  | 7.0734 |  |  | 27.4214 |  |  | 263.8528 |  |  | 61.014 |  |  | 28.6978 |  |  | 20.0674 |  |  | 16.4735 |  |  | 15.4129 |  |  | 14.1829 |  |  | 20.4852
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 7.2234 |  |  | 28.7462 |  |  | #NUM! |  |  | 61.014 |  |  | 28.6978 |  |  | 20.0674 |  |  | 16.4735 |  |  | 15.4129 |  |  | 14.1829 |  |  | 20.4852
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.2234 | 1649.8657 |  | 23.7462 | 5645.5002 |  | 7174 | 13961.9938 |  | 7174 | 27194.4001 |  | 7174 | 44724.7758 |  | 7174 | 62729.9413 |  | 7174 | 79650.3799 |  | 7174 | 93396.3346 |  | 7174 | 104199.3342 |  | 7174 | 116251.8989
[13 empty] | Next iteration flow rate |  |  | 1682.863 | Abs Value of | Flow this | 5701.9552 | Abs Value of | Flow this | 14101.6137 | Abs Value of | Flow this | 27466.3441 | Abs Value of | Flow this | 45172.0236 | Abs Value of | Flow this | 63357.2407 | Abs Value of | Flow this | 80446.8837 | Abs Value of | Flow this | 94330.2979 | Abs Value of | Flow this | 105241.3275 | Abs Value of | Flow this | 117414.4179 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.3935 |  |  | 87.5581 |  |  | 21.2268 |  |  | -200.3032 |  |  | -713.1554 |  |  | -1500.163 |  |  | -2480.1446 |  |  | -3447.7418 |  |  | -4316.0584 |  |  | -5396.8659
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47946 |  |  | 0.42236 |  |  | 0.10239 |  |  | -0.96623 |  |  | -3.4401 |  |  | -7.2365 |  |  | -11.9638 |  |  | -16.6313 |  |  | -20.8199 |  |  | -26.0335
[13 empty] | Delta P at this iteration flow rate |  |  | 49.3935 |  |  | 37.5581 |  |  | -28.7732 |  |  | -250.3032 |  |  | -763.1554 |  |  | -1550.163 |  |  | -2530.1446 |  |  | -3497.7418 |  |  | -4366.0584 |  |  | -5446.8659
[13 empty] | Press drop ratio this iteration |  |  | 0.49695 |  |  | 0.42895 |  |  | -1.3555 |  |  | 1.2496 |  |  | 1.0701 |  |  | 1.0333 |  |  | 1.0202 |  |  | 1.0145 |  |  | 1.0116 |  |  | 1.0093
[13 empty] | Expansion factor | 12 |  | 0.74118 |  |  | 0.77665 |  |  | 1.7164 |  |  | 0.33051 |  |  | 0.41096 |  |  | 0.39877 |  |  | 0.36546 |  |  | 0.31055 |  |  | 0.43188 |  |  | 0.13953
[13 empty] | C Non choked w/ reducers | 5 |  | 7.3716 |  |  | 29.1422 |  |  | #NUM! |  |  | 85.1558 |  |  | 34.5928 |  |  | 24.7121 |  |  | 21.5577 |  |  | 22.7768 |  |  | 16.6043 |  |  | 60.3251
[13 empty] | C Choked w/ reducers | 5 |  | 7.218 |  |  | 27.7764 |  |  | 286.107 |  |  | 59.8005 |  |  | 28.3332 |  |  | 19.842 |  |  | 16.2971 |  |  | 15.2514 |  |  | 14.0359 |  |  | 20.2748
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 7.3716 |  |  | 29.1422 |  |  | #NUM! |  |  | 59.8005 |  |  | 28.3332 |  |  | 19.842 |  |  | 16.2971 |  |  | 15.2514 |  |  | 14.0359 |  |  | 20.2748
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.3716 | 1682.863 |  | 24.1422 | 5701.9552 |  | 7174 | 14101.6137 |  | 7174 | 27466.3441 |  | 7174 | 45172.0236 |  | 7174 | 63357.2407 |  | 7174 | 80446.8837 |  | 7174 | 94330.2979 |  | 7174 | 105241.3275 |  | 7174 | 117414.4179
[13 empty] | Next iteration flow rate |  |  | 1716.5203 | Abs Value of | Flow this | 5758.9747 | Abs Value of | Flow this | 14242.6298 | Abs Value of | Flow this | 27741.0076 | Abs Value of | Flow this | 45623.7438 | Abs Value of | Flow this | 63990.8131 | Abs Value of | Flow this | 81251.3526 | Abs Value of | Flow this | 95273.6009 | Abs Value of | Flow this | 106293.7408 | Abs Value of | Flow this | 118588.5621 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.3479 |  |  | 87.2975 |  |  | 19.6329 |  |  | -206.3498 |  |  | -729.5103 |  |  | -1532.3368 |  |  | -2532.016 |  |  | -3519.0619 |  |  | -4404.8317 |  |  | -5507.3634
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47924 |  |  | 0.42111 |  |  | 0.094706 |  |  | -0.99539 |  |  | -3.519 |  |  | -7.3917 |  |  | -12.214 |  |  | -16.9753 |  |  | -21.2481 |  |  | -26.5665
[13 empty] | Delta P at this iteration flow rate |  |  | 49.3479 |  |  | 37.2975 |  |  | -30.3671 |  |  | -256.3498 |  |  | -779.5103 |  |  | -1582.3368 |  |  | -2582.016 |  |  | -3569.0619 |  |  | -4454.8317 |  |  | -5557.3634
[13 empty] | Press drop ratio this iteration |  |  | 0.49672 |  |  | 0.42725 |  |  | -1.5467 |  |  | 1.2423 |  |  | 1.0685 |  |  | 1.0326 |  |  | 1.0197 |  |  | 1.0142 |  |  | 1.0114 |  |  | 1.0091
[13 empty] | Expansion factor | 12 |  | 0.7413 |  |  | 0.77753 |  |  | 1.8175 |  |  | 0.33443 |  |  | 0.41183 |  |  | 0.39917 |  |  | 0.36572 |  |  | 0.31075 |  |  | 0.43201 |  |  | 0.13968
[13 empty] | C Non choked w/ reducers | 5 |  | 7.523 |  |  | 29.5465 |  |  | #NUM! |  |  | 82.7513 |  |  | 34.1088 |  |  | 24.4186 |  |  | 21.3166 |  |  | 22.5271 |  |  | 16.4293 |  |  | 59.6436
[13 empty] | C Choked w/ reducers | 5 |  | 7.3658 |  |  | 28.138 |  |  | 312.4271 |  |  | 58.6287 |  |  | 27.975 |  |  | 19.6196 |  |  | 16.1229 |  |  | 15.0917 |  |  | 13.8905 |  |  | 20.0667
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 7.523 |  |  | 29.5465 |  |  | #NUM! |  |  | 58.6287 |  |  | 27.975 |  |  | 19.6196 |  |  | 16.1229 |  |  | 15.0917 |  |  | 13.8905 |  |  | 20.0667
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.523 | 1716.5203 |  | 24.5465 | 5758.9747 |  | 7174 | 14242.6298 |  | 7174 | 27741.0076 |  | 7174 | 45623.7438 |  | 7174 | 63990.8131 |  | 7174 | 81251.3526 |  | 7174 | 95273.6009 |  | 7174 | 106293.7408 |  | 7174 | 118588.5621
[13 empty] | Next iteration flow rate |  |  | 1750.8507 | Abs Value of | Flow this | 5816.5645 | Abs Value of | Flow this | 14385.0561 | Abs Value of | Flow this | 28018.4176 | Abs Value of | Flow this | 46079.9813 | Abs Value of | Flow this | 64630.7212 | Abs Value of | Flow this | 82063.8661 | Abs Value of | Flow this | 96226.3369 | Abs Value of | Flow this | 107356.6782 | Abs Value of | Flow this | 119774.4477 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.3004 |  |  | 87.0317 |  |  | 18.0071 |  |  | -212.5179 |  |  | -746.194 |  |  | -1565.1573 |  |  | -2584.9301 |  |  | -3591.8156 |  |  | -4495.3894 |  |  | -5620.0819
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47901 |  |  | 0.41983 |  |  | 0.086863 |  |  | -1.0251 |  |  | -3.5995 |  |  | -7.55 |  |  | -12.4692 |  |  | -17.3263 |  |  | -21.685 |  |  | -27.1103
[13 empty] | Delta P at this iteration flow rate |  |  | 49.3004 |  |  | 37.0317 |  |  | -31.9929 |  |  | -262.5179 |  |  | -796.194 |  |  | -1615.1573 |  |  | -2634.9301 |  |  | -3641.8156 |  |  | -4545.3894 |  |  | -5670.0819
[13 empty] | Press drop ratio this iteration |  |  | 0.49648 |  |  | 0.4255 |  |  | -1.7767 |  |  | 1.2353 |  |  | 1.067 |  |  | 1.0319 |  |  | 1.0193 |  |  | 1.0139 |  |  | 1.0111 |  |  | 1.0089
[13 empty] | Expansion factor | 12 |  | 0.74143 |  |  | 0.77845 |  |  | 1.939 |  |  | 0.3382 |  |  | 0.41267 |  |  | 0.39957 |  |  | 0.36597 |  |  | 0.31094 |  |  | 0.43214 |  |  | 0.13984
[13 empty] | C Non choked w/ reducers | 5 |  | 7.6777 |  |  | 29.9595 |  |  | #NUM! |  |  | 80.477 |  |  | 33.6349 |  |  | 24.1295 |  |  | 21.0787 |  |  | 22.2807 |  |  | 16.2563 |  |  | 58.9717
[13 empty] | C Choked w/ reducers | 5 |  | 7.5167 |  |  | 28.5061 |  |  | 344.043 |  |  | 57.4963 |  |  | 27.623 |  |  | 19.4003 |  |  | 15.9508 |  |  | 14.9339 |  |  | 13.7468 |  |  | 19.8608
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 7.6777 |  |  | 29.9595 |  |  | #NUM! |  |  | 57.4963 |  |  | 27.623 |  |  | 19.4003 |  |  | 15.9508 |  |  | 14.9339 |  |  | 13.7468 |  |  | 19.8608
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.6777 | 1750.8507 |  | 24.9595 | 5816.5645 |  | 7174 | 14385.0561 |  | 7174 | 28018.4176 |  | 7174 | 46079.9813 |  | 7174 | 64630.7212 |  | 7174 | 82063.8661 |  | 7174 | 96226.3369 |  | 7174 | 107356.6782 |  | 7174 | 119774.4477
[13 empty] | Next iteration flow rate |  |  | 1785.8677 | Abs Value of | Flow this | 5874.7301 | Abs Value of | Flow this | 14528.9067 | Abs Value of | Flow this | 28298.6018 | Abs Value of | Flow this | 46540.7811 | Abs Value of | Flow this | 65277.0284 | Abs Value of | Flow this | 82884.5048 | Abs Value of | Flow this | 97188.6003 | Abs Value of | Flow this | 108430.245 | Abs Value of | Flow this | 120972.1922 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.251 |  |  | 86.7605 |  |  | 16.3485 |  |  | -218.81 |  |  | -763.213 |  |  | -1598.6375 |  |  | -2638.9077 |  |  | -3666.0316 |  |  | -4587.7672 |  |  | -5735.0661
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47877 |  |  | 0.41852 |  |  | 0.078862 |  |  | -1.0555 |  |  | -3.6816 |  |  | -7.7115 |  |  | -12.7296 |  |  | -17.6843 |  |  | -22.1306 |  |  | -27.6649
[13 empty] | Delta P at this iteration flow rate |  |  | 49.251 |  |  | 36.7605 |  |  | -33.6515 |  |  | -268.81 |  |  | -813.213 |  |  | -1648.6375 |  |  | -2688.9077 |  |  | -3716.0316 |  |  | -4637.7672 |  |  | -5785.0661
[13 empty] | Press drop ratio this iteration |  |  | 0.49623 |  |  | 0.4237 |  |  | -2.0584 |  |  | 1.2285 |  |  | 1.0655 |  |  | 1.0313 |  |  | 1.0189 |  |  | 1.0136 |  |  | 1.0109 |  |  | 1.0087
[13 empty] | Expansion factor | 12 |  | 0.74156 |  |  | 0.77938 |  |  | 2.0879 |  |  | 0.34182 |  |  | 0.4135 |  |  | 0.39996 |  |  | 0.36622 |  |  | 0.31114 |  |  | 0.43227 |  |  | 0.13999
[13 empty] | C Non choked w/ reducers | 5 |  | 7.8357 |  |  | 30.3815 |  |  | #NUM! |  |  | 78.3221 |  |  | 33.1709 |  |  | 23.8449 |  |  | 20.8441 |  |  | 22.0374 |  |  | 16.0853 |  |  | 58.309
[13 empty] | C Choked w/ reducers | 5 |  | 7.6708 |  |  | 28.8812 |  |  | 382.7359 |  |  | 56.4014 |  |  | 27.2771 |  |  | 19.1839 |  |  | 15.7807 |  |  | 14.7779 |  |  | 13.6047 |  |  | 19.6573
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 7.8357 |  |  | 30.3815 |  |  | #NUM! |  |  | 56.4014 |  |  | 27.2771 |  |  | 19.1839 |  |  | 15.7807 |  |  | 14.7779 |  |  | 13.6047 |  |  | 19.6573
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.8357 | 1785.8677 |  | 25.3815 | 5874.7301 |  | 7174 | 14528.9067 |  | 7174 | 28298.6018 |  | 7174 | 46540.7811 |  | 7174 | 65277.0284 |  | 7174 | 82884.5048 |  | 7174 | 97188.6003 |  | 7174 | 108430.245 |  | 7174 | 120972.1922
[13 empty] | Next iteration flow rate |  |  | 1821.5851 | Abs Value of | Flow this | 5933.4774 | Abs Value of | Flow this | 14674.1958 | Abs Value of | Flow this | 28581.5878 | Abs Value of | Flow this | 47006.1889 | Abs Value of | Flow this | 65929.7987 | Abs Value of | Flow this | 83713.3498 | Abs Value of | Flow this | 98160.4863 | Abs Value of | Flow this | 109514.5474 | Abs Value of | Flow this | 122181.9141 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.1996 |  |  | 86.4839 |  |  | 14.6566 |  |  | -225.2286 |  |  | -780.5741 |  |  | -1632.7906 |  |  | -2693.9702 |  |  | -3741.7393 |  |  | -4682.0018 |  |  | -5852.3614
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47852 |  |  | 0.41718 |  |  | 0.070701 |  |  | -1.0865 |  |  | -3.7654 |  |  | -7.8763 |  |  | -12.9952 |  |  | -18.0495 |  |  | -22.5851 |  |  | -28.2307
[13 empty] | Delta P at this iteration flow rate |  |  | 49.1996 |  |  | 36.4839 |  |  | -35.3434 |  |  | -275.2286 |  |  | -830.5741 |  |  | -1682.7906 |  |  | -2743.9702 |  |  | -3791.7393 |  |  | -4732.0018 |  |  | -5902.3614
[13 empty] | Press drop ratio this iteration |  |  | 0.49597 |  |  | 0.42186 |  |  | -2.4114 |  |  | 1.222 |  |  | 1.0641 |  |  | 1.0306 |  |  | 1.0186 |  |  | 1.0134 |  |  | 1.0107 |  |  | 1.0085
[13 empty] | Expansion factor | 12 |  | 0.7417 |  |  | 0.78034 |  |  | 2.2745 |  |  | 0.34531 |  |  | 0.4143 |  |  | 0.40034 |  |  | 0.36646 |  |  | 0.31132 |  |  | 0.43239 |  |  | 0.14014
[13 empty] | C Non choked w/ reducers | 5 |  | 7.9972 |  |  | 30.8127 |  |  | #NUM! |  |  | 76.2769 |  |  | 32.7164 |  |  | 23.5647 |  |  | 20.6126 |  |  | 21.7973 |  |  | 15.9164 |  |  | 57.6554
[13 empty] | C Choked w/ reducers | 5 |  | 7.8283 |  |  | 29.2633 |  |  | 431.1867 |  |  | 55.342 |  |  | 26.9371 |  |  | 18.9705 |  |  | 15.6128 |  |  | 14.6237 |  |  | 13.4642 |  |  | 19.4559
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 7.9972 |  |  | 30.8127 |  |  | #NUM! |  |  | 55.342 |  |  | 26.9371 |  |  | 18.9705 |  |  | 15.6128 |  |  | 14.6237 |  |  | 13.4642 |  |  | 19.4559
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.9972 | 1821.5851 |  | 25.8127 | 5933.4774 |  | 7174 | 14674.1958 |  | 7174 | 28581.5878 |  | 7174 | 47006.1889 |  | 7174 | 65929.7987 |  | 7174 | 83713.3498 |  | 7174 | 98160.4863 |  | 7174 | 109514.5474 |  | 7174 | 122181.9141
[13 empty] | Next iteration flow rate |  |  | 1858.0168 | Abs Value of | Flow this | 5992.8122 | Abs Value of | Flow this | 14820.9377 | Abs Value of | Flow this | 28867.4037 | Abs Value of | Flow this | 47476.2508 | Abs Value of | Flow this | 66589.0967 | Abs Value of | Flow this | 84550.4833 | Abs Value of | Flow this | 99142.0911 | Abs Value of | Flow this | 110609.6929 | Abs Value of | Flow this | 123403.7332 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.1462 |  |  | 86.2017 |  |  | 12.9307 |  |  | -231.7762 |  |  | -798.2842 |  |  | -1667.6302 |  |  | -2750.1395 |  |  | -3818.9688 |  |  | -4778.1306 |  |  | -5972.0144
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47826 |  |  | 0.41582 |  |  | 0.062375 |  |  | -1.118 |  |  | -3.8508 |  |  | -8.0444 |  |  | -13.2662 |  |  | -18.422 |  |  | -23.0489 |  |  | -28.8079
[13 empty] | Delta P at this iteration flow rate |  |  | 49.1462 |  |  | 36.2017 |  |  | -37.0693 |  |  | -281.7762 |  |  | -848.2842 |  |  | -1717.6302 |  |  | -2800.1395 |  |  | -3868.9688 |  |  | -4828.1306 |  |  | -6022.0144
[13 empty] | Press drop ratio this iteration |  |  | 0.49569 |  |  | 0.41997 |  |  | -2.8668 |  |  | 1.2157 |  |  | 1.0626 |  |  | 1.03 |  |  | 1.0182 |  |  | 1.0131 |  |  | 1.0105 |  |  | 1.0084
[13 empty] | Expansion factor | 12 |  | 0.74184 |  |  | 0.78133 |  |  | 2.5151 |  |  | 0.34867 |  |  | 0.41508 |  |  | 0.40071 |  |  | 0.36669 |  |  | 0.31151 |  |  | 0.43251 |  |  | 0.14029
[13 empty] | C Non choked w/ reducers | 5 |  | 8.1623 |  |  | 31.2535 |  |  | #NUM! |  |  | 74.3329 |  |  | 32.2712 |  |  | 23.2887 |  |  | 20.3842 |  |  | 21.5602 |  |  | 15.7494 |  |  | 57.0107
[13 empty] | C Choked w/ reducers | 5 |  | 7.9892 |  |  | 29.6527 |  |  | 493.6263 |  |  | 54.3164 |  |  | 26.6029 |  |  | 18.7599 |  |  | 15.4468 |  |  | 14.4712 |  |  | 13.3253 |  |  | 19.2568
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 8.1623 |  |  | 31.2535 |  |  | #NUM! |  |  | 54.3164 |  |  | 26.6029 |  |  | 18.7599 |  |  | 15.4468 |  |  | 14.4712 |  |  | 13.3253 |  |  | 19.2568
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 6.1623 | 1858.0168 |  | 26.2535 | 5992.8122 |  | 7174 | 14820.9377 |  | 7174 | 28867.4037 |  | 7174 | 47476.2508 |  | 7174 | 66589.0967 |  | 7174 | 84550.4833 |  | 7174 | 99142.0911 |  | 7174 | 110609.6929 |  | 7174 | 123403.7332
[13 empty] | Next iteration flow rate |  |  | 1895.1771 | Abs Value of | Flow this | 6052.7403 | Abs Value of | Flow this | 14969.1471 | Abs Value of | Flow this | 29156.0778 | Abs Value of | Flow this | 47951.0133 | Abs Value of | Flow this | 67254.9877 | Abs Value of | Flow this | 85395.9881 | Abs Value of | Flow this | 100133.5121 | Abs Value of | Flow this | 111715.7898 | Abs Value of | Flow this | 124637.7706 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.0906 |  |  | 85.9139 |  |  | 11.1701 |  |  | -238.4554 |  |  | -816.3502 |  |  | -1703.1701 |  |  | -2807.4379 |  |  | -3897.7506 |  |  | -4876.1915 |  |  | -6094.0724
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.478 |  |  | 0.41443 |  |  | 0.053882 |  |  | -1.1503 |  |  | -3.9379 |  |  | -8.2158 |  |  | -13.5426 |  |  | -18.8021 |  |  | -23.5219 |  |  | -29.3967
[13 empty] | Delta P at this iteration flow rate |  |  | 49.0906 |  |  | 35.9139 |  |  | -38.8299 |  |  | -288.4554 |  |  | -866.3502 |  |  | -1753.1701 |  |  | -2857.4379 |  |  | -3947.7506 |  |  | -4926.1915 |  |  | -6144.0724
[13 empty] | Press drop ratio this iteration |  |  | 0.49541 |  |  | 0.41802 |  |  | -3.4762 |  |  | 1.2097 |  |  | 1.0612 |  |  | 1.0294 |  |  | 1.0178 |  |  | 1.0128 |  |  | 1.0103 |  |  | 1.0082
[13 empty] | Expansion factor | 12 |  | 0.74198 |  |  | 0.78234 |  |  | 2.8372 |  |  | 0.35191 |  |  | 0.41584 |  |  | 0.40108 |  |  | 0.36693 |  |  | 0.31169 |  |  | 0.43263 |  |  | 0.14043
[13 empty] | C Non choked w/ reducers | 5 |  | 8.3309 |  |  | 31.7042 |  |  | #NUM! |  |  | 72.4824 |  |  | 31.8349 |  |  | 23.0168 |  |  | 20.1588 |  |  | 21.3261 |  |  | 15.5844 |  |  | 56.3747
[13 empty] | C Choked w/ reducers | 5 |  | 8.1535 |  |  | 30.0496 |  |  | 577.1448 |  |  | 53.3229 |  |  | 26.2743 |  |  | 18.5521 |  |  | 15.2829 |  |  | 14.3205 |  |  | 13.1879 |  |  | 19.0598
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 8.3309 |  |  | 31.7042 |  |  | #NUM! |  |  | 53.3229 |  |  | 26.2743 |  |  | 18.5521 |  |  | 15.2829 |  |  | 14.3205 |  |  | 13.1879 |  |  | 19.0598
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 6.3309 | 1895.1771 |  | 26.7042 | 6052.7403 |  | 7174 | 14969.1471 |  | 7174 | 29156.0778 |  | 7174 | 47951.0133 |  | 7174 | 67254.9877 |  | 7174 | 85395.9881 |  | 7174 | 100133.5121 |  | 7174 | 111715.7898 |  | 7174 | 124637.7706
[13 empty] | Next iteration flow rate |  |  | 1933.0806 | Abs Value of | Flow this | 6113.2677 | Abs Value of | Flow this | 15118.8386 | Abs Value of | Flow this | 29447.6385 | Abs Value of | Flow this | 48430.5234 | Abs Value of | Flow this | 67927.5376 | Abs Value of | Flow this | 86249.948 | Abs Value of | Flow this | 101134.8472 | Abs Value of | Flow this | 112832.9477 | Abs Value of | Flow this | 125884.1483 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 99.0327 |  |  | 85.6202 |  |  | 9.3741 |  |  | -245.2689 |  |  | -834.7793 |  |  | -1739.4243 |  |  | -2865.8879 |  |  | -3978.1159 |  |  | -4976.2235 |  |  | -6218.5838
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47772 |  |  | 0.41302 |  |  | 0.045219 |  |  | -1.1831 |  |  | -4.0268 |  |  | -8.3907 |  |  | -13.8245 |  |  | -19.1897 |  |  | -24.0044 |  |  | -29.9973
[13 empty] | Delta P at this iteration flow rate |  |  | 49.0327 |  |  | 35.6202 |  |  | -40.6259 |  |  | -295.2689 |  |  | -884.7793 |  |  | -1789.4243 |  |  | -2915.8879 |  |  | -4028.1159 |  |  | -5026.2235 |  |  | -6268.5838
[13 empty] | Press drop ratio this iteration |  |  | 0.49512 |  |  | 0.41603 |  |  | -4.3338 |  |  | 1.2039 |  |  | 1.0599 |  |  | 1.0287 |  |  | 1.0174 |  |  | 1.0126 |  |  | 1.01 |  |  | 1.008
[13 empty] | Expansion factor | 12 |  | 0.74214 |  |  | 0.78338 |  |  | 3.2905 |  |  | 0.35503 |  |  | 0.41659 |  |  | 0.40143 |  |  | 0.36715 |  |  | 0.31186 |  |  | 0.43275 |  |  | 0.14057
[13 empty] | C Non choked w/ reducers | 5 |  | 8.5033 |  |  | 32.1653 |  |  | #NUM! |  |  | 70.7184 |  |  | 31.4072 |  |  | 22.749 |  |  | 19.9365 |  |  | 21.095 |  |  | 15.4213 |  |  | 55.7474
[13 empty] | C Choked w/ reducers | 5 |  | 8.3214 |  |  | 30.4541 |  |  | 694.5976 |  |  | 52.36 |  |  | 25.9512 |  |  | 18.3471 |  |  | 15.1209 |  |  | 14.1715 |  |  | 13.052 |  |  | 18.8649
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 8.5033 |  |  | 32.1653 |  |  | #NUM! |  |  | 52.36 |  |  | 25.9512 |  |  | 18.3471 |  |  | 15.1209 |  |  | 14.1715 |  |  | 13.052 |  |  | 18.8649
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 6.5033 | 1933.0806 |  | 27.1653 | 6113.2677 |  | 7174 | 15118.8386 |  | 7174 | 29447.6385 |  | 7174 | 48430.5234 |  | 7174 | 67927.5376 |  | 7174 | 86249.948 |  | 7174 | 101134.8472 |  | 7174 | 112832.9477 |  | 7174 | 125884.1483
[13 empty] | Next iteration flow rate |  |  | 1971.7423 | Abs Value of | Flow this | 6174.4004 | Abs Value of | Flow this | 15270.027 | Abs Value of | Flow this | 29742.1149 | Abs Value of | Flow this | 48914.8286 | Abs Value of | Flow this | 68606.8129 | Abs Value of | Flow this | 87112.4475 | Abs Value of | Flow this | 102146.1957 | Abs Value of | Flow this | 113961.2772 | Abs Value of | Flow this | 127142.9897 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 98.9725 |  |  | 85.3207 |  |  | 7.542 |  |  | -252.2193 |  |  | -853.5789 |  |  | -1776.4072 |  |  | -2925.5127 |  |  | -4060.0965 |  |  | -5078.2661 |  |  | -6345.5978
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47743 |  |  | 0.41157 |  |  | 0.036381 |  |  | -1.2167 |  |  | -4.1175 |  |  | -8.5691 |  |  | -14.1122 |  |  | -19.5852 |  |  | -24.4967 |  |  | -30.61
[13 empty] | Delta P at this iteration flow rate |  |  | 48.9725 |  |  | 35.3207 |  |  | -42.458 |  |  | -302.2193 |  |  | -903.5789 |  |  | -1826.4072 |  |  | -2975.5127 |  |  | -4110.0965 |  |  | -5128.2661 |  |  | -6395.5978
[13 empty] | Press drop ratio this iteration |  |  | 0.49481 |  |  | 0.41398 |  |  | -5.6295 |  |  | 1.1982 |  |  | 1.0586 |  |  | 1.0281 |  |  | 1.0171 |  |  | 1.0123 |  |  | 1.0098 |  |  | 1.0079
[13 empty] | Expansion factor | 12 |  | 0.7423 |  |  | 0.78444 |  |  | 3.9753 |  |  | 0.35804 |  |  | 0.41731 |  |  | 0.40178 |  |  | 0.36737 |  |  | 0.31204 |  |  | 0.43286 |  |  | 0.14071
[13 empty] | C Non choked w/ reducers | 5 |  | 8.6794 |  |  | 32.6372 |  |  | #NUM! |  |  | 69.0347 |  |  | 30.9879 |  |  | 22.4852 |  |  | 19.717 |  |  | 20.8669 |  |  | 15.26 |  |  | 55.1285
[13 empty] | C Choked w/ reducers | 5 |  | 8.493 |  |  | 30.8667 |  |  | 871.9611 |  |  | 51.4263 |  |  | 25.6334 |  |  | 18.1448 |  |  | 14.9608 |  |  | 14.0242 |  |  | 12.9176 |  |  | 18.6722
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 8.6794 |  |  | 32.6372 |  |  | #NUM! |  |  | 51.4263 |  |  | 25.6334 |  |  | 18.1448 |  |  | 14.9608 |  |  | 14.0242 |  |  | 12.9176 |  |  | 18.6722
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 6.6794 | 1971.7423 |  | 27.6372 | 6174.4004 |  | 7174 | 15270.027 |  | 7174 | 29742.1149 |  | 7174 | 48914.8286 |  | 7174 | 68606.8129 |  | 7174 | 87112.4475 |  | 7174 | 102146.1957 |  | 7174 | 113961.2772 |  | 7174 | 127142.9897
[13 empty] | Next iteration flow rate |  |  | 2011.1771 | Abs Value of | Flow this | 6236.1444 | Abs Value of | Flow this | 15422.7272 | Abs Value of | Flow this | 30039.5361 | Abs Value of | Flow this | 49403.9769 | Abs Value of | Flow this | 69292.8811 | Abs Value of | Flow this | 87983.572 | Abs Value of | Flow this | 103167.6576 | Abs Value of | Flow this | 115100.89 | Abs Value of | Flow this | 128414.4196 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 98.9099 |  |  | 85.0151 |  |  | 5.6731 |  |  | -259.3094 |  |  | -872.7563 |  |  | -1814.1335 |  |  | -2986.336 |  |  | -4143.725 |  |  | -5182.3597 |  |  | -6475.1648
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47712 |  |  | 0.4101 |  |  | 0.027366 |  |  | -1.2509 |  |  | -4.21 |  |  | -8.7511 |  |  | -14.4056 |  |  | -19.9886 |  |  | -24.9988 |  |  | -31.235
[13 empty] | Delta P at this iteration flow rate |  |  | 48.9099 |  |  | 35.0151 |  |  | -44.3269 |  |  | -309.3094 |  |  | -922.7563 |  |  | -1864.1335 |  |  | -3036.336 |  |  | -4193.725 |  |  | -5232.3597 |  |  | -6525.1648
[13 empty] | Press drop ratio this iteration |  |  | 0.49449 |  |  | 0.41187 |  |  | -7.8135 |  |  | 1.1928 |  |  | 1.0573 |  |  | 1.0276 |  |  | 1.0167 |  |  | 1.0121 |  |  | 1.0096 |  |  | 1.0077
[13 empty] | Expansion factor | 12 |  | 0.74246 |  |  | 0.78554 |  |  | 5.1295 |  |  | 0.36094 |  |  | 0.41802 |  |  | 0.40212 |  |  | 0.36759 |  |  | 0.3122 |  |  | 0.43297 |  |  | 0.14084
[13 empty] | C Non choked w/ reducers | 5 |  | 8.8595 |  |  | 33.1202 |  |  | #NUM! |  |  | 67.4256 |  |  | 30.5768 |  |  | 22.2253 |  |  | 19.5004 |  |  | 20.6415 |  |  | 15.1007 |  |  | 54.5178
[13 empty] | C Choked w/ reducers | 5 |  | 8.6684 |  |  | 31.2874 |  |  | 1170.8076 |  |  | 50.5204 |  |  | 25.3209 |  |  | 17.9451 |  |  | 14.8027 |  |  | 13.8786 |  |  | 12.7847 |  |  | 18.4816
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 8.8595 |  |  | 33.1202 |  |  | #NUM! |  |  | 50.5204 |  |  | 25.3209 |  |  | 17.9451 |  |  | 14.8027 |  |  | 13.8786 |  |  | 12.7847 |  |  | 18.4816
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 6.8595 | 2011.1771 |  | 28.1202 | 6236.1444 |  | 7174 | 15422.7272 |  | 7174 | 30039.5361 |  | 7174 | 49403.9769 |  | 7174 | 69292.8811 |  | 7174 | 87983.572 |  | 7174 | 103167.6576 |  | 7174 | 115100.89 |  | 7174 | 128414.4196
[13 empty] | Next iteration flow rate |  |  | 2051.4006 | Abs Value of | Flow this | 6298.5059 | Abs Value of | Flow this | 15576.9545 | Abs Value of | Flow this | 30339.9314 | Abs Value of | Flow this | 49898.0167 | Abs Value of | Flow this | 69985.8099 | Abs Value of | Flow this | 88863.4077 | Abs Value of | Flow this | 104199.3342 | Abs Value of | Flow this | 116251.8989 | Abs Value of | Flow this | 129698.5638 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 98.8447 |  |  | 84.7034 |  |  | 3.7666 |  |  | -266.542 |  |  | -892.3192 |  |  | -1852.6181 |  |  | -3048.3819 |  |  | -4229.0343 |  |  | -5288.5456 |  |  | -6607.3362
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47681 |  |  | 0.40859 |  |  | 0.018169 |  |  | -1.2858 |  |  | -4.3044 |  |  | -8.9367 |  |  | -14.7049 |  |  | -20.4001 |  |  | -25.511 |  |  | -31.8726
[13 empty] | Delta P at this iteration flow rate |  |  | 48.8447 |  |  | 34.7034 |  |  | -46.2334 |  |  | -316.542 |  |  | -942.3192 |  |  | -1902.6181 |  |  | -3098.3819 |  |  | -4279.0343 |  |  | -5338.5456 |  |  | -6657.3362
[13 empty] | Press drop ratio this iteration |  |  | 0.49416 |  |  | 0.40971 |  |  | -12.2745 |  |  | 1.1876 |  |  | 1.056 |  |  | 1.027 |  |  | 1.0164 |  |  | 1.0118 |  |  | 1.0095 |  |  | 1.0076
[13 empty] | Expansion factor | 12 |  | 0.74264 |  |  | 0.78667 |  |  | 7.4872 |  |  | 0.36374 |  |  | 0.41871 |  |  | 0.40245 |  |  | 0.3678 |  |  | 0.31237 |  |  | 0.43308 |  |  | 0.14097
[13 empty] | C Non choked w/ reducers | 5 |  | 9.0436 |  |  | 33.6149 |  |  | #NUM! |  |  | 65.8861 |  |  | 30.1736 |  |  | 21.9692 |  |  | 19.2867 |  |  | 20.419 |  |  | 14.9431 |  |  | 53.9152
[13 empty] | C Choked w/ reducers | 5 |  | 8.8476 |  |  | 31.7165 |  |  | 1781.0486 |  |  | 49.641 |  |  | 25.0134 |  |  | 17.7481 |  |  | 14.6464 |  |  | 13.7346 |  |  | 12.6533 |  |  | 18.293
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 9.0436 |  |  | 33.6149 |  |  | #NUM! |  |  | 49.641 |  |  | 25.0134 |  |  | 17.7481 |  |  | 14.6464 |  |  | 13.7346 |  |  | 12.6533 |  |  | 18.293
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7.0436 | 2051.4006 |  | 28.6149 | 6298.5059 |  | 7174 | 15576.9545 |  | 7174 | 30339.9314 |  | 7174 | 49898.0167 |  | 7174 | 69985.8099 |  | 7174 | 88863.4077 |  | 7174 | 104199.3342 |  | 7174 | 116251.8989 |  | 7174 | 129698.5638
[13 empty] | Next iteration flow rate |  |  | 2092.4287 | Abs Value of | Flow this | 6361.4909 | Abs Value of | Flow this | 15732.724 | Abs Value of | Flow this | 30643.3307 | Abs Value of | Flow this | 50396.9969 | Abs Value of | Flow this | 70685.668 | Abs Value of | Flow this | 89752.0418 | Abs Value of | Flow this | 105241.3275 | Abs Value of | Flow this | 117414.4179 | Abs Value of | Flow this | 130995.5495 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 98.7769 |  |  | 84.3855 |  |  | 1.8218 |  |  | -273.92 |  |  | -912.2754 |  |  | -1891.8762 |  |  | -3111.6749 |  |  | -4316.0584 |  |  | -5396.8659 |  |  | -6742.1641
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47648 |  |  | 0.40706 |  |  | 0.0087881 |  |  | -1.3213 |  |  | -4.4007 |  |  | -9.1261 |  |  | -15.0102 |  |  | -20.8199 |  |  | -26.0335 |  |  | -32.523
[13 empty] | Delta P at this iteration flow rate |  |  | 48.7769 |  |  | 34.3855 |  |  | -48.1782 |  |  | -323.92 |  |  | -962.2754 |  |  | -1941.8762 |  |  | -3161.6749 |  |  | -4366.0584 |  |  | -5446.8659 |  |  | -6792.1641
[13 empty] | Press drop ratio this iteration |  |  | 0.49381 |  |  | 0.40748 |  |  | -26.4452 |  |  | 1.1825 |  |  | 1.0548 |  |  | 1.0264 |  |  | 1.0161 |  |  | 1.0116 |  |  | 1.0093 |  |  | 1.0074
[13 empty] | Expansion factor | 12 |  | 0.74282 |  |  | 0.78783 |  |  | 14.9765 |  |  | 0.36645 |  |  | 0.41939 |  |  | 0.40278 |  |  | 0.36801 |  |  | 0.31253 |  |  | 0.43319 |  |  | 0.1411
[13 empty] | C Non choked w/ reducers | 5 |  | 9.2318 |  |  | 34.1216 |  |  | #NUM! |  |  | 64.4114 |  |  | 29.778 |  |  | 21.7168 |  |  | 19.0757 |  |  | 20.1993 |  |  | 14.7874 |  |  | 53.3206
[13 empty] | C Choked w/ reducers | 5 |  | 9.0307 |  |  | 32.1544 |  |  | 3719.1549 |  |  | 48.787 |  |  | 24.7109 |  |  | 17.5536 |  |  | 14.492 |  |  | 13.5923 |  |  | 12.5233 |  |  | 18.1064
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 9.2318 |  |  | 34.1216 |  |  | #NUM! |  |  | 48.787 |  |  | 24.7109 |  |  | 17.5536 |  |  | 14.492 |  |  | 13.5923 |  |  | 12.5233 |  |  | 18.1064
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7.2318 | 2092.4287 |  | 29.1216 | 6361.4909 |  | 7174 | 15732.724 |  | 7174 | 30643.3307 |  | 7174 | 50396.9969 |  | 7174 | 70685.668 |  | 7174 | 89752.0418 |  | 7174 | 105241.3275 |  | 7174 | 117414.4179 |  | 7174 | 130995.5495
[13 empty] | Next iteration flow rate |  |  | 2134.2772 | Abs Value of | Flow this | 6425.1058 | Abs Value of | Flow this | 15890.0513 | Abs Value of | Flow this | 30949.764 | Abs Value of | Flow this | 50900.9668 | Abs Value of | Flow this | 71392.5247 | Abs Value of | Flow this | 90649.5622 | Abs Value of | Flow this | 106293.7408 | Abs Value of | Flow this | 118588.5621 | Abs Value of | Flow this | 132305.505 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 98.7064 |  |  | 84.0611 |  |  | -0.16208 |  |  | -281.4463 |  |  | -932.6326 |  |  | -1931.9235 |  |  | -3176.24 |  |  | -4404.8317 |  |  | -5507.3634 |  |  | -6879.7021
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47614 |  |  | 0.4055 |  |  | -0.00078183 |  |  | -1.3576 |  |  | -4.4989 |  |  | -9.3193 |  |  | -15.3216 |  |  | -21.2481 |  |  | -26.5665 |  |  | -33.1865
[13 empty] | Delta P at this iteration flow rate |  |  | 48.7064 |  |  | 34.0611 |  |  | -50.1621 |  |  | -331.4463 |  |  | -982.6326 |  |  | -1981.9235 |  |  | -3226.24 |  |  | -4454.8317 |  |  | -5557.3634 |  |  | -6929.7021
[13 empty] | Press drop ratio this iteration |  |  | 0.49345 |  |  | 0.40519 |  |  | 309.4959 |  |  | 1.1777 |  |  | 1.0536 |  |  | 1.0259 |  |  | 1.0157 |  |  | 1.0114 |  |  | 1.0091 |  |  | 1.0073
[13 empty] | Expansion factor | 12 |  | 0.74301 |  |  | 0.78902 |  |  | -162.5711 |  |  | 0.36907 |  |  | 0.42005 |  |  | 0.4031 |  |  | 0.36821 |  |  | 0.31269 |  |  | 0.43329 |  |  | 0.14123
[13 empty] | C Non choked w/ reducers | 5 |  | 9.4242 |  |  | 34.6409 |  |  | -7.8202 |  |  | 62.9974 |  |  | 29.3898 |  |  | 21.468 |  |  | 18.8674 |  |  | 19.9823 |  |  | 14.6334 |  |  | 52.7338
[13 empty] | C Choked w/ reducers | 5 |  | 9.2179 |  |  | 32.6013 |  |  | 42222.9657 |  |  | 47.9572 |  |  | 24.4132 |  |  | 17.3616 |  |  | 14.3394 |  |  | 13.4515 |  |  | 12.3948 |  |  | 17.9219
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 9.4242 |  |  | 34.6409 |  |  | 42222.9657 |  |  | 47.9572 |  |  | 24.4132 |  |  | 17.3616 |  |  | 14.3394 |  |  | 13.4515 |  |  | 12.3948 |  |  | 17.9219
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7.4242 | 2134.2772 |  | 29.6409 | 6425.1058 |  | 7174 | 15890.0513 |  | 7174 | 30949.764 |  | 7174 | 50900.9668 |  | 7174 | 71392.5247 |  | 7174 | 90649.5622 |  | 7174 | 106293.7408 |  | 7174 | 118588.5621 |  | 7174 | 132305.505
[13 empty] | Next iteration flow rate |  |  | 2176.9628 | Abs Value of | Flow this | 6489.3569 | Abs Value of | Flow this | 16048.9518 | Abs Value of | Flow this | 31259.2617 | Abs Value of | Flow this | 51409.9765 | Abs Value of | Flow this | 72106.4499 | Abs Value of | Flow this | 91556.0578 | Abs Value of | Flow this | 107356.6782 | Abs Value of | Flow this | 119774.4477 | Abs Value of | Flow this | 133628.56 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 98.633 |  |  | 83.7302 |  |  | -2.1858 |  |  | -289.1239 |  |  | -953.399 |  |  | -1972.7756 |  |  | -3242.103 |  |  | -4495.3894 |  |  | -5620.0819 |  |  | -7020.0047
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47579 |  |  | 0.4039 |  |  | -0.010544 |  |  | -1.3947 |  |  | -4.599 |  |  | -9.5163 |  |  | -15.6393 |  |  | -21.685 |  |  | -27.1103 |  |  | -33.8633
[13 empty] | Delta P at this iteration flow rate |  |  | 48.633 |  |  | 33.7302 |  |  | -52.1858 |  |  | -339.1239 |  |  | -1003.399 |  |  | -2022.7756 |  |  | -3292.103 |  |  | -4545.3894 |  |  | -5670.0819 |  |  | -7070.0047
[13 empty] | Press drop ratio this iteration |  |  | 0.49307 |  |  | 0.40284 |  |  | 23.8745 |  |  | 1.1729 |  |  | 1.0524 |  |  | 1.0253 |  |  | 1.0154 |  |  | 1.0111 |  |  | 1.0089 |  |  | 1.0071
[13 empty] | Expansion factor | 12 |  | 0.7432 |  |  | 0.79024 |  |  | -11.6179 |  |  | 0.37159 |  |  | 0.42069 |  |  | 0.40341 |  |  | 0.36841 |  |  | 0.31285 |  |  | 0.43339 |  |  | 0.14135
[13 empty] | C Non choked w/ reducers | 5 |  | 9.621 |  |  | 35.1734 |  |  | -29.5066 |  |  | 61.64 |  |  | 29.0089 |  |  | 21.2228 |  |  | 18.6618 |  |  | 19.768 |  |  | 14.4812 |  |  | 52.1547
[13 empty] | C Choked w/ reducers | 5 |  | 9.4093 |  |  | 33.0574 |  |  | 3162.0732 |  |  | 47.1505 |  |  | 24.1203 |  |  | 17.1721 |  |  | 14.1886 |  |  | 13.3124 |  |  | 12.2677 |  |  | 17.7394
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 9.621 |  |  | 35.1734 |  |  | 3162.0732 |  |  | 47.1505 |  |  | 24.1203 |  |  | 17.1721 |  |  | 14.1886 |  |  | 13.3124 |  |  | 12.2677 |  |  | 17.7394
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7.621 | 2176.9628 |  | 30.1734 | 6489.3569 |  | 7174 | 16048.9518 |  | 7174 | 31259.2617 |  | 7174 | 51409.9765 |  | 7174 | 72106.4499 |  | 7174 | 91556.0578 |  | 7174 | 107356.6782 |  | 7174 | 119774.4477 |  | 7174 | 133628.56
[13 empty] | Next iteration flow rate |  |  | 2220.502 | Abs Value of | Flow this | 6554.2504 | Abs Value of | Flow this | 16209.4413 | Abs Value of | Flow this | 31571.8543 | Abs Value of | Flow this | 51924.0763 | Abs Value of | Flow this | 72827.5144 | Abs Value of | Flow this | 92471.6184 | Abs Value of | Flow this | 108430.245 | Abs Value of | Flow this | 120972.1922 | Abs Value of | Flow this | 134964.8456 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 98.5566 |  |  | 83.3927 |  |  | -4.2503 |  |  | -296.9558 |  |  | -974.5829 |  |  | -2014.4489 |  |  | -3309.2898 |  |  | -4587.7672 |  |  | -5735.0661 |  |  | -7163.1273
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47542 |  |  | 0.40227 |  |  | -0.020503 |  |  | -1.4325 |  |  | -4.7012 |  |  | -9.7173 |  |  | -15.9634 |  |  | -22.1306 |  |  | -27.6649 |  |  | -34.5537
[13 empty] | Delta P at this iteration flow rate |  |  | 48.5566 |  |  | 33.3927 |  |  | -54.2503 |  |  | -346.9558 |  |  | -1024.5829 |  |  | -2064.4489 |  |  | -3359.2898 |  |  | -4637.7672 |  |  | -5785.0661 |  |  | -7213.1273
[13 empty] | Press drop ratio this iteration |  |  | 0.49268 |  |  | 0.40043 |  |  | 12.7639 |  |  | 1.1684 |  |  | 1.0513 |  |  | 1.0248 |  |  | 1.0151 |  |  | 1.0109 |  |  | 1.0087 |  |  | 1.007
[13 empty] | Expansion factor | 12 |  | 0.74341 |  |  | 0.7915 |  |  | -5.7458 |  |  | 0.37404 |  |  | 0.42132 |  |  | 0.40372 |  |  | 0.36861 |  |  | 0.313 |  |  | 0.43349 |  |  | 0.14147
[13 empty] | C Non choked w/ reducers | 5 |  | 9.8222 |  |  | 35.7195 |  |  | -42.3827 |  |  | 60.3359 |  |  | 28.635 |  |  | 20.9811 |  |  | 18.4589 |  |  | 19.5563 |  |  | 14.3307 |  |  | 51.5831
[13 empty] | C Choked w/ reducers | 5 |  | 9.6049 |  |  | 33.5231 |  |  | 1642.457 |  |  | 46.366 |  |  | 23.832 |  |  | 16.985 |  |  | 14.0395 |  |  | 13.1747 |  |  | 12.1419 |  |  | 17.5588
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 9.8222 |  |  | 35.7195 |  |  | 1642.457 |  |  | 46.366 |  |  | 23.832 |  |  | 16.985 |  |  | 14.0395 |  |  | 13.1747 |  |  | 12.1419 |  |  | 17.5588
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7.8222 | 2220.502 |  | 30.7195 | 6554.2504 |  | 7174 | 16209.4413 |  | 7174 | 31571.8543 |  | 7174 | 51924.0763 |  | 7174 | 72827.5144 |  | 7174 | 92471.6184 |  | 7174 | 108430.245 |  | 7174 | 120972.1922 |  | 7174 | 134964.8456
[13 empty] | Next iteration flow rate |  |  | 2264.9121 | Abs Value of | Flow this | 6619.793 | Abs Value of | Flow this | 16371.5357 | Abs Value of | Flow this | 31887.5728 | Abs Value of | Flow this | 52443.317 | Abs Value of | Flow this | 73555.7895 | Abs Value of | Flow this | 93396.3346 | Abs Value of | Flow this | 109514.5474 | Abs Value of | Flow this | 122181.9141 | Abs Value of | Flow this | 136314.4941 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 98.4772 |  |  | 83.0484 |  |  | -6.3562 |  |  | -304.9451 |  |  | -996.1925 |  |  | -2056.9599 |  |  | -3377.827 |  |  | -4682.0018 |  |  | -5852.3614 |  |  | -7309.1266
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47504 |  |  | 0.40061 |  |  | -0.030661 |  |  | -1.471 |  |  | -4.8055 |  |  | -9.9224 |  |  | -16.294 |  |  | -22.5851 |  |  | -28.2307 |  |  | -35.2579
[13 empty] | Delta P at this iteration flow rate |  |  | 48.4772 |  |  | 33.0484 |  |  | -56.3562 |  |  | -354.9451 |  |  | -1046.1925 |  |  | -2106.9599 |  |  | -3427.827 |  |  | -4732.0018 |  |  | -5902.3614 |  |  | -7359.1266
[13 empty] | Press drop ratio this iteration |  |  | 0.49227 |  |  | 0.39794 |  |  | 8.8663 |  |  | 1.164 |  |  | 1.0502 |  |  | 1.0243 |  |  | 1.0148 |  |  | 1.0107 |  |  | 1.0085 |  |  | 1.0068
[13 empty] | Expansion factor | 12 |  | 0.74362 |  |  | 0.79279 |  |  | -3.6859 |  |  | 0.3764 |  |  | 0.42193 |  |  | 0.40401 |  |  | 0.3688 |  |  | 0.31315 |  |  | 0.43359 |  |  | 0.14159
[13 empty] | C Non choked w/ reducers | 5 |  | 10.028 |  |  | 36.2799 |  |  | -53.5374 |  |  | 59.0818 |  |  | 28.2678 |  |  | 20.7428 |  |  | 18.2585 |  |  | 19.3472 |  |  | 14.182 |  |  | 51.019
[13 empty] | C Choked w/ reducers | 5 |  | 9.8049 |  |  | 33.9987 |  |  | 1109.2624 |  |  | 45.6028 |  |  | 23.5482 |  |  | 16.8003 |  |  | 13.8922 |  |  | 13.0387 |  |  | 12.0176 |  |  | 17.3801
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 10.028 |  |  | 36.2799 |  |  | 1109.2624 |  |  | 45.6028 |  |  | 23.5482 |  |  | 16.8003 |  |  | 13.8922 |  |  | 13.0387 |  |  | 12.0176 |  |  | 17.3801
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 8.028 | 2264.9121 |  | 31.2799 | 6619.793 |  | 7174 | 16371.5357 |  | 7174 | 31887.5728 |  | 7174 | 52443.317 |  | 7174 | 73555.7895 |  | 7174 | 93396.3346 |  | 7174 | 109514.5474 |  | 7174 | 122181.9141 |  | 7174 | 136314.4941
[13 empty] | Next iteration flow rate |  |  | 2310.2103 | Abs Value of | Flow this | 6685.9909 | Abs Value of | Flow this | 16535.2511 | Abs Value of | Flow this | 32206.4486 | Abs Value of | Flow this | 52967.7502 | Abs Value of | Flow this | 74291.3474 | Abs Value of | Flow this | 94330.2979 | Abs Value of | Flow this | 110609.6929 | Abs Value of | Flow this | 123403.7332 | Abs Value of | Flow this | 137677.639 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 98.3946 |  |  | 82.6971 |  |  | -8.5045 |  |  | -313.0951 |  |  | -1018.2365 |  |  | -2100.3253 |  |  | -3447.7418 |  |  | -4778.1306 |  |  | -5972.0144 |  |  | -7458.0606
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47464 |  |  | 0.39892 |  |  | -0.041024 |  |  | -1.5103 |  |  | -4.9118 |  |  | -10.1316 |  |  | -16.6313 |  |  | -23.0489 |  |  | -28.8079 |  |  | -35.9764
[13 empty] | Delta P at this iteration flow rate |  |  | 48.3946 |  |  | 32.6971 |  |  | -58.5045 |  |  | -363.0951 |  |  | -1068.2365 |  |  | -2150.3253 |  |  | -3497.7418 |  |  | -4828.1306 |  |  | -6022.0144 |  |  | -7508.0606
[13 empty] | Press drop ratio this iteration |  |  | 0.49184 |  |  | 0.39538 |  |  | 6.8792 |  |  | 1.1597 |  |  | 1.0491 |  |  | 1.0238 |  |  | 1.0145 |  |  | 1.0105 |  |  | 1.0084 |  |  | 1.0067
[13 empty] | Expansion factor | 12 |  | 0.74384 |  |  | 0.79412 |  |  | -2.6357 |  |  | 0.37869 |  |  | 0.42253 |  |  | 0.40431 |  |  | 0.36898 |  |  | 0.31329 |  |  | 0.43369 |  |  | 0.14171
[13 empty] | C Non choked w/ reducers | 5 |  | 10.2385 |  |  | 36.8552 |  |  | -64.1613 |  |  | 57.8746 |  |  | 27.9073 |  |  | 20.5079 |  |  | 18.0606 |  |  | 19.1407 |  |  | 14.0349 |  |  | 50.4621
[13 empty] | C Choked w/ reducers | 5 |  | 10.0094 |  |  | 34.4846 |  |  | 837.349 |  |  | 44.8599 |  |  | 23.2687 |  |  | 16.618 |  |  | 13.7466 |  |  | 12.9041 |  |  | 11.8945 |  |  | 17.2034
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 10.2385 |  |  | 36.8552 |  |  | 837.349 |  |  | 44.8599 |  |  | 23.2687 |  |  | 16.618 |  |  | 13.7466 |  |  | 12.9041 |  |  | 11.8945 |  |  | 17.2034
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 8.2385 | 2310.2103 |  | 31.8552 | 6685.9909 |  | 7174 | 16535.2511 |  | 7174 | 32206.4486 |  | 7174 | 52967.7502 |  | 7174 | 74291.3474 |  | 7174 | 94330.2979 |  | 7174 | 110609.6929 |  | 7174 | 123403.7332 |  | 7174 | 137677.639
[13 empty] | Next iteration flow rate |  |  | 2356.4145 | Abs Value of | Flow this | 6752.8508 | Abs Value of | Flow this | 16700.6036 | Abs Value of | Flow this | 32528.5131 | Abs Value of | Flow this | 53497.4277 | Abs Value of | Flow this | 75034.2609 | Abs Value of | Flow this | 95273.6009 | Abs Value of | Flow this | 111715.7898 | Abs Value of | Flow this | 124637.7706 | Abs Value of | Flow this | 139054.4154 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 98.3086 |  |  | 82.3389 |  |  | -10.6959 |  |  | -321.4088 |  |  | -1040.7235 |  |  | -2144.5623 |  |  | -3519.0619 |  |  | -4876.1915 |  |  | -6094.0724 |  |  | -7609.9881
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47422 |  |  | 0.39719 |  |  | -0.051595 |  |  | -1.5504 |  |  | -5.0203 |  |  | -10.345 |  |  | -16.9753 |  |  | -23.5219 |  |  | -29.3967 |  |  | -36.7092
[13 empty] | Delta P at this iteration flow rate |  |  | 48.3086 |  |  | 32.3389 |  |  | -60.6959 |  |  | -371.4088 |  |  | -1090.7235 |  |  | -2194.5623 |  |  | -3569.0619 |  |  | -4926.1915 |  |  | -6144.0724 |  |  | -7659.9881
[13 empty] | Press drop ratio this iteration |  |  | 0.4914 |  |  | 0.39275 |  |  | 5.6747 |  |  | 1.1556 |  |  | 1.048 |  |  | 1.0233 |  |  | 1.0142 |  |  | 1.0103 |  |  | 1.0082 |  |  | 1.0066
[13 empty] | Expansion factor | 12 |  | 0.74407 |  |  | 0.79549 |  |  | -1.9991 |  |  | 0.3809 |  |  | 0.42311 |  |  | 0.40459 |  |  | 0.36917 |  |  | 0.31344 |  |  | 0.43378 |  |  | 0.14182
[13 empty] | C Non choked w/ reducers | 5 |  | 10.4539 |  |  | 37.4462 |  |  | -74.798 |  |  | 56.7116 |  |  | 27.5532 |  |  | 20.2763 |  |  | 17.8653 |  |  | 18.9366 |  |  | 13.8895 |  |  | 49.9123
[13 empty] | C Choked w/ reducers | 5 |  | 10.2185 |  |  | 34.981 |  |  | 672.4458 |  |  | 44.1365 |  |  | 22.9936 |  |  | 16.438 |  |  | 13.6027 |  |  | 12.7711 |  |  | 11.7729 |  |  | 17.0285
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 10.4539 |  |  | 37.4462 |  |  | 672.4458 |  |  | 44.1365 |  |  | 22.9936 |  |  | 16.438 |  |  | 13.6027 |  |  | 12.7711 |  |  | 11.7729 |  |  | 17.0285
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 8.4539 | 2356.4145 |  | 32.4462 | 6752.8508 |  | 7174 | 16700.6036 |  | 7174 | 32528.5131 |  | 7174 | 53497.4277 |  | 7174 | 75034.2609 |  | 7174 | 95273.6009 |  | 7174 | 111715.7898 |  | 7174 | 124637.7706 |  | 7174 | 139054.4154
[13 empty] | Next iteration flow rate |  |  | 2403.5428 | Abs Value of | Flow this | 6820.3793 | Abs Value of | Flow this | 16867.6096 | Abs Value of | Flow this | 32853.7982 | Abs Value of | Flow this | 54032.402 | Abs Value of | Flow this | 75784.6035 | Abs Value of | Flow this | 96226.3369 | Abs Value of | Flow this | 112832.9477 | Abs Value of | Flow this | 125884.1483 | Abs Value of | Flow this | 140444.9596 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 98.2191 |  |  | 81.9734 |  |  | -12.9314 |  |  | -329.8896 |  |  | -1063.6626 |  |  | -2189.6885 |  |  | -3591.8156 |  |  | -4976.2235 |  |  | -6218.5838 |  |  | -7764.9694
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47379 |  |  | 0.39542 |  |  | -0.062379 |  |  | -1.5913 |  |  | -5.1309 |  |  | -10.5627 |  |  | -17.3263 |  |  | -24.0044 |  |  | -29.9973 |  |  | -37.4568
[13 empty] | Delta P at this iteration flow rate |  |  | 48.2191 |  |  | 31.9734 |  |  | -62.9314 |  |  | -379.8896 |  |  | -1113.6626 |  |  | -2239.6885 |  |  | -3641.8156 |  |  | -5026.2235 |  |  | -6268.5838 |  |  | -7814.9694
[13 empty] | Press drop ratio this iteration |  |  | 0.49093 |  |  | 0.39005 |  |  | 4.8665 |  |  | 1.1516 |  |  | 1.047 |  |  | 1.0228 |  |  | 1.0139 |  |  | 1.01 |  |  | 1.008 |  |  | 1.0064
[13 empty] | Expansion factor | 12 |  | 0.74432 |  |  | 0.7969 |  |  | -1.572 |  |  | 0.38304 |  |  | 0.42368 |  |  | 0.40487 |  |  | 0.36934 |  |  | 0.31358 |  |  | 0.43387 |  |  | 0.14193
[13 empty] | C Non choked w/ reducers | 5 |  | 10.6743 |  |  | 38.0534 |  |  | -85.8074 |  |  | 55.5903 |  |  | 27.2054 |  |  | 20.0478 |  |  | 17.6724 |  |  | 18.7351 |  |  | 13.7457 |  |  | 49.3696
[13 empty] | C Choked w/ reducers | 5 |  | 10.4324 |  |  | 35.4883 |  |  | 561.76 |  |  | 43.4319 |  |  | 22.7227 |  |  | 16.2602 |  |  | 13.4604 |  |  | 12.6395 |  |  | 11.6525 |  |  | 16.8555
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 10.6743 |  |  | 38.0534 |  |  | 561.76 |  |  | 43.4319 |  |  | 22.7227 |  |  | 16.2602 |  |  | 13.4604 |  |  | 12.6395 |  |  | 11.6525 |  |  | 16.8555
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 8.6743 | 2403.5428 |  | 33.0534 | 6820.3793 |  | 7174 | 16867.6096 |  | 7174 | 32853.7982 |  | 7174 | 54032.402 |  | 7174 | 75784.6035 |  | 7174 | 96226.3369 |  | 7174 | 112832.9477 |  | 7174 | 125884.1483 |  | 7174 | 140444.9596
[13 empty] | Next iteration flow rate |  |  | 2451.6137 | Abs Value of | Flow this | 6888.5831 | Abs Value of | Flow this | 17036.2857 | Abs Value of | Flow this | 33182.3362 | Abs Value of | Flow this | 54572.726 | Abs Value of | Flow this | 76542.4496 | Abs Value of | Flow this | 97188.6003 | Abs Value of | Flow this | 113961.2772 | Abs Value of | Flow this | 127142.9897 | Abs Value of | Flow this | 141849.4092 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 98.1261 |  |  | 81.6005 |  |  | -15.2119 |  |  | -338.5409 |  |  | -1087.0627 |  |  | -2235.7218 |  |  | -3666.0316 |  |  | -5078.2661 |  |  | -6345.5978 |  |  | -7923.0658
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47334 |  |  | 0.39363 |  |  | -0.073379 |  |  | -1.6331 |  |  | -5.2438 |  |  | -10.7847 |  |  | -17.6843 |  |  | -24.4967 |  |  | -30.61 |  |  | -38.2195
[13 empty] | Delta P at this iteration flow rate |  |  | 48.1261 |  |  | 31.6005 |  |  | -65.2119 |  |  | -388.5409 |  |  | -1137.0627 |  |  | -2285.7218 |  |  | -3716.0316 |  |  | -5128.2661 |  |  | -6395.5978 |  |  | -7973.0658
[13 empty] | Press drop ratio this iteration |  |  | 0.49045 |  |  | 0.38726 |  |  | 4.2869 |  |  | 1.1477 |  |  | 1.046 |  |  | 1.0224 |  |  | 1.0136 |  |  | 1.0098 |  |  | 1.0079 |  |  | 1.0063
[13 empty] | Expansion factor | 12 |  | 0.74457 |  |  | 0.79836 |  |  | -1.2657 |  |  | 0.38512 |  |  | 0.42424 |  |  | 0.40515 |  |  | 0.36952 |  |  | 0.31371 |  |  | 0.43396 |  |  | 0.14204
[13 empty] | C Non choked w/ reducers | 5 |  | 10.8998 |  |  | 38.6778 |  |  | -97.4956 |  |  | 54.5083 |  |  | 26.8637 |  |  | 19.8226 |  |  | 17.4819 |  |  | 18.5359 |  |  | 13.6035 |  |  | 48.8337
[13 empty] | C Choked w/ reducers | 5 |  | 10.6511 |  |  | 36.007 |  |  | 482.3214 |  |  | 42.7452 |  |  | 22.4559 |  |  | 16.0846 |  |  | 13.3198 |  |  | 12.5094 |  |  | 11.5335 |  |  | 16.6844
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 10.8998 |  |  | 38.6778 |  |  | 482.3214 |  |  | 42.7452 |  |  | 22.4559 |  |  | 16.0846 |  |  | 13.3198 |  |  | 12.5094 |  |  | 11.5335 |  |  | 16.6844
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 8.8998 | 2451.6137 |  | 33.6778 | 6888.5831 |  | 7174 | 17036.2857 |  | 7174 | 33182.3362 |  | 7174 | 54572.726 |  | 7174 | 76542.4496 |  | 7174 | 97188.6003 |  | 7174 | 113961.2772 |  | 7174 | 127142.9897 |  | 7174 | 141849.4092
[13 empty] | Next iteration flow rate |  |  | 2500.6459 | Abs Value of | Flow this | 6957.4689 | Abs Value of | Flow this | 17206.6486 | Abs Value of | Flow this | 33514.1595 | Abs Value of | Flow this | 55118.4533 | Abs Value of | Flow this | 77307.8741 | Abs Value of | Flow this | 98160.4863 | Abs Value of | Flow this | 115100.89 | Abs Value of | Flow this | 128414.4196 | Abs Value of | Flow this | 143267.9032 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 98.0292 |  |  | 81.2202 |  |  | -17.5381 |  |  | -347.3661 |  |  | -1110.9332 |  |  | -2282.6803 |  |  | -3741.7393 |  |  | -5182.3597 |  |  | -6475.1648 |  |  | -8084.3399
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47288 |  |  | 0.39179 |  |  | -0.084601 |  |  | -1.6756 |  |  | -5.3589 |  |  | -11.0112 |  |  | -18.0495 |  |  | -24.9988 |  |  | -31.235 |  |  | -38.9974
[13 empty] | Delta P at this iteration flow rate |  |  | 48.0292 |  |  | 31.2202 |  |  | -67.5381 |  |  | -397.3661 |  |  | -1160.9332 |  |  | -2332.6803 |  |  | -3791.7393 |  |  | -5232.3597 |  |  | -6525.1648 |  |  | -8134.3399
[13 empty] | Press drop ratio this iteration |  |  | 0.48995 |  |  | 0.38439 |  |  | 3.8509 |  |  | 1.1439 |  |  | 1.045 |  |  | 1.0219 |  |  | 1.0134 |  |  | 1.0096 |  |  | 1.0077 |  |  | 1.0062
[13 empty] | Expansion factor | 12 |  | 0.74483 |  |  | 0.79985 |  |  | -1.0352 |  |  | 0.38713 |  |  | 0.42478 |  |  | 0.40541 |  |  | 0.36969 |  |  | 0.31385 |  |  | 0.43405 |  |  | 0.14215
[13 empty] | C Non choked w/ reducers | 5 |  | 11.1306 |  |  | 39.3202 |  |  | -110.1715 |  |  | 53.4636 |  |  | 26.5278 |  |  | 19.6004 |  |  | 17.2938 |  |  | 18.3392 |  |  | 13.4629 |  |  | 48.3046
[13 empty] | C Choked w/ reducers | 5 |  | 10.8749 |  |  | 36.5373 |  |  | 422.5295 |  |  | 42.0758 |  |  | 22.1932 |  |  | 15.9113 |  |  | 13.1808 |  |  | 12.3807 |  |  | 11.4157 |  |  | 16.5151
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 11.1306 |  |  | 39.3202 |  |  | 422.5295 |  |  | 42.0758 |  |  | 22.1932 |  |  | 15.9113 |  |  | 13.1808 |  |  | 12.3807 |  |  | 11.4157 |  |  | 16.5151
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 9.1306 | 2500.6459 |  | 34.3202 | 6957.4689 |  | 7174 | 17206.6486 |  | 7174 | 33514.1595 |  | 7174 | 55118.4533 |  | 7174 | 77307.8741 |  | 7174 | 98160.4863 |  | 7174 | 115100.89 |  | 7174 | 128414.4196 |  | 7174 | 143267.9032
[13 empty] | Next iteration flow rate |  |  | 2550.6589 | Abs Value of | Flow this | 7027.0436 | Abs Value of | Flow this | 17378.7151 | Abs Value of | Flow this | 33849.3011 | Abs Value of | Flow this | 55669.6378 | Abs Value of | Flow this | 78080.9528 | Abs Value of | Flow this | 99142.0911 | Abs Value of | Flow this | 116251.8989 | Abs Value of | Flow this | 129698.5638 | Abs Value of | Flow this | 144700.5823 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 97.9285 |  |  | 80.8322 |  |  | -19.9112 |  |  | -356.3686 |  |  | -1135.2834 |  |  | -2330.5827 |  |  | -3818.9688 |  |  | -5288.5456 |  |  | -6607.3362 |  |  | -8248.8556
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47239 |  |  | 0.38992 |  |  | -0.096048 |  |  | -1.7191 |  |  | -5.4764 |  |  | -11.2423 |  |  | -18.422 |  |  | -25.511 |  |  | -31.8726 |  |  | -39.791
[13 empty] | Delta P at this iteration flow rate |  |  | 47.9285 |  |  | 30.8322 |  |  | -69.9112 |  |  | -406.3686 |  |  | -1185.2834 |  |  | -2380.5827 |  |  | -3868.9688 |  |  | -5338.5456 |  |  | -6657.3362 |  |  | -8298.8556
[13 empty] | Press drop ratio this iteration |  |  | 0.48942 |  |  | 0.38143 |  |  | 3.5112 |  |  | 1.1403 |  |  | 1.044 |  |  | 1.0215 |  |  | 1.0131 |  |  | 1.0095 |  |  | 1.0076 |  |  | 1.0061
[13 empty] | Expansion factor | 12 |  | 0.7451 |  |  | 0.80139 |  |  | -0.85567 |  |  | 0.38908 |  |  | 0.42531 |  |  | 0.40568 |  |  | 0.36986 |  |  | 0.31398 |  |  | 0.43414 |  |  | 0.14226
[13 empty] | C Non choked w/ reducers | 5 |  | 11.3668 |  |  | 39.9813 |  |  | -124.1857 |  |  | 52.454 |  |  | 26.1978 |  |  | 19.3813 |  |  | 17.108 |  |  | 18.1448 |  |  | 13.3239 |  |  | 47.7823
[13 empty] | C Choked w/ reducers | 5 |  | 11.1038 |  |  | 37.0798 |  |  | 375.8939 |  |  | 41.4231 |  |  | 21.9343 |  |  | 15.7401 |  |  | 13.0434 |  |  | 12.2534 |  |  | 11.2992 |  |  | 16.3475
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 11.3668 |  |  | 39.9813 |  |  | 375.8939 |  |  | 41.4231 |  |  | 21.9343 |  |  | 15.7401 |  |  | 13.0434 |  |  | 12.2534 |  |  | 11.2992 |  |  | 16.3475
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 9.3668 | 2550.6589 |  | 34.9813 | 7027.0436 |  | 7174 | 17378.7151 |  | 7174 | 33849.3011 |  | 7174 | 55669.6378 |  | 7174 | 78080.9528 |  | 7174 | 99142.0911 |  | 7174 | 116251.8989 |  | 7174 | 129698.5638 |  | 7174 | 144700.5823
[13 empty] | Next iteration flow rate |  |  | 2601.672 | Abs Value of | Flow this | 7097.314 | Abs Value of | Flow this | 17552.5022 | Abs Value of | Flow this | 34187.7941 | Abs Value of | Flow this | 56226.3342 | Abs Value of | Flow this | 78861.7623 | Abs Value of | Flow this | 100133.5121 | Abs Value of | Flow this | 117414.4179 | Abs Value of | Flow this | 130995.5495 | Abs Value of | Flow this | 146147.5881 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 97.8237 |  |  | 80.4364 |  |  | -22.3319 |  |  | -365.5521 |  |  | -1160.1231 |  |  | -2379.4479 |  |  | -3897.7506 |  |  | -5396.8659 |  |  | -6742.1641 |  |  | -8416.6781
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47188 |  |  | 0.38801 |  |  | -0.10773 |  |  | -1.7634 |  |  | -5.5962 |  |  | -11.478 |  |  | -18.8021 |  |  | -26.0335 |  |  | -32.523 |  |  | -40.6006
[13 empty] | Delta P at this iteration flow rate |  |  | 47.8237 |  |  | 30.4364 |  |  | -72.3319 |  |  | -415.5521 |  |  | -1210.1231 |  |  | -2429.4479 |  |  | -3947.7506 |  |  | -5446.8659 |  |  | -6792.1641 |  |  | -8466.6781
[13 empty] | Press drop ratio this iteration |  |  | 0.48888 |  |  | 0.37839 |  |  | 3.239 |  |  | 1.1368 |  |  | 1.0431 |  |  | 1.021 |  |  | 1.0128 |  |  | 1.0093 |  |  | 1.0074 |  |  | 1.0059
[13 empty] | Expansion factor | 12 |  | 0.74539 |  |  | 0.80297 |  |  | -0.71181 |  |  | 0.39097 |  |  | 0.42583 |  |  | 0.40593 |  |  | 0.37002 |  |  | 0.31411 |  |  | 0.43422 |  |  | 0.14236
[13 empty] | C Non choked w/ reducers | 5 |  | 11.6086 |  |  | 40.6623 |  |  | -139.9683 |  |  | 51.4778 |  |  | 25.8734 |  |  | 19.1651 |  |  | 16.9245 |  |  | 17.9527 |  |  | 13.1864 |  |  | 47.2664
[13 empty] | C Choked w/ reducers | 5 |  | 11.338 |  |  | 37.6349 |  |  | 338.4994 |  |  | 40.7862 |  |  | 21.6793 |  |  | 15.571 |  |  | 12.9075 |  |  | 12.1275 |  |  | 11.184 |  |  | 16.1818
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 11.6086 |  |  | 40.6623 |  |  | 338.4994 |  |  | 40.7862 |  |  | 21.6793 |  |  | 15.571 |  |  | 12.9075 |  |  | 12.1275 |  |  | 11.184 |  |  | 16.1818
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 9.6086 | 2601.672 |  | 35.6623 | 7097.314 |  | 7174 | 17552.5022 |  | 7174 | 34187.7941 |  | 7174 | 56226.3342 |  | 7174 | 78861.7623 |  | 7174 | 100133.5121 |  | 7174 | 117414.4179 |  | 7174 | 130995.5495 |  | 7174 | 146147.5881
[13 empty] | Next iteration flow rate |  |  | 2653.7055 | Abs Value of | Flow this | 7168.2872 | Abs Value of | Flow this | 17728.0272 | Abs Value of | Flow this | 34529.6721 | Abs Value of | Flow this | 56788.5975 | Abs Value of | Flow this | 79650.3799 | Abs Value of | Flow this | 101134.8472 | Abs Value of | Flow this | 118588.5621 | Abs Value of | Flow this | 132305.505 | Abs Value of | Flow this | 147609.064 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 97.7146 |  |  | 80.0327 |  |  | -24.8013 |  |  | -374.9203 |  |  | -1185.4621 |  |  | -2429.2953 |  |  | -3978.1159 |  |  | -5507.3634 |  |  | -6879.7021 |  |  | -8587.8739
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47136 |  |  | 0.38606 |  |  | -0.11964 |  |  | -1.8085 |  |  | -5.7185 |  |  | -11.7185 |  |  | -19.1897 |  |  | -26.5665 |  |  | -33.1865 |  |  | -41.4264
[13 empty] | Delta P at this iteration flow rate |  |  | 47.7146 |  |  | 30.0327 |  |  | -74.8013 |  |  | -424.9203 |  |  | -1235.4621 |  |  | -2479.2953 |  |  | -4028.1159 |  |  | -5557.3634 |  |  | -6929.7021 |  |  | -8637.8739
[13 empty] | Press drop ratio this iteration |  |  | 0.48831 |  |  | 0.37526 |  |  | 3.016 |  |  | 1.1334 |  |  | 1.0422 |  |  | 1.0206 |  |  | 1.0126 |  |  | 1.0091 |  |  | 1.0073 |  |  | 1.0058
[13 empty] | Expansion factor | 12 |  | 0.74568 |  |  | 0.80461 |  |  | -0.59399 |  |  | 0.3928 |  |  | 0.42634 |  |  | 0.40618 |  |  | 0.37019 |  |  | 0.31424 |  |  | 0.43431 |  |  | 0.14246
[13 empty] | C Non choked w/ reducers | 5 |  | 11.8562 |  |  | 41.3641 |  |  | -158.0776 |  |  | 50.5331 |  |  | 25.5544 |  |  | 18.9519 |  |  | 16.7433 |  |  | 17.763 |  |  | 13.0505 |  |  | 46.757
[13 empty] | C Choked w/ reducers | 5 |  | 11.5776 |  |  | 38.203 |  |  | 307.8441 |  |  | 40.1648 |  |  | 21.4281 |  |  | 15.404 |  |  | 12.7733 |  |  | 12.0031 |  |  | 11.07 |  |  | 16.0178
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 11.8562 |  |  | 41.3641 |  |  | 307.8441 |  |  | 40.1648 |  |  | 21.4281 |  |  | 15.404 |  |  | 12.7733 |  |  | 12.0031 |  |  | 11.07 |  |  | 16.0178
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 9.8562 | 2653.7055 |  | 36.3641 | 7168.2872 |  | 7174 | 17728.0272 |  | 7174 | 34529.6721 |  | 7174 | 56788.5975 |  | 7174 | 79650.3799 |  | 7174 | 101134.8472 |  | 7174 | 118588.5621 |  | 7174 | 132305.505 |  | 7174 | 147609.064
[13 empty] | Next iteration flow rate |  |  | 2706.7796 | Abs Value of | Flow this | 7239.9701 | Abs Value of | Flow this | 17905.3075 | Abs Value of | Flow this | 34874.9688 | Abs Value of | Flow this | 57356.4835 | Abs Value of | Flow this | 80446.8837 | Abs Value of | Flow this | 102146.1957 | Abs Value of | Flow this | 119774.4477 | Abs Value of | Flow this | 133628.56 | Abs Value of | Flow this | 149085.1546 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 97.6012 |  |  | 79.6208 |  |  | -27.3203 |  |  | -384.4767 |  |  | -1211.3104 |  |  | -2480.1446 |  |  | -4060.0965 |  |  | -5620.0819 |  |  | -7020.0047 |  |  | -8762.5106
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47081 |  |  | 0.38408 |  |  | -0.13179 |  |  | -1.8546 |  |  | -5.8431 |  |  | -11.9638 |  |  | -19.5852 |  |  | -27.1103 |  |  | -33.8633 |  |  | -42.2688
[13 empty] | Delta P at this iteration flow rate |  |  | 47.6012 |  |  | 29.6208 |  |  | -77.3203 |  |  | -434.4767 |  |  | -1261.3104 |  |  | -2530.1446 |  |  | -4110.0965 |  |  | -5670.0819 |  |  | -7070.0047 |  |  | -8812.5106
[13 empty] | Press drop ratio this iteration |  |  | 0.48771 |  |  | 0.37202 |  |  | 2.8301 |  |  | 1.13 |  |  | 1.0413 |  |  | 1.0202 |  |  | 1.0123 |  |  | 1.0089 |  |  | 1.0071 |  |  | 1.0057
[13 empty] | Expansion factor | 12 |  | 0.74599 |  |  | 0.80629 |  |  | -0.49575 |  |  | 0.39457 |  |  | 0.42684 |  |  | 0.40643 |  |  | 0.37034 |  |  | 0.31436 |  |  | 0.43439 |  |  | 0.14256
[13 empty] | C Non choked w/ reducers | 5 |  | 12.1097 |  |  | 42.0878 |  |  | -179.2712 |  |  | 49.6185 |  |  | 25.2408 |  |  | 18.7415 |  |  | 16.5643 |  |  | 17.5754 |  |  | 12.9161 |  |  | 46.2539
[13 empty] | C Choked w/ reducers | 5 |  | 11.8229 |  |  | 38.7846 |  |  | 282.2545 |  |  | 39.5581 |  |  | 21.1805 |  |  | 15.2391 |  |  | 12.6405 |  |  | 11.88 |  |  | 10.9573 |  |  | 15.8556
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 12.1097 |  |  | 42.0878 |  |  | 282.2545 |  |  | 39.5581 |  |  | 21.1805 |  |  | 15.2391 |  |  | 12.6405 |  |  | 11.88 |  |  | 10.9573 |  |  | 15.8556
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 10.1097 | 2706.7796 |  | 37.0878 | 7239.9701 |  | 7174 | 17905.3075 |  | 7174 | 34874.9688 |  | 7174 | 57356.4835 |  | 7174 | 80446.8837 |  | 7174 | 102146.1957 |  | 7174 | 119774.4477 |  | 7174 | 133628.56 |  | 7174 | 149085.1546
[13 empty] | Next iteration flow rate |  |  | 2760.9152 | Abs Value of | Flow this | 7312.3698 | Abs Value of | Flow this | 18084.3606 | Abs Value of | Flow this | 35223.7185 | Abs Value of | Flow this | 57930.0483 | Abs Value of | Flow this | 81251.3526 | Abs Value of | Flow this | 103167.6576 | Abs Value of | Flow this | 120972.1922 | Abs Value of | Flow this | 134964.8456 | Abs Value of | Flow this | 150576.0062 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 97.4832 |  |  | 79.2007 |  |  | -29.8899 |  |  | -394.2251 |  |  | -1237.6783 |  |  | -2532.016 |  |  | -4143.725 |  |  | -5735.0661 |  |  | -7163.1273 |  |  | -8940.6576
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.47024 |  |  | 0.38205 |  |  | -0.14418 |  |  | -1.9017 |  |  | -5.9703 |  |  | -12.214 |  |  | -19.9886 |  |  | -27.6649 |  |  | -34.5537 |  |  | -43.1281
[13 empty] | Delta P at this iteration flow rate |  |  | 47.4832 |  |  | 29.2007 |  |  | -79.8899 |  |  | -444.2251 |  |  | -1287.6783 |  |  | -2582.016 |  |  | -4193.725 |  |  | -5785.0661 |  |  | -7213.1273 |  |  | -8990.6576
[13 empty] | Press drop ratio this iteration |  |  | 0.48709 |  |  | 0.36869 |  |  | 2.6728 |  |  | 1.1268 |  |  | 1.0404 |  |  | 1.0197 |  |  | 1.0121 |  |  | 1.0087 |  |  | 1.007 |  |  | 1.0056
[13 empty] | Expansion factor | 12 |  | 0.74632 |  |  | 0.80802 |  |  | -0.4126 |  |  | 0.3963 |  |  | 0.42732 |  |  | 0.40667 |  |  | 0.3705 |  |  | 0.31448 |  |  | 0.43447 |  |  | 0.14266
[13 empty] | C Non choked w/ reducers | 5 |  | 12.3694 |  |  | 42.8347 |  |  | -204.621 |  |  | 48.7323 |  |  | 24.9323 |  |  | 18.5339 |  |  | 16.3875 |  |  | 17.3901 |  |  | 12.7831 |  |  | 45.7571
[13 empty] | C Choked w/ reducers | 5 |  | 12.074 |  |  | 39.3803 |  |  | 260.5689 |  |  | 38.9657 |  |  | 20.9366 |  |  | 15.0762 |  |  | 12.5092 |  |  | 11.7582 |  |  | 10.8457 |  |  | 15.695
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 12.3694 |  |  | 42.8347 |  |  | 260.5689 |  |  | 38.9657 |  |  | 20.9366 |  |  | 15.0762 |  |  | 12.5092 |  |  | 11.7582 |  |  | 10.8457 |  |  | 15.695
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 10.3694 | 2760.9152 |  | 37.8347 | 7312.3698 |  | 7174 | 18084.3606 |  | 7174 | 35223.7185 |  | 7174 | 57930.0483 |  | 7174 | 81251.3526 |  | 7174 | 103167.6576 |  | 7174 | 120972.1922 |  | 7174 | 134964.8456 |  | 7174 | 150576.0062
[13 empty] | Next iteration flow rate |  |  | 2816.1335 | Abs Value of | Flow this | 7385.4935 | Abs Value of | Flow this | 18265.2042 | Abs Value of | Flow this | 35575.9557 | Abs Value of | Flow this | 58509.3488 | Abs Value of | Flow this | 82063.8661 | Abs Value of | Flow this | 104199.3342 | Abs Value of | Flow this | 122181.9141 | Abs Value of | Flow this | 136314.4941 | Abs Value of | Flow this | 152081.7662 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 97.3604 |  |  | 78.7721 |  |  | -32.5112 |  |  | -404.1696 |  |  | -1264.5761 |  |  | -2584.9301 |  |  | -4229.0343 |  |  | -5852.3614 |  |  | -7309.1266 |  |  | -9122.3853
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.46965 |  |  | 0.37998 |  |  | -0.15683 |  |  | -1.9496 |  |  | -6.1001 |  |  | -12.4692 |  |  | -20.4001 |  |  | -28.2307 |  |  | -35.2579 |  |  | -44.0048
[13 empty] | Delta P at this iteration flow rate |  |  | 47.3604 |  |  | 28.7721 |  |  | -82.5112 |  |  | -454.1696 |  |  | -1314.5761 |  |  | -2634.9301 |  |  | -4279.0343 |  |  | -5902.3614 |  |  | -7359.1266 |  |  | -9172.3853
[13 empty] | Press drop ratio this iteration |  |  | 0.48644 |  |  | 0.36526 |  |  | 2.5379 |  |  | 1.1237 |  |  | 1.0395 |  |  | 1.0193 |  |  | 1.0118 |  |  | 1.0085 |  |  | 1.0068 |  |  | 1.0055
[13 empty] | Expansion factor | 12 |  | 0.74665 |  |  | 0.80981 |  |  | -0.34132 |  |  | 0.39797 |  |  | 0.42779 |  |  | 0.4069 |  |  | 0.37065 |  |  | 0.3146 |  |  | 0.43455 |  |  | 0.14275
[13 empty] | C Non choked w/ reducers | 5 |  | 12.6353 |  |  | 43.6059 |  |  | -235.7095 |  |  | 47.8732 |  |  | 24.6289 |  |  | 18.3291 |  |  | 16.2128 |  |  | 17.207 |  |  | 12.6517 |  |  | 45.2664
[13 empty] | C Choked w/ reducers | 5 |  | 12.331 |  |  | 39.9905 |  |  | 241.9555 |  |  | 38.3871 |  |  | 20.6962 |  |  | 14.9152 |  |  | 12.3795 |  |  | 11.6377 |  |  | 10.7354 |  |  | 15.5362
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 12.6353 |  |  | 43.6059 |  |  | 241.9555 |  |  | 38.3871 |  |  | 20.6962 |  |  | 14.9152 |  |  | 12.3795 |  |  | 11.6377 |  |  | 10.7354 |  |  | 15.5362
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 10.6353 | 2816.1335 |  | 38.6059 | 7385.4935 |  | 7174 | 18265.2042 |  | 7174 | 35575.9557 |  | 7174 | 58509.3488 |  | 7174 | 82063.8661 |  | 7174 | 104199.3342 |  | 7174 | 122181.9141 |  | 7174 | 136314.4941 |  | 7174 | 152081.7662
[13 empty] | Next iteration flow rate |  |  | 2872.4562 | Abs Value of | Flow this | 7459.3484 | Abs Value of | Flow this | 18447.8562 | Abs Value of | Flow this | 35931.7152 | Abs Value of | Flow this | 59094.4423 | Abs Value of | Flow this | 82884.5048 | Abs Value of | Flow this | 105241.3275 | Abs Value of | Flow this | 123403.7332 | Abs Value of | Flow this | 137677.639 | Abs Value of | Flow this | 153602.5839 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 97.2326 |  |  | 78.3349 |  |  | -35.1852 |  |  | -414.3139 |  |  | -1292.0146 |  |  | -2638.9077 |  |  | -4316.0584 |  |  | -5972.0144 |  |  | -7458.0606 |  |  | -9307.7658
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.46903 |  |  | 0.37787 |  |  | -0.16973 |  |  | -1.9986 |  |  | -6.2324 |  |  | -12.7296 |  |  | -20.8199 |  |  | -28.8079 |  |  | -35.9764 |  |  | -44.899
[13 empty] | Delta P at this iteration flow rate |  |  | 47.2326 |  |  | 28.3349 |  |  | -85.1852 |  |  | -464.3139 |  |  | -1342.0146 |  |  | -2688.9077 |  |  | -4366.0584 |  |  | -6022.0144 |  |  | -7508.0606 |  |  | -9357.7658
[13 empty] | Press drop ratio this iteration |  |  | 0.48577 |  |  | 0.36172 |  |  | 2.4211 |  |  | 1.1207 |  |  | 1.0387 |  |  | 1.0189 |  |  | 1.0116 |  |  | 1.0084 |  |  | 1.0067 |  |  | 1.0054
[13 empty] | Expansion factor | 12 |  | 0.74701 |  |  | 0.81166 |  |  | -0.27955 |  |  | 0.39959 |  |  | 0.42825 |  |  | 0.40713 |  |  | 0.3708 |  |  | 0.31472 |  |  | 0.43462 |  |  | 0.14284
[13 empty] | C Non choked w/ reducers | 5 |  | 12.9079 |  |  | 44.403 |  |  | -274.9886 |  |  | 47.04 |  |  | 24.3305 |  |  | 18.127 |  |  | 16.0402 |  |  | 17.026 |  |  | 12.5216 |  |  | 44.7817
[13 empty] | C Choked w/ reducers | 5 |  | 12.5941 |  |  | 40.6158 |  |  | 225.8032 |  |  | 37.8216 |  |  | 20.4592 |  |  | 14.7562 |  |  | 12.2512 |  |  | 11.5186 |  |  | 10.6262 |  |  | 15.379
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 12.9079 |  |  | 44.403 |  |  | 225.8032 |  |  | 37.8216 |  |  | 20.4592 |  |  | 14.7562 |  |  | 12.2512 |  |  | 11.5186 |  |  | 10.6262 |  |  | 15.379
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 10.9079 | 2872.4562 |  | 39.403 | 7459.3484 |  | 7174 | 18447.8562 |  | 7174 | 35931.7152 |  | 7174 | 59094.4423 |  | 7174 | 82884.5048 |  | 7174 | 105241.3275 |  | 7174 | 123403.7332 |  | 7174 | 137677.639 |  | 7174 | 153602.5839
[13 empty] | Next iteration flow rate |  |  | 2929.9053 | Abs Value of | Flow this | 7533.9419 | Abs Value of | Flow this | 18632.3348 | Abs Value of | Flow this | 36291.0324 | Abs Value of | Flow this | 59685.3867 | Abs Value of | Flow this | 83713.3498 | Abs Value of | Flow this | 106293.7408 | Abs Value of | Flow this | 124637.7706 | Abs Value of | Flow this | 139054.4154 | Abs Value of | Flow this | 155138.6097 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 97.0997 |  |  | 77.889 |  |  | -37.9129 |  |  | -424.6621 |  |  | -1320.0046 |  |  | -2693.9702 |  |  | -4404.8317 |  |  | -6094.0724 |  |  | -7609.9881 |  |  | -9496.8724
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.46839 |  |  | 0.37572 |  |  | -0.18289 |  |  | -2.0485 |  |  | -6.3675 |  |  | -12.9952 |  |  | -21.2481 |  |  | -29.3967 |  |  | -36.7092 |  |  | -45.8112
[13 empty] | Delta P at this iteration flow rate |  |  | 47.0997 |  |  | 27.889 |  |  | -87.9129 |  |  | -474.6621 |  |  | -1370.0046 |  |  | -2743.9702 |  |  | -4454.8317 |  |  | -6144.0724 |  |  | -7659.9881 |  |  | -9546.8724
[13 empty] | Press drop ratio this iteration |  |  | 0.48507 |  |  | 0.35806 |  |  | 2.3188 |  |  | 1.1177 |  |  | 1.0379 |  |  | 1.0186 |  |  | 1.0114 |  |  | 1.0082 |  |  | 1.0066 |  |  | 1.0053
[13 empty] | Expansion factor | 12 |  | 0.74737 |  |  | 0.81356 |  |  | -0.22551 |  |  | 0.40117 |  |  | 0.42871 |  |  | 0.40736 |  |  | 0.37094 |  |  | 0.31483 |  |  | 0.4347 |  |  | 0.14294
[13 empty] | C Non choked w/ reducers | 5 |  | 13.1871 |  |  | 45.2274 |  |  | -326.4855 |  |  | 46.2313 |  |  | 24.0369 |  |  | 17.9275 |  |  | 15.8697 |  |  | 16.8471 |  |  | 12.3931 |  |  | 44.303
[13 empty] | C Choked w/ reducers | 5 |  | 12.8636 |  |  | 41.2568 |  |  | 211.6528 |  |  | 37.269 |  |  | 20.2257 |  |  | 14.5992 |  |  | 12.1243 |  |  | 11.4008 |  |  | 10.5182 |  |  | 15.2235
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 13.1871 |  |  | 45.2274 |  |  | 211.6528 |  |  | 37.269 |  |  | 20.2257 |  |  | 14.5992 |  |  | 12.1243 |  |  | 11.4008 |  |  | 10.5182 |  |  | 15.2235
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 11.1871 | 2929.9053 |  | 40.2274 | 7533.9419 |  | 7174 | 18632.3348 |  | 7174 | 36291.0324 |  | 7174 | 59685.3867 |  | 7174 | 83713.3498 |  | 7174 | 106293.7408 |  | 7174 | 124637.7706 |  | 7174 | 139054.4154 |  | 7174 | 155138.6097
[13 empty] | Next iteration flow rate |  |  | 2988.5034 | Abs Value of | Flow this | 7609.2813 | Abs Value of | Flow this | 18818.6582 | Abs Value of | Flow this | 36653.9427 | Abs Value of | Flow this | 60282.2406 | Abs Value of | Flow this | 84550.4833 | Abs Value of | Flow this | 107356.6782 | Abs Value of | Flow this | 125884.1483 | Abs Value of | Flow this | 140444.9596 | Abs Value of | Flow this | 156689.9958 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 96.9614 |  |  | 77.434 |  |  | -40.6955 |  |  | -435.2183 |  |  | -1348.5572 |  |  | -2750.1395 |  |  | -4495.3894 |  |  | -6218.5838 |  |  | -7764.9694 |  |  | -9689.78
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.46772 |  |  | 0.37353 |  |  | -0.19631 |  |  | -2.0994 |  |  | -6.5052 |  |  | -13.2662 |  |  | -21.685 |  |  | -29.9973 |  |  | -37.4568 |  |  | -46.7418
[13 empty] | Delta P at this iteration flow rate |  |  | 46.9614 |  |  | 27.434 |  |  | -90.6955 |  |  | -485.2183 |  |  | -1398.5572 |  |  | -2800.1395 |  |  | -4545.3894 |  |  | -6268.5838 |  |  | -7814.9694 |  |  | -9739.78
[13 empty] | Press drop ratio this iteration |  |  | 0.48433 |  |  | 0.35429 |  |  | 2.2286 |  |  | 1.1149 |  |  | 1.0371 |  |  | 1.0182 |  |  | 1.0111 |  |  | 1.008 |  |  | 1.0064 |  |  | 1.0052
[13 empty] | Expansion factor | 12 |  | 0.74775 |  |  | 0.81552 |  |  | -0.17785 |  |  | 0.4027 |  |  | 0.42915 |  |  | 0.40758 |  |  | 0.37108 |  |  | 0.31494 |  |  | 0.43477 |  |  | 0.14303
[13 empty] | C Non choked w/ reducers | 5 |  | 13.4734 |  |  | 46.0807 |  |  | -397.3244 |  |  | 45.446 |  |  | 23.748 |  |  | 17.7307 |  |  | 15.7013 |  |  | 16.6704 |  |  | 12.2659 |  |  | 43.8301
[13 empty] | C Choked w/ reducers | 5 |  | 13.1396 |  |  | 41.9142 |  |  | 199.1528 |  |  | 36.7287 |  |  | 19.9954 |  |  | 14.444 |  |  | 11.9989 |  |  | 11.2843 |  |  | 10.4113 |  |  | 15.0697
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 13.4734 |  |  | 46.0807 |  |  | 199.1528 |  |  | 36.7287 |  |  | 19.9954 |  |  | 14.444 |  |  | 11.9989 |  |  | 11.2843 |  |  | 10.4113 |  |  | 15.0697
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 11.4734 | 2988.5034 |  | 41.0807 | 7609.2813 |  | 7174 | 18818.6582 |  | 7174 | 36653.9427 |  | 7174 | 60282.2406 |  | 7174 | 84550.4833 |  | 7174 | 107356.6782 |  | 7174 | 125884.1483 |  | 7174 | 140444.9596 |  | 7174 | 156689.9958
[13 empty] | Next iteration flow rate |  |  | 3048.2735 | Abs Value of | Flow this | 7685.3741 | Abs Value of | Flow this | 19006.8447 | Abs Value of | Flow this | 37020.4821 | Abs Value of | Flow this | 60885.063 | Abs Value of | Flow this | 85395.9881 | Abs Value of | Flow this | 108430.245 | Abs Value of | Flow this | 127142.9897 | Abs Value of | Flow this | 141849.4092 | Abs Value of | Flow this | 158256.8958 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 96.8175 |  |  | 76.9699 |  |  | -43.534 |  |  | -445.9867 |  |  | -1377.6837 |  |  | -2807.4379 |  |  | -4587.7672 |  |  | -6345.5978 |  |  | -7923.0658 |  |  | -9886.5651
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.46703 |  |  | 0.37129 |  |  | -0.21 |  |  | -2.1514 |  |  | -6.6457 |  |  | -13.5426 |  |  | -22.1306 |  |  | -30.61 |  |  | -38.2195 |  |  | -47.691
[13 empty] | Delta P at this iteration flow rate |  |  | 46.8175 |  |  | 26.9699 |  |  | -93.534 |  |  | -495.9867 |  |  | -1427.6837 |  |  | -2857.4379 |  |  | -4637.7672 |  |  | -6395.5978 |  |  | -7973.0658 |  |  | -9936.5651
[13 empty] | Press drop ratio this iteration |  |  | 0.48356 |  |  | 0.3504 |  |  | 2.1485 |  |  | 1.1121 |  |  | 1.0363 |  |  | 1.0178 |  |  | 1.0109 |  |  | 1.0079 |  |  | 1.0063 |  |  | 1.0051
[13 empty] | Expansion factor | 12 |  | 0.74815 |  |  | 0.81755 |  |  | -0.13551 |  |  | 0.40418 |  |  | 0.42958 |  |  | 0.4078 |  |  | 0.37122 |  |  | 0.31505 |  |  | 0.43484 |  |  | 0.14311
[13 empty] | C Non choked w/ reducers | 5 |  | 13.7668 |  |  | 46.9648 |  |  | -501.4282 |  |  | 44.6832 |  |  | 23.4637 |  |  | 17.5364 |  |  | 15.5349 |  |  | 16.4956 |  |  | 12.1401 |  |  | 43.3629
[13 empty] | C Choked w/ reducers | 5 |  | 13.4223 |  |  | 42.5886 |  |  | 188.0294 |  |  | 36.2003 |  |  | 19.7684 |  |  | 14.2907 |  |  | 11.8748 |  |  | 11.169 |  |  | 10.3056 |  |  | 14.9174
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 13.7668 |  |  | 46.9648 |  |  | 188.0294 |  |  | 36.2003 |  |  | 19.7684 |  |  | 14.2907 |  |  | 11.8748 |  |  | 11.169 |  |  | 10.3056 |  |  | 14.9174
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 11.7668 | 3048.2735 |  | 41.9648 | 7685.3741 |  | 7174 | 19006.8447 |  | 7174 | 37020.4821 |  | 7174 | 60885.063 |  | 7174 | 85395.9881 |  | 7174 | 108430.245 |  | 7174 | 127142.9897 |  | 7174 | 141849.4092 |  | 7174 | 158256.8958
[13 empty] | Next iteration flow rate |  |  | 3109.2389 | Abs Value of | Flow this | 7762.2278 | Abs Value of | Flow this | 19196.9132 | Abs Value of | Flow this | 37390.687 | Abs Value of | Flow this | 61493.9136 | Abs Value of | Flow this | 86249.948 | Abs Value of | Flow this | 109514.5474 | Abs Value of | Flow this | 128414.4196 | Abs Value of | Flow this | 143267.9032 | Abs Value of | Flow this | 159839.4647 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 96.6678 |  |  | 76.4965 |  |  | -46.4295 |  |  | -456.9716 |  |  | -1407.3957 |  |  | -2865.8879 |  |  | -4682.0018 |  |  | -6475.1648 |  |  | -8084.3399 |  |  | -10087.3056
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.46631 |  |  | 0.36901 |  |  | -0.22397 |  |  | -2.2043 |  |  | -6.789 |  |  | -13.8245 |  |  | -22.5851 |  |  | -31.235 |  |  | -38.9974 |  |  | -48.6594
[13 empty] | Delta P at this iteration flow rate |  |  | 46.6678 |  |  | 26.4965 |  |  | -96.4295 |  |  | -506.9716 |  |  | -1457.3957 |  |  | -2915.8879 |  |  | -4732.0018 |  |  | -6525.1648 |  |  | -8134.3399 |  |  | -10137.3056
[13 empty] | Press drop ratio this iteration |  |  | 0.48276 |  |  | 0.34638 |  |  | 2.0769 |  |  | 1.1094 |  |  | 1.0355 |  |  | 1.0174 |  |  | 1.0107 |  |  | 1.0077 |  |  | 1.0062 |  |  | 1.005
[13 empty] | Expansion factor | 12 |  | 0.74857 |  |  | 0.81964 |  |  | -0.097659 |  |  | 0.40563 |  |  | 0.43 |  |  | 0.40801 |  |  | 0.37136 |  |  | 0.31516 |  |  | 0.43491 |  |  | 0.1432
[13 empty] | C Non choked w/ reducers | 5 |  | 14.0677 |  |  | 47.8816 |  |  | -670.1937 |  |  | 43.9416 |  |  | 23.1838 |  |  | 17.3447 |  |  | 15.3705 |  |  | 16.323 |  |  | 12.0157 |  |  | 42.9014
[13 empty] | C Choked w/ reducers | 5 |  | 13.712 |  |  | 43.2807 |  |  | 178.0662 |  |  | 35.6834 |  |  | 19.5446 |  |  | 14.1393 |  |  | 11.7522 |  |  | 11.0549 |  |  | 10.201 |  |  | 14.7667
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 14.0677 |  |  | 47.8816 |  |  | 178.0662 |  |  | 35.6834 |  |  | 19.5446 |  |  | 14.1393 |  |  | 11.7522 |  |  | 11.0549 |  |  | 10.201 |  |  | 14.7667
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 12.0677 | 3109.2389 |  | 42.8816 | 7762.2278 |  | 7174 | 19196.9132 |  | 7174 | 37390.687 |  | 7174 | 61493.9136 |  | 7174 | 86249.948 |  | 7174 | 109514.5474 |  | 7174 | 128414.4196 |  | 7174 | 143267.9032 |  | 7174 | 159839.4647
[13 empty] | Next iteration flow rate |  |  | 3171.4237 | Abs Value of | Flow this | 7839.8501 | Abs Value of | Flow this | 19388.8823 | Abs Value of | Flow this | 37764.5938 | Abs Value of | Flow this | 62108.8528 | Abs Value of | Flow this | 87112.4475 | Abs Value of | Flow this | 110609.6929 | Abs Value of | Flow this | 129698.5638 | Abs Value of | Flow this | 144700.5823 | Abs Value of | Flow this | 161437.8594 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 96.5121 |  |  | 76.0136 |  |  | -49.3833 |  |  | -468.1772 |  |  | -1437.7048 |  |  | -2925.5127 |  |  | -4778.1306 |  |  | -6607.3362 |  |  | -8248.8556 |  |  | -10292.0809
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.46556 |  |  | 0.36668 |  |  | -0.23822 |  |  | -2.2584 |  |  | -6.9352 |  |  | -14.1122 |  |  | -23.0489 |  |  | -31.8726 |  |  | -39.791 |  |  | -49.6472
[13 empty] | Delta P at this iteration flow rate |  |  | 46.5121 |  |  | 26.0136 |  |  | -99.3833 |  |  | -518.1772 |  |  | -1487.7048 |  |  | -2975.5127 |  |  | -4828.1306 |  |  | -6657.3362 |  |  | -8298.8556 |  |  | -10342.0809
[13 empty] | Press drop ratio this iteration |  |  | 0.48193 |  |  | 0.34222 |  |  | 2.0125 |  |  | 1.1068 |  |  | 1.0348 |  |  | 1.0171 |  |  | 1.0105 |  |  | 1.0076 |  |  | 1.0061 |  |  | 1.0049
[13 empty] | Expansion factor | 12 |  | 0.74901 |  |  | 0.82181 |  |  | -0.063617 |  |  | 0.40703 |  |  | 0.43041 |  |  | 0.40821 |  |  | 0.37149 |  |  | 0.31526 |  |  | 0.43498 |  |  | 0.14328
[13 empty] | C Non choked w/ reducers | 5 |  | 14.3763 |  |  | 48.8332 |  |  | -992.4737 |  |  | 43.2205 |  |  | 22.9083 |  |  | 17.1554 |  |  | 15.208 |  |  | 16.1523 |  |  | 11.8926 |  |  | 42.4455
[13 empty] | C Choked w/ reducers | 5 |  | 14.0088 |  |  | 43.9912 |  |  | 169.0897 |  |  | 35.1776 |  |  | 19.3239 |  |  | 13.9896 |  |  | 11.6309 |  |  | 10.9421 |  |  | 10.0976 |  |  | 14.6177
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 14.3763 |  |  | 48.8332 |  |  | 169.0897 |  |  | 35.1776 |  |  | 19.3239 |  |  | 13.9896 |  |  | 11.6309 |  |  | 10.9421 |  |  | 10.0976 |  |  | 14.6177
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 12.3763 | 3171.4237 |  | 43.8332 | 7839.8501 |  | 7174 | 19388.8823 |  | 7174 | 37764.5938 |  | 7174 | 62108.8528 |  | 7174 | 87112.4475 |  | 7174 | 110609.6929 |  | 7174 | 129698.5638 |  | 7174 | 144700.5823 |  | 7174 | 161437.8594
[13 empty] | Next iteration flow rate |  |  | 3234.8522 | Abs Value of | Flow this | 7918.2486 | Abs Value of | Flow this | 19582.7711 | Abs Value of | Flow this | 38142.2398 | Abs Value of | Flow this | 62729.9413 | Abs Value of | Flow this | 87983.572 | Abs Value of | Flow this | 111715.7898 | Abs Value of | Flow this | 130995.5495 | Abs Value of | Flow this | 146147.5881 | Abs Value of | Flow this | 163052.238 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 96.35 |  |  | 75.521 |  |  | -52.3964 |  |  | -479.6081 |  |  | -1468.6232 |  |  | -2986.336 |  |  | -4876.1915 |  |  | -6742.1641 |  |  | -8416.6781 |  |  | -10500.9723
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.46478 |  |  | 0.3643 |  |  | -0.25275 |  |  | -2.3135 |  |  | -7.0844 |  |  | -14.4056 |  |  | -23.5219 |  |  | -32.523 |  |  | -40.6006 |  |  | -50.6548
[13 empty] | Delta P at this iteration flow rate |  |  | 46.35 |  |  | 25.521 |  |  | -102.3964 |  |  | -529.6081 |  |  | -1518.6232 |  |  | -3036.336 |  |  | -4926.1915 |  |  | -6792.1641 |  |  | -8466.6781 |  |  | -10550.9723
[13 empty] | Press drop ratio this iteration |  |  | 0.48106 |  |  | 0.33793 |  |  | 1.9543 |  |  | 1.1043 |  |  | 1.034 |  |  | 1.0167 |  |  | 1.0103 |  |  | 1.0074 |  |  | 1.0059 |  |  | 1.0048
[13 empty] | Expansion factor | 12 |  | 0.74946 |  |  | 0.82404 |  |  | -0.032845 |  |  | 0.40839 |  |  | 0.43082 |  |  | 0.40842 |  |  | 0.37163 |  |  | 0.31537 |  |  | 0.43505 |  |  | 0.14336
[13 empty] | C Non choked w/ reducers | 5 |  | 14.6929 |  |  | 49.822 |  |  | -1856.9506 |  |  | 42.519 |  |  | 22.6371 |  |  | 16.9685 |  |  | 15.0474 |  |  | 15.9835 |  |  | 11.7709 |  |  | 41.995
[13 empty] | C Choked w/ reducers | 5 |  | 14.313 |  |  | 44.7209 |  |  | 160.9597 |  |  | 34.6826 |  |  | 19.1062 |  |  | 13.8417 |  |  | 11.511 |  |  | 10.8305 |  |  | 9.9952 |  |  | 14.4702
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 14.6929 |  |  | 49.822 |  |  | 160.9597 |  |  | 34.6826 |  |  | 19.1062 |  |  | 13.8417 |  |  | 11.511 |  |  | 10.8305 |  |  | 9.9952 |  |  | 14.4702
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 12.6929 | 3234.8522 |  | 44.822 | 7918.2486 |  | 7174 | 19582.7711 |  | 7174 | 38142.2398 |  | 7174 | 62729.9413 |  | 7174 | 87983.572 |  | 7174 | 111715.7898 |  | 7174 | 130995.5495 |  | 7174 | 146147.5881 |  | 7174 | 163052.238
[13 empty] | Next iteration flow rate |  |  | 3299.5492 | Abs Value of | Flow this | 7997.4311 | Abs Value of | Flow this | 19778.5989 | Abs Value of | Flow this | 38523.6622 | Abs Value of | Flow this | 63357.2407 | Abs Value of | Flow this | 88863.4077 | Abs Value of | Flow this | 112832.9477 | Abs Value of | Flow this | 132305.505 | Abs Value of | Flow this | 147609.064 | Abs Value of | Flow this | 164682.7604 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 96.1815 |  |  | 75.0184 |  |  | -55.47 |  |  | -491.2687 |  |  | -1500.163 |  |  | -3048.3819 |  |  | -4976.2235 |  |  | -6879.7021 |  |  | -8587.8739 |  |  | -10714.0623
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.46396 |  |  | 0.36188 |  |  | -0.26758 |  |  | -2.3698 |  |  | -7.2365 |  |  | -14.7049 |  |  | -24.0044 |  |  | -33.1865 |  |  | -41.4264 |  |  | -51.6827
[13 empty] | Delta P at this iteration flow rate |  |  | 46.1815 |  |  | 25.0184 |  |  | -105.47 |  |  | -541.2687 |  |  | -1550.163 |  |  | -3098.3819 |  |  | -5026.2235 |  |  | -6929.7021 |  |  | -8637.8739 |  |  | -10764.0623
[13 empty] | Press drop ratio this iteration |  |  | 0.48015 |  |  | 0.3335 |  |  | 1.9014 |  |  | 1.1018 |  |  | 1.0333 |  |  | 1.0164 |  |  | 1.01 |  |  | 1.0073 |  |  | 1.0058 |  |  | 1.0047
[13 empty] | Expansion factor | 12 |  | 0.74993 |  |  | 0.82635 |  |  | -0.0048986 |  |  | 0.40972 |  |  | 0.43121 |  |  | 0.40861 |  |  | 0.37175 |  |  | 0.31547 |  |  | 0.43512 |  |  | 0.14345
[13 empty] | C Non choked w/ reducers | 5 |  | 15.0178 |  |  | 50.8505 |  |  | -12042.3583 |  |  | 41.8361 |  |  | 22.3701 |  |  | 16.784 |  |  | 14.8888 |  |  | 15.8167 |  |  | 11.6506 |  |  | 41.5499
[13 empty] | C Choked w/ reducers | 5 |  | 14.6248 |  |  | 45.4707 |  |  | 153.5611 |  |  | 34.198 |  |  | 18.8916 |  |  | 13.6956 |  |  | 11.3924 |  |  | 10.7202 |  |  | 9.8939 |  |  | 14.3242
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 15.0178 |  |  | 50.8505 |  |  | 153.5611 |  |  | 34.198 |  |  | 18.8916 |  |  | 13.6956 |  |  | 11.3924 |  |  | 10.7202 |  |  | 9.8939 |  |  | 14.3242
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 13.0178 | 3299.5492 |  | 45.8505 | 7997.4311 |  | 7174 | 19778.5989 |  | 7174 | 38523.6622 |  | 7174 | 63357.2407 |  | 7174 | 88863.4077 |  | 7174 | 112832.9477 |  | 7174 | 132305.505 |  | 7174 | 147609.064 |  | 7174 | 164682.7604
[13 empty] | Next iteration flow rate |  |  | 3365.5402 | Abs Value of | Flow this | 8077.4054 | Abs Value of | Flow this | 19976.3848 | Abs Value of | Flow this | 38908.8988 | Abs Value of | Flow this | 63990.8131 | Abs Value of | Flow this | 89752.0418 | Abs Value of | Flow this | 113961.2772 | Abs Value of | Flow this | 133628.56 | Abs Value of | Flow this | 149085.1546 | Abs Value of | Flow this | 166329.588 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 96.0061 |  |  | 74.5058 |  |  | -58.6055 |  |  | -503.1637 |  |  | -1532.3368 |  |  | -3111.6749 |  |  | -5078.2661 |  |  | -7020.0047 |  |  | -8762.5106 |  |  | -10931.4355
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.46312 |  |  | 0.3594 |  |  | -0.2827 |  |  | -2.4272 |  |  | -7.3917 |  |  | -15.0102 |  |  | -24.4967 |  |  | -33.8633 |  |  | -42.2688 |  |  | -52.7313
[13 empty] | Delta P at this iteration flow rate |  |  | 46.0061 |  |  | 24.5058 |  |  | -108.6055 |  |  | -553.1637 |  |  | -1582.3368 |  |  | -3161.6749 |  |  | -5128.2661 |  |  | -7070.0047 |  |  | -8812.5106 |  |  | -10981.4355
[13 empty] | Press drop ratio this iteration |  |  | 0.4792 |  |  | 0.32891 |  |  | 1.8532 |  |  | 1.0994 |  |  | 1.0326 |  |  | 1.0161 |  |  | 1.0098 |  |  | 1.0071 |  |  | 1.0057 |  |  | 1.0046
[13 empty] | Expansion factor | 12 |  | 0.75043 |  |  | 0.82874 |  |  | 0.020589 |  |  | 0.41101 |  |  | 0.4316 |  |  | 0.40881 |  |  | 0.37188 |  |  | 0.31556 |  |  | 0.43518 |  |  | 0.14352
[13 empty] | C Non choked w/ reducers | 5 |  | 15.3512 |  |  | 51.9216 |  |  | 2774.4363 |  |  | 41.1711 |  |  | 22.1072 |  |  | 16.6019 |  |  | 14.732 |  |  | 15.6519 |  |  | 11.5315 |  |  | 41.1102
[13 empty] | C Choked w/ reducers | 5 |  | 14.9446 |  |  | 46.2414 |  |  | 146.7988 |  |  | 33.7234 |  |  | 18.6799 |  |  | 13.5512 |  |  | 11.2751 |  |  | 10.611 |  |  | 9.7937 |  |  | 14.1797
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 15.3512 |  |  | 51.9216 |  |  | 146.7988 |  |  | 33.7234 |  |  | 18.6799 |  |  | 13.5512 |  |  | 11.2751 |  |  | 10.611 |  |  | 9.7937 |  |  | 14.1797
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 13.3512 | 3365.5402 |  | 46.9216 | 8077.4054 |  | 7174 | 19976.3848 |  | 7174 | 38908.8988 |  | 7174 | 63990.8131 |  | 7174 | 89752.0418 |  | 7174 | 113961.2772 |  | 7174 | 133628.56 |  | 7174 | 149085.1546 |  | 7174 | 166329.588
[13 empty] | Next iteration flow rate |  |  | 3432.851 | Abs Value of | Flow this | 8158.1795 | Abs Value of | Flow this | 20176.1487 | Abs Value of | Flow this | 39297.9878 | Abs Value of | Flow this | 64630.7212 | Abs Value of | Flow this | 90649.5622 | Abs Value of | Flow this | 115100.89 | Abs Value of | Flow this | 134964.8456 | Abs Value of | Flow this | 150576.0062 | Abs Value of | Flow this | 167992.8839 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 95.8236 |  |  | 73.9828 |  |  | -61.804 |  |  | -515.2978 |  |  | -1565.1573 |  |  | -3176.24 |  |  | -5182.3597 |  |  | -7163.1273 |  |  | -8940.6576 |  |  | -11153.1779
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.46224 |  |  | 0.35688 |  |  | -0.29813 |  |  | -2.4857 |  |  | -7.55 |  |  | -15.3216 |  |  | -24.9988 |  |  | -34.5537 |  |  | -43.1281 |  |  | -53.8009
[13 empty] | Delta P at this iteration flow rate |  |  | 45.8236 |  |  | 23.9828 |  |  | -111.804 |  |  | -565.2978 |  |  | -1615.1573 |  |  | -3226.24 |  |  | -5232.3597 |  |  | -7213.1273 |  |  | -8990.6576 |  |  | -11203.1779
[13 empty] | Press drop ratio this iteration |  |  | 0.47821 |  |  | 0.32417 |  |  | 1.809 |  |  | 1.097 |  |  | 1.0319 |  |  | 1.0157 |  |  | 1.0096 |  |  | 1.007 |  |  | 1.0056 |  |  | 1.0045
[13 empty] | Expansion factor | 12 |  | 0.75094 |  |  | 0.83121 |  |  | 0.043924 |  |  | 0.41226 |  |  | 0.43197 |  |  | 0.409 |  |  | 0.372 |  |  | 0.31566 |  |  | 0.43525 |  |  | 0.1436
[13 empty] | C Non choked w/ reducers | 5 |  | 15.6935 |  |  | 53.0384 |  |  | 1260.6193 |  |  | 40.5233 |  |  | 21.8482 |  |  | 16.4221 |  |  | 14.5771 |  |  | 15.4889 |  |  | 11.4137 |  |  | 40.6756
[13 empty] | C Choked w/ reducers | 5 |  | 15.2725 |  |  | 47.034 |  |  | 140.5937 |  |  | 33.2586 |  |  | 18.471 |  |  | 13.4085 |  |  | 11.1591 |  |  | 10.5029 |  |  | 9.6945 |  |  | 14.0368
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 15.6935 |  |  | 53.0384 |  |  | 140.5937 |  |  | 33.2586 |  |  | 18.471 |  |  | 13.4085 |  |  | 11.1591 |  |  | 10.5029 |  |  | 9.6945 |  |  | 14.0368
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 13.6935 | 3432.851 |  | 48.0384 | 8158.1795 |  | 7174 | 20176.1487 |  | 7174 | 39297.9878 |  | 7174 | 64630.7212 |  | 7174 | 90649.5622 |  | 7174 | 115100.89 |  | 7174 | 134964.8456 |  | 7174 | 150576.0062 |  | 7174 | 167992.8839
[13 empty] | Next iteration flow rate |  |  | 3501.508 | Abs Value of | Flow this | 8239.7613 | Abs Value of | Flow this | 20377.9102 | Abs Value of | Flow this | 39690.9677 | Abs Value of | Flow this | 65277.0284 | Abs Value of | Flow this | 91556.0578 | Abs Value of | Flow this | 116251.8989 | Abs Value of | Flow this | 136314.4941 | Abs Value of | Flow this | 152081.7662 | Abs Value of | Flow this | 169672.8127 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 95.6337 |  |  | 73.4494 |  |  | -65.0667 |  |  | -527.6758 |  |  | -1598.6375 |  |  | -3242.103 |  |  | -5288.5456 |  |  | -7309.1266 |  |  | -9122.3853 |  |  | -11379.3772
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.46132 |  |  | 0.35431 |  |  | -0.31387 |  |  | -2.5454 |  |  | -7.7115 |  |  | -15.6393 |  |  | -25.511 |  |  | -35.2579 |  |  | -44.0048 |  |  | -54.8921
[13 empty] | Delta P at this iteration flow rate |  |  | 45.6337 |  |  | 23.4494 |  |  | -115.0667 |  |  | -577.6758 |  |  | -1648.6375 |  |  | -3292.103 |  |  | -5338.5456 |  |  | -7359.1266 |  |  | -9172.3853 |  |  | -11429.3772
[13 empty] | Press drop ratio this iteration |  |  | 0.47717 |  |  | 0.31926 |  |  | 1.7684 |  |  | 1.0948 |  |  | 1.0313 |  |  | 1.0154 |  |  | 1.0095 |  |  | 1.0068 |  |  | 1.0055 |  |  | 1.0044
[13 empty] | Expansion factor | 12 |  | 0.75148 |  |  | 0.83376 |  |  | 0.065364 |  |  | 0.41348 |  |  | 0.43234 |  |  | 0.40918 |  |  | 0.37212 |  |  | 0.31576 |  |  | 0.43531 |  |  | 0.14368
[13 empty] | C Non choked w/ reducers | 5 |  | 16.045 |  |  | 54.2044 |  |  | 821.9553 |  |  | 39.892 |  |  | 21.5932 |  |  | 16.2445 |  |  | 14.4239 |  |  | 15.3277 |  |  | 11.2972 |  |  | 40.2462
[13 empty] | C Choked w/ reducers | 5 |  | 15.6089 |  |  | 47.8493 |  |  | 134.8791 |  |  | 32.8032 |  |  | 18.265 |  |  | 13.2674 |  |  | 11.0444 |  |  | 10.3961 |  |  | 9.5964 |  |  | 13.8954
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 16.045 |  |  | 54.2044 |  |  | 134.8791 |  |  | 32.8032 |  |  | 18.265 |  |  | 13.2674 |  |  | 11.0444 |  |  | 10.3961 |  |  | 9.5964 |  |  | 13.8954
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 14.045 | 3501.508 |  | 49.2044 | 8239.7613 |  | 7174 | 20377.9102 |  | 7174 | 39690.9677 |  | 7174 | 65277.0284 |  | 7174 | 91556.0578 |  | 7174 | 116251.8989 |  | 7174 | 136314.4941 |  | 7174 | 152081.7662 |  | 7174 | 169672.8127
[13 empty] | Next iteration flow rate |  |  | 3571.5382 | Abs Value of | Flow this | 8322.1589 | Abs Value of | Flow this | 20581.6893 | Abs Value of | Flow this | 40087.8773 | Abs Value of | Flow this | 65929.7987 | Abs Value of | Flow this | 92471.6184 | Abs Value of | Flow this | 117414.4179 | Abs Value of | Flow this | 137677.639 | Abs Value of | Flow this | 153602.5839 | Abs Value of | Flow this | 171369.5408 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 95.4362 |  |  | 72.9052 |  |  | -68.3951 |  |  | -540.3026 |  |  | -1632.7906 |  |  | -3309.2898 |  |  | -5396.8659 |  |  | -7458.0606 |  |  | -9307.7658 |  |  | -11610.1232
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.46037 |  |  | 0.35168 |  |  | -0.32993 |  |  | -2.6063 |  |  | -7.8763 |  |  | -15.9634 |  |  | -26.0335 |  |  | -35.9764 |  |  | -44.899 |  |  | -56.0052
[13 empty] | Delta P at this iteration flow rate |  |  | 45.4362 |  |  | 22.9052 |  |  | -118.3951 |  |  | -590.3026 |  |  | -1682.7906 |  |  | -3359.2898 |  |  | -5446.8659 |  |  | -7508.0606 |  |  | -9357.7658 |  |  | -11660.1232
[13 empty] | Press drop ratio this iteration |  |  | 0.47609 |  |  | 0.31418 |  |  | 1.731 |  |  | 1.0925 |  |  | 1.0306 |  |  | 1.0151 |  |  | 1.0093 |  |  | 1.0067 |  |  | 1.0054 |  |  | 1.0043
[13 empty] | Expansion factor | 12 |  | 0.75205 |  |  | 0.83641 |  |  | 0.085128 |  |  | 0.41467 |  |  | 0.4327 |  |  | 0.40937 |  |  | 0.37224 |  |  | 0.31585 |  |  | 0.43537 |  |  | 0.14375
[13 empty] | C Non choked w/ reducers | 5 |  | 16.4061 |  |  | 55.4234 |  |  | 612.9333 |  |  | 39.2765 |  |  | 21.3419 |  |  | 16.0692 |  |  | 14.2726 |  |  | 15.1684 |  |  | 11.1819 |  |  | 39.8219
[13 empty] | C Choked w/ reducers | 5 |  | 15.954 |  |  | 48.6885 |  |  | 129.5986 |  |  | 32.357 |  |  | 18.0618 |  |  | 13.1281 |  |  | 10.9309 |  |  | 10.2904 |  |  | 9.4993 |  |  | 13.7554
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 16.4061 |  |  | 55.4234 |  |  | 129.5986 |  |  | 32.357 |  |  | 18.0618 |  |  | 13.1281 |  |  | 10.9309 |  |  | 10.2904 |  |  | 9.4993 |  |  | 13.7554
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 14.4061 | 3571.5382 |  | 50.4234 | 8322.1589 |  | 7174 | 20581.6893 |  | 7174 | 40087.8773 |  | 7174 | 65929.7987 |  | 7174 | 92471.6184 |  | 7174 | 117414.4179 |  | 7174 | 137677.639 |  | 7174 | 153602.5839 |  | 7174 | 171369.5408
[13 empty] | Next iteration flow rate |  |  | 3642.9689 | Abs Value of | Flow this | 8405.3805 | Abs Value of | Flow this | 20787.5062 | Abs Value of | Flow this | 40488.7561 | Abs Value of | Flow this | 66589.0967 | Abs Value of | Flow this | 93396.3346 | Abs Value of | Flow this | 118588.5621 | Abs Value of | Flow this | 139054.4154 | Abs Value of | Flow this | 155138.6097 | Abs Value of | Flow this | 173083.2362 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 95.2307 |  |  | 72.3501 |  |  | -71.7903 |  |  | -553.1832 |  |  | -1667.6302 |  |  | -3377.827 |  |  | -5507.3634 |  |  | -7609.9881 |  |  | -9496.8724 |  |  | -11845.5072
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.45938 |  |  | 0.349 |  |  | -0.3463 |  |  | -2.6685 |  |  | -8.0444 |  |  | -16.294 |  |  | -26.5665 |  |  | -36.7092 |  |  | -45.8112 |  |  | -57.1406
[13 empty] | Delta P at this iteration flow rate |  |  | 45.2307 |  |  | 22.3501 |  |  | -121.7903 |  |  | -603.1832 |  |  | -1717.6302 |  |  | -3427.827 |  |  | -5557.3634 |  |  | -7659.9881 |  |  | -9546.8724 |  |  | -11895.5072
[13 empty] | Press drop ratio this iteration |  |  | 0.47496 |  |  | 0.30892 |  |  | 1.6965 |  |  | 1.0904 |  |  | 1.03 |  |  | 1.0148 |  |  | 1.0091 |  |  | 1.0066 |  |  | 1.0053 |  |  | 1.0042
[13 empty] | Expansion factor | 12 |  | 0.75264 |  |  | 0.83915 |  |  | 0.1034 |  |  | 0.41582 |  |  | 0.43305 |  |  | 0.40955 |  |  | 0.37236 |  |  | 0.31594 |  |  | 0.43543 |  |  | 0.14383
[13 empty] | C Non choked w/ reducers | 5 |  | 16.7771 |  |  | 56.6998 |  |  | 490.4824 |  |  | 38.6762 |  |  | 21.0944 |  |  | 15.8961 |  |  | 14.123 |  |  | 15.0109 |  |  | 11.0679 |  |  | 39.4026
[13 empty] | C Choked w/ reducers | 5 |  | 16.3082 |  |  | 49.5527 |  |  | 124.704 |  |  | 31.9196 |  |  | 17.8613 |  |  | 12.9903 |  |  | 10.8188 |  |  | 10.1858 |  |  | 9.4033 |  |  | 13.6169
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 16.7771 |  |  | 56.6998 |  |  | 124.704 |  |  | 31.9196 |  |  | 17.8613 |  |  | 12.9903 |  |  | 10.8188 |  |  | 10.1858 |  |  | 9.4033 |  |  | 13.6169
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 14.7771 | 3642.9689 |  | 51.6998 | 8405.3805 |  | 7174 | 20787.5062 |  | 7174 | 40488.7561 |  | 7174 | 66589.0967 |  | 7174 | 93396.3346 |  | 7174 | 118588.5621 |  | 7174 | 139054.4154 |  | 7174 | 155138.6097 |  | 7174 | 173083.2362
[13 empty] | Next iteration flow rate |  |  | 3715.8283 | Abs Value of | Flow this | 8489.4343 | Abs Value of | Flow this | 20995.3812 | Abs Value of | Flow this | 40893.6437 | Abs Value of | Flow this | 67254.9877 | Abs Value of | Flow this | 94330.2979 | Abs Value of | Flow this | 119774.4477 | Abs Value of | Flow this | 140444.9596 | Abs Value of | Flow this | 156689.9958 | Abs Value of | Flow this | 174814.0686 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 95.0169 |  |  | 71.7838 |  |  | -75.2538 |  |  | -566.3227 |  |  | -1703.1701 |  |  | -3447.7418 |  |  | -5620.0819 |  |  | -7764.9694 |  |  | -9689.78 |  |  | -12085.6224
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.45834 |  |  | 0.34627 |  |  | -0.36301 |  |  | -2.7318 |  |  | -8.2158 |  |  | -16.6313 |  |  | -27.1103 |  |  | -37.4568 |  |  | -46.7418 |  |  | -58.2989
[13 empty] | Delta P at this iteration flow rate |  |  | 45.0169 |  |  | 21.7838 |  |  | -125.2538 |  |  | -616.3227 |  |  | -1753.1701 |  |  | -3497.7418 |  |  | -5670.0819 |  |  | -7814.9694 |  |  | -9739.78 |  |  | -12135.6224
[13 empty] | Press drop ratio this iteration |  |  | 0.47378 |  |  | 0.30346 |  |  | 1.6644 |  |  | 1.0883 |  |  | 1.0294 |  |  | 1.0145 |  |  | 1.0089 |  |  | 1.0064 |  |  | 1.0052 |  |  | 1.0041
[13 empty] | Expansion factor | 12 |  | 0.75325 |  |  | 0.84199 |  |  | 0.12034 |  |  | 0.41694 |  |  | 0.4334 |  |  | 0.40972 |  |  | 0.37247 |  |  | 0.31603 |  |  | 0.43549 |  |  | 0.1439
[13 empty] | C Non choked w/ reducers | 5 |  | 17.1585 |  |  | 58.0383 |  |  | 409.9504 |  |  | 38.0904 |  |  | 20.8505 |  |  | 15.7251 |  |  | 13.9752 |  |  | 14.8552 |  |  | 10.9552 |  |  | 38.9882
[13 empty] | C Choked w/ reducers | 5 |  | 16.6718 |  |  | 50.4431 |  |  | 120.1543 |  |  | 31.4908 |  |  | 17.6635 |  |  | 12.8541 |  |  | 10.7078 |  |  | 10.0823 |  |  | 9.3082 |  |  | 13.4798
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 17.1585 |  |  | 58.0383 |  |  | 120.1543 |  |  | 31.4908 |  |  | 17.6635 |  |  | 12.8541 |  |  | 10.7078 |  |  | 10.0823 |  |  | 9.3082 |  |  | 13.4798
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 15.1585 | 3715.8283 |  | 53.0383 | 8489.4343 |  | 7174 | 20995.3812 |  | 7174 | 40893.6437 |  | 7174 | 67254.9877 |  | 7174 | 94330.2979 |  | 7174 | 119774.4477 |  | 7174 | 140444.9596 |  | 7174 | 156689.9958 |  | 7174 | 174814.0686
[13 empty] | Next iteration flow rate |  |  | 3790.1449 | Abs Value of | Flow this | 8574.3286 | Abs Value of | Flow this | 21205.335 | Abs Value of | Flow this | 41302.5801 | Abs Value of | Flow this | 67927.5376 | Abs Value of | Flow this | 95273.6009 | Abs Value of | Flow this | 120972.1922 | Abs Value of | Flow this | 141849.4092 | Abs Value of | Flow this | 158256.8958 | Abs Value of | Flow this | 176562.2093 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 94.7945 |  |  | 71.2062 |  |  | -78.7869 |  |  | -579.7263 |  |  | -1739.4243 |  |  | -3519.0619 |  |  | -5735.0661 |  |  | -7923.0658 |  |  | -9886.5651 |  |  | -12330.5639
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.45727 |  |  | 0.34349 |  |  | -0.38005 |  |  | -2.7965 |  |  | -8.3907 |  |  | -16.9753 |  |  | -27.6649 |  |  | -38.2195 |  |  | -47.691 |  |  | -59.4804
[13 empty] | Delta P at this iteration flow rate |  |  | 44.7945 |  |  | 21.2062 |  |  | -128.7869 |  |  | -629.7263 |  |  | -1789.4243 |  |  | -3569.0619 |  |  | -5785.0661 |  |  | -7973.0658 |  |  | -9936.5651 |  |  | -12380.5639
[13 empty] | Press drop ratio this iteration |  |  | 0.47254 |  |  | 0.29781 |  |  | 1.6346 |  |  | 1.0862 |  |  | 1.0287 |  |  | 1.0142 |  |  | 1.0087 |  |  | 1.0063 |  |  | 1.0051 |  |  | 1.0041
[13 empty] | Expansion factor | 12 |  | 0.75389 |  |  | 0.84493 |  |  | 0.13609 |  |  | 0.41804 |  |  | 0.43373 |  |  | 0.40989 |  |  | 0.37258 |  |  | 0.31612 |  |  | 0.43555 |  |  | 0.14397
[13 empty] | C Non choked w/ reducers | 5 |  | 17.5507 |  |  | 59.4445 |  |  | 352.8936 |  |  | 37.5187 |  |  | 20.6102 |  |  | 15.5562 |  |  | 13.829 |  |  | 14.7013 |  |  | 10.8436 |  |  | 38.5786
[13 empty] | C Choked w/ reducers | 5 |  | 17.0451 |  |  | 51.3608 |  |  | 115.9138 |  |  | 31.0703 |  |  | 17.4683 |  |  | 12.7196 |  |  | 10.598 |  |  | 9.9799 |  |  | 9.2142 |  |  | 13.3441
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 17.5507 |  |  | 59.4445 |  |  | 115.9138 |  |  | 31.0703 |  |  | 17.4683 |  |  | 12.7196 |  |  | 10.598 |  |  | 9.9799 |  |  | 9.2142 |  |  | 13.3441
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 15.5507 | 3790.1449 |  | 54.4445 | 8574.3286 |  | 7174 | 21205.335 |  | 7174 | 41302.5801 |  | 7174 | 67927.5376 |  | 7174 | 95273.6009 |  | 7174 | 120972.1922 |  | 7174 | 141849.4092 |  | 7174 | 158256.8958 |  | 7174 | 176562.2093
[13 empty] | Next iteration flow rate |  |  | 3865.9478 | Abs Value of | Flow this | 8660.0719 | Abs Value of | Flow this | 21417.3884 | Abs Value of | Flow this | 41715.6059 | Abs Value of | Flow this | 68606.8129 | Abs Value of | Flow this | 96226.3369 | Abs Value of | Flow this | 122181.9141 | Abs Value of | Flow this | 143267.9032 | Abs Value of | Flow this | 159839.4647 | Abs Value of | Flow this | 178327.8314 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 94.5631 |  |  | 70.6169 |  |  | -82.3911 |  |  | -593.3993 |  |  | -1776.4072 |  |  | -3591.8156 |  |  | -5852.3614 |  |  | -8084.3399 |  |  | -10087.3056 |  |  | -12580.4288
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.45616 |  |  | 0.34064 |  |  | -0.39744 |  |  | -2.8625 |  |  | -8.5691 |  |  | -17.3263 |  |  | -28.2307 |  |  | -38.9974 |  |  | -48.6594 |  |  | -60.6857
[13 empty] | Delta P at this iteration flow rate |  |  | 44.5631 |  |  | 20.6169 |  |  | -132.3911 |  |  | -643.3993 |  |  | -1826.4072 |  |  | -3641.8156 |  |  | -5902.3614 |  |  | -8134.3399 |  |  | -10137.3056 |  |  | -12630.4288
[13 empty] | Press drop ratio this iteration |  |  | 0.47125 |  |  | 0.29195 |  |  | 1.6069 |  |  | 1.0843 |  |  | 1.0281 |  |  | 1.0139 |  |  | 1.0085 |  |  | 1.0062 |  |  | 1.005 |  |  | 1.004
[13 empty] | Expansion factor | 12 |  | 0.75457 |  |  | 0.84798 |  |  | 0.15076 |  |  | 0.4191 |  |  | 0.43406 |  |  | 0.41006 |  |  | 0.37269 |  |  | 0.3162 |  |  | 0.4356 |  |  | 0.14404
[13 empty] | C Non choked w/ reducers | 5 |  | 17.954 |  |  | 60.9245 |  |  | 310.308 |  |  | 36.9606 |  |  | 20.3734 |  |  | 15.3894 |  |  | 13.6846 |  |  | 14.549 |  |  | 10.7332 |  |  | 38.1739
[13 empty] | C Choked w/ reducers | 5 |  | 17.4286 |  |  | 52.3073 |  |  | 111.9516 |  |  | 30.658 |  |  | 17.2757 |  |  | 12.5866 |  |  | 10.4895 |  |  | 9.8786 |  |  | 9.1211 |  |  | 13.2099
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 17.954 |  |  | 60.9245 |  |  | 111.9516 |  |  | 30.658 |  |  | 17.2757 |  |  | 12.5866 |  |  | 10.4895 |  |  | 9.8786 |  |  | 9.1211 |  |  | 13.2099
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 15.954 | 3865.9478 |  | 55.9245 | 8660.0719 |  | 7174 | 21417.3884 |  | 7174 | 41715.6059 |  | 7174 | 68606.8129 |  | 7174 | 96226.3369 |  | 7174 | 122181.9141 |  | 7174 | 143267.9032 |  | 7174 | 159839.4647 |  | 7174 | 178327.8314
[13 empty] | Next iteration flow rate |  |  | 3943.2667 | Abs Value of | Flow this | 8746.6726 | Abs Value of | Flow this | 21631.5623 | Abs Value of | Flow this | 42132.762 | Abs Value of | Flow this | 69292.8811 | Abs Value of | Flow this | 97188.6003 | Abs Value of | Flow this | 123403.7332 | Abs Value of | Flow this | 144700.5823 | Abs Value of | Flow this | 161437.8594 | Abs Value of | Flow this | 180111.1097 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 94.3223 |  |  | 70.0158 |  |  | -86.0676 |  |  | -607.3471 |  |  | -1814.1335 |  |  | -3666.0316 |  |  | -5972.0144 |  |  | -8248.8556 |  |  | -10292.0809 |  |  | -12835.3159
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.45499 |  |  | 0.33774 |  |  | -0.41517 |  |  | -2.9297 |  |  | -8.7511 |  |  | -17.6843 |  |  | -28.8079 |  |  | -39.791 |  |  | -49.6472 |  |  | -61.9153
[13 empty] | Delta P at this iteration flow rate |  |  | 44.3223 |  |  | 20.0158 |  |  | -136.0676 |  |  | -657.3471 |  |  | -1864.1335 |  |  | -3716.0316 |  |  | -6022.0144 |  |  | -8298.8556 |  |  | -10342.0809 |  |  | -12885.3159
[13 empty] | Press drop ratio this iteration |  |  | 0.4699 |  |  | 0.28588 |  |  | 1.5809 |  |  | 1.0823 |  |  | 1.0276 |  |  | 1.0136 |  |  | 1.0084 |  |  | 1.0061 |  |  | 1.0049 |  |  | 1.0039
[13 empty] | Expansion factor | 12 |  | 0.75527 |  |  | 0.85115 |  |  | 0.16446 |  |  | 0.42014 |  |  | 0.43439 |  |  | 0.41022 |  |  | 0.3728 |  |  | 0.31629 |  |  | 0.43566 |  |  | 0.1441
[13 empty] | C Non choked w/ reducers | 5 |  | 18.3691 |  |  | 62.4851 |  |  | 277.2748 |  |  | 36.4154 |  |  | 20.14 |  |  | 15.2247 |  |  | 13.5418 |  |  | 14.3985 |  |  | 10.624 |  |  | 37.7738
[13 empty] | C Choked w/ reducers | 5 |  | 17.8225 |  |  | 53.2839 |  |  | 108.2411 |  |  | 30.2534 |  |  | 17.0856 |  |  | 12.4551 |  |  | 10.3821 |  |  | 9.7784 |  |  | 9.0291 |  |  | 13.0771
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 18.3691 |  |  | 62.4851 |  |  | 108.2411 |  |  | 30.2534 |  |  | 17.0856 |  |  | 12.4551 |  |  | 10.3821 |  |  | 9.7784 |  |  | 9.0291 |  |  | 13.0771
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 16.3691 | 3943.2667 |  | 57.4851 | 8746.6726 |  | 7174 | 21631.5623 |  | 7174 | 42132.762 |  | 7174 | 69292.8811 |  | 7174 | 97188.6003 |  | 7174 | 123403.7332 |  | 7174 | 144700.5823 |  | 7174 | 161437.8594 |  | 7174 | 180111.1097
[13 empty] | Next iteration flow rate |  |  | 4022.1321 | Abs Value of | Flow this | 8834.1394 | Abs Value of | Flow this | 21847.8779 | Abs Value of | Flow this | 42554.0896 | Abs Value of | Flow this | 69985.8099 | Abs Value of | Flow this | 98160.4863 | Abs Value of | Flow this | 124637.7706 | Abs Value of | Flow this | 146147.5881 | Abs Value of | Flow this | 163052.238 | Abs Value of | Flow this | 181912.2208 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 94.0718 |  |  | 69.4026 |  |  | -89.8181 |  |  | -621.5753 |  |  | -1852.6181 |  |  | -3741.7393 |  |  | -6094.0724 |  |  | -8416.6781 |  |  | -10500.9723 |  |  | -13095.3263
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.45379 |  |  | 0.33479 |  |  | -0.43327 |  |  | -2.9984 |  |  | -8.9367 |  |  | -18.0495 |  |  | -29.3967 |  |  | -40.6006 |  |  | -50.6548 |  |  | -63.1695
[13 empty] | Delta P at this iteration flow rate |  |  | 44.0718 |  |  | 19.4026 |  |  | -139.8181 |  |  | -671.5753 |  |  | -1902.6181 |  |  | -3791.7393 |  |  | -6144.0724 |  |  | -8466.6781 |  |  | -10550.9723 |  |  | -13145.3263
[13 empty] | Press drop ratio this iteration |  |  | 0.46849 |  |  | 0.27957 |  |  | 1.5567 |  |  | 1.0804 |  |  | 1.027 |  |  | 1.0134 |  |  | 1.0082 |  |  | 1.0059 |  |  | 1.0048 |  |  | 1.0038
[13 empty] | Expansion factor | 12 |  | 0.756 |  |  | 0.85443 |  |  | 0.17728 |  |  | 0.42115 |  |  | 0.4347 |  |  | 0.41038 |  |  | 0.3729 |  |  | 0.31637 |  |  | 0.43571 |  |  | 0.14417
[13 empty] | C Non choked w/ reducers | 5 |  | 18.7964 |  |  | 64.1345 |  |  | 250.8795 |  |  | 35.8827 |  |  | 19.9099 |  |  | 15.0619 |  |  | 13.4006 |  |  | 14.2497 |  |  | 10.516 |  |  | 37.3784
[13 empty] | C Choked w/ reducers | 5 |  | 18.2274 |  |  | 54.2922 |  |  | 104.7585 |  |  | 29.8565 |  |  | 16.898 |  |  | 12.3251 |  |  | 10.2759 |  |  | 9.6793 |  |  | 8.9379 |  |  | 12.9456
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 18.7964 |  |  | 64.1345 |  |  | 104.7585 |  |  | 29.8565 |  |  | 16.898 |  |  | 12.3251 |  |  | 10.2759 |  |  | 9.6793 |  |  | 8.9379 |  |  | 12.9456
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 16.7964 | 4022.1321 |  | 59.1345 | 8834.1394 |  | 7174 | 21847.8779 |  | 7174 | 42554.0896 |  | 7174 | 69985.8099 |  | 7174 | 98160.4863 |  | 7174 | 124637.7706 |  | 7174 | 146147.5881 |  | 7174 | 163052.238 |  | 7174 | 181912.2208
[13 empty] | Next iteration flow rate |  |  | 4102.5747 | Abs Value of | Flow this | 8922.4807 | Abs Value of | Flow this | 22066.3567 | Abs Value of | Flow this | 42979.6305 | Abs Value of | Flow this | 70685.668 | Abs Value of | Flow this | 99142.0911 | Abs Value of | Flow this | 125884.1483 | Abs Value of | Flow this | 147609.064 | Abs Value of | Flow this | 164682.7604 | Abs Value of | Flow this | 183731.343 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 93.8112 |  |  | 68.7771 |  |  | -93.644 |  |  | -636.0895 |  |  | -1891.8762 |  |  | -3818.9688 |  |  | -6218.5838 |  |  | -8587.8739 |  |  | -10714.0623 |  |  | -13360.5628
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.45253 |  |  | 0.33177 |  |  | -0.45172 |  |  | -3.0684 |  |  | -9.1261 |  |  | -18.422 |  |  | -29.9973 |  |  | -41.4264 |  |  | -51.6827 |  |  | -64.449
[13 empty] | Delta P at this iteration flow rate |  |  | 43.8112 |  |  | 18.7771 |  |  | -143.644 |  |  | -686.0895 |  |  | -1941.8762 |  |  | -3868.9688 |  |  | -6268.5838 |  |  | -8637.8739 |  |  | -10764.0623 |  |  | -13410.5628
[13 empty] | Press drop ratio this iteration |  |  | 0.46701 |  |  | 0.27301 |  |  | 1.5339 |  |  | 1.0786 |  |  | 1.0264 |  |  | 1.0131 |  |  | 1.008 |  |  | 1.0058 |  |  | 1.0047 |  |  | 1.0037
[13 empty] | Expansion factor | 12 |  | 0.75677 |  |  | 0.85784 |  |  | 0.1893 |  |  | 0.42213 |  |  | 0.43501 |  |  | 0.41054 |  |  | 0.373 |  |  | 0.31645 |  |  | 0.43577 |  |  | 0.14423
[13 empty] | C Non choked w/ reducers | 5 |  | 19.2364 |  |  | 65.8816 |  |  | 229.2851 |  |  | 35.3622 |  |  | 19.6832 |  |  | 14.9012 |  |  | 13.2611 |  |  | 14.1025 |  |  | 10.4092 |  |  | 36.9875
[13 empty] | C Choked w/ reducers | 5 |  | 18.6436 |  |  | 55.3339 |  |  | 101.4834 |  |  | 29.467 |  |  | 16.7128 |  |  | 12.1966 |  |  | 10.1709 |  |  | 9.5812 |  |  | 8.8478 |  |  | 12.8155
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 19.2364 |  |  | 65.8816 |  |  | 101.4834 |  |  | 29.467 |  |  | 16.7128 |  |  | 12.1966 |  |  | 10.1709 |  |  | 9.5812 |  |  | 8.8478 |  |  | 12.8155
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 17.2364 | 4102.5747 |  | 60.8816 | 8922.4807 |  | 7174 | 22066.3567 |  | 7174 | 42979.6305 |  | 7174 | 70685.668 |  | 7174 | 99142.0911 |  | 7174 | 125884.1483 |  | 7174 | 147609.064 |  | 7174 | 164682.7604 |  | 7174 | 183731.343
[13 empty] | Next iteration flow rate |  |  | 4184.6262 | Abs Value of | Flow this | 9011.7056 | Abs Value of | Flow this | 22287.0202 | Abs Value of | Flow this | 43409.4268 | Abs Value of | Flow this | 71392.5247 | Abs Value of | Flow this | 100133.5121 | Abs Value of | Flow this | 127142.9897 | Abs Value of | Flow this | 149085.1546 | Abs Value of | Flow this | 166329.588 | Abs Value of | Flow this | 185568.6564 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 93.54 |  |  | 68.139 |  |  | -97.5467 |  |  | -650.8954 |  |  | -1931.9235 |  |  | -3897.7506 |  |  | -6345.5978 |  |  | -8762.5106 |  |  | -10931.4355 |  |  | -13631.1307
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.45122 |  |  | 0.32869 |  |  | -0.47055 |  |  | -3.1398 |  |  | -9.3193 |  |  | -18.8021 |  |  | -30.61 |  |  | -42.2688 |  |  | -52.7313 |  |  | -65.7541
[13 empty] | Delta P at this iteration flow rate |  |  | 43.54 |  |  | 18.139 |  |  | -147.5467 |  |  | -700.8954 |  |  | -1981.9235 |  |  | -3947.7506 |  |  | -6395.5978 |  |  | -8812.5106 |  |  | -10981.4355 |  |  | -13681.1307
[13 empty] | Press drop ratio this iteration |  |  | 0.46547 |  |  | 0.26621 |  |  | 1.5126 |  |  | 1.0768 |  |  | 1.0259 |  |  | 1.0128 |  |  | 1.0079 |  |  | 1.0057 |  |  | 1.0046 |  |  | 1.0037
[13 empty] | Expansion factor | 12 |  | 0.75758 |  |  | 0.86139 |  |  | 0.20059 |  |  | 0.42309 |  |  | 0.43531 |  |  | 0.41069 |  |  | 0.3731 |  |  | 0.31653 |  |  | 0.43582 |  |  | 0.1443
[13 empty] | C Non choked w/ reducers | 5 |  | 19.6897 |  |  | 67.737 |  |  | 211.2764 |  |  | 34.8532 |  |  | 19.4596 |  |  | 14.7424 |  |  | 13.1231 |  |  | 13.957 |  |  | 10.3034 |  |  | 36.6011
[13 empty] | C Choked w/ reducers | 5 |  | 19.0716 |  |  | 56.4106 |  |  | 98.3974 |  |  | 29.0847 |  |  | 16.53 |  |  | 12.0696 |  |  | 10.0669 |  |  | 9.4842 |  |  | 8.7586 |  |  | 12.6867
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 19.6897 |  |  | 67.737 |  |  | 98.3974 |  |  | 29.0847 |  |  | 16.53 |  |  | 12.0696 |  |  | 10.0669 |  |  | 9.4842 |  |  | 8.7586 |  |  | 12.6867
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 17.6897 | 4184.6262 |  | 62.737 | 9011.7056 |  | 7174 | 22287.0202 |  | 7174 | 43409.4268 |  | 7174 | 71392.5247 |  | 7174 | 100133.5121 |  | 7174 | 127142.9897 |  | 7174 | 149085.1546 |  | 7174 | 166329.588 |  | 7174 | 185568.6564
[13 empty] | Next iteration flow rate |  |  | 4268.3187 | Abs Value of | Flow this | 9101.8226 | Abs Value of | Flow this | 22509.8904 | Abs Value of | Flow this | 43843.521 | Abs Value of | Flow this | 72106.4499 | Abs Value of | Flow this | 101134.8472 | Abs Value of | Flow this | 128414.4196 | Abs Value of | Flow this | 150576.0062 | Abs Value of | Flow this | 167992.8839 | Abs Value of | Flow this | 187424.343 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 93.2579 |  |  | 67.4881 |  |  | -101.5279 |  |  | -665.9989 |  |  | -1972.7756 |  |  | -3978.1159 |  |  | -6475.1648 |  |  | -8940.6576 |  |  | -11153.1779 |  |  | -13907.1369
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.44986 |  |  | 0.32555 |  |  | -0.48975 |  |  | -3.2127 |  |  | -9.5163 |  |  | -19.1897 |  |  | -31.235 |  |  | -43.1281 |  |  | -53.8009 |  |  | -67.0856
[13 empty] | Delta P at this iteration flow rate |  |  | 43.2579 |  |  | 17.4881 |  |  | -151.5279 |  |  | -715.9989 |  |  | -2022.7756 |  |  | -4028.1159 |  |  | -6525.1648 |  |  | -8990.6576 |  |  | -11203.1779 |  |  | -13957.1369
[13 empty] | Press drop ratio this iteration |  |  | 0.46385 |  |  | 0.25913 |  |  | 1.4925 |  |  | 1.0751 |  |  | 1.0253 |  |  | 1.0126 |  |  | 1.0077 |  |  | 1.0056 |  |  | 1.0045 |  |  | 1.0036
[13 empty] | Expansion factor | 12 |  | 0.75842 |  |  | 0.86507 |  |  | 0.21121 |  |  | 0.42402 |  |  | 0.43561 |  |  | 0.41084 |  |  | 0.3732 |  |  | 0.3166 |  |  | 0.43587 |  |  | 0.14436
[13 empty] | C Non choked w/ reducers | 5 |  | 20.1569 |  |  | 69.7129 |  |  | 196.017 |  |  | 34.3555 |  |  | 19.2392 |  |  | 14.5855 |  |  | 12.9867 |  |  | 13.8131 |  |  | 10.1988 |  |  | 36.2192
[13 empty] | C Choked w/ reducers | 5 |  | 19.5118 |  |  | 57.5242 |  |  | 95.4843 |  |  | 28.7094 |  |  | 16.3496 |  |  | 11.944 |  |  | 9.9642 |  |  | 9.3881 |  |  | 8.6703 |  |  | 12.5593
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 20.1569 |  |  | 69.7129 |  |  | 95.4843 |  |  | 28.7094 |  |  | 16.3496 |  |  | 11.944 |  |  | 9.9642 |  |  | 9.3881 |  |  | 8.6703 |  |  | 12.5593
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18.1569 | 4268.3187 |  | 64.7129 | 9101.8226 |  | 7174 | 22509.8904 |  | 7174 | 43843.521 |  | 7174 | 72106.4499 |  | 7174 | 101134.8472 |  | 7174 | 128414.4196 |  | 7174 | 150576.0062 |  | 7174 | 167992.8839 |  | 7174 | 187424.343
[13 empty] | Next iteration flow rate |  |  | 4353.6851 | Abs Value of | Flow this | 9192.8408 | Abs Value of | Flow this | 22734.9894 | Abs Value of | Flow this | 44281.9563 | Abs Value of | Flow this | 72827.5144 | Abs Value of | Flow this | 102146.1957 | Abs Value of | Flow this | 129698.5638 | Abs Value of | Flow this | 152081.7662 | Abs Value of | Flow this | 169672.8127 | Abs Value of | Flow this | 189298.5864 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 92.9644 |  |  | 66.8241 |  |  | -105.5891 |  |  | -681.406 |  |  | -2014.4489 |  |  | -4060.0965 |  |  | -6607.3362 |  |  | -9122.3853 |  |  | -11379.3772 |  |  | -14188.6908
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.44844 |  |  | 0.32235 |  |  | -0.50934 |  |  | -3.287 |  |  | -9.7173 |  |  | -19.5852 |  |  | -31.8726 |  |  | -44.0048 |  |  | -54.8921 |  |  | -68.4437
[13 empty] | Delta P at this iteration flow rate |  |  | 42.9644 |  |  | 16.8241 |  |  | -155.5891 |  |  | -731.406 |  |  | -2064.4489 |  |  | -4110.0965 |  |  | -6657.3362 |  |  | -9172.3853 |  |  | -11429.3772 |  |  | -14238.6908
[13 empty] | Press drop ratio this iteration |  |  | 0.46216 |  |  | 0.25177 |  |  | 1.4735 |  |  | 1.0734 |  |  | 1.0248 |  |  | 1.0123 |  |  | 1.0076 |  |  | 1.0055 |  |  | 1.0044 |  |  | 1.0035
[13 empty] | Expansion factor | 12 |  | 0.7593 |  |  | 0.86891 |  |  | 0.22123 |  |  | 0.42493 |  |  | 0.43589 |  |  | 0.41099 |  |  | 0.3733 |  |  | 0.31668 |  |  | 0.43592 |  |  | 0.14442
[13 empty] | C Non choked w/ reducers | 5 |  | 20.6387 |  |  | 71.8235 |  |  | 182.9126 |  |  | 33.8687 |  |  | 19.0219 |  |  | 14.4306 |  |  | 12.8519 |  |  | 13.6708 |  |  | 10.0954 |  |  | 35.8417
[13 empty] | C Choked w/ reducers | 5 |  | 19.9649 |  |  | 58.6767 |  |  | 92.7299 |  |  | 28.3408 |  |  | 16.1715 |  |  | 11.8199 |  |  | 9.8625 |  |  | 9.2931 |  |  | 8.5829 |  |  | 12.4331
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 20.6387 |  |  | 71.8235 |  |  | 92.7299 |  |  | 28.3408 |  |  | 16.1715 |  |  | 11.8199 |  |  | 9.8625 |  |  | 9.2931 |  |  | 8.5829 |  |  | 12.4331
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18.6387 | 4353.6851 |  | 66.8235 | 9192.8408 |  | 7174 | 22734.9894 |  | 7174 | 44281.9563 |  | 7174 | 72827.5144 |  | 7174 | 102146.1957 |  | 7174 | 129698.5638 |  | 7174 | 152081.7662 |  | 7174 | 169672.8127 |  | 7174 | 189298.5864
[13 empty] | Next iteration flow rate |  |  | 4440.7588 | Abs Value of | Flow this | 9284.7692 | Abs Value of | Flow this | 22962.3392 | Abs Value of | Flow this | 44724.7758 | Abs Value of | Flow this | 73555.7895 | Abs Value of | Flow this | 103167.6576 | Abs Value of | Flow this | 130995.5495 | Abs Value of | Flow this | 153602.5839 | Abs Value of | Flow this | 171369.5408 | Abs Value of | Flow this | 191191.5723 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 92.6591 |  |  | 66.1467 |  |  | -109.732 |  |  | -697.1227 |  |  | -2056.9599 |  |  | -4143.725 |  |  | -6742.1641 |  |  | -9307.7658 |  |  | -11610.1232 |  |  | -14475.904
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.44697 |  |  | 0.31908 |  |  | -0.52933 |  |  | -3.3628 |  |  | -9.9224 |  |  | -19.9886 |  |  | -32.523 |  |  | -44.899 |  |  | -56.0052 |  |  | -69.8292
[13 empty] | Delta P at this iteration flow rate |  |  | 42.6591 |  |  | 16.1467 |  |  | -159.732 |  |  | -747.1227 |  |  | -2106.9599 |  |  | -4193.725 |  |  | -6792.1641 |  |  | -9357.7658 |  |  | -11660.1232 |  |  | -14525.904
[13 empty] | Press drop ratio this iteration |  |  | 0.46039 |  |  | 0.2441 |  |  | 1.4557 |  |  | 1.0717 |  |  | 1.0243 |  |  | 1.0121 |  |  | 1.0074 |  |  | 1.0054 |  |  | 1.0043 |  |  | 1.0035
[13 empty] | Expansion factor | 12 |  | 0.76022 |  |  | 0.8729 |  |  | 0.23067 |  |  | 0.42582 |  |  | 0.43618 |  |  | 0.41114 |  |  | 0.37339 |  |  | 0.31675 |  |  | 0.43597 |  |  | 0.14448
[13 empty] | C Non choked w/ reducers | 5 |  | 21.1357 |  |  | 74.0857 |  |  | 171.5292 |  |  | 33.3923 |  |  | 18.8076 |  |  | 14.2775 |  |  | 12.7186 |  |  | 13.5301 |  |  | 9.993 |  |  | 35.4685
[13 empty] | C Choked w/ reducers | 5 |  | 20.4313 |  |  | 59.8704 |  |  | 90.1212 |  |  | 27.9789 |  |  | 15.9956 |  |  | 11.6971 |  |  | 9.7619 |  |  | 9.1991 |  |  | 8.4964 |  |  | 12.3083
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 21.1357 |  |  | 74.0857 |  |  | 90.1212 |  |  | 27.9789 |  |  | 15.9956 |  |  | 11.6971 |  |  | 9.7619 |  |  | 9.1991 |  |  | 8.4964 |  |  | 12.3083
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 19.1357 | 4440.7588 |  | 69.0857 | 9284.7692 |  | 7174 | 22962.3392 |  | 7174 | 44724.7758 |  | 7174 | 73555.7895 |  | 7174 | 103167.6576 |  | 7174 | 130995.5495 |  | 7174 | 153602.5839 |  | 7174 | 171369.5408 |  | 7174 | 191191.5723
[13 empty] | Next iteration flow rate |  |  | 4529.574 | Abs Value of | Flow this | 9377.6169 | Abs Value of | Flow this | 23191.9626 | Abs Value of | Flow this | 45172.0236 | Abs Value of | Flow this | 74291.3474 | Abs Value of | Flow this | 104199.3342 | Abs Value of | Flow this | 132305.505 | Abs Value of | Flow this | 155138.6097 | Abs Value of | Flow this | 173083.2362 | Abs Value of | Flow this | 193103.488 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 92.3414 |  |  | 65.4558 |  |  | -113.9581 |  |  | -713.1554 |  |  | -2100.3253 |  |  | -4229.0343 |  |  | -6879.7021 |  |  | -9496.8724 |  |  | -11845.5072 |  |  | -14768.8902
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.44544 |  |  | 0.31575 |  |  | -0.54971 |  |  | -3.4401 |  |  | -10.1316 |  |  | -20.4001 |  |  | -33.1865 |  |  | -45.8112 |  |  | -57.1406 |  |  | -71.2425
[13 empty] | Delta P at this iteration flow rate |  |  | 42.3414 |  |  | 15.4558 |  |  | -163.9581 |  |  | -763.1554 |  |  | -2150.3253 |  |  | -4279.0343 |  |  | -6929.7021 |  |  | -9546.8724 |  |  | -11895.5072 |  |  | -14818.8902
[13 empty] | Press drop ratio this iteration |  |  | 0.45853 |  |  | 0.23613 |  |  | 1.4388 |  |  | 1.0701 |  |  | 1.0238 |  |  | 1.0118 |  |  | 1.0073 |  |  | 1.0053 |  |  | 1.0042 |  |  | 1.0034
[13 empty] | Expansion factor | 12 |  | 0.76119 |  |  | 0.87705 |  |  | 0.2396 |  |  | 0.42668 |  |  | 0.43645 |  |  | 0.41128 |  |  | 0.37348 |  |  | 0.31683 |  |  | 0.43602 |  |  | 0.14454
[13 empty] | C Non choked w/ reducers | 5 |  | 21.6488 |  |  | 76.5192 |  |  | 161.5423 |  |  | 32.926 |  |  | 18.5962 |  |  | 14.1262 |  |  | 12.5868 |  |  | 13.3909 |  |  | 9.8917 |  |  | 35.0995
[13 empty] | C Choked w/ reducers | 5 |  | 20.9116 |  |  | 61.1074 |  |  | 87.6469 |  |  | 27.6234 |  |  | 15.822 |  |  | 11.5758 |  |  | 9.6624 |  |  | 9.1061 |  |  | 8.4109 |  |  | 12.1848
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 21.6488 |  |  | 76.5192 |  |  | 87.6469 |  |  | 27.6234 |  |  | 15.822 |  |  | 11.5758 |  |  | 9.6624 |  |  | 9.1061 |  |  | 8.4109 |  |  | 12.1848
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 19.6488 | 4529.574 |  | 71.5192 | 9377.6169 |  | 7174 | 23191.9626 |  | 7174 | 45172.0236 |  | 7174 | 74291.3474 |  | 7174 | 104199.3342 |  | 7174 | 132305.505 |  | 7174 | 155138.6097 |  | 7174 | 173083.2362 |  | 7174 | 193103.488
[13 empty] | Next iteration flow rate |  |  | 4620.1655 | Abs Value of | Flow this | 9471.3931 | Abs Value of | Flow this | 23423.8823 | Abs Value of | Flow this | 45623.7438 | Abs Value of | Flow this | 75034.2609 | Abs Value of | Flow this | 105241.3275 | Abs Value of | Flow this | 133628.56 | Abs Value of | Flow this | 156689.9958 | Abs Value of | Flow this | 174814.0686 | Abs Value of | Flow this | 195034.5229 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 92.0108 |  |  | 64.7509 |  |  | -118.2692 |  |  | -729.5103 |  |  | -2144.5623 |  |  | -4316.0584 |  |  | -7020.0047 |  |  | -9689.78 |  |  | -12085.6224 |  |  | -15067.7654
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.44384 |  |  | 0.31235 |  |  | -0.57051 |  |  | -3.519 |  |  | -10.345 |  |  | -20.8199 |  |  | -33.8633 |  |  | -46.7418 |  |  | -58.2989 |  |  | -72.6842
[13 empty] | Delta P at this iteration flow rate |  |  | 42.0108 |  |  | 14.7509 |  |  | -168.2692 |  |  | -779.5103 |  |  | -2194.5623 |  |  | -4366.0584 |  |  | -7070.0047 |  |  | -9739.78 |  |  | -12135.6224 |  |  | -15117.7654
[13 empty] | Press drop ratio this iteration |  |  | 0.45659 |  |  | 0.22781 |  |  | 1.4228 |  |  | 1.0685 |  |  | 1.0233 |  |  | 1.0116 |  |  | 1.0071 |  |  | 1.0052 |  |  | 1.0041 |  |  | 1.0033
[13 empty] | Expansion factor | 12 |  | 0.7622 |  |  | 0.88138 |  |  | 0.24806 |  |  | 0.42753 |  |  | 0.43672 |  |  | 0.41142 |  |  | 0.37357 |  |  | 0.3169 |  |  | 0.43606 |  |  | 0.1446
[13 empty] | C Non choked w/ reducers | 5 |  | 22.1788 |  |  | 79.148 |  |  | 152.7046 |  |  | 32.4696 |  |  | 18.3878 |  |  | 13.9767 |  |  | 12.4565 |  |  | 13.2533 |  |  | 9.7915 |  |  | 34.7347
[13 empty] | C Choked w/ reducers | 5 |  | 21.4065 |  |  | 62.3903 |  |  | 85.2965 |  |  | 27.2742 |  |  | 15.6506 |  |  | 11.4558 |  |  | 9.564 |  |  | 9.0141 |  |  | 8.3262 |  |  | 12.0625
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 22.1788 |  |  | 79.148 |  |  | 85.2965 |  |  | 27.2742 |  |  | 15.6506 |  |  | 11.4558 |  |  | 9.564 |  |  | 9.0141 |  |  | 8.3262 |  |  | 12.0625
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 20.1788 | 4620.1655 |  | 74.148 | 9471.3931 |  | 7174 | 23423.8823 |  | 7174 | 45623.7438 |  | 7174 | 75034.2609 |  | 7174 | 105241.3275 |  | 7174 | 133628.56 |  | 7174 | 156689.9958 |  | 7174 | 174814.0686 |  | 7174 | 195034.5229
[13 empty] | Next iteration flow rate |  |  | 4712.5688 | Abs Value of | Flow this | 9566.107 | Abs Value of | Flow this | 23658.1211 | Abs Value of | Flow this | 46079.9813 | Abs Value of | Flow this | 75784.6035 | Abs Value of | Flow this | 106293.7408 | Abs Value of | Flow this | 134964.8456 | Abs Value of | Flow this | 158256.8958 | Abs Value of | Flow this | 176562.2093 | Abs Value of | Flow this | 196984.8681 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 91.667 |  |  | 64.0319 |  |  | -122.6669 |  |  | -746.194 |  |  | -2189.6885 |  |  | -4404.8317 |  |  | -7163.1273 |  |  | -9886.5651 |  |  | -12330.5639 |  |  | -15372.648
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.44219 |  |  | 0.30888 |  |  | -0.59172 |  |  | -3.5995 |  |  | -10.5627 |  |  | -21.2481 |  |  | -34.5537 |  |  | -47.691 |  |  | -59.4804 |  |  | -74.1549
[13 empty] | Delta P at this iteration flow rate |  |  | 41.667 |  |  | 14.0319 |  |  | -172.6669 |  |  | -796.194 |  |  | -2239.6885 |  |  | -4454.8317 |  |  | -7213.1273 |  |  | -9936.5651 |  |  | -12380.5639 |  |  | -15422.648
[13 empty] | Press drop ratio this iteration |  |  | 0.45455 |  |  | 0.21914 |  |  | 1.4076 |  |  | 1.067 |  |  | 1.0228 |  |  | 1.0114 |  |  | 1.007 |  |  | 1.0051 |  |  | 1.0041 |  |  | 1.0033
[13 empty] | Expansion factor | 12 |  | 0.76327 |  |  | 0.88589 |  |  | 0.25607 |  |  | 0.42835 |  |  | 0.43699 |  |  | 0.41155 |  |  | 0.37366 |  |  | 0.31697 |  |  | 0.43611 |  |  | 0.14465
[13 empty] | C Non choked w/ reducers | 5 |  | 22.7264 |  |  | 82.0008 |  |  | 144.824 |  |  | 32.0226 |  |  | 18.1822 |  |  | 13.829 |  |  | 12.3276 |  |  | 13.1172 |  |  | 9.6923 |  |  | 34.3741
[13 empty] | C Choked w/ reducers | 5 |  | 21.9165 |  |  | 63.7218 |  |  | 83.061 |  |  | 26.931 |  |  | 15.4813 |  |  | 11.3372 |  |  | 9.4666 |  |  | 8.923 |  |  | 8.2424 |  |  | 11.9415
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 22.7264 |  |  | 82.0008 |  |  | 83.061 |  |  | 26.931 |  |  | 15.4813 |  |  | 11.3372 |  |  | 9.4666 |  |  | 8.923 |  |  | 8.2424 |  |  | 11.9415
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 20.7264 | 4712.5688 |  | 77.0008 | 9566.107 |  | 7174 | 23658.1211 |  | 7174 | 46079.9813 |  | 7174 | 75784.6035 |  | 7174 | 106293.7408 |  | 7174 | 134964.8456 |  | 7174 | 158256.8958 |  | 7174 | 176562.2093 |  | 7174 | 196984.8681
[13 empty] | Next iteration flow rate |  |  | 4806.8202 | Abs Value of | Flow this | 9661.7681 | Abs Value of | Flow this | 23894.7023 | Abs Value of | Flow this | 46540.7811 | Abs Value of | Flow this | 76542.4496 | Abs Value of | Flow this | 107356.6782 | Abs Value of | Flow this | 136314.4941 | Abs Value of | Flow this | 159839.4647 | Abs Value of | Flow this | 178327.8314 | Abs Value of | Flow this | 198954.7168 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 91.3092 |  |  | 63.2985 |  |  | -127.153 |  |  | -763.213 |  |  | -2235.7218 |  |  | -4495.3894 |  |  | -7309.1266 |  |  | -10087.3056 |  |  | -12580.4288 |  |  | -15683.6587
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.44046 |  |  | 0.30534 |  |  | -0.61336 |  |  | -3.6816 |  |  | -10.7847 |  |  | -21.685 |  |  | -35.2579 |  |  | -48.6594 |  |  | -60.6857 |  |  | -75.6552
[13 empty] | Delta P at this iteration flow rate |  |  | 41.3092 |  |  | 13.2985 |  |  | -177.153 |  |  | -813.213 |  |  | -2285.7218 |  |  | -4545.3894 |  |  | -7359.1266 |  |  | -10137.3056 |  |  | -12630.4288 |  |  | -15733.6587
[13 empty] | Press drop ratio this iteration |  |  | 0.45241 |  |  | 0.21009 |  |  | 1.3932 |  |  | 1.0655 |  |  | 1.0224 |  |  | 1.0111 |  |  | 1.0068 |  |  | 1.005 |  |  | 1.004 |  |  | 1.0032
[13 empty] | Expansion factor | 12 |  | 0.76438 |  |  | 0.89061 |  |  | 0.26367 |  |  | 0.42915 |  |  | 0.43725 |  |  | 0.41169 |  |  | 0.37375 |  |  | 0.31704 |  |  | 0.43616 |  |  | 0.14471
[13 empty] | C Non choked w/ reducers | 5 |  | 23.2927 |  |  | 85.113 |  |  | 137.7494 |  |  | 31.5847 |  |  | 17.9794 |  |  | 13.683 |  |  | 12.2002 |  |  | 12.9825 |  |  | 9.5942 |  |  | 34.0175
[13 empty] | C Choked w/ reducers | 5 |  | 22.4425 |  |  | 65.1048 |  |  | 80.9318 |  |  | 26.5938 |  |  | 15.3142 |  |  | 11.2199 |  |  | 9.3703 |  |  | 8.8329 |  |  | 8.1595 |  |  | 11.8218
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 23.2927 |  |  | 85.113 |  |  | 80.9318 |  |  | 26.5938 |  |  | 15.3142 |  |  | 11.2199 |  |  | 9.3703 |  |  | 8.8329 |  |  | 8.1595 |  |  | 11.8218
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 21.2927 | 4806.8202 |  | 80.113 | 9661.7681 |  | 7174 | 23894.7023 |  | 7174 | 46540.7811 |  | 7174 | 76542.4496 |  | 7174 | 107356.6782 |  | 7174 | 136314.4941 |  | 7174 | 159839.4647 |  | 7174 | 178327.8314 |  | 7174 | 198954.7168
[13 empty] | Next iteration flow rate |  |  | 4902.9566 | Abs Value of | Flow this | 9758.3858 | Abs Value of | Flow this | 24133.6493 | Abs Value of | Flow this | 47006.1889 | Abs Value of | Flow this | 77307.8741 | Abs Value of | Flow this | 108430.245 | Abs Value of | Flow this | 137677.639 | Abs Value of | Flow this | 161437.8594 | Abs Value of | Flow this | 180111.1097 | Abs Value of | Flow this | 200944.264 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.937 |  |  | 62.5503 |  |  | -131.7293 |  |  | -780.5741 |  |  | -2282.6803 |  |  | -4587.7672 |  |  | -7458.0606 |  |  | -10292.0809 |  |  | -12835.3159 |  |  | -16000.9208
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.43866 |  |  | 0.30173 |  |  | -0.63544 |  |  | -3.7654 |  |  | -11.0112 |  |  | -22.1306 |  |  | -35.9764 |  |  | -49.6472 |  |  | -61.9153 |  |  | -77.1856
[13 empty] | Delta P at this iteration flow rate |  |  | 40.937 |  |  | 12.5503 |  |  | -181.7293 |  |  | -830.5741 |  |  | -2332.6803 |  |  | -4637.7672 |  |  | -7508.0606 |  |  | -10342.0809 |  |  | -12885.3159 |  |  | -16050.9208
[13 empty] | Press drop ratio this iteration |  |  | 0.45017 |  |  | 0.20064 |  |  | 1.3796 |  |  | 1.0641 |  |  | 1.0219 |  |  | 1.0109 |  |  | 1.0067 |  |  | 1.0049 |  |  | 1.0039 |  |  | 1.0031
[13 empty] | Expansion factor | 12 |  | 0.76555 |  |  | 0.89553 |  |  | 0.27089 |  |  | 0.42993 |  |  | 0.4375 |  |  | 0.41182 |  |  | 0.37383 |  |  | 0.3171 |  |  | 0.4362 |  |  | 0.14476
[13 empty] | C Non choked w/ reducers | 5 |  | 23.8787 |  |  | 88.5281 |  |  | 131.36 |  |  | 31.1557 |  |  | 17.7793 |  |  | 13.5388 |  |  | 12.0742 |  |  | 12.8494 |  |  | 9.4971 |  |  | 33.665
[13 empty] | C Choked w/ reducers | 5 |  | 22.985 |  |  | 66.5424 |  |  | 78.9014 |  |  | 26.2623 |  |  | 15.1492 |  |  | 11.1039 |  |  | 9.275 |  |  | 8.7437 |  |  | 8.0774 |  |  | 11.7033
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 23.8787 |  |  | 88.5281 |  |  | 78.9014 |  |  | 26.2623 |  |  | 15.1492 |  |  | 11.1039 |  |  | 9.275 |  |  | 8.7437 |  |  | 8.0774 |  |  | 11.7033
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 21.8787 | 4902.9566 |  | 83.5281 | 9758.3858 |  | 7174 | 24133.6493 |  | 7174 | 47006.1889 |  | 7174 | 77307.8741 |  | 7174 | 108430.245 |  | 7174 | 137677.639 |  | 7174 | 161437.8594 |  | 7174 | 180111.1097 |  | 7174 | 200944.264
[13 empty] | Next iteration flow rate |  |  | 5001.0157 | Abs Value of | Flow this | 9855.9696 | Abs Value of | Flow this | 24374.9858 | Abs Value of | Flow this | 47476.2508 | Abs Value of | Flow this | 78080.9528 | Abs Value of | Flow this | 109514.5474 | Abs Value of | Flow this | 139054.4154 | Abs Value of | Flow this | 163052.238 | Abs Value of | Flow this | 181912.2208 | Abs Value of | Flow this | 202953.7066 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.5497 |  |  | 61.787 |  |  | -136.3975 |  |  | -798.2842 |  |  | -2330.5827 |  |  | -4682.0018 |  |  | -7609.9881 |  |  | -10500.9723 |  |  | -13095.3263 |  |  | -16324.5598
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4368 |  |  | 0.29805 |  |  | -0.65796 |  |  | -3.8508 |  |  | -11.2423 |  |  | -22.5851 |  |  | -36.7092 |  |  | -50.6548 |  |  | -63.1695 |  |  | -78.7468
[13 empty] | Delta P at this iteration flow rate |  |  | 40.5497 |  |  | 11.787 |  |  | -186.3975 |  |  | -848.2842 |  |  | -2380.5827 |  |  | -4732.0018 |  |  | -7659.9881 |  |  | -10550.9723 |  |  | -13145.3263 |  |  | -16374.5598
[13 empty] | Press drop ratio this iteration |  |  | 0.44782 |  |  | 0.19077 |  |  | 1.3666 |  |  | 1.0626 |  |  | 1.0215 |  |  | 1.0107 |  |  | 1.0066 |  |  | 1.0048 |  |  | 1.0038 |  |  | 1.0031
[13 empty] | Expansion factor | 12 |  | 0.76677 |  |  | 0.90067 |  |  | 0.27775 |  |  | 0.43069 |  |  | 0.43775 |  |  | 0.41194 |  |  | 0.37392 |  |  | 0.31717 |  |  | 0.43624 |  |  | 0.14481
[13 empty] | C Non choked w/ reducers | 5 |  | 24.4854 |  |  | 92.301 |  |  | 125.558 |  |  | 30.7353 |  |  | 17.5819 |  |  | 13.3963 |  |  | 11.9496 |  |  | 12.7177 |  |  | 9.401 |  |  | 33.3164
[13 empty] | C Choked w/ reducers | 5 |  | 23.545 |  |  | 68.038 |  |  | 76.963 |  |  | 25.9365 |  |  | 14.9862 |  |  | 10.9892 |  |  | 9.1808 |  |  | 8.6555 |  |  | 7.9962 |  |  | 11.5859
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 24.4854 |  |  | 92.301 |  |  | 76.963 |  |  | 25.9365 |  |  | 14.9862 |  |  | 10.9892 |  |  | 9.1808 |  |  | 8.6555 |  |  | 7.9962 |  |  | 11.5859
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 22.4854 | 5001.0157 |  | 87.301 | 9855.9696 |  | 7174 | 24374.9858 |  | 7174 | 47476.2508 |  | 7174 | 78080.9528 |  | 7174 | 109514.5474 |  | 7174 | 139054.4154 |  | 7174 | 163052.238 |  | 7174 | 181912.2208 |  | 7174 | 202953.7066
[13 empty] | Next iteration flow rate |  |  | 5101.036 | Abs Value of | Flow this | 9954.5293 | Abs Value of | Flow this | 24618.7357 | Abs Value of | Flow this | 47951.0133 | Abs Value of | Flow this | 78861.7623 | Abs Value of | Flow this | 110609.6929 | Abs Value of | Flow this | 140444.9596 | Abs Value of | Flow this | 164682.7604 | Abs Value of | Flow this | 183731.343 | Abs Value of | Flow this | 204983.2437 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1468 |  |  | 61.0084 |  |  | -141.1596 |  |  | -816.3502 |  |  | -2379.4479 |  |  | -4778.1306 |  |  | -7764.9694 |  |  | -10714.0623 |  |  | -13360.5628 |  |  | -16654.704
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.43485 |  |  | 0.29429 |  |  | -0.68093 |  |  | -3.9379 |  |  | -11.478 |  |  | -23.0489 |  |  | -37.4568 |  |  | -51.6827 |  |  | -64.449 |  |  | -80.3393
[13 empty] | Delta P at this iteration flow rate |  |  | 40.1468 |  |  | 11.0084 |  |  | -191.1596 |  |  | -866.3502 |  |  | -2429.4479 |  |  | -4828.1306 |  |  | -7814.9694 |  |  | -10764.0623 |  |  | -13410.5628 |  |  | -16704.704
[13 empty] | Press drop ratio this iteration |  |  | 0.44535 |  |  | 0.18044 |  |  | 1.3542 |  |  | 1.0612 |  |  | 1.021 |  |  | 1.0105 |  |  | 1.0064 |  |  | 1.0047 |  |  | 1.0037 |  |  | 1.003
[13 empty] | Expansion factor | 12 |  | 0.76806 |  |  | 0.90604 |  |  | 0.28429 |  |  | 0.43143 |  |  | 0.43799 |  |  | 0.41207 |  |  | 0.374 |  |  | 0.31723 |  |  | 0.43629 |  |  | 0.14486
[13 empty] | C Non choked w/ reducers | 5 |  | 25.114 |  |  | 96.5019 |  |  | 120.2638 |  |  | 30.3232 |  |  | 17.3872 |  |  | 13.2554 |  |  | 11.8264 |  |  | 12.5874 |  |  | 9.306 |  |  | 32.9718
[13 empty] | C Choked w/ reducers | 5 |  | 24.1232 |  |  | 69.5954 |  |  | 75.1103 |  |  | 25.6161 |  |  | 14.8252 |  |  | 10.8758 |  |  | 9.0875 |  |  | 8.5682 |  |  | 7.9159 |  |  | 11.4698
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 25.114 |  |  | 96.5019 |  |  | 75.1103 |  |  | 25.6161 |  |  | 14.8252 |  |  | 10.8758 |  |  | 9.0875 |  |  | 8.5682 |  |  | 7.9159 |  |  | 11.4698
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 23.114 | 5101.036 |  | 91.5019 | 9954.5293 |  | 7174 | 24618.7357 |  | 7174 | 47951.0133 |  | 7174 | 78861.7623 |  | 7174 | 110609.6929 |  | 7174 | 140444.9596 |  | 7174 | 164682.7604 |  | 7174 | 183731.343 |  | 7174 | 204983.2437
[13 empty] | Next iteration flow rate |  |  | 5203.0567 | Abs Value of | Flow this | 10054.0746 | Abs Value of | Flow this | 24864.923 | Abs Value of | Flow this | 48430.5234 | Abs Value of | Flow this | 79650.3799 | Abs Value of | Flow this | 111715.7898 | Abs Value of | Flow this | 141849.4092 | Abs Value of | Flow this | 166329.588 | Abs Value of | Flow this | 185568.6564 | Abs Value of | Flow this | 207033.0761 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.7276 |  |  | 60.2142 |  |  | -146.0175 |  |  | -834.7793 |  |  | -2429.2953 |  |  | -4876.1915 |  |  | -7923.0658 |  |  | -10931.4355 |  |  | -13631.1307 |  |  | -16991.484
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.43283 |  |  | 0.29046 |  |  | -0.70436 |  |  | -4.0268 |  |  | -11.7185 |  |  | -23.5219 |  |  | -38.2195 |  |  | -52.7313 |  |  | -65.7541 |  |  | -81.9639
[13 empty] | Delta P at this iteration flow rate |  |  | 39.7276 |  |  | 10.2142 |  |  | -196.0175 |  |  | -884.7793 |  |  | -2479.2953 |  |  | -4926.1915 |  |  | -7973.0658 |  |  | -10981.4355 |  |  | -13681.1307 |  |  | -17041.484
[13 empty] | Press drop ratio this iteration |  |  | 0.44276 |  |  | 0.16963 |  |  | 1.3424 |  |  | 1.0599 |  |  | 1.0206 |  |  | 1.0103 |  |  | 1.0063 |  |  | 1.0046 |  |  | 1.0037 |  |  | 1.0029
[13 empty] | Expansion factor | 12 |  | 0.76941 |  |  | 0.91167 |  |  | 0.29052 |  |  | 0.43216 |  |  | 0.43823 |  |  | 0.41219 |  |  | 0.37408 |  |  | 0.3173 |  |  | 0.43633 |  |  | 0.14492
[13 empty] | C Non choked w/ reducers | 5 |  | 25.7659 |  |  | 101.2217 |  |  | 115.4113 |  |  | 29.9192 |  |  | 17.195 |  |  | 13.1162 |  |  | 11.7046 |  |  | 12.4586 |  |  | 9.212 |  |  | 32.631
[13 empty] | C Choked w/ reducers | 5 |  | 24.7206 |  |  | 71.2185 |  |  | 73.3376 |  |  | 25.3011 |  |  | 14.6662 |  |  | 10.7637 |  |  | 8.9952 |  |  | 8.4818 |  |  | 7.8363 |  |  | 11.3549
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 25.7659 |  |  | 101.2217 |  |  | 73.3376 |  |  | 25.3011 |  |  | 14.6662 |  |  | 10.7637 |  |  | 8.9952 |  |  | 8.4818 |  |  | 7.8363 |  |  | 11.3549
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 23.7659 | 5203.0567 |  | 96.2217 | 10054.0746 |  | 7174 | 24864.923 |  | 7174 | 48430.5234 |  | 7174 | 79650.3799 |  | 7174 | 111715.7898 |  | 7174 | 141849.4092 |  | 7174 | 166329.588 |  | 7174 | 185568.6564 |  | 7174 | 207033.0761
[13 empty] | Next iteration flow rate |  |  | 5307.1179 | Abs Value of | Flow this | 10154.6154 | Abs Value of | Flow this | 25113.5723 | Abs Value of | Flow this | 48914.8286 | Abs Value of | Flow this | 80446.8837 | Abs Value of | Flow this | 112832.9477 | Abs Value of | Flow this | 143267.9032 | Abs Value of | Flow this | 167992.8839 | Abs Value of | Flow this | 187424.343 | Abs Value of | Flow this | 209103.4069 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.2915 |  |  | 59.404 |  |  | -150.9729 |  |  | -853.5789 |  |  | -2480.1446 |  |  | -4976.2235 |  |  | -8084.3399 |  |  | -11153.1779 |  |  | -13907.1369 |  |  | -17335.0334
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.43073 |  |  | 0.28655 |  |  | -0.72827 |  |  | -4.1175 |  |  | -11.9638 |  |  | -24.0044 |  |  | -38.9974 |  |  | -53.8009 |  |  | -67.0856 |  |  | -83.6211
[13 empty] | Delta P at this iteration flow rate |  |  | 39.2915 |  |  | 9.404 |  |  | -200.9729 |  |  | -903.5789 |  |  | -2530.1446 |  |  | -5026.2235 |  |  | -8134.3399 |  |  | -11203.1779 |  |  | -13957.1369 |  |  | -17385.0334
[13 empty] | Press drop ratio this iteration |  |  | 0.44004 |  |  | 0.15831 |  |  | 1.3312 |  |  | 1.0586 |  |  | 1.0202 |  |  | 1.01 |  |  | 1.0062 |  |  | 1.0045 |  |  | 1.0036 |  |  | 1.0029
[13 empty] | Expansion factor | 12 |  | 0.77082 |  |  | 0.91757 |  |  | 0.29646 |  |  | 0.43286 |  |  | 0.43846 |  |  | 0.41231 |  |  | 0.37416 |  |  | 0.31736 |  |  | 0.43637 |  |  | 0.14497
[13 empty] | C Non choked w/ reducers | 5 |  | 26.4424 |  |  | 106.5817 |  |  | 110.9458 |  |  | 29.523 |  |  | 17.0054 |  |  | 12.9786 |  |  | 11.5841 |  |  | 12.3312 |  |  | 9.1189 |  |  | 32.294
[13 empty] | C Choked w/ reducers | 5 |  | 25.3382 |  |  | 72.9117 |  |  | 71.6397 |  |  | 24.9913 |  |  | 14.5092 |  |  | 10.6528 |  |  | 8.9039 |  |  | 8.3963 |  |  | 7.7576 |  |  | 11.2412
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 26.4424 |  |  | 106.5817 |  |  | 71.6397 |  |  | 24.9913 |  |  | 14.5092 |  |  | 10.6528 |  |  | 8.9039 |  |  | 8.3963 |  |  | 7.7576 |  |  | 11.2412
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 24.4424 | 5307.1179 |  | 101.5817 | 10154.6154 |  | 7174 | 25113.5723 |  | 7174 | 48914.8286 |  | 7174 | 80446.8837 |  | 7174 | 112832.9477 |  | 7174 | 143267.9032 |  | 7174 | 167992.8839 |  | 7174 | 187424.343 |  | 7174 | 209103.4069
[13 empty] | Next iteration flow rate |  |  | 5413.2602 | Abs Value of | Flow this | 10256.1615 | Abs Value of | Flow this | 25364.708 | Abs Value of | Flow this | 49403.9769 | Abs Value of | Flow this | 81251.3526 | Abs Value of | Flow this | 113961.2772 | Abs Value of | Flow this | 144700.5823 | Abs Value of | Flow this | 169672.8127 | Abs Value of | Flow this | 189298.5864 | Abs Value of | Flow this | 211194.4409 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.8377 |  |  | 58.5775 |  |  | -156.028 |  |  | -872.7563 |  |  | -2532.016 |  |  | -5078.2661 |  |  | -8248.8556 |  |  | -11379.3772 |  |  | -14188.6908 |  |  | -17685.488
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.42854 |  |  | 0.28257 |  |  | -0.75265 |  |  | -4.21 |  |  | -12.214 |  |  | -24.4967 |  |  | -39.791 |  |  | -54.8921 |  |  | -68.4437 |  |  | -85.3116
[13 empty] | Delta P at this iteration flow rate |  |  | 38.8377 |  |  | 8.5775 |  |  | -206.028 |  |  | -922.7563 |  |  | -2582.016 |  |  | -5128.2661 |  |  | -8298.8556 |  |  | -11429.3772 |  |  | -14238.6908 |  |  | -17735.488
[13 empty] | Press drop ratio this iteration |  |  | 0.43718 |  |  | 0.14643 |  |  | 1.3205 |  |  | 1.0573 |  |  | 1.0197 |  |  | 1.0098 |  |  | 1.0061 |  |  | 1.0044 |  |  | 1.0035 |  |  | 1.0028
[13 empty] | Expansion factor | 12 |  | 0.77231 |  |  | 0.92375 |  |  | 0.30213 |  |  | 0.43355 |  |  | 0.43869 |  |  | 0.41243 |  |  | 0.37423 |  |  | 0.31742 |  |  | 0.43641 |  |  | 0.14501
[13 empty] | C Non choked w/ reducers | 5 |  | 27.1451 |  |  | 112.747 |  |  | 106.8211 |  |  | 29.1343 |  |  | 16.8183 |  |  | 12.8426 |  |  | 11.4649 |  |  | 12.2051 |  |  | 9.0268 |  |  | 31.9608
[13 empty] | C Choked w/ reducers | 5 |  | 25.977 |  |  | 74.6798 |  |  | 70.0118 |  |  | 24.6866 |  |  | 14.354 |  |  | 10.5431 |  |  | 8.8136 |  |  | 8.3116 |  |  | 7.6797 |  |  | 11.1286
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 27.1451 |  |  | 112.747 |  |  | 70.0118 |  |  | 24.6866 |  |  | 14.354 |  |  | 10.5431 |  |  | 8.8136 |  |  | 8.3116 |  |  | 7.6797 |  |  | 11.1286
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 25.1451 | 5413.2602 |  | 107.747 | 10256.1615 |  | 7174 | 25364.708 |  | 7174 | 49403.9769 |  | 7174 | 81251.3526 |  | 7174 | 113961.2772 |  | 7174 | 144700.5823 |  | 7174 | 169672.8127 |  | 7174 | 189298.5864 |  | 7174 | 211194.4409
[13 empty] | Next iteration flow rate |  |  | 5521.5254 | Abs Value of | Flow this | 10358.7232 | Abs Value of | Flow this | 25618.3551 | Abs Value of | Flow this | 49898.0167 | Abs Value of | Flow this | 82063.8661 | Abs Value of | Flow this | 115100.89 | Abs Value of | Flow this | 146147.5881 | Abs Value of | Flow this | 171369.5408 | Abs Value of | Flow this | 191191.5723 | Abs Value of | Flow this | 213306.3853 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.3656 |  |  | 57.7344 |  |  | -161.1847 |  |  | -892.3192 |  |  | -2584.9301 |  |  | -5182.3597 |  |  | -8416.6781 |  |  | -11610.1232 |  |  | -14475.904 |  |  | -18042.9869
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.42626 |  |  | 0.2785 |  |  | -0.77753 |  |  | -4.3044 |  |  | -12.4692 |  |  | -24.9988 |  |  | -40.6006 |  |  | -56.0052 |  |  | -69.8292 |  |  | -87.0362
[13 empty] | Delta P at this iteration flow rate |  |  | 38.3656 |  |  | 7.7344 |  |  | -211.1847 |  |  | -942.3192 |  |  | -2634.9301 |  |  | -5232.3597 |  |  | -8466.6781 |  |  | -11660.1232 |  |  | -14525.904 |  |  | -18092.9869
[13 empty] | Press drop ratio this iteration |  |  | 0.43417 |  |  | 0.13397 |  |  | 1.3102 |  |  | 1.056 |  |  | 1.0193 |  |  | 1.0096 |  |  | 1.0059 |  |  | 1.0043 |  |  | 1.0035 |  |  | 1.0028
[13 empty] | Expansion factor | 12 |  | 0.77388 |  |  | 0.93024 |  |  | 0.30755 |  |  | 0.43423 |  |  | 0.43891 |  |  | 0.41254 |  |  | 0.37431 |  |  | 0.31748 |  |  | 0.43645 |  |  | 0.14506
[13 empty] | C Non choked w/ reducers | 5 |  | 27.8756 |  |  | 119.9501 |  |  | 102.9983 |  |  | 28.753 |  |  | 16.6336 |  |  | 12.7082 |  |  | 11.3471 |  |  | 12.0804 |  |  | 8.9357 |  |  | 31.6312
[13 empty] | C Choked w/ reducers | 5 |  | 26.6381 |  |  | 76.5281 |  |  | 68.4497 |  |  | 24.3868 |  |  | 14.2008 |  |  | 10.4347 |  |  | 8.7243 |  |  | 8.2279 |  |  | 7.6026 |  |  | 11.0172
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 27.8756 |  |  | 119.9501 |  |  | 68.4497 |  |  | 24.3868 |  |  | 14.2008 |  |  | 10.4347 |  |  | 8.7243 |  |  | 8.2279 |  |  | 7.6026 |  |  | 11.0172
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 25.8756 | 5521.5254 |  | 114.9501 | 10358.7232 |  | 7174 | 25618.3551 |  | 7174 | 49898.0167 |  | 7174 | 82063.8661 |  | 7174 | 115100.89 |  | 7174 | 146147.5881 |  | 7174 | 171369.5408 |  | 7174 | 191191.5723 |  | 7174 | 213306.3853
[13 empty] | Next iteration flow rate |  |  | 5631.9559 | Abs Value of | Flow this | 10462.3104 | Abs Value of | Flow this | 25874.5386 | Abs Value of | Flow this | 50396.9969 | Abs Value of | Flow this | 82884.5048 | Abs Value of | Flow this | 116251.8989 | Abs Value of | Flow this | 147609.064 | Abs Value of | Flow this | 173083.2362 | Abs Value of | Flow this | 193103.488 | Abs Value of | Flow this | 215439.4492 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.8745 |  |  | 56.8743 |  |  | -166.445 |  |  | -912.2754 |  |  | -2638.9077 |  |  | -5288.5456 |  |  | -8587.8739 |  |  | -11845.5072 |  |  | -14768.8902 |  |  | -18407.6714
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.42389 |  |  | 0.27435 |  |  | -0.8029 |  |  | -4.4007 |  |  | -12.7296 |  |  | -25.511 |  |  | -41.4264 |  |  | -57.1406 |  |  | -71.2425 |  |  | -88.7953
[13 empty] | Delta P at this iteration flow rate |  |  | 37.8745 |  |  | 6.8743 |  |  | -216.445 |  |  | -962.2754 |  |  | -2688.9077 |  |  | -5338.5456 |  |  | -8637.8739 |  |  | -11895.5072 |  |  | -14818.8902 |  |  | -18457.6714
[13 empty] | Press drop ratio this iteration |  |  | 0.43101 |  |  | 0.12087 |  |  | 1.3004 |  |  | 1.0548 |  |  | 1.0189 |  |  | 1.0095 |  |  | 1.0058 |  |  | 1.0042 |  |  | 1.0034 |  |  | 1.0027
[13 empty] | Expansion factor | 12 |  | 0.77553 |  |  | 0.93706 |  |  | 0.31273 |  |  | 0.43488 |  |  | 0.43913 |  |  | 0.41266 |  |  | 0.37438 |  |  | 0.31754 |  |  | 0.43649 |  |  | 0.14511
[13 empty] | C Non choked w/ reducers | 5 |  | 28.6358 |  |  | 128.5307 |  |  | 99.4443 |  |  | 28.3789 |  |  | 16.4514 |  |  | 12.5754 |  |  | 11.2306 |  |  | 11.9571 |  |  | 8.8455 |  |  | 31.3054
[13 empty] | C Choked w/ reducers | 5 |  | 27.3227 |  |  | 78.4622 |  |  | 66.9493 |  |  | 24.0919 |  |  | 14.0494 |  |  | 10.3274 |  |  | 8.6359 |  |  | 8.1451 |  |  | 7.5263 |  |  | 10.9069
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 28.6358 |  |  | 128.5307 |  |  | 66.9493 |  |  | 24.0919 |  |  | 14.0494 |  |  | 10.3274 |  |  | 8.6359 |  |  | 8.1451 |  |  | 7.5263 |  |  | 10.9069
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 26.6358 | 5631.9559 |  | 123.5307 | 10462.3104 |  | 7174 | 25874.5386 |  | 7174 | 50396.9969 |  | 7174 | 82884.5048 |  | 7174 | 116251.8989 |  | 7174 | 147609.064 |  | 7174 | 173083.2362 |  | 7174 | 193103.488 |  | 7174 | 215439.4492
[13 empty] | Next iteration flow rate |  |  | 5744.5951 | Abs Value of | Flow this | 10566.9335 | Abs Value of | Flow this | 26133.284 | Abs Value of | Flow this | 50900.9668 | Abs Value of | Flow this | 83713.3498 | Abs Value of | Flow this | 117414.4179 | Abs Value of | Flow this | 149085.1546 | Abs Value of | Flow this | 174814.0686 | Abs Value of | Flow this | 195034.5229 | Abs Value of | Flow this | 217593.8437 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.3635 |  |  | 55.997 |  |  | -171.811 |  |  | -932.6326 |  |  | -2693.9702 |  |  | -5396.8659 |  |  | -8762.5106 |  |  | -12085.6224 |  |  | -15067.7654 |  |  | -18779.6861
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.42143 |  |  | 0.27012 |  |  | -0.82879 |  |  | -4.4989 |  |  | -12.9952 |  |  | -26.0335 |  |  | -42.2688 |  |  | -58.2989 |  |  | -72.6842 |  |  | -90.5899
[13 empty] | Delta P at this iteration flow rate |  |  | 37.3635 |  |  | 5.997 |  |  | -221.811 |  |  | -982.6326 |  |  | -2743.9702 |  |  | -5446.8659 |  |  | -8812.5106 |  |  | -12135.6224 |  |  | -15117.7654 |  |  | -18829.6861
[13 empty] | Press drop ratio this iteration |  |  | 0.42768 |  |  | 0.1071 |  |  | 1.291 |  |  | 1.0536 |  |  | 1.0186 |  |  | 1.0093 |  |  | 1.0057 |  |  | 1.0041 |  |  | 1.0033 |  |  | 1.0027
[13 empty] | Expansion factor | 12 |  | 0.77726 |  |  | 0.94424 |  |  | 0.31769 |  |  | 0.43552 |  |  | 0.43934 |  |  | 0.41277 |  |  | 0.37445 |  |  | 0.31759 |  |  | 0.43652 |  |  | 0.14515
[13 empty] | C Non choked w/ reducers | 5 |  | 29.4277 |  |  | 139.0083 |  |  | 96.1305 |  |  | 28.0116 |  |  | 16.2715 |  |  | 12.444 |  |  | 11.1153 |  |  | 11.8351 |  |  | 8.7563 |  |  | 30.9831
[13 empty] | C Choked w/ reducers | 5 |  | 28.0322 |  |  | 80.4884 |  |  | 65.5069 |  |  | 23.8017 |  |  | 13.8999 |  |  | 10.2213 |  |  | 8.5484 |  |  | 8.0631 |  |  | 7.4508 |  |  | 10.7978
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 29.4277 |  |  | 139.0083 |  |  | 65.5069 |  |  | 23.8017 |  |  | 13.8999 |  |  | 10.2213 |  |  | 8.5484 |  |  | 8.0631 |  |  | 7.4508 |  |  | 10.7978
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 27.4277 | 5744.5951 |  | 134.0083 | 10566.9335 |  | 7174 | 26133.284 |  | 7174 | 50900.9668 |  | 7174 | 83713.3498 |  | 7174 | 117414.4179 |  | 7174 | 149085.1546 |  | 7174 | 174814.0686 |  | 7174 | 195034.5229 |  | 7174 | 217593.8437
[13 empty] | Next iteration flow rate |  |  | 5859.487 | Abs Value of | Flow this | 10672.6028 | Abs Value of | Flow this | 26394.6168 | Abs Value of | Flow this | 51409.9765 | Abs Value of | Flow this | 84550.4833 | Abs Value of | Flow this | 118588.5621 | Abs Value of | Flow this | 150576.0062 | Abs Value of | Flow this | 176562.2093 | Abs Value of | Flow this | 196984.8681 | Abs Value of | Flow this | 219769.7821 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.8319 |  |  | 55.102 |  |  | -177.2849 |  |  | -953.399 |  |  | -2750.1395 |  |  | -5507.3634 |  |  | -8940.6576 |  |  | -12330.5639 |  |  | -15372.648 |  |  | -19159.1783
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.41886 |  |  | 0.2658 |  |  | -0.85519 |  |  | -4.599 |  |  | -13.2662 |  |  | -26.5665 |  |  | -43.1281 |  |  | -59.4804 |  |  | -74.1549 |  |  | -92.4205
[13 empty] | Delta P at this iteration flow rate |  |  | 36.8319 |  |  | 5.102 |  |  | -227.2849 |  |  | -1003.399 |  |  | -2800.1395 |  |  | -5557.3634 |  |  | -8990.6576 |  |  | -12380.5639 |  |  | -15422.648 |  |  | -19209.1783
[13 empty] | Press drop ratio this iteration |  |  | 0.42417 |  |  | 0.092593 |  |  | 1.282 |  |  | 1.0524 |  |  | 1.0182 |  |  | 1.0091 |  |  | 1.0056 |  |  | 1.0041 |  |  | 1.0033 |  |  | 1.0026
[13 empty] | Expansion factor | 12 |  | 0.77909 |  |  | 0.95179 |  |  | 0.32244 |  |  | 0.43615 |  |  | 0.43955 |  |  | 0.41288 |  |  | 0.37452 |  |  | 0.31765 |  |  | 0.43656 |  |  | 0.1452
[13 empty] | C Non choked w/ reducers | 5 |  | 30.2535 |  |  | 152.2288 |  |  | 93.0324 |  |  | 27.6511 |  |  | 16.0939 |  |  | 12.3142 |  |  | 11.0013 |  |  | 11.7144 |  |  | 8.668 |  |  | 30.6644
[13 empty] | C Choked w/ reducers | 5 |  | 28.7679 |  |  | 82.6137 |  |  | 64.1191 |  |  | 23.5161 |  |  | 13.7522 |  |  | 10.1164 |  |  | 8.4618 |  |  | 7.9819 |  |  | 7.3761 |  |  | 10.6897
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 30.2535 |  |  | 152.2288 |  |  | 64.1191 |  |  | 23.5161 |  |  | 13.7522 |  |  | 10.1164 |  |  | 8.4618 |  |  | 7.9819 |  |  | 7.3761 |  |  | 10.6897
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 28.2535 | 5859.487 |  | 147.2288 | 10672.6028 |  | 7174 | 26394.6168 |  | 7174 | 51409.9765 |  | 7174 | 84550.4833 |  | 7174 | 118588.5621 |  | 7174 | 150576.0062 |  | 7174 | 176562.2093 |  | 7174 | 196984.8681 |  | 7174 | 219769.7821
[13 empty] | Next iteration flow rate |  |  | 5976.6767 | Abs Value of | Flow this | 10779.3289 | Abs Value of | Flow this | 26658.563 | Abs Value of | Flow this | 51924.0763 | Abs Value of | Flow this | 85395.9881 | Abs Value of | Flow this | 119774.4477 | Abs Value of | Flow this | 152081.7662 | Abs Value of | Flow this | 178327.8314 | Abs Value of | Flow this | 198954.7168 | Abs Value of | Flow this | 221967.4799 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.2787 |  |  | 54.1891 |  |  | -182.8689 |  |  | -974.5829 |  |  | -2807.4379 |  |  | -5620.0819 |  |  | -9122.3853 |  |  | -12580.4288 |  |  | -15683.6587 |  |  | -19546.2983
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.41619 |  |  | 0.2614 |  |  | -0.88213 |  |  | -4.7012 |  |  | -13.5426 |  |  | -27.1103 |  |  | -44.0048 |  |  | -60.6857 |  |  | -75.6552 |  |  | -94.2879
[13 empty] | Delta P at this iteration flow rate |  |  | 36.2787 |  |  | 4.1891 |  |  | -232.8689 |  |  | -1024.5829 |  |  | -2857.4379 |  |  | -5670.0819 |  |  | -9172.3853 |  |  | -12630.4288 |  |  | -15733.6587 |  |  | -19596.2983
[13 empty] | Press drop ratio this iteration |  |  | 0.42048 |  |  | 0.077305 |  |  | 1.2734 |  |  | 1.0513 |  |  | 1.0178 |  |  | 1.0089 |  |  | 1.0055 |  |  | 1.004 |  |  | 1.0032 |  |  | 1.0026
[13 empty] | Expansion factor | 12 |  | 0.78101 |  |  | 0.95975 |  |  | 0.32699 |  |  | 0.43676 |  |  | 0.43975 |  |  | 0.41298 |  |  | 0.37459 |  |  | 0.3177 |  |  | 0.4366 |  |  | 0.14524
[13 empty] | C Non choked w/ reducers | 5 |  | 31.1156 |  |  | 169.6842 |  |  | 90.1288 |  |  | 27.2972 |  |  | 15.9186 |  |  | 12.1859 |  |  | 10.8886 |  |  | 11.5951 |  |  | 8.5807 |  |  | 30.3493
[13 empty] | C Choked w/ reducers | 5 |  | 29.5313 |  |  | 84.8456 |  |  | 62.7829 |  |  | 23.235 |  |  | 13.6062 |  |  | 10.0126 |  |  | 8.3762 |  |  | 7.9016 |  |  | 7.3021 |  |  | 10.5828
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 31.1156 |  |  | 169.6842 |  |  | 62.7829 |  |  | 23.235 |  |  | 13.6062 |  |  | 10.0126 |  |  | 8.3762 |  |  | 7.9016 |  |  | 7.3021 |  |  | 10.5828
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 29.1156 | 5976.6767 |  | 164.6842 | 10779.3289 |  | 7174 | 26658.563 |  | 7174 | 51924.0763 |  | 7174 | 85395.9881 |  | 7174 | 119774.4477 |  | 7174 | 152081.7662 |  | 7174 | 178327.8314 |  | 7174 | 198954.7168 |  | 7174 | 221967.4799
[13 empty] | Next iteration flow rate |  |  | 6096.2102 | Abs Value of | Flow this | 10887.1221 | Abs Value of | Flow this | 26925.1486 | Abs Value of | Flow this | 52443.317 | Abs Value of | Flow this | 86249.948 | Abs Value of | Flow this | 120972.1922 | Abs Value of | Flow this | 153602.5839 | Abs Value of | Flow this | 180111.1097 | Abs Value of | Flow this | 200944.264 | Abs Value of | Flow this | 224187.1547 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 85.7033 |  |  | 53.2578 |  |  | -188.565 |  |  | -996.1925 |  |  | -2865.8879 |  |  | -5735.0661 |  |  | -9307.7658 |  |  | -12835.3159 |  |  | -16000.9208 |  |  | -19941.1994
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.41342 |  |  | 0.25691 |  |  | -0.9096 |  |  | -4.8055 |  |  | -13.8245 |  |  | -27.6649 |  |  | -44.899 |  |  | -61.9153 |  |  | -77.1856 |  |  | -96.1928
[13 empty] | Delta P at this iteration flow rate |  |  | 35.7033 |  |  | 3.2578 |  |  | -238.565 |  |  | -1046.1925 |  |  | -2915.8879 |  |  | -5785.0661 |  |  | -9357.7658 |  |  | -12885.3159 |  |  | -16050.9208 |  |  | -19991.1994
[13 empty] | Press drop ratio this iteration |  |  | 0.41659 |  |  | 0.06117 |  |  | 1.2652 |  |  | 1.0502 |  |  | 1.0174 |  |  | 1.0087 |  |  | 1.0054 |  |  | 1.0039 |  |  | 1.0031 |  |  | 1.0025
[13 empty] | Expansion factor | 12 |  | 0.78303 |  |  | 0.96815 |  |  | 0.33135 |  |  | 0.43736 |  |  | 0.43995 |  |  | 0.41309 |  |  | 0.37466 |  |  | 0.31776 |  |  | 0.43663 |  |  | 0.14529
[13 empty] | C Non choked w/ reducers | 5 |  | 32.0168 |  |  | 194.3305 |  |  | 87.4012 |  |  | 26.9496 |  |  | 15.7455 |  |  | 12.059 |  |  | 10.777 |  |  | 11.477 |  |  | 8.4942 |  |  | 30.0375
[13 empty] | C Choked w/ reducers | 5 |  | 30.3242 |  |  | 87.1926 |  |  | 61.4952 |  |  | 22.9582 |  |  | 13.462 |  |  | 9.91 |  |  | 8.2915 |  |  | 7.8222 |  |  | 7.2289 |  |  | 10.477
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 32.0168 |  |  | 194.3305 |  |  | 61.4952 |  |  | 22.9582 |  |  | 13.462 |  |  | 9.91 |  |  | 8.2915 |  |  | 7.8222 |  |  | 7.2289 |  |  | 10.477
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 30.0168 | 6096.2102 |  | 189.3305 | 10887.1221 |  | 7174 | 26925.1486 |  | 7174 | 52443.317 |  | 7174 | 86249.948 |  | 7174 | 120972.1922 |  | 7174 | 153602.5839 |  | 7174 | 180111.1097 |  | 7174 | 200944.264 |  | 7174 | 224187.1547
[13 empty] | Next iteration flow rate |  |  | 6218.1344 | Abs Value of | Flow this | 10995.9934 | Abs Value of | Flow this | 27194.4001 | Abs Value of | Flow this | 52967.7502 | Abs Value of | Flow this | 87112.4475 | Abs Value of | Flow this | 122181.9141 | Abs Value of | Flow this | 155138.6097 | Abs Value of | Flow this | 181912.2208 | Abs Value of | Flow this | 202953.7066 | Abs Value of | Flow this | 226429.0263 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 85.1046 |  |  | 52.3077 |  |  | -194.3757 |  |  | -1018.2365 |  |  | -2925.5127 |  |  | -5852.3614 |  |  | -9496.8724 |  |  | -13095.3263 |  |  | -16324.5598 |  |  | -20344.038
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.41053 |  |  | 0.25232 |  |  | -0.93763 |  |  | -4.9118 |  |  | -14.1122 |  |  | -28.2307 |  |  | -45.8112 |  |  | -63.1695 |  |  | -78.7468 |  |  | -98.136
[13 empty] | Delta P at this iteration flow rate |  |  | 35.1046 |  |  | 2.3077 |  |  | -244.3757 |  |  | -1068.2365 |  |  | -2975.5127 |  |  | -5902.3614 |  |  | -9546.8724 |  |  | -13145.3263 |  |  | -16374.5598 |  |  | -20394.038
[13 empty] | Press drop ratio this iteration |  |  | 0.41249 |  |  | 0.044119 |  |  | 1.2572 |  |  | 1.0491 |  |  | 1.0171 |  |  | 1.0085 |  |  | 1.0053 |  |  | 1.0038 |  |  | 1.0031 |  |  | 1.0025
[13 empty] | Expansion factor | 12 |  | 0.78517 |  |  | 0.97703 |  |  | 0.33554 |  |  | 0.43794 |  |  | 0.44015 |  |  | 0.41319 |  |  | 0.37473 |  |  | 0.31781 |  |  | 0.43667 |  |  | 0.14533
[13 empty] | C Non choked w/ reducers | 5 |  | 32.9602 |  |  | 233.17 |  |  | 84.8333 |  |  | 26.6082 |  |  | 15.5746 |  |  | 11.9336 |  |  | 10.6667 |  |  | 11.3601 |  |  | 8.4087 |  |  | 29.7293
[13 empty] | C Choked w/ reducers | 5 |  | 31.1483 |  |  | 89.6639 |  |  | 60.2534 |  |  | 22.6858 |  |  | 13.3195 |  |  | 9.8085 |  |  | 8.2076 |  |  | 7.7435 |  |  | 7.1564 |  |  | 10.3722
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 32.9602 |  |  | 233.17 |  |  | 60.2534 |  |  | 22.6858 |  |  | 13.3195 |  |  | 9.8085 |  |  | 8.2076 |  |  | 7.7435 |  |  | 7.1564 |  |  | 10.3722
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 30.9602 | 6218.1344 |  | 228.17 | 10995.9934 |  | 7174 | 27194.4001 |  | 7174 | 52967.7502 |  | 7174 | 87112.4475 |  | 7174 | 122181.9141 |  | 7174 | 155138.6097 |  | 7174 | 181912.2208 |  | 7174 | 202953.7066 |  | 7174 | 226429.0263
[13 empty] | Next iteration flow rate |  |  | 6342.4971 | Abs Value of | Flow this | 11105.9533 | Abs Value of | Flow this | 27466.3441 | Abs Value of | Flow this | 53497.4277 | Abs Value of | Flow this | 87983.572 | Abs Value of | Flow this | 123403.7332 | Abs Value of | Flow this | 156689.9958 | Abs Value of | Flow this | 183731.343 | Abs Value of | Flow this | 204983.2437 | Abs Value of | Flow this | 228693.3165 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 84.4817 |  |  | 51.3386 |  |  | -200.3032 |  |  | -1040.7235 |  |  | -2986.336 |  |  | -5972.0144 |  |  | -9689.78 |  |  | -13360.5628 |  |  | -16654.704 |  |  | -20754.9737
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.40752 |  |  | 0.24765 |  |  | -0.96623 |  |  | -5.0203 |  |  | -14.4056 |  |  | -28.8079 |  |  | -46.7418 |  |  | -64.449 |  |  | -80.3393 |  |  | -100.1183
[13 empty] | Delta P at this iteration flow rate |  |  | 34.4817 |  |  | 1.3386 |  |  | -250.3032 |  |  | -1090.7235 |  |  | -3036.336 |  |  | -6022.0144 |  |  | -9739.78 |  |  | -13410.5628 |  |  | -16704.704 |  |  | -20804.9737
[13 empty] | Press drop ratio this iteration |  |  | 0.40816 |  |  | 0.026074 |  |  | 1.2496 |  |  | 1.048 |  |  | 1.0167 |  |  | 1.0084 |  |  | 1.0052 |  |  | 1.0037 |  |  | 1.003 |  |  | 1.0024
[13 empty] | Expansion factor | 12 |  | 0.78743 |  |  | 0.98642 |  |  | 0.33956 |  |  | 0.43851 |  |  | 0.44034 |  |  | 0.41329 |  |  | 0.37479 |  |  | 0.31786 |  |  | 0.4367 |  |  | 0.14537
[13 empty] | C Non choked w/ reducers | 5 |  | 33.9489 |  |  | 309.1456 |  |  | 82.4109 |  |  | 26.2728 |  |  | 15.4059 |  |  | 11.8096 |  |  | 10.5576 |  |  | 11.2446 |  |  | 8.324 |  |  | 29.4244
[13 empty] | C Choked w/ reducers | 5 |  | 32.0055 |  |  | 92.2701 |  |  | 59.0551 |  |  | 22.4176 |  |  | 13.1787 |  |  | 9.7081 |  |  | 8.1247 |  |  | 7.6657 |  |  | 7.0847 |  |  | 10.2685
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 33.9489 |  |  | 309.1456 |  |  | 59.0551 |  |  | 22.4176 |  |  | 13.1787 |  |  | 9.7081 |  |  | 8.1247 |  |  | 7.6657 |  |  | 7.0847 |  |  | 10.2685
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 31.9489 | 6342.4971 |  | 304.1456 | 11105.9533 |  | 7174 | 27466.3441 |  | 7174 | 53497.4277 |  | 7174 | 87983.572 |  | 7174 | 123403.7332 |  | 7174 | 156689.9958 |  | 7174 | 183731.343 |  | 7174 | 204983.2437 |  | 7174 | 228693.3165
[13 empty] | Next iteration flow rate |  |  | 6469.3471 | Abs Value of | Flow this | 11217.0128 | Abs Value of | Flow this | 27741.0076 | Abs Value of | Flow this | 54032.402 | Abs Value of | Flow this | 88863.4077 | Abs Value of | Flow this | 124637.7706 | Abs Value of | Flow this | 158256.8958 | Abs Value of | Flow this | 185568.6564 | Abs Value of | Flow this | 207033.0761 | Abs Value of | Flow this | 230980.2497 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 83.8336 |  |  | 50.35 |  |  | -206.3498 |  |  | -1063.6626 |  |  | -3048.3819 |  |  | -6094.0724 |  |  | -9886.5651 |  |  | -13631.1307 |  |  | -16991.484 |  |  | -21174.1692
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.4044 |  |  | 0.24288 |  |  | -0.99539 |  |  | -5.1309 |  |  | -14.7049 |  |  | -29.3967 |  |  | -47.691 |  |  | -65.7541 |  |  | -81.9639 |  |  | -102.1404
[13 empty] | Delta P at this iteration flow rate |  |  | 33.8336 |  |  | 0.35002 |  |  | -256.3498 |  |  | -1113.6626 |  |  | -3098.3819 |  |  | -6144.0724 |  |  | -9936.5651 |  |  | -13681.1307 |  |  | -17041.484 |  |  | -21224.1692
[13 empty] | Press drop ratio this iteration |  |  | 0.40358 |  |  | 0.0069518 |  |  | 1.2423 |  |  | 1.047 |  |  | 1.0164 |  |  | 1.0082 |  |  | 1.0051 |  |  | 1.0037 |  |  | 1.0029 |  |  | 1.0024
[13 empty] | Expansion factor | 12 |  | 0.78981 |  |  | 0.99638 |  |  | 0.34343 |  |  | 0.43906 |  |  | 0.44053 |  |  | 0.41338 |  |  | 0.37486 |  |  | 0.31791 |  |  | 0.43674 |  |  | 0.14541
[13 empty] | C Non choked w/ reducers | 5 |  | 34.987 |  |  | 610.4158 |  |  | 80.1213 |  |  | 25.9433 |  |  | 15.2393 |  |  | 11.687 |  |  | 10.4497 |  |  | 11.1302 |  |  | 8.2402 |  |  | 29.1228
[13 empty] | C Choked w/ reducers | 5 |  | 32.898 |  |  | 95.0226 |  |  | 57.8978 |  |  | 22.1535 |  |  | 13.0396 |  |  | 9.6088 |  |  | 8.0426 |  |  | 7.5887 |  |  | 7.0137 |  |  | 10.1659
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 34.987 |  |  | 610.4158 |  |  | 57.8978 |  |  | 22.1535 |  |  | 13.0396 |  |  | 9.6088 |  |  | 8.0426 |  |  | 7.5887 |  |  | 7.0137 |  |  | 10.1659
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 32.987 | 6469.3471 |  | 605.4158 | 11217.0128 |  | 7174 | 27741.0076 |  | 7174 | 54032.402 |  | 7174 | 88863.4077 |  | 7174 | 124637.7706 |  | 7174 | 158256.8958 |  | 7174 | 185568.6564 |  | 7174 | 207033.0761 |  | 7174 | 230980.2497
[13 empty] | Next iteration flow rate |  |  | 6598.734 | Abs Value of | Flow this | 11329.183 | Abs Value of | Flow this | 28018.4176 | Abs Value of | Flow this | 54572.726 | Abs Value of | Flow this | 89752.0418 | Abs Value of | Flow this | 125884.1483 | Abs Value of | Flow this | 159839.4647 | Abs Value of | Flow this | 187424.343 | Abs Value of | Flow this | 209103.4069 | Abs Value of | Flow this | 233290.0522 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 83.1594 |  |  | 49.3416 |  |  | -212.5179 |  |  | -1087.0627 |  |  | -3111.6749 |  |  | -6218.5838 |  |  | -10087.3056 |  |  | -13907.1369 |  |  | -17335.0334 |  |  | -21601.7905
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.40115 |  |  | 0.23801 |  |  | -1.0251 |  |  | -5.2438 |  |  | -15.0102 |  |  | -29.9973 |  |  | -48.6594 |  |  | -67.0856 |  |  | -83.6211 |  |  | -104.2032
[13 empty] | Delta P at this iteration flow rate |  |  | 33.1594 |  |  | -0.65845 |  |  | -262.5179 |  |  | -1137.0627 |  |  | -3161.6749 |  |  | -6268.5838 |  |  | -10137.3056 |  |  | -13957.1369 |  |  | -17385.0334 |  |  | -21651.7905
[13 empty] | Press drop ratio this iteration |  |  | 0.39874 |  |  | -0.013345 |  |  | 1.2353 |  |  | 1.046 |  |  | 1.0161 |  |  | 1.008 |  |  | 1.005 |  |  | 1.0036 |  |  | 1.0029 |  |  | 1.0023
[13 empty] | Expansion factor | 12 |  | 0.79233 |  |  | 1.0069 |  |  | 0.34715 |  |  | 0.4396 |  |  | 0.44071 |  |  | 0.41348 |  |  | 0.37492 |  |  | 0.31796 |  |  | 0.43677 |  |  | 0.14545
[13 empty] | C Non choked w/ reducers | 5 |  | 36.0785 |  |  | #NUM! |  |  | 77.9535 |  |  | 25.6194 |  |  | 15.0749 |  |  | 11.5658 |  |  | 10.343 |  |  | 11.0171 |  |  | 8.1573 |  |  | 28.8245
[13 empty] | C Choked w/ reducers | 5 |  | 33.828 |  |  | 97.9344 |  |  | 56.7796 |  |  | 21.8934 |  |  | 12.9021 |  |  | 9.5106 |  |  | 7.9614 |  |  | 7.5124 |  |  | 6.9435 |  |  | 10.0643
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 36.0785 |  |  | #NUM! |  |  | 56.7796 |  |  | 21.8934 |  |  | 12.9021 |  |  | 9.5106 |  |  | 7.9614 |  |  | 7.5124 |  |  | 6.9435 |  |  | 10.0643
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 34.0785 | 6598.734 |  | 7174 | 11329.183 |  | 7174 | 28018.4176 |  | 7174 | 54572.726 |  | 7174 | 89752.0418 |  | 7174 | 125884.1483 |  | 7174 | 159839.4647 |  | 7174 | 187424.343 |  | 7174 | 209103.4069 |  | 7174 | 233290.0522
[13 empty] | Next iteration flow rate |  |  | 6730.7087 | Abs Value of | Flow this | 11442.4748 | Abs Value of | Flow this | 28298.6018 | Abs Value of | Flow this | 55118.4533 | Abs Value of | Flow this | 90649.5622 | Abs Value of | Flow this | 127142.9897 | Abs Value of | Flow this | 161437.8594 | Abs Value of | Flow this | 189298.5864 | Abs Value of | Flow this | 211194.4409 | Abs Value of | Flow this | 235622.9527 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 82.4579 |  |  | 48.3128 |  |  | -218.81 |  |  | -1110.9332 |  |  | -3176.24 |  |  | -6345.5978 |  |  | -10292.0809 |  |  | -14188.6908 |  |  | -17685.488 |  |  | -22038.007
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.39776 |  |  | 0.23305 |  |  | -1.0555 |  |  | -5.3589 |  |  | -15.3216 |  |  | -30.61 |  |  | -49.6472 |  |  | -68.4437 |  |  | -85.3116 |  |  | -106.3074
[13 empty] | Delta P at this iteration flow rate |  |  | 32.4579 |  |  | -1.6872 |  |  | -268.81 |  |  | -1160.9332 |  |  | -3226.24 |  |  | -6395.5978 |  |  | -10342.0809 |  |  | -14238.6908 |  |  | -17735.488 |  |  | -22088.007
[13 empty] | Press drop ratio this iteration |  |  | 0.39363 |  |  | -0.034922 |  |  | 1.2285 |  |  | 1.045 |  |  | 1.0157 |  |  | 1.0079 |  |  | 1.0049 |  |  | 1.0035 |  |  | 1.0028 |  |  | 1.0023
[13 empty] | Expansion factor | 12 |  | 0.79499 |  |  | 1.0182 |  |  | 0.35072 |  |  | 0.44013 |  |  | 0.44089 |  |  | 0.41357 |  |  | 0.37498 |  |  | 0.31801 |  |  | 0.4368 |  |  | 0.14549
[13 empty] | C Non choked w/ reducers | 5 |  | 37.2283 |  |  | #NUM! |  |  | 75.8975 |  |  | 25.3011 |  |  | 14.9124 |  |  | 11.446 |  |  | 10.2374 |  |  | 10.9052 |  |  | 8.0753 |  |  | 28.5295
[13 empty] | C Choked w/ reducers | 5 |  | 34.7981 |  |  | 101.0199 |  |  | 55.6983 |  |  | 21.6372 |  |  | 12.7662 |  |  | 9.4134 |  |  | 7.881 |  |  | 7.437 |  |  | 6.8739 |  |  | 9.9637
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 37.2283 |  |  | #NUM! |  |  | 55.6983 |  |  | 21.6372 |  |  | 12.7662 |  |  | 9.4134 |  |  | 7.881 |  |  | 7.437 |  |  | 6.8739 |  |  | 9.9637
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 35.2283 | 6730.7087 |  | 7174 | 11442.4748 |  | 7174 | 28298.6018 |  | 7174 | 55118.4533 |  | 7174 | 90649.5622 |  | 7174 | 127142.9897 |  | 7174 | 161437.8594 |  | 7174 | 189298.5864 |  | 7174 | 211194.4409 |  | 7174 | 235622.9527
[13 empty] | Next iteration flow rate |  |  | 6865.3229 | Abs Value of | Flow this | 11556.8995 | Abs Value of | Flow this | 28581.5878 | Abs Value of | Flow this | 55669.6378 | Abs Value of | Flow this | 91556.0578 | Abs Value of | Flow this | 128414.4196 | Abs Value of | Flow this | 163052.238 | Abs Value of | Flow this | 191191.5723 | Abs Value of | Flow this | 213306.3853 | Abs Value of | Flow this | 237979.1823 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 81.7281 |  |  | 47.2634 |  |  | -225.2286 |  |  | -1135.2834 |  |  | -3242.103 |  |  | -6475.1648 |  |  | -10500.9723 |  |  | -14475.904 |  |  | -18042.9869 |  |  | -22482.9914
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.39424 |  |  | 0.22799 |  |  | -1.0865 |  |  | -5.4764 |  |  | -15.6393 |  |  | -31.235 |  |  | -50.6548 |  |  | -69.8292 |  |  | -87.0362 |  |  | -108.4539
[13 empty] | Delta P at this iteration flow rate |  |  | 31.7281 |  |  | -2.7366 |  |  | -275.2286 |  |  | -1185.2834 |  |  | -3292.103 |  |  | -6525.1648 |  |  | -10550.9723 |  |  | -14525.904 |  |  | -18092.9869 |  |  | -22532.9914
[13 empty] | Press drop ratio this iteration |  |  | 0.38822 |  |  | -0.057901 |  |  | 1.222 |  |  | 1.044 |  |  | 1.0154 |  |  | 1.0077 |  |  | 1.0048 |  |  | 1.0035 |  |  | 1.0028 |  |  | 1.0022
[13 empty] | Expansion factor | 12 |  | 0.79781 |  |  | 1.0301 |  |  | 0.35416 |  |  | 0.44065 |  |  | 0.44107 |  |  | 0.41367 |  |  | 0.37504 |  |  | 0.31806 |  |  | 0.43683 |  |  | 0.14553
[13 empty] | C Non choked w/ reducers | 5 |  | 38.4419 |  |  | #NUM! |  |  | 73.9445 |  |  | 24.9882 |  |  | 14.752 |  |  | 11.3275 |  |  | 10.1329 |  |  | 10.7945 |  |  | 7.9941 |  |  | 28.2377
[13 empty] | C Choked w/ reducers | 5 |  | 35.811 |  |  | 104.2956 |  |  | 54.6521 |  |  | 21.3848 |  |  | 12.6319 |  |  | 9.3173 |  |  | 7.8014 |  |  | 7.3623 |  |  | 6.8051 |  |  | 9.8642
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 38.4419 |  |  | #NUM! |  |  | 54.6521 |  |  | 21.3848 |  |  | 12.6319 |  |  | 9.3173 |  |  | 7.8014 |  |  | 7.3623 |  |  | 6.8051 |  |  | 9.8642
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 36.4419 | 6865.3229 |  | 7174 | 11556.8995 |  | 7174 | 28581.5878 |  | 7174 | 55669.6378 |  | 7174 | 91556.0578 |  | 7174 | 128414.4196 |  | 7174 | 163052.238 |  | 7174 | 191191.5723 |  | 7174 | 213306.3853 |  | 7174 | 237979.1823
[13 empty] | Next iteration flow rate |  |  | 7002.6293 | Abs Value of | Flow this | 11672.4685 | Abs Value of | Flow this | 28867.4037 | Abs Value of | Flow this | 56226.3342 | Abs Value of | Flow this | 92471.6184 | Abs Value of | Flow this | 129698.5638 | Abs Value of | Flow this | 164682.7604 | Abs Value of | Flow this | 193103.488 | Abs Value of | Flow this | 215439.4492 | Abs Value of | Flow this | 240358.9741 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 80.9688 |  |  | 46.1929 |  |  | -231.7762 |  |  | -1160.1231 |  |  | -3309.2898 |  |  | -6607.3362 |  |  | -10714.0623 |  |  | -14768.8902 |  |  | -18407.6714 |  |  | -22936.9201
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.39058 |  |  | 0.22283 |  |  | -1.118 |  |  | -5.5962 |  |  | -15.9634 |  |  | -31.8726 |  |  | -51.6827 |  |  | -71.2425 |  |  | -88.7953 |  |  | -110.6436
[13 empty] | Delta P at this iteration flow rate |  |  | 30.9688 |  |  | -3.8071 |  |  | -281.7762 |  |  | -1210.1231 |  |  | -3359.2898 |  |  | -6657.3362 |  |  | -10764.0623 |  |  | -14818.8902 |  |  | -18457.6714 |  |  | -22986.9201
[13 empty] | Press drop ratio this iteration |  |  | 0.38248 |  |  | -0.082418 |  |  | 1.2157 |  |  | 1.0431 |  |  | 1.0151 |  |  | 1.0076 |  |  | 1.0047 |  |  | 1.0034 |  |  | 1.0027 |  |  | 1.0022
[13 empty] | Expansion factor | 12 |  | 0.8008 |  |  | 1.0429 |  |  | 0.35748 |  |  | 0.44115 |  |  | 0.44124 |  |  | 0.41375 |  |  | 0.3751 |  |  | 0.3181 |  |  | 0.43686 |  |  | 0.14557
[13 empty] | C Non choked w/ reducers | 5 |  | 39.7254 |  |  | #NUM! |  |  | 72.0865 |  |  | 24.6806 |  |  | 14.5936 |  |  | 11.2103 |  |  | 10.0296 |  |  | 10.6849 |  |  | 7.9137 |  |  | 27.9491
[13 empty] | C Choked w/ reducers | 5 |  | 36.8698 |  |  | 107.7797 |  |  | 53.6393 |  |  | 21.1362 |  |  | 12.4992 |  |  | 9.2222 |  |  | 7.7228 |  |  | 7.2885 |  |  | 6.737 |  |  | 9.7657
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 39.7254 |  |  | #NUM! |  |  | 53.6393 |  |  | 21.1362 |  |  | 12.4992 |  |  | 9.2222 |  |  | 7.7228 |  |  | 7.2885 |  |  | 6.737 |  |  | 9.7657
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 37.7254 | 7002.6293 |  | 7174 | 11672.4685 |  | 7174 | 28867.4037 |  | 7174 | 56226.3342 |  | 7174 | 92471.6184 |  | 7174 | 129698.5638 |  | 7174 | 164682.7604 |  | 7174 | 193103.488 |  | 7174 | 215439.4492 |  | 7174 | 240358.9741
[13 empty] | Next iteration flow rate |  |  | 7142.6819 | Abs Value of | Flow this | 11789.1932 | Abs Value of | Flow this | 29156.0778 | Abs Value of | Flow this | 56788.5975 | Abs Value of | Flow this | 93396.3346 | Abs Value of | Flow this | 130995.5495 | Abs Value of | Flow this | 166329.588 | Abs Value of | Flow this | 195034.5229 | Abs Value of | Flow this | 217593.8437 | Abs Value of | Flow this | 242762.5638 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 80.1788 |  |  | 45.1008 |  |  | -238.4554 |  |  | -1185.4621 |  |  | -3377.827 |  |  | -6742.1641 |  |  | -10931.4355 |  |  | -15067.7654 |  |  | -18779.6861 |  |  | -23399.9727
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.38677 |  |  | 0.21756 |  |  | -1.1503 |  |  | -5.7185 |  |  | -16.294 |  |  | -32.523 |  |  | -52.7313 |  |  | -72.6842 |  |  | -90.5899 |  |  | -112.8773
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1788 |  |  | -4.8992 |  |  | -288.4554 |  |  | -1235.4621 |  |  | -3427.827 |  |  | -6792.1641 |  |  | -10981.4355 |  |  | -15117.7654 |  |  | -18829.6861 |  |  | -23449.9727
[13 empty] | Press drop ratio this iteration |  |  | 0.37639 |  |  | -0.10863 |  |  | 1.2097 |  |  | 1.0422 |  |  | 1.0148 |  |  | 1.0074 |  |  | 1.0046 |  |  | 1.0033 |  |  | 1.0027 |  |  | 1.0021
[13 empty] | Expansion factor | 12 |  | 0.80397 |  |  | 1.0566 |  |  | 0.36067 |  |  | 0.44165 |  |  | 0.44141 |  |  | 0.41384 |  |  | 0.37516 |  |  | 0.31815 |  |  | 0.43689 |  |  | 0.1456
[13 empty] | C Non choked w/ reducers | 5 |  | 41.0859 |  |  | #NUM! |  |  | 70.3163 |  |  | 24.3781 |  |  | 14.4371 |  |  | 11.0945 |  |  | 9.9274 |  |  | 10.5766 |  |  | 7.8342 |  |  | 27.6636
[13 empty] | C Choked w/ reducers | 5 |  | 37.9777 |  |  | 111.4933 |  |  | 52.6582 |  |  | 20.8913 |  |  | 12.3681 |  |  | 9.1282 |  |  | 7.6449 |  |  | 7.2153 |  |  | 6.6696 |  |  | 9.6681
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 41.0859 |  |  | #NUM! |  |  | 52.6582 |  |  | 20.8913 |  |  | 12.3681 |  |  | 9.1282 |  |  | 7.6449 |  |  | 7.2153 |  |  | 6.6696 |  |  | 9.6681
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 39.0859 | 7142.6819 |  | 7174 | 11789.1932 |  | 7174 | 29156.0778 |  | 7174 | 56788.5975 |  | 7174 | 93396.3346 |  | 7174 | 130995.5495 |  | 7174 | 166329.588 |  | 7174 | 195034.5229 |  | 7174 | 217593.8437 |  | 7174 | 242762.5638
[13 empty] | Next iteration flow rate |  |  | 7285.5355 | Abs Value of | Flow this | 11907.0851 | Abs Value of | Flow this | 29447.6385 | Abs Value of | Flow this | 57356.4835 | Abs Value of | Flow this | 94330.2979 | Abs Value of | Flow this | 132305.505 | Abs Value of | Flow this | 167992.8839 | Abs Value of | Flow this | 196984.8681 | Abs Value of | Flow this | 219769.7821 | Abs Value of | Flow this | 245190.1895 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 79.3569 |  |  | 43.9869 |  |  | -245.2689 |  |  | -1211.3104 |  |  | -3447.7418 |  |  | -6879.7021 |  |  | -11153.1779 |  |  | -15372.648 |  |  | -19159.1783 |  |  | -23872.3326
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.3828 |  |  | 0.21218 |  |  | -1.1831 |  |  | -5.8431 |  |  | -16.6313 |  |  | -33.1865 |  |  | -53.8009 |  |  | -74.1549 |  |  | -92.4205 |  |  | -115.1559
[13 empty] | Delta P at this iteration flow rate |  |  | 29.3569 |  |  | -6.0131 |  |  | -295.2689 |  |  | -1261.3104 |  |  | -3497.7418 |  |  | -6929.7021 |  |  | -11203.1779 |  |  | -15422.648 |  |  | -19209.1783 |  |  | -23922.3326
[13 empty] | Press drop ratio this iteration |  |  | 0.36994 |  |  | -0.1367 |  |  | 1.2039 |  |  | 1.0413 |  |  | 1.0145 |  |  | 1.0073 |  |  | 1.0045 |  |  | 1.0033 |  |  | 1.0026 |  |  | 1.0021
[13 empty] | Expansion factor | 12 |  | 0.80733 |  |  | 1.0712 |  |  | 0.36375 |  |  | 0.44213 |  |  | 0.44157 |  |  | 0.41393 |  |  | 0.37521 |  |  | 0.31819 |  |  | 0.43692 |  |  | 0.14564
[13 empty] | C Non choked w/ reducers | 5 |  | 42.5317 |  |  | #NUM! |  |  | 68.6277 |  |  | 24.0806 |  |  | 14.2826 |  |  | 10.9799 |  |  | 9.8263 |  |  | 10.4693 |  |  | 7.7555 |  |  | 27.3811
[13 empty] | C Choked w/ reducers | 5 |  | 39.1385 |  |  | 115.4601 |  |  | 51.7073 |  |  | 20.6499 |  |  | 12.2385 |  |  | 9.0351 |  |  | 7.5678 |  |  | 7.1429 |  |  | 6.6028 |  |  | 9.5716
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 42.5317 |  |  | #NUM! |  |  | 51.7073 |  |  | 20.6499 |  |  | 12.2385 |  |  | 9.0351 |  |  | 7.5678 |  |  | 7.1429 |  |  | 6.6028 |  |  | 9.5716
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 40.5317 | 7285.5355 |  | 7174 | 11907.0851 |  | 7174 | 29447.6385 |  | 7174 | 57356.4835 |  | 7174 | 94330.2979 |  | 7174 | 132305.505 |  | 7174 | 167992.8839 |  | 7174 | 196984.8681 |  | 7174 | 219769.7821 |  | 7174 | 245190.1895
[13 empty] | Next iteration flow rate |  |  | 7431.2463 | Abs Value of | Flow this | 12026.156 | Abs Value of | Flow this | 29742.1149 | Abs Value of | Flow this | 57930.0483 | Abs Value of | Flow this | 95273.6009 | Abs Value of | Flow this | 133628.56 | Abs Value of | Flow this | 169672.8127 | Abs Value of | Flow this | 198954.7168 | Abs Value of | Flow this | 221967.4799 | Abs Value of | Flow this | 247642.0914 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 78.5018 |  |  | 42.8505 |  |  | -252.2193 |  |  | -1237.6783 |  |  | -3519.0619 |  |  | -7020.0047 |  |  | -11379.3772 |  |  | -15683.6587 |  |  | -19546.2983 |  |  | -24354.187
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.37868 |  |  | 0.2067 |  |  | -1.2167 |  |  | -5.9703 |  |  | -16.9753 |  |  | -33.8633 |  |  | -54.8921 |  |  | -75.6552 |  |  | -94.2879 |  |  | -117.4803
[13 empty] | Delta P at this iteration flow rate |  |  | 28.5018 |  |  | -7.1495 |  |  | -302.2193 |  |  | -1287.6783 |  |  | -3569.0619 |  |  | -7070.0047 |  |  | -11429.3772 |  |  | -15733.6587 |  |  | -19596.2983 |  |  | -24404.187
[13 empty] | Press drop ratio this iteration |  |  | 0.36307 |  |  | -0.16685 |  |  | 1.1982 |  |  | 1.0404 |  |  | 1.0142 |  |  | 1.0071 |  |  | 1.0044 |  |  | 1.0032 |  |  | 1.0026 |  |  | 1.0021
[13 empty] | Expansion factor | 12 |  | 0.81091 |  |  | 1.0869 |  |  | 0.36672 |  |  | 0.4426 |  |  | 0.44174 |  |  | 0.41401 |  |  | 0.37527 |  |  | 0.31824 |  |  | 0.43695 |  |  | 0.14567
[13 empty] | C Non choked w/ reducers | 5 |  | 44.0724 |  |  | #NUM! |  |  | 67.0147 |  |  | 23.788 |  |  | 14.1299 |  |  | 10.8666 |  |  | 9.7263 |  |  | 10.3633 |  |  | 7.6776 |  |  | 27.1018
[13 empty] | C Choked w/ reducers | 5 |  | 40.3561 |  |  | 119.7072 |  |  | 50.7853 |  |  | 20.4121 |  |  | 12.1103 |  |  | 8.9431 |  |  | 7.4916 |  |  | 7.0713 |  |  | 6.5368 |  |  | 9.476
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 44.0724 |  |  | #NUM! |  |  | 50.7853 |  |  | 20.4121 |  |  | 12.1103 |  |  | 8.9431 |  |  | 7.4916 |  |  | 7.0713 |  |  | 6.5368 |  |  | 9.476
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 42.0724 | 7431.2463 |  | 7174 | 12026.156 |  | 7174 | 29742.1149 |  | 7174 | 57930.0483 |  | 7174 | 95273.6009 |  | 7174 | 133628.56 |  | 7174 | 169672.8127 |  | 7174 | 198954.7168 |  | 7174 | 221967.4799 |  | 7174 | 247642.0914
[13 empty] | Next iteration flow rate |  |  | 7579.8712 | Abs Value of | Flow this | 12146.4176 | Abs Value of | Flow this | 30039.5361 | Abs Value of | Flow this | 58509.3488 | Abs Value of | Flow this | 96226.3369 | Abs Value of | Flow this | 134964.8456 | Abs Value of | Flow this | 171369.5408 | Abs Value of | Flow this | 200944.264 | Abs Value of | Flow this | 224187.1547 | Abs Value of | Flow this | 250118.5123 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 77.6121 |  |  | 41.6913 |  |  | -259.3094 |  |  | -1264.5761 |  |  | -3591.8156 |  |  | -7163.1273 |  |  | -11610.1232 |  |  | -16000.9208 |  |  | -19941.1994 |  |  | -24845.7267
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.37439 |  |  | 0.20111 |  |  | -1.2509 |  |  | -6.1001 |  |  | -17.3263 |  |  | -34.5537 |  |  | -56.0052 |  |  | -77.1856 |  |  | -96.1928 |  |  | -119.8514
[13 empty] | Delta P at this iteration flow rate |  |  | 27.6121 |  |  | -8.3087 |  |  | -309.3094 |  |  | -1314.5761 |  |  | -3641.8156 |  |  | -7213.1273 |  |  | -11660.1232 |  |  | -16050.9208 |  |  | -19991.1994 |  |  | -24895.7267
[13 empty] | Press drop ratio this iteration |  |  | 0.35577 |  |  | -0.19929 |  |  | 1.1928 |  |  | 1.0395 |  |  | 1.0139 |  |  | 1.007 |  |  | 1.0043 |  |  | 1.0031 |  |  | 1.0025 |  |  | 1.002
[13 empty] | Expansion factor | 12 |  | 0.81471 |  |  | 1.1038 |  |  | 0.36959 |  |  | 0.44306 |  |  | 0.44189 |  |  | 0.4141 |  |  | 0.37532 |  |  | 0.31828 |  |  | 0.43698 |  |  | 0.14571
[13 empty] | C Non choked w/ reducers | 5 |  | 45.7189 |  |  | #NUM! |  |  | 65.4721 |  |  | 23.5001 |  |  | 13.9791 |  |  | 10.7546 |  |  | 9.6273 |  |  | 10.2583 |  |  | 7.6005 |  |  | 26.8254
[13 empty] | C Choked w/ reducers | 5 |  | 41.6351 |  |  | 124.266 |  |  | 49.8906 |  |  | 20.1777 |  |  | 11.9837 |  |  | 8.8521 |  |  | 7.4161 |  |  | 7.0004 |  |  | 6.4714 |  |  | 9.3815
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 45.7189 |  |  | #NUM! |  |  | 49.8906 |  |  | 20.1777 |  |  | 11.9837 |  |  | 8.8521 |  |  | 7.4161 |  |  | 7.0004 |  |  | 6.4714 |  |  | 9.3815
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 43.7189 | 7579.8712 |  | 7174 | 12146.4176 |  | 7174 | 30039.5361 |  | 7174 | 58509.3488 |  | 7174 | 96226.3369 |  | 7174 | 134964.8456 |  | 7174 | 171369.5408 |  | 7174 | 200944.264 |  | 7174 | 224187.1547 |  | 7174 | 250118.5123
[13 empty] | Next iteration flow rate |  |  | 7731.4686 | Abs Value of | Flow this | 12267.8817 | Abs Value of | Flow this | 30339.9314 | Abs Value of | Flow this | 59094.4423 | Abs Value of | Flow this | 97188.6003 | Abs Value of | Flow this | 136314.4941 | Abs Value of | Flow this | 173083.2362 | Abs Value of | Flow this | 202953.7066 | Abs Value of | Flow this | 226429.0263 | Abs Value of | Flow this | 252619.6974 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 76.6866 |  |  | 40.5088 |  |  | -266.542 |  |  | -1292.0146 |  |  | -3666.0316 |  |  | -7309.1266 |  |  | -11845.5072 |  |  | -16324.5598 |  |  | -20344.038 |  |  | -25347.1463
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.36992 |  |  | 0.19541 |  |  | -1.2858 |  |  | -6.2324 |  |  | -17.6843 |  |  | -35.2579 |  |  | -57.1406 |  |  | -78.7468 |  |  | -98.136 |  |  | -122.2701
[13 empty] | Delta P at this iteration flow rate |  |  | 26.6866 |  |  | -9.4912 |  |  | -316.542 |  |  | -1342.0146 |  |  | -3716.0316 |  |  | -7359.1266 |  |  | -11895.5072 |  |  | -16374.5598 |  |  | -20394.038 |  |  | -25397.1463
[13 empty] | Press drop ratio this iteration |  |  | 0.348 |  |  | -0.2343 |  |  | 1.1876 |  |  | 1.0387 |  |  | 1.0136 |  |  | 1.0068 |  |  | 1.0042 |  |  | 1.0031 |  |  | 1.0025 |  |  | 1.002
[13 empty] | Expansion factor | 12 |  | 0.81876 |  |  | 1.122 |  |  | 0.37235 |  |  | 0.44351 |  |  | 0.44205 |  |  | 0.41418 |  |  | 0.37538 |  |  | 0.31832 |  |  | 0.43701 |  |  | 0.14574
[13 empty] | C Non choked w/ reducers | 5 |  | 47.4845 |  |  | #NUM! |  |  | 63.9953 |  |  | 23.2168 |  |  | 13.8301 |  |  | 10.6439 |  |  | 9.5294 |  |  | 10.1544 |  |  | 7.5242 |  |  | 26.5521
[13 empty] | C Choked w/ reducers | 5 |  | 42.9803 |  |  | 129.1725 |  |  | 49.0222 |  |  | 19.9467 |  |  | 11.8585 |  |  | 8.762 |  |  | 7.3414 |  |  | 6.9302 |  |  | 6.4067 |  |  | 9.2878
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 47.4845 |  |  | #NUM! |  |  | 49.0222 |  |  | 19.9467 |  |  | 11.8585 |  |  | 8.762 |  |  | 7.3414 |  |  | 6.9302 |  |  | 6.4067 |  |  | 9.2878
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 45.4845 | 7731.4686 |  | 7174 | 12267.8817 |  | 7174 | 30339.9314 |  | 7174 | 59094.4423 |  | 7174 | 97188.6003 |  | 7174 | 136314.4941 |  | 7174 | 173083.2362 |  | 7174 | 202953.7066 |  | 7174 | 226429.0263 |  | 7174 | 252619.6974
[13 empty] | Next iteration flow rate |  |  | 7886.098 | Abs Value of | Flow this | 12390.5606 | Abs Value of | Flow this | 30643.3307 | Abs Value of | Flow this | 59685.3867 | Abs Value of | Flow this | 98160.4863 | Abs Value of | Flow this | 137677.639 | Abs Value of | Flow this | 174814.0686 | Abs Value of | Flow this | 204983.2437 | Abs Value of | Flow this | 228693.3165 | Abs Value of | Flow this | 255145.8944 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 75.7236 |  |  | 39.3025 |  |  | -273.92 |  |  | -1320.0046 |  |  | -3741.7393 |  |  | -7458.0606 |  |  | -12085.6224 |  |  | -16654.704 |  |  | -20754.9737 |  |  | -25858.6444
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.36528 |  |  | 0.18959 |  |  | -1.3213 |  |  | -6.3675 |  |  | -18.0495 |  |  | -35.9764 |  |  | -58.2989 |  |  | -80.3393 |  |  | -100.1183 |  |  | -124.7375
[13 empty] | Delta P at this iteration flow rate |  |  | 25.7236 |  |  | -10.6975 |  |  | -323.92 |  |  | -1370.0046 |  |  | -3791.7393 |  |  | -7508.0606 |  |  | -12135.6224 |  |  | -16704.704 |  |  | -20804.9737 |  |  | -25908.6444
[13 empty] | Press drop ratio this iteration |  |  | 0.3397 |  |  | -0.27218 |  |  | 1.1825 |  |  | 1.0379 |  |  | 1.0134 |  |  | 1.0067 |  |  | 1.0041 |  |  | 1.003 |  |  | 1.0024 |  |  | 1.0019
[13 empty] | Expansion factor | 12 |  | 0.82308 |  |  | 1.1417 |  |  | 0.37502 |  |  | 0.44395 |  |  | 0.4422 |  |  | 0.41426 |  |  | 0.37543 |  |  | 0.31836 |  |  | 0.43704 |  |  | 0.14578
[13 empty] | C Non choked w/ reducers | 5 |  | 49.3846 |  |  | #NUM! |  |  | 62.5797 |  |  | 22.9381 |  |  | 13.683 |  |  | 10.5343 |  |  | 9.4326 |  |  | 10.0517 |  |  | 7.4487 |  |  | 26.2816
[13 empty] | C Choked w/ reducers | 5 |  | 44.3975 |  |  | 134.4684 |  |  | 48.1788 |  |  | 19.719 |  |  | 11.7347 |  |  | 8.6729 |  |  | 7.2675 |  |  | 6.8608 |  |  | 6.3427 |  |  | 9.1952
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 49.3846 |  |  | #NUM! |  |  | 48.1788 |  |  | 19.719 |  |  | 11.7347 |  |  | 8.6729 |  |  | 7.2675 |  |  | 6.8608 |  |  | 6.3427 |  |  | 9.1952
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 47.3846 | 7886.098 |  | 7174 | 12390.5606 |  | 7174 | 30643.3307 |  | 7174 | 59685.3867 |  | 7174 | 98160.4863 |  | 7174 | 137677.639 |  | 7174 | 174814.0686 |  | 7174 | 204983.2437 |  | 7174 | 228693.3165 |  | 7174 | 255145.8944
[13 empty] | Next iteration flow rate |  |  | 8043.8199 | Abs Value of | Flow this | 12514.4662 | Abs Value of | Flow this | 30949.764 | Abs Value of | Flow this | 60282.2406 | Abs Value of | Flow this | 99142.0911 | Abs Value of | Flow this | 139054.4154 | Abs Value of | Flow this | 176562.2093 | Abs Value of | Flow this | 207033.0761 | Abs Value of | Flow this | 230980.2497 | Abs Value of | Flow this | 257697.3533 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 74.7217 |  |  | 38.072 |  |  | -281.4463 |  |  | -1348.5572 |  |  | -3818.9688 |  |  | -7609.9881 |  |  | -12330.5639 |  |  | -16991.484 |  |  | -21174.1692 |  |  | -26380.4237
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.36044 |  |  | 0.18365 |  |  | -1.3576 |  |  | -6.5052 |  |  | -18.422 |  |  | -36.7092 |  |  | -59.4804 |  |  | -81.9639 |  |  | -102.1404 |  |  | -127.2545
[13 empty] | Delta P at this iteration flow rate |  |  | 24.7217 |  |  | -11.928 |  |  | -331.4463 |  |  | -1398.5572 |  |  | -3868.9688 |  |  | -7659.9881 |  |  | -12380.5639 |  |  | -17041.484 |  |  | -21224.1692 |  |  | -26430.4237
[13 empty] | Press drop ratio this iteration |  |  | 0.33085 |  |  | -0.3133 |  |  | 1.1777 |  |  | 1.0371 |  |  | 1.0131 |  |  | 1.0066 |  |  | 1.0041 |  |  | 1.0029 |  |  | 1.0024 |  |  | 1.0019
[13 empty] | Expansion factor | 12 |  | 0.82769 |  |  | 1.1631 |  |  | 0.3776 |  |  | 0.44438 |  |  | 0.44235 |  |  | 0.41434 |  |  | 0.37548 |  |  | 0.31841 |  |  | 0.43706 |  |  | 0.14581
[13 empty] | C Non choked w/ reducers | 5 |  | 51.4381 |  |  | #NUM! |  |  | 61.2215 |  |  | 22.6638 |  |  | 13.5376 |  |  | 10.426 |  |  | 9.3368 |  |  | 9.95 |  |  | 7.374 |  |  | 26.0141
[13 empty] | C Choked w/ reducers | 5 |  | 45.8926 |  |  | 140.2027 |  |  | 47.3594 |  |  | 19.4945 |  |  | 11.6124 |  |  | 8.5848 |  |  | 7.1944 |  |  | 6.7921 |  |  | 6.2793 |  |  | 9.1034
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 51.4381 |  |  | #NUM! |  |  | 47.3594 |  |  | 19.4945 |  |  | 11.6124 |  |  | 8.5848 |  |  | 7.1944 |  |  | 6.7921 |  |  | 6.2793 |  |  | 9.1034
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 49.4381 | 8043.8199 |  | 7174 | 12514.4662 |  | 7174 | 30949.764 |  | 7174 | 60282.2406 |  | 7174 | 99142.0911 |  | 7174 | 139054.4154 |  | 7174 | 176562.2093 |  | 7174 | 207033.0761 |  | 7174 | 230980.2497 |  | 7174 | 257697.3533
[13 empty] | Next iteration flow rate |  |  | 8204.6963 | Abs Value of | Flow this | 12639.6108 | Abs Value of | Flow this | 31259.2617 | Abs Value of | Flow this | 60885.063 | Abs Value of | Flow this | 100133.5121 | Abs Value of | Flow this | 140444.9596 | Abs Value of | Flow this | 178327.8314 | Abs Value of | Flow this | 209103.4069 | Abs Value of | Flow this | 233290.0522 | Abs Value of | Flow this | 260274.3268 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 73.6793 |  |  | 36.8167 |  |  | -289.1239 |  |  | -1377.6837 |  |  | -3897.7506 |  |  | -7764.9694 |  |  | -12580.4288 |  |  | -17335.0334 |  |  | -21601.7905 |  |  | -26912.6907
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.35542 |  |  | 0.1776 |  |  | -1.3947 |  |  | -6.6457 |  |  | -18.8021 |  |  | -37.4568 |  |  | -60.6857 |  |  | -83.6211 |  |  | -104.2032 |  |  | -129.822
[13 empty] | Delta P at this iteration flow rate |  |  | 23.6793 |  |  | -13.1833 |  |  | -339.1239 |  |  | -1427.6837 |  |  | -3947.7506 |  |  | -7814.9694 |  |  | -12630.4288 |  |  | -17385.0334 |  |  | -21651.7905 |  |  | -26962.6907
[13 empty] | Press drop ratio this iteration |  |  | 0.32138 |  |  | -0.35808 |  |  | 1.1729 |  |  | 1.0363 |  |  | 1.0128 |  |  | 1.0064 |  |  | 1.004 |  |  | 1.0029 |  |  | 1.0023 |  |  | 1.0019
[13 empty] | Expansion factor | 12 |  | 0.83262 |  |  | 1.1865 |  |  | 0.38009 |  |  | 0.4448 |  |  | 0.4425 |  |  | 0.41441 |  |  | 0.37553 |  |  | 0.31844 |  |  | 0.43709 |  |  | 0.14584
[13 empty] | C Non choked w/ reducers | 5 |  | 53.6674 |  |  | #NUM! |  |  | 59.917 |  |  | 22.3938 |  |  | 13.3939 |  |  | 10.3188 |  |  | 9.242 |  |  | 9.8494 |  |  | 7.3 |  |  | 25.7494
[13 empty] | C Choked w/ reducers | 5 |  | 47.4727 |  |  | 146.4328 |  |  | 46.5628 |  |  | 19.2732 |  |  | 11.4915 |  |  | 8.4975 |  |  | 7.122 |  |  | 6.724 |  |  | 6.2165 |  |  | 9.0126
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 53.6674 |  |  | #NUM! |  |  | 46.5628 |  |  | 19.2732 |  |  | 11.4915 |  |  | 8.4975 |  |  | 7.122 |  |  | 6.724 |  |  | 6.2165 |  |  | 9.0126
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 51.6674 | 8204.6963 |  | 7174 | 12639.6108 |  | 7174 | 31259.2617 |  | 7174 | 60885.063 |  | 7174 | 100133.5121 |  | 7174 | 140444.9596 |  | 7174 | 178327.8314 |  | 7174 | 209103.4069 |  | 7174 | 233290.0522 |  | 7174 | 260274.3268
[13 empty] | Next iteration flow rate |  |  | 8368.7903 | Abs Value of | Flow this | 12766.0069 | Abs Value of | Flow this | 31571.8543 | Abs Value of | Flow this | 61493.9136 | Abs Value of | Flow this | 101134.8472 | Abs Value of | Flow this | 141849.4092 | Abs Value of | Flow this | 180111.1097 | Abs Value of | Flow this | 211194.4409 | Abs Value of | Flow this | 235622.9527 | Abs Value of | Flow this | 262877.0701 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 72.5948 |  |  | 35.5362 |  |  | -296.9558 |  |  | -1407.3957 |  |  | -3978.1159 |  |  | -7923.0658 |  |  | -12835.3159 |  |  | -17685.488 |  |  | -22038.007 |  |  | -27455.6563
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.35018 |  |  | 0.17142 |  |  | -1.4325 |  |  | -6.789 |  |  | -19.1897 |  |  | -38.2195 |  |  | -61.9153 |  |  | -85.3116 |  |  | -106.3074 |  |  | -132.4412
[13 empty] | Delta P at this iteration flow rate |  |  | 22.5948 |  |  | -14.4638 |  |  | -346.9558 |  |  | -1457.3957 |  |  | -4028.1159 |  |  | -7973.0658 |  |  | -12885.3159 |  |  | -17735.488 |  |  | -22088.007 |  |  | -27505.6563
[13 empty] | Press drop ratio this iteration |  |  | 0.31125 |  |  | -0.40702 |  |  | 1.1684 |  |  | 1.0355 |  |  | 1.0126 |  |  | 1.0063 |  |  | 1.0039 |  |  | 1.0028 |  |  | 1.0023 |  |  | 1.0018
[13 empty] | Expansion factor | 12 |  | 0.8379 |  |  | 1.2119 |  |  | 0.3825 |  |  | 0.44521 |  |  | 0.44264 |  |  | 0.41449 |  |  | 0.37558 |  |  | 0.31848 |  |  | 0.43711 |  |  | 0.14587
[13 empty] | C Non choked w/ reducers | 5 |  | 56.1003 |  |  | #NUM! |  |  | 58.663 |  |  | 22.128 |  |  | 13.252 |  |  | 10.2129 |  |  | 9.1482 |  |  | 9.7499 |  |  | 7.2268 |  |  | 25.4876
[13 empty] | C Choked w/ reducers | 5 |  | 49.1455 |  |  | 153.2263 |  |  | 45.7881 |  |  | 19.0549 |  |  | 11.3719 |  |  | 8.4113 |  |  | 7.0504 |  |  | 6.6567 |  |  | 6.1544 |  |  | 8.9227
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 56.1003 |  |  | #NUM! |  |  | 45.7881 |  |  | 19.0549 |  |  | 11.3719 |  |  | 8.4113 |  |  | 7.0504 |  |  | 6.6567 |  |  | 6.1544 |  |  | 8.9227
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 54.1003 | 8368.7903 |  | 7174 | 12766.0069 |  | 7174 | 31571.8543 |  | 7174 | 61493.9136 |  | 7174 | 101134.8472 |  | 7174 | 141849.4092 |  | 7174 | 180111.1097 |  | 7174 | 211194.4409 |  | 7174 | 235622.9527 |  | 7174 | 262877.0701
[13 empty] | Next iteration flow rate |  |  | 8536.1661 | Abs Value of | Flow this | 12893.667 | Abs Value of | Flow this | 31887.5728 | Abs Value of | Flow this | 62108.8528 | Abs Value of | Flow this | 102146.1957 | Abs Value of | Flow this | 143267.9032 | Abs Value of | Flow this | 181912.2208 | Abs Value of | Flow this | 213306.3853 | Abs Value of | Flow this | 237979.1823 | Abs Value of | Flow this | 265505.8408 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 71.4666 |  |  | 34.23 |  |  | -304.9451 |  |  | -1437.7048 |  |  | -4060.0965 |  |  | -8084.3399 |  |  | -13095.3263 |  |  | -18042.9869 |  |  | -22482.9914 |  |  | -28009.5355
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.34474 |  |  | 0.16512 |  |  | -1.471 |  |  | -6.9352 |  |  | -19.5852 |  |  | -38.9974 |  |  | -63.1695 |  |  | -87.0362 |  |  | -108.4539 |  |  | -135.113
[13 empty] | Delta P at this iteration flow rate |  |  | 21.4666 |  |  | -15.77 |  |  | -354.9451 |  |  | -1487.7048 |  |  | -4110.0965 |  |  | -8134.3399 |  |  | -13145.3263 |  |  | -18092.9869 |  |  | -22532.9914 |  |  | -28059.5355
[13 empty] | Press drop ratio this iteration |  |  | 0.30037 |  |  | -0.46071 |  |  | 1.164 |  |  | 1.0348 |  |  | 1.0123 |  |  | 1.0062 |  |  | 1.0038 |  |  | 1.0028 |  |  | 1.0022 |  |  | 1.0018
[13 empty] | Expansion factor | 12 |  | 0.84356 |  |  | 1.2399 |  |  | 0.38484 |  |  | 0.44561 |  |  | 0.44278 |  |  | 0.41456 |  |  | 0.37563 |  |  | 0.31852 |  |  | 0.43714 |  |  | 0.1459
[13 empty] | C Non choked w/ reducers | 5 |  | 58.7713 |  |  | #NUM! |  |  | 57.4564 |  |  | 21.8664 |  |  | 13.1118 |  |  | 10.1081 |  |  | 9.0554 |  |  | 9.6514 |  |  | 7.1543 |  |  | 25.2286
[13 empty] | C Choked w/ reducers | 5 |  | 50.9199 |  |  | 160.6643 |  |  | 45.0343 |  |  | 18.8398 |  |  | 11.2537 |  |  | 8.3259 |  |  | 6.9795 |  |  | 6.59 |  |  | 6.0929 |  |  | 8.8337
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 58.7713 |  |  | #NUM! |  |  | 45.0343 |  |  | 18.8398 |  |  | 11.2537 |  |  | 8.3259 |  |  | 6.9795 |  |  | 6.59 |  |  | 6.0929 |  |  | 8.8337
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 56.7713 | 8536.1661 |  | 7174 | 12893.667 |  | 7174 | 31887.5728 |  | 7174 | 62108.8528 |  | 7174 | 102146.1957 |  | 7174 | 143267.9032 |  | 7174 | 181912.2208 |  | 7174 | 213306.3853 |  | 7174 | 237979.1823 |  | 7174 | 265505.8408
[13 empty] | Next iteration flow rate |  |  | 8706.8894 | Abs Value of | Flow this | 13022.6037 | Abs Value of | Flow this | 32206.4486 | Abs Value of | Flow this | 62729.9413 | Abs Value of | Flow this | 103167.6576 | Abs Value of | Flow this | 144700.5823 | Abs Value of | Flow this | 183731.343 | Abs Value of | Flow this | 215439.4492 | Abs Value of | Flow this | 240358.9741 | Abs Value of | Flow this | 268160.8992 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 70.2927 |  |  | 32.8975 |  |  | -313.0951 |  |  | -1468.6232 |  |  | -4143.725 |  |  | -8248.8556 |  |  | -13360.5628 |  |  | -18407.6714 |  |  | -22936.9201 |  |  | -28574.5477
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.33908 |  |  | 0.15869 |  |  | -1.5103 |  |  | -7.0844 |  |  | -19.9886 |  |  | -39.791 |  |  | -64.449 |  |  | -88.7953 |  |  | -110.6436 |  |  | -137.8385
[13 empty] | Delta P at this iteration flow rate |  |  | 20.2927 |  |  | -17.1025 |  |  | -363.0951 |  |  | -1518.6232 |  |  | -4193.725 |  |  | -8298.8556 |  |  | -13410.5628 |  |  | -18457.6714 |  |  | -22986.9201 |  |  | -28624.5477
[13 empty] | Press drop ratio this iteration |  |  | 0.28869 |  |  | -0.51987 |  |  | 1.1597 |  |  | 1.034 |  |  | 1.0121 |  |  | 1.0061 |  |  | 1.0037 |  |  | 1.0027 |  |  | 1.0022 |  |  | 1.0017
[13 empty] | Expansion factor | 12 |  | 0.84965 |  |  | 1.2707 |  |  | 0.38709 |  |  | 0.44601 |  |  | 0.44291 |  |  | 0.41463 |  |  | 0.37568 |  |  | 0.31856 |  |  | 0.43716 |  |  | 0.14593
[13 empty] | C Non choked w/ reducers | 5 |  | 61.7236 |  |  | #NUM! |  |  | 56.2943 |  |  | 21.6087 |  |  | 12.9732 |  |  | 10.0044 |  |  | 8.9636 |  |  | 9.5539 |  |  | 7.0826 |  |  | 24.9723
[13 empty] | C Choked w/ reducers | 5 |  | 52.8056 |  |  | 168.8436 |  |  | 44.3007 |  |  | 18.6276 |  |  | 11.1369 |  |  | 8.2414 |  |  | 6.9093 |  |  | 6.5241 |  |  | 6.0321 |  |  | 8.7457
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 61.7236 |  |  | #NUM! |  |  | 44.3007 |  |  | 18.6276 |  |  | 11.1369 |  |  | 8.2414 |  |  | 6.9093 |  |  | 6.5241 |  |  | 6.0321 |  |  | 8.7457
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 59.7236 | 8706.8894 |  | 7174 | 13022.6037 |  | 7174 | 32206.4486 |  | 7174 | 62729.9413 |  | 7174 | 103167.6576 |  | 7174 | 144700.5823 |  | 7174 | 183731.343 |  | 7174 | 215439.4492 |  | 7174 | 240358.9741 |  | 7174 | 268160.8992
[13 empty] | Next iteration flow rate |  |  | 8881.0272 | Abs Value of | Flow this | 13152.8297 | Abs Value of | Flow this | 32528.5131 | Abs Value of | Flow this | 63357.2407 | Abs Value of | Flow this | 104199.3342 | Abs Value of | Flow this | 146147.5881 | Abs Value of | Flow this | 185568.6564 | Abs Value of | Flow this | 217593.8437 | Abs Value of | Flow this | 242762.5638 | Abs Value of | Flow this | 270842.5082 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 69.0714 |  |  | 31.5382 |  |  | -321.4088 |  |  | -1500.163 |  |  | -4229.0343 |  |  | -8416.6781 |  |  | -13631.1307 |  |  | -18779.6861 |  |  | -23399.9727 |  |  | -29150.9166
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.33319 |  |  | 0.15213 |  |  | -1.5504 |  |  | -7.2365 |  |  | -20.4001 |  |  | -40.6006 |  |  | -65.7541 |  |  | -90.5899 |  |  | -112.8773 |  |  | -140.6188
[13 empty] | Delta P at this iteration flow rate |  |  | 19.0714 |  |  | -18.4618 |  |  | -371.4088 |  |  | -1550.163 |  |  | -4279.0343 |  |  | -8466.6781 |  |  | -13681.1307 |  |  | -18829.6861 |  |  | -23449.9727 |  |  | -29200.9166
[13 empty] | Press drop ratio this iteration |  |  | 0.27611 |  |  | -0.58538 |  |  | 1.1556 |  |  | 1.0333 |  |  | 1.0118 |  |  | 1.0059 |  |  | 1.0037 |  |  | 1.0027 |  |  | 1.0021 |  |  | 1.0017
[13 empty] | Expansion factor | 12 |  | 0.8562 |  |  | 1.3048 |  |  | 0.38927 |  |  | 0.44639 |  |  | 0.44305 |  |  | 0.4147 |  |  | 0.37572 |  |  | 0.3186 |  |  | 0.43719 |  |  | 0.14596
[13 empty] | C Non choked w/ reducers | 5 |  | 65.0131 |  |  | #NUM! |  |  | 55.1743 |  |  | 21.355 |  |  | 12.8363 |  |  | 9.9019 |  |  | 8.8728 |  |  | 9.4575 |  |  | 7.0117 |  |  | 24.7188
[13 empty] | C Choked w/ reducers | 5 |  | 54.8141 |  |  | 177.8818 |  |  | 43.5864 |  |  | 18.4183 |  |  | 11.0213 |  |  | 8.1579 |  |  | 6.8399 |  |  | 6.4588 |  |  | 5.9718 |  |  | 8.6585
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 65.0131 |  |  | #NUM! |  |  | 43.5864 |  |  | 18.4183 |  |  | 11.0213 |  |  | 8.1579 |  |  | 6.8399 |  |  | 6.4588 |  |  | 5.9718 |  |  | 8.6585
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 63.0131 | 8881.0272 |  | 7174 | 13152.8297 |  | 7174 | 32528.5131 |  | 7174 | 63357.2407 |  | 7174 | 104199.3342 |  | 7174 | 146147.5881 |  | 7174 | 185568.6564 |  | 7174 | 217593.8437 |  | 7174 | 242762.5638 |  | 7174 | 270842.5082
[13 empty] | Next iteration flow rate |  |  | 9058.6477 | Abs Value of | Flow this | 13284.358 | Abs Value of | Flow this | 32853.7982 | Abs Value of | Flow this | 63990.8131 | Abs Value of | Flow this | 105241.3275 | Abs Value of | Flow this | 147609.064 | Abs Value of | Flow this | 187424.343 | Abs Value of | Flow this | 219769.7821 | Abs Value of | Flow this | 245190.1895 | Abs Value of | Flow this | 273550.9333 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 67.8007 |  |  | 30.1516 |  |  | -329.8896 |  |  | -1532.3368 |  |  | -4316.0584 |  |  | -8587.8739 |  |  | -13907.1369 |  |  | -19159.1783 |  |  | -23872.3326 |  |  | -29738.8705
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.32706 |  |  | 0.14545 |  |  | -1.5913 |  |  | -7.3917 |  |  | -20.8199 |  |  | -41.4264 |  |  | -67.0856 |  |  | -92.4205 |  |  | -115.1559 |  |  | -143.455
[13 empty] | Delta P at this iteration flow rate |  |  | 17.8007 |  |  | -19.8484 |  |  | -379.8896 |  |  | -1582.3368 |  |  | -4366.0584 |  |  | -8637.8739 |  |  | -13957.1369 |  |  | -19209.1783 |  |  | -23922.3326 |  |  | -29788.8705
[13 empty] | Press drop ratio this iteration |  |  | 0.26255 |  |  | -0.65829 |  |  | 1.1516 |  |  | 1.0326 |  |  | 1.0116 |  |  | 1.0058 |  |  | 1.0036 |  |  | 1.0026 |  |  | 1.0021 |  |  | 1.0017
[13 empty] | Expansion factor | 12 |  | 0.86326 |  |  | 1.3428 |  |  | 0.39139 |  |  | 0.44676 |  |  | 0.44318 |  |  | 0.41477 |  |  | 0.37577 |  |  | 0.31863 |  |  | 0.43721 |  |  | 0.14599
[13 empty] | C Non choked w/ reducers | 5 |  | 68.7125 |  |  | #NUM! |  |  | 54.0939 |  |  | 21.1051 |  |  | 12.701 |  |  | 9.8005 |  |  | 8.7829 |  |  | 9.362 |  |  | 6.9414 |  |  | 24.4679
[13 empty] | C Choked w/ reducers | 5 |  | 56.9582 |  |  | 187.9227 |  |  | 42.8905 |  |  | 18.2119 |  |  | 10.9071 |  |  | 8.0752 |  |  | 6.7712 |  |  | 6.3942 |  |  | 5.9122 |  |  | 8.5722
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 68.7125 |  |  | #NUM! |  |  | 42.8905 |  |  | 18.2119 |  |  | 10.9071 |  |  | 8.0752 |  |  | 6.7712 |  |  | 6.3942 |  |  | 5.9122 |  |  | 8.5722
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 66.7125 | 9058.6477 |  | 7174 | 13284.358 |  | 7174 | 32853.7982 |  | 7174 | 63990.8131 |  | 7174 | 105241.3275 |  | 7174 | 147609.064 |  | 7174 | 187424.343 |  | 7174 | 219769.7821 |  | 7174 | 245190.1895 |  | 7174 | 273550.9333
[13 empty] | Next iteration flow rate |  |  | 9239.8207 | Abs Value of | Flow this | 13417.2016 | Abs Value of | Flow this | 33182.3362 | Abs Value of | Flow this | 64630.7212 | Abs Value of | Flow this | 106293.7408 | Abs Value of | Flow this | 149085.1546 | Abs Value of | Flow this | 189298.5864 | Abs Value of | Flow this | 221967.4799 | Abs Value of | Flow this | 247642.0914 | Abs Value of | Flow this | 276286.4426 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 66.4788 |  |  | 28.7372 |  |  | -338.5409 |  |  | -1565.1573 |  |  | -4404.8317 |  |  | -8762.5106 |  |  | -14188.6908 |  |  | -19546.2983 |  |  | -24354.187 |  |  | -30338.6423
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.32068 |  |  | 0.13862 |  |  | -1.6331 |  |  | -7.55 |  |  | -21.2481 |  |  | -42.2688 |  |  | -68.4437 |  |  | -94.2879 |  |  | -117.4803 |  |  | -146.3482
[13 empty] | Delta P at this iteration flow rate |  |  | 16.4788 |  |  | -21.2628 |  |  | -388.5409 |  |  | -1615.1573 |  |  | -4454.8317 |  |  | -8812.5106 |  |  | -14238.6908 |  |  | -19596.2983 |  |  | -24404.187 |  |  | -30388.6423
[13 empty] | Press drop ratio this iteration |  |  | 0.24788 |  |  | -0.73991 |  |  | 1.1477 |  |  | 1.0319 |  |  | 1.0114 |  |  | 1.0057 |  |  | 1.0035 |  |  | 1.0026 |  |  | 1.0021 |  |  | 1.0016
[13 empty] | Expansion factor | 12 |  | 0.8709 |  |  | 1.3853 |  |  | 0.39344 |  |  | 0.44713 |  |  | 0.44331 |  |  | 0.41484 |  |  | 0.37581 |  |  | 0.31867 |  |  | 0.43724 |  |  | 0.14602
[13 empty] | C Non choked w/ reducers | 5 |  | 72.9193 |  |  | #NUM! |  |  | 53.051 |  |  | 20.859 |  |  | 12.5673 |  |  | 9.7002 |  |  | 8.694 |  |  | 9.2676 |  |  | 6.8719 |  |  | 24.2198
[13 empty] | C Choked w/ reducers | 5 |  | 59.2526 |  |  | 199.1441 |  |  | 42.2124 |  |  | 18.0083 |  |  | 10.7942 |  |  | 7.9934 |  |  | 6.7032 |  |  | 6.3302 |  |  | 5.8532 |  |  | 8.4867
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 72.9193 |  |  | #NUM! |  |  | 42.2124 |  |  | 18.0083 |  |  | 10.7942 |  |  | 7.9934 |  |  | 6.7032 |  |  | 6.3302 |  |  | 5.8532 |  |  | 8.4867
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 70.9193 | 9239.8207 |  | 7174 | 13417.2016 |  | 7174 | 33182.3362 |  | 7174 | 64630.7212 |  | 7174 | 106293.7408 |  | 7174 | 149085.1546 |  | 7174 | 189298.5864 |  | 7174 | 221967.4799 |  | 7174 | 247642.0914 |  | 7174 | 276286.4426
[13 empty] | Next iteration flow rate |  |  | 9424.6171 | Abs Value of | Flow this | 13551.3736 | Abs Value of | Flow this | 33514.1595 | Abs Value of | Flow this | 65277.0284 | Abs Value of | Flow this | 107356.6782 | Abs Value of | Flow this | 150576.0062 | Abs Value of | Flow this | 191191.5723 | Abs Value of | Flow this | 224187.1547 | Abs Value of | Flow this | 250118.5123 | Abs Value of | Flow this | 279049.3071 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 65.1034 |  |  | 27.2943 |  |  | -347.3661 |  |  | -1598.6375 |  |  | -4495.3894 |  |  | -8940.6576 |  |  | -14475.904 |  |  | -19941.1994 |  |  | -24845.7267 |  |  | -30950.4696
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.31405 |  |  | 0.13166 |  |  | -1.6756 |  |  | -7.7115 |  |  | -21.685 |  |  | -43.1281 |  |  | -69.8292 |  |  | -96.1928 |  |  | -119.8514 |  |  | -149.2996
[13 empty] | Delta P at this iteration flow rate |  |  | 15.1034 |  |  | -22.7057 |  |  | -397.3661 |  |  | -1648.6375 |  |  | -4545.3894 |  |  | -8990.6576 |  |  | -14525.904 |  |  | -19991.1994 |  |  | -24895.7267 |  |  | -31000.4696
[13 empty] | Press drop ratio this iteration |  |  | 0.23199 |  |  | -0.83189 |  |  | 1.1439 |  |  | 1.0313 |  |  | 1.0111 |  |  | 1.0056 |  |  | 1.0035 |  |  | 1.0025 |  |  | 1.002 |  |  | 1.0016
[13 empty] | Expansion factor | 12 |  | 0.87918 |  |  | 1.4332 |  |  | 0.39542 |  |  | 0.44749 |  |  | 0.44343 |  |  | 0.4149 |  |  | 0.37585 |  |  | 0.3187 |  |  | 0.43726 |  |  | 0.14605
[13 empty] | C Non choked w/ reducers | 5 |  | 77.7679 |  |  | #NUM! |  |  | 52.0434 |  |  | 20.6165 |  |  | 12.4351 |  |  | 9.601 |  |  | 8.606 |  |  | 9.1741 |  |  | 6.8031 |  |  | 23.9742
[13 empty] | C Choked w/ reducers | 5 |  | 61.7145 |  |  | 211.7684 |  |  | 41.5513 |  |  | 17.8075 |  |  | 10.6825 |  |  | 7.9125 |  |  | 6.6359 |  |  | 6.2669 |  |  | 5.7947 |  |  | 8.4021
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 77.7679 |  |  | #NUM! |  |  | 41.5513 |  |  | 17.8075 |  |  | 10.6825 |  |  | 7.9125 |  |  | 6.6359 |  |  | 6.2669 |  |  | 5.7947 |  |  | 8.4021
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 75.7679 | 9424.6171 |  | 7174 | 13551.3736 |  | 7174 | 33514.1595 |  | 7174 | 65277.0284 |  | 7174 | 107356.6782 |  | 7174 | 150576.0062 |  | 7174 | 191191.5723 |  | 7174 | 224187.1547 |  | 7174 | 250118.5123 |  | 7174 | 279049.3071
[13 empty] | Next iteration flow rate |  |  | 9613.1094 | Abs Value of | Flow this | 13686.8873 | Abs Value of | Flow this | 33849.3011 | Abs Value of | Flow this | 65929.7987 | Abs Value of | Flow this | 108430.245 | Abs Value of | Flow this | 152081.7662 | Abs Value of | Flow this | 193103.488 | Abs Value of | Flow this | 226429.0263 | Abs Value of | Flow this | 252619.6974 | Abs Value of | Flow this | 281839.8001 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 63.6725 |  |  | 25.8224 |  |  | -356.3686 |  |  | -1632.7906 |  |  | -4587.7672 |  |  | -9122.3853 |  |  | -14768.8902 |  |  | -20344.038 |  |  | -25347.1463 |  |  | -31574.5945
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.30714 |  |  | 0.12456 |  |  | -1.7191 |  |  | -7.8763 |  |  | -22.1306 |  |  | -44.0048 |  |  | -71.2425 |  |  | -98.136 |  |  | -122.2701 |  |  | -152.3102
[13 empty] | Delta P at this iteration flow rate |  |  | 13.6725 |  |  | -24.1776 |  |  | -406.3686 |  |  | -1682.7906 |  |  | -4637.7672 |  |  | -9172.3853 |  |  | -14818.8902 |  |  | -20394.038 |  |  | -25397.1463 |  |  | -31624.5945
[13 empty] | Press drop ratio this iteration |  |  | 0.21473 |  |  | -0.9363 |  |  | 1.1403 |  |  | 1.0306 |  |  | 1.0109 |  |  | 1.0055 |  |  | 1.0034 |  |  | 1.0025 |  |  | 1.002 |  |  | 1.0016
[13 empty] | Expansion factor | 12 |  | 0.88817 |  |  | 1.4875 |  |  | 0.39734 |  |  | 0.44784 |  |  | 0.44356 |  |  | 0.41497 |  |  | 0.3759 |  |  | 0.31873 |  |  | 0.43728 |  |  | 0.14607
[13 empty] | C Non choked w/ reducers | 5 |  | 83.4493 |  |  | #NUM! |  |  | 51.0694 |  |  | 20.3776 |  |  | 12.3045 |  |  | 9.5029 |  |  | 8.519 |  |  | 9.0817 |  |  | 6.735 |  |  | 23.7313
[13 empty] | C Choked w/ reducers | 5 |  | 64.3635 |  |  | 226.0777 |  |  | 40.9067 |  |  | 17.6093 |  |  | 10.572 |  |  | 7.8324 |  |  | 6.5693 |  |  | 6.2042 |  |  | 5.7369 |  |  | 8.3184
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 83.4493 |  |  | #NUM! |  |  | 40.9067 |  |  | 17.6093 |  |  | 10.572 |  |  | 7.8324 |  |  | 6.5693 |  |  | 6.2042 |  |  | 5.7369 |  |  | 8.3184
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 81.4493 | 9613.1094 |  | 7174 | 13686.8873 |  | 7174 | 33849.3011 |  | 7174 | 65929.7987 |  | 7174 | 108430.245 |  | 7174 | 152081.7662 |  | 7174 | 193103.488 |  | 7174 | 226429.0263 |  | 7174 | 252619.6974 |  | 7174 | 281839.8001
[13 empty] | Next iteration flow rate |  |  | 9805.3716 | Abs Value of | Flow this | 13823.7562 | Abs Value of | Flow this | 34187.7941 | Abs Value of | Flow this | 66589.0967 | Abs Value of | Flow this | 109514.5474 | Abs Value of | Flow this | 153602.5839 | Abs Value of | Flow this | 195034.5229 | Abs Value of | Flow this | 228693.3165 | Abs Value of | Flow this | 255145.8944 | Abs Value of | Flow this | 284658.1981 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 62.1837 |  |  | 24.3209 |  |  | -365.5521 |  |  | -1667.6302 |  |  | -4682.0018 |  |  | -9307.7658 |  |  | -15067.7654 |  |  | -20754.9737 |  |  | -25858.6444 |  |  | -32211.2644
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.29996 |  |  | 0.11732 |  |  | -1.7634 |  |  | -8.0444 |  |  | -22.5851 |  |  | -44.899 |  |  | -72.6842 |  |  | -100.1183 |  |  | -124.7375 |  |  | -155.3814
[13 empty] | Delta P at this iteration flow rate |  |  | 12.1837 |  |  | -25.6791 |  |  | -415.5521 |  |  | -1717.6302 |  |  | -4732.0018 |  |  | -9357.7658 |  |  | -15117.7654 |  |  | -20804.9737 |  |  | -25908.6444 |  |  | -32261.2644
[13 empty] | Press drop ratio this iteration |  |  | 0.19593 |  |  | -1.0558 |  |  | 1.1368 |  |  | 1.03 |  |  | 1.0107 |  |  | 1.0054 |  |  | 1.0033 |  |  | 1.0024 |  |  | 1.0019 |  |  | 1.0016
[13 empty] | Expansion factor | 12 |  | 0.89796 |  |  | 1.5498 |  |  | 0.3992 |  |  | 0.44818 |  |  | 0.44368 |  |  | 0.41503 |  |  | 0.37594 |  |  | 0.31877 |  |  | 0.4373 |  |  | 0.1461
[13 empty] | C Non choked w/ reducers | 5 |  | 90.247 |  |  | #NUM! |  |  | 50.1272 |  |  | 20.1423 |  |  | 12.1754 |  |  | 9.4058 |  |  | 8.4329 |  |  | 8.9902 |  |  | 6.6676 |  |  | 23.4909
[13 empty] | C Choked w/ reducers | 5 |  | 67.2225 |  |  | 242.4352 |  |  | 40.2778 |  |  | 17.4139 |  |  | 10.4629 |  |  | 7.7532 |  |  | 6.5034 |  |  | 6.1422 |  |  | 5.6797 |  |  | 8.2355
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 90.247 |  |  | #NUM! |  |  | 40.2778 |  |  | 17.4139 |  |  | 10.4629 |  |  | 7.7532 |  |  | 6.5034 |  |  | 6.1422 |  |  | 5.6797 |  |  | 8.2355
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 88.247 | 9805.3716 |  | 7174 | 13823.7562 |  | 7174 | 34187.7941 |  | 7174 | 66589.0967 |  | 7174 | 109514.5474 |  | 7174 | 153602.5839 |  | 7174 | 195034.5229 |  | 7174 | 228693.3165 |  | 7174 | 255145.8944 |  | 7174 | 284658.1981
[13 empty] | Next iteration flow rate |  |  | 10001.479 | Abs Value of | Flow this | 13961.9938 | Abs Value of | Flow this | 34529.6721 | Abs Value of | Flow this | 67254.9877 | Abs Value of | Flow this | 110609.6929 | Abs Value of | Flow this | 155138.6097 | Abs Value of | Flow this | 196984.8681 | Abs Value of | Flow this | 230980.2497 | Abs Value of | Flow this | 257697.3533 | Abs Value of | Flow this | 287504.7801 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 60.6348 |  |  | 22.7892 |  |  | -374.9203 |  |  | -1703.1701 |  |  | -4778.1306 |  |  | -9496.8724 |  |  | -15372.648 |  |  | -21174.1692 |  |  | -26380.4237 |  |  | -32860.7313
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.29249 |  |  | 0.10993 |  |  | -1.8085 |  |  | -8.2158 |  |  | -23.0489 |  |  | -45.8112 |  |  | -74.1549 |  |  | -102.1404 |  |  | -127.2545 |  |  | -158.5143
[13 empty] | Delta P at this iteration flow rate |  |  | 10.6348 |  |  | -27.2108 |  |  | -424.9203 |  |  | -1753.1701 |  |  | -4828.1306 |  |  | -9546.8724 |  |  | -15422.648 |  |  | -21224.1692 |  |  | -26430.4237 |  |  | -32910.7313
[13 empty] | Press drop ratio this iteration |  |  | 0.17539 |  |  | -1.194 |  |  | 1.1334 |  |  | 1.0294 |  |  | 1.0105 |  |  | 1.0053 |  |  | 1.0033 |  |  | 1.0024 |  |  | 1.0019 |  |  | 1.0015
[13 empty] | Expansion factor | 12 |  | 0.90865 |  |  | 1.6217 |  |  | 0.40101 |  |  | 0.44852 |  |  | 0.4438 |  |  | 0.41509 |  |  | 0.37598 |  |  | 0.3188 |  |  | 0.43732 |  |  | 0.14613
[13 empty] | C Non choked w/ reducers | 5 |  | 98.6034 |  |  | #NUM! |  |  | 49.2151 |  |  | 19.9103 |  |  | 12.0479 |  |  | 9.3098 |  |  | 8.3476 |  |  | 8.8996 |  |  | 6.6009 |  |  | 23.2531
[13 empty] | C Choked w/ reducers | 5 |  | 70.3185 |  |  | 261.3165 |  |  | 39.6641 |  |  | 17.221 |  |  | 10.3549 |  |  | 7.6748 |  |  | 6.4382 |  |  | 6.0808 |  |  | 5.623 |  |  | 8.1535
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 98.6034 |  |  | #NUM! |  |  | 39.6641 |  |  | 17.221 |  |  | 10.3549 |  |  | 7.6748 |  |  | 6.4382 |  |  | 6.0808 |  |  | 5.623 |  |  | 8.1535
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 96.6034 | 10001.479 |  | 7174 | 13961.9938 |  | 7174 | 34529.6721 |  | 7174 | 67254.9877 |  | 7174 | 110609.6929 |  | 7174 | 155138.6097 |  | 7174 | 196984.8681 |  | 7174 | 230980.2497 |  | 7174 | 257697.3533 |  | 7174 | 287504.7801
[13 empty] | Next iteration flow rate |  |  | 10201.5086 | Abs Value of | Flow this | 14101.6137 | Abs Value of | Flow this | 34874.9688 | Abs Value of | Flow this | 67927.5376 | Abs Value of | Flow this | 111715.7898 | Abs Value of | Flow this | 156689.9958 | Abs Value of | Flow this | 198954.7168 | Abs Value of | Flow this | 233290.0522 | Abs Value of | Flow this | 260274.3268 | Abs Value of | Flow this | 290379.8279 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 59.0233 |  |  | 21.2268 |  |  | -384.4767 |  |  | -1739.4243 |  |  | -4876.1915 |  |  | -9689.78 |  |  | -15683.6587 |  |  | -21601.7905 |  |  | -26912.6907 |  |  | -33523.2525
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.28472 |  |  | 0.10239 |  |  | -1.8546 |  |  | -8.3907 |  |  | -23.5219 |  |  | -46.7418 |  |  | -75.6552 |  |  | -104.2032 |  |  | -129.822 |  |  | -161.7102
[13 empty] | Delta P at this iteration flow rate |  |  | 9.0233 |  |  | -28.7732 |  |  | -434.4767 |  |  | -1789.4243 |  |  | -4926.1915 |  |  | -9739.78 |  |  | -15733.6587 |  |  | -21651.7905 |  |  | -26962.6907 |  |  | -33573.2525
[13 empty] | Press drop ratio this iteration |  |  | 0.15288 |  |  | -1.3555 |  |  | 1.13 |  |  | 1.0287 |  |  | 1.0103 |  |  | 1.0052 |  |  | 1.0032 |  |  | 1.0023 |  |  | 1.0019 |  |  | 1.0015
[13 empty] | Expansion factor | 12 |  | 0.92038 |  |  | 1.7058 |  |  | 0.40276 |  |  | 0.44885 |  |  | 0.44391 |  |  | 0.41516 |  |  | 0.37602 |  |  | 0.31883 |  |  | 0.43734 |  |  | 0.14615
[13 empty] | C Non choked w/ reducers | 5 |  | 109.2582 |  |  | #NUM! |  |  | 48.3316 |  |  | 19.6818 |  |  | 11.9218 |  |  | 9.2149 |  |  | 8.2633 |  |  | 8.81 |  |  | 6.5348 |  |  | 23.0178
[13 empty] | C Choked w/ reducers | 5 |  | 73.6831 |  |  | 283.3568 |  |  | 39.065 |  |  | 17.0307 |  |  | 10.2481 |  |  | 7.5972 |  |  | 6.3736 |  |  | 6.02 |  |  | 5.5669 |  |  | 8.0723
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 109.2582 |  |  | #NUM! |  |  | 39.065 |  |  | 17.0307 |  |  | 10.2481 |  |  | 7.5972 |  |  | 6.3736 |  |  | 6.02 |  |  | 5.5669 |  |  | 8.0723
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 107.2582 | 10201.5086 |  | 7174 | 14101.6137 |  | 7174 | 34874.9688 |  | 7174 | 67927.5376 |  | 7174 | 111715.7898 |  | 7174 | 156689.9958 |  | 7174 | 198954.7168 |  | 7174 | 233290.0522 |  | 7174 | 260274.3268 |  | 7174 | 290379.8279
[13 empty] | Next iteration flow rate |  |  | 10405.5388 | Abs Value of | Flow this | 14242.6298 | Abs Value of | Flow this | 35223.7185 | Abs Value of | Flow this | 68606.8129 | Abs Value of | Flow this | 112832.9477 | Abs Value of | Flow this | 158256.8958 | Abs Value of | Flow this | 200944.264 | Abs Value of | Flow this | 235622.9527 | Abs Value of | Flow this | 262877.0701 | Abs Value of | Flow this | 293283.6262 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 57.3468 |  |  | 19.6329 |  |  | -394.2251 |  |  | -1776.4072 |  |  | -4976.2235 |  |  | -9886.5651 |  |  | -16000.9208 |  |  | -22038.007 |  |  | -27455.6563 |  |  | -34199.0904
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.27663 |  |  | 0.094706 |  |  | -1.9017 |  |  | -8.5691 |  |  | -24.0044 |  |  | -47.691 |  |  | -77.1856 |  |  | -106.3074 |  |  | -132.4412 |  |  | -164.9703
[13 empty] | Delta P at this iteration flow rate |  |  | 7.3468 |  |  | -30.3671 |  |  | -444.2251 |  |  | -1826.4072 |  |  | -5026.2235 |  |  | -9936.5651 |  |  | -16050.9208 |  |  | -22088.007 |  |  | -27505.6563 |  |  | -34249.0904
[13 empty] | Press drop ratio this iteration |  |  | 0.12811 |  |  | -1.5467 |  |  | 1.1268 |  |  | 1.0281 |  |  | 1.01 |  |  | 1.0051 |  |  | 1.0031 |  |  | 1.0023 |  |  | 1.0018 |  |  | 1.0015
[13 empty] | Expansion factor | 12 |  | 0.93328 |  |  | 1.8054 |  |  | 0.40446 |  |  | 0.44917 |  |  | 0.44403 |  |  | 0.41522 |  |  | 0.37606 |  |  | 0.31886 |  |  | 0.43737 |  |  | 0.14618
[13 empty] | C Non choked w/ reducers | 5 |  | 123.5672 |  |  | #NUM! |  |  | 47.4754 |  |  | 19.4565 |  |  | 11.7971 |  |  | 9.1209 |  |  | 8.1799 |  |  | 8.7213 |  |  | 6.4695 |  |  | 22.785
[13 empty] | C Choked w/ reducers | 5 |  | 77.354 |  |  | 309.424 |  |  | 38.48 |  |  | 16.8429 |  |  | 10.1425 |  |  | 7.5205 |  |  | 6.3097 |  |  | 5.9599 |  |  | 5.5114 |  |  | 7.9919
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 123.5672 |  |  | #NUM! |  |  | 38.48 |  |  | 16.8429 |  |  | 10.1425 |  |  | 7.5205 |  |  | 6.3097 |  |  | 5.9599 |  |  | 5.5114 |  |  | 7.9919
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 121.5672 | 10405.5388 |  | 7174 | 14242.6298 |  | 7174 | 35223.7185 |  | 7174 | 68606.8129 |  | 7174 | 112832.9477 |  | 7174 | 158256.8958 |  | 7174 | 200944.264 |  | 7174 | 235622.9527 |  | 7174 | 262877.0701 |  | 7174 | 293283.6262
[13 empty] | Next iteration flow rate |  |  | 10613.6496 | Abs Value of | Flow this | 14385.0561 | Abs Value of | Flow this | 35575.9557 | Abs Value of | Flow this | 69292.8811 | Abs Value of | Flow this | 113961.2772 | Abs Value of | Flow this | 159839.4647 | Abs Value of | Flow this | 202953.7066 | Abs Value of | Flow this | 237979.1823 | Abs Value of | Flow this | 265505.8408 | Abs Value of | Flow this | 296216.4624 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.6024 |  |  | 18.0071 |  |  | -404.1696 |  |  | -1814.1335 |  |  | -5078.2661 |  |  | -10087.3056 |  |  | -16324.5598 |  |  | -22482.9914 |  |  | -28009.5355 |  |  | -34888.5126
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.26822 |  |  | 0.086863 |  |  | -1.9496 |  |  | -8.7511 |  |  | -24.4967 |  |  | -48.6594 |  |  | -78.7468 |  |  | -108.4539 |  |  | -135.113 |  |  | -168.296
[13 empty] | Delta P at this iteration flow rate |  |  | 5.6024 |  |  | -31.9929 |  |  | -454.1696 |  |  | -1864.1335 |  |  | -5128.2661 |  |  | -10137.3056 |  |  | -16374.5598 |  |  | -22532.9914 |  |  | -28059.5355 |  |  | -34938.5126
[13 empty] | Press drop ratio this iteration |  |  | 0.10076 |  |  | -1.7767 |  |  | 1.1237 |  |  | 1.0276 |  |  | 1.0098 |  |  | 1.005 |  |  | 1.0031 |  |  | 1.0022 |  |  | 1.0018 |  |  | 1.0014
[13 empty] | Expansion factor | 12 |  | 0.94752 |  |  | 1.9251 |  |  | 0.40611 |  |  | 0.44948 |  |  | 0.44414 |  |  | 0.41527 |  |  | 0.3761 |  |  | 0.31889 |  |  | 0.43739 |  |  | 0.1462
[13 empty] | C Non choked w/ reducers | 5 |  | 144.3747 |  |  | #NUM! |  |  | 46.6451 |  |  | 19.2345 |  |  | 11.6739 |  |  | 9.028 |  |  | 8.0973 |  |  | 8.6336 |  |  | 6.4048 |  |  | 22.5546
[13 empty] | C Choked w/ reducers | 5 |  | 81.3763 |  |  | 340.736 |  |  | 37.9085 |  |  | 16.6576 |  |  | 10.0381 |  |  | 7.4445 |  |  | 6.2465 |  |  | 5.9004 |  |  | 5.4564 |  |  | 7.9123
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 144.3747 |  |  | #NUM! |  |  | 37.9085 |  |  | 16.6576 |  |  | 10.0381 |  |  | 7.4445 |  |  | 6.2465 |  |  | 5.9004 |  |  | 5.4564 |  |  | 7.9123
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 142.3747 | 10613.6496 |  | 7174 | 14385.0561 |  | 7174 | 35575.9557 |  | 7174 | 69292.8811 |  | 7174 | 113961.2772 |  | 7174 | 159839.4647 |  | 7174 | 202953.7066 |  | 7174 | 237979.1823 |  | 7174 | 265505.8408 |  | 7174 | 296216.4624
[13 empty] | Next iteration flow rate |  |  | 10825.9226 | Abs Value of | Flow this | 14528.9067 | Abs Value of | Flow this | 35931.7152 | Abs Value of | Flow this | 69985.8099 | Abs Value of | Flow this | 115100.89 | Abs Value of | Flow this | 161437.8594 | Abs Value of | Flow this | 204983.2437 | Abs Value of | Flow this | 240358.9741 | Abs Value of | Flow this | 268160.8992 | Abs Value of | Flow this | 299178.6271 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.7877 |  |  | 16.3485 |  |  | -414.3139 |  |  | -1852.6181 |  |  | -5182.3597 |  |  | -10292.0809 |  |  | -16654.704 |  |  | -22936.9201 |  |  | -28574.5477 |  |  | -35591.7922
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.25946 |  |  | 0.078862 |  |  | -1.9986 |  |  | -8.9367 |  |  | -24.9988 |  |  | -49.6472 |  |  | -80.3393 |  |  | -110.6436 |  |  | -137.8385 |  |  | -171.6885
[13 empty] | Delta P at this iteration flow rate |  |  | 3.7877 |  |  | -33.6515 |  |  | -464.3139 |  |  | -1902.6181 |  |  | -5232.3597 |  |  | -10342.0809 |  |  | -16704.704 |  |  | -22986.9201 |  |  | -28624.5477 |  |  | -35641.7922
[13 empty] | Press drop ratio this iteration |  |  | 0.070419 |  |  | -2.0584 |  |  | 1.1207 |  |  | 1.027 |  |  | 1.0096 |  |  | 1.0049 |  |  | 1.003 |  |  | 1.0022 |  |  | 1.0017 |  |  | 1.0014
[13 empty] | Expansion factor | 12 |  | 0.96333 |  |  | 2.0718 |  |  | 0.40771 |  |  | 0.44979 |  |  | 0.44425 |  |  | 0.41533 |  |  | 0.37614 |  |  | 0.31892 |  |  | 0.43741 |  |  | 0.14623
[13 empty] | C Non choked w/ reducers | 5 |  | 179.109 |  |  | #NUM! |  |  | 45.8394 |  |  | 19.0156 |  |  | 11.5521 |  |  | 8.936 |  |  | 8.0156 |  |  | 8.5467 |  |  | 6.3407 |  |  | 22.3267
[13 empty] | C Choked w/ reducers | 5 |  | 85.8044 |  |  | 379.0569 |  |  | 37.3502 |  |  | 16.4746 |  |  | 9.9348 |  |  | 7.3693 |  |  | 6.1839 |  |  | 5.8414 |  |  | 5.402 |  |  | 7.8335
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 179.109 |  |  | #NUM! |  |  | 37.3502 |  |  | 16.4746 |  |  | 9.9348 |  |  | 7.3693 |  |  | 6.1839 |  |  | 5.8414 |  |  | 5.402 |  |  | 7.8335
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 177.109 | 10825.9226 |  | 7174 | 14528.9067 |  | 7174 | 35931.7152 |  | 7174 | 69985.8099 |  | 7174 | 115100.89 |  | 7174 | 161437.8594 |  | 7174 | 204983.2437 |  | 7174 | 240358.9741 |  | 7174 | 268160.8992 |  | 7174 | 299178.6271
[13 empty] | Next iteration flow rate |  |  | 11042.441 | Abs Value of | Flow this | 14674.1958 | Abs Value of | Flow this | 36291.0324 | Abs Value of | Flow this | 70685.668 | Abs Value of | Flow this | 116251.8989 | Abs Value of | Flow this | 163052.238 | Abs Value of | Flow this | 207033.0761 | Abs Value of | Flow this | 242762.5638 | Abs Value of | Flow this | 270842.5082 | Abs Value of | Flow this | 302170.4133 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 51.8996 |  |  | 14.6566 |  |  | -424.6621 |  |  | -1891.8762 |  |  | -5288.5456 |  |  | -10500.9723 |  |  | -16991.484 |  |  | -23399.9727 |  |  | -29150.9166 |  |  | -36309.2078
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.25035 |  |  | 0.070701 |  |  | -2.0485 |  |  | -9.1261 |  |  | -25.511 |  |  | -50.6548 |  |  | -81.9639 |  |  | -112.8773 |  |  | -140.6188 |  |  | -175.1492
[13 empty] | Delta P at this iteration flow rate |  |  | 1.8996 |  |  | -35.3434 |  |  | -474.6621 |  |  | -1941.8762 |  |  | -5338.5456 |  |  | -10550.9723 |  |  | -17041.484 |  |  | -23449.9727 |  |  | -29200.9166 |  |  | -36359.2078
[13 empty] | Press drop ratio this iteration |  |  | 0.036601 |  |  | -2.4114 |  |  | 1.1177 |  |  | 1.0264 |  |  | 1.0095 |  |  | 1.0048 |  |  | 1.0029 |  |  | 1.0021 |  |  | 1.0017 |  |  | 1.0014
[13 empty] | Expansion factor | 12 |  | 0.98094 |  |  | 2.2556 |  |  | 0.40927 |  |  | 0.45009 |  |  | 0.44435 |  |  | 0.41539 |  |  | 0.37617 |  |  | 0.31895 |  |  | 0.43742 |  |  | 0.14625
[13 empty] | C Non choked w/ reducers | 5 |  | 257.9094 |  |  | #NUM! |  |  | 45.0572 |  |  | 18.7998 |  |  | 11.4317 |  |  | 8.8451 |  |  | 7.9347 |  |  | 8.4608 |  |  | 6.2774 |  |  | 22.1011
[13 empty] | C Choked w/ reducers | 5 |  | 90.7044 |  |  | 427.042 |  |  | 36.8044 |  |  | 16.2941 |  |  | 9.8327 |  |  | 7.295 |  |  | 6.1219 |  |  | 5.7831 |  |  | 5.3482 |  |  | 7.7555
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 257.9094 |  |  | #NUM! |  |  | 36.8044 |  |  | 16.2941 |  |  | 9.8327 |  |  | 7.295 |  |  | 6.1219 |  |  | 5.7831 |  |  | 5.3482 |  |  | 7.7555
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 255.9094 | 11042.441 |  | 7174 | 14674.1958 |  | 7174 | 36291.0324 |  | 7174 | 70685.668 |  | 7174 | 116251.8989 |  | 7174 | 163052.238 |  | 7174 | 207033.0761 |  | 7174 | 242762.5638 |  | 7174 | 270842.5082 |  | 7174 | 302170.4133
[13 empty] | Next iteration flow rate |  |  | 11263.2898 | Abs Value of | Flow this | 14820.9377 | Abs Value of | Flow this | 36653.9427 | Abs Value of | Flow this | 71392.5247 | Abs Value of | Flow this | 117414.4179 | Abs Value of | Flow this | 164682.7604 | Abs Value of | Flow this | 209103.4069 | Abs Value of | Flow this | 245190.1895 | Abs Value of | Flow this | 273550.9333 | Abs Value of | Flow this | 305192.1175 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 49.9352 |  |  | 12.9307 |  |  | -435.2183 |  |  | -1931.9235 |  |  | -5396.8659 |  |  | -10714.0623 |  |  | -17335.0334 |  |  | -23872.3326 |  |  | -29738.8705 |  |  | -37041.0433
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.24088 |  |  | 0.062375 |  |  | -2.0994 |  |  | -9.3193 |  |  | -26.0335 |  |  | -51.6827 |  |  | -83.6211 |  |  | -115.1559 |  |  | -143.455 |  |  | -178.6794
[13 empty] | Delta P at this iteration flow rate |  |  | -0.064817 |  |  | -37.0693 |  |  | -485.2183 |  |  | -1981.9235 |  |  | -5446.8659 |  |  | -10764.0623 |  |  | -17385.0334 |  |  | -23922.3326 |  |  | -29788.8705 |  |  | -37091.0433
[13 empty] | Press drop ratio this iteration |  |  | -0.001298 |  |  | -2.8668 |  |  | 1.1149 |  |  | 1.0259 |  |  | 1.0093 |  |  | 1.0047 |  |  | 1.0029 |  |  | 1.0021 |  |  | 1.0017 |  |  | 1.0013
[13 empty] | Expansion factor | 12 |  | 1.0007 |  |  | 2.4927 |  |  | 0.41077 |  |  | 0.45038 |  |  | 0.44446 |  |  | 0.41544 |  |  | 0.37621 |  |  | 0.31898 |  |  | 0.43744 |  |  | 0.14627
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 44.2974 |  |  | 18.587 |  |  | 11.3127 |  |  | 8.7551 |  |  | 7.8547 |  |  | 8.3757 |  |  | 6.2146 |  |  | 21.8779
[13 empty] | C Choked w/ reducers | 5 |  | 96.1581 |  |  | 488.8814 |  |  | 36.2708 |  |  | 16.1159 |  |  | 9.7317 |  |  | 7.2214 |  |  | 6.0606 |  |  | 5.7253 |  |  | 5.2949 |  |  | 7.6783
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 36.2708 |  |  | 16.1159 |  |  | 9.7317 |  |  | 7.2214 |  |  | 6.0606 |  |  | 5.7253 |  |  | 5.2949 |  |  | 7.6783
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 11263.2898 |  | 7174 | 14820.9377 |  | 7174 | 36653.9427 |  | 7174 | 71392.5247 |  | 7174 | 117414.4179 |  | 7174 | 164682.7604 |  | 7174 | 209103.4069 |  | 7174 | 245190.1895 |  | 7174 | 273550.9333 |  | 7174 | 305192.1175
[13 empty] | Next iteration flow rate |  |  | 11488.5556 | Abs Value of | Flow this | 14969.1471 | Abs Value of | Flow this | 37020.4821 | Abs Value of | Flow this | 72106.4499 | Abs Value of | Flow this | 118588.5621 | Abs Value of | Flow this | 166329.588 | Abs Value of | Flow this | 211194.4409 | Abs Value of | Flow this | 247642.0914 | Abs Value of | Flow this | 276286.4426 | Abs Value of | Flow this | 308244.0386 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 47.8914 |  |  | 11.1701 |  |  | -445.9867 |  |  | -1972.7756 |  |  | -5507.3634 |  |  | -10931.4355 |  |  | -17685.488 |  |  | -24354.187 |  |  | -30338.6423 |  |  | -37787.5888
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.23102 |  |  | 0.053882 |  |  | -2.1514 |  |  | -9.5163 |  |  | -26.5665 |  |  | -52.7313 |  |  | -85.3116 |  |  | -117.4803 |  |  | -146.3482 |  |  | -182.2806
[13 empty] | Delta P at this iteration flow rate |  |  | -2.1086 |  |  | -38.8299 |  |  | -495.9867 |  |  | -2022.7756 |  |  | -5557.3634 |  |  | -10981.4355 |  |  | -17735.488 |  |  | -24404.187 |  |  | -30388.6423 |  |  | -37837.5888
[13 empty] | Press drop ratio this iteration |  |  | -0.044028 |  |  | -3.4762 |  |  | 1.1121 |  |  | 1.0253 |  |  | 1.0091 |  |  | 1.0046 |  |  | 1.0028 |  |  | 1.0021 |  |  | 1.0016 |  |  | 1.0013
[13 empty] | Expansion factor | 12 |  | 1.0229 |  |  | 2.8101 |  |  | 0.41224 |  |  | 0.45067 |  |  | 0.44456 |  |  | 0.4155 |  |  | 0.37624 |  |  | 0.31901 |  |  | 0.43746 |  |  | 0.1463
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 43.5591 |  |  | 18.3772 |  |  | 11.1951 |  |  | 8.6661 |  |  | 7.7756 |  |  | 8.2915 |  |  | 6.1525 |  |  | 21.6571
[13 empty] | C Choked w/ reducers | 5 |  | 102.2668 |  |  | 571.5971 |  |  | 35.749 |  |  | 15.94 |  |  | 9.6318 |  |  | 7.1486 |  |  | 5.9999 |  |  | 5.6682 |  |  | 5.2421 |  |  | 7.6019
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 35.749 |  |  | 15.94 |  |  | 9.6318 |  |  | 7.1486 |  |  | 5.9999 |  |  | 5.6682 |  |  | 5.2421 |  |  | 7.6019
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 11488.5556 |  | 7174 | 14969.1471 |  | 7174 | 37020.4821 |  | 7174 | 72106.4499 |  | 7174 | 118588.5621 |  | 7174 | 166329.588 |  | 7174 | 211194.4409 |  | 7174 | 247642.0914 |  | 7174 | 276286.4426 |  | 7174 | 308244.0386
[13 empty] | Next iteration flow rate |  |  | 11718.3267 | Abs Value of | Flow this | 15118.8386 | Abs Value of | Flow this | 37390.687 | Abs Value of | Flow this | 72827.5144 | Abs Value of | Flow this | 119774.4477 | Abs Value of | Flow this | 167992.8839 | Abs Value of | Flow this | 213306.3853 | Abs Value of | Flow this | 250118.5123 | Abs Value of | Flow this | 279049.3071 | Abs Value of | Flow this | 311326.479 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 45.7651 |  |  | 9.3741 |  |  | -456.9716 |  |  | -2014.4489 |  |  | -5620.0819 |  |  | -11153.1779 |  |  | -18042.9869 |  |  | -24845.7267 |  |  | -30950.4696 |  |  | -38549.1399
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.22076 |  |  | 0.045219 |  |  | -2.2043 |  |  | -9.7173 |  |  | -27.1103 |  |  | -53.8009 |  |  | -87.0362 |  |  | -119.8514 |  |  | -149.2996 |  |  | -185.9542
[13 empty] | Delta P at this iteration flow rate |  |  | -4.2349 |  |  | -40.6259 |  |  | -506.9716 |  |  | -2064.4489 |  |  | -5670.0819 |  |  | -11203.1779 |  |  | -18092.9869 |  |  | -24895.7267 |  |  | -31000.4696 |  |  | -38599.1399
[13 empty] | Press drop ratio this iteration |  |  | -0.092535 |  |  | -4.3338 |  |  | 1.1094 |  |  | 1.0248 |  |  | 1.0089 |  |  | 1.0045 |  |  | 1.0028 |  |  | 1.002 |  |  | 1.0016 |  |  | 1.0013
[13 empty] | Expansion factor | 12 |  | 1.0482 |  |  | 3.2566 |  |  | 0.41366 |  |  | 0.45095 |  |  | 0.44466 |  |  | 0.41555 |  |  | 0.37628 |  |  | 0.31904 |  |  | 0.43748 |  |  | 0.14632
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 42.8412 |  |  | 18.1704 |  |  | 11.0787 |  |  | 8.578 |  |  | 7.6972 |  |  | 8.2082 |  |  | 6.091 |  |  | 21.4385
[13 empty] | C Choked w/ reducers | 5 |  | 109.1586 |  |  | 687.9209 |  |  | 35.2386 |  |  | 15.7663 |  |  | 9.533 |  |  | 7.0765 |  |  | 5.9398 |  |  | 5.6116 |  |  | 5.1898 |  |  | 7.5262
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 35.2386 |  |  | 15.7663 |  |  | 9.533 |  |  | 7.0765 |  |  | 5.9398 |  |  | 5.6116 |  |  | 5.1898 |  |  | 7.5262
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 11718.3267 |  | 7174 | 15118.8386 |  | 7174 | 37390.687 |  | 7174 | 72827.5144 |  | 7174 | 119774.4477 |  | 7174 | 167992.8839 |  | 7174 | 213306.3853 |  | 7174 | 250118.5123 |  | 7174 | 279049.3071 |  | 7174 | 311326.479
[13 empty] | Next iteration flow rate |  |  | 11952.6933 | Abs Value of | Flow this | 15270.027 | Abs Value of | Flow this | 37764.5938 | Abs Value of | Flow this | 73555.7895 | Abs Value of | Flow this | 120972.1922 | Abs Value of | Flow this | 169672.8127 | Abs Value of | Flow this | 215439.4492 | Abs Value of | Flow this | 252619.6974 | Abs Value of | Flow this | 281839.8001 | Abs Value of | Flow this | 314439.7438 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 43.5529 |  |  | 7.542 |  |  | -468.1772 |  |  | -2056.9599 |  |  | -5735.0661 |  |  | -11379.3772 |  |  | -18407.6714 |  |  | -25347.1463 |  |  | -31574.5945 |  |  | -39325.9981
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.21009 |  |  | 0.036381 |  |  | -2.2584 |  |  | -9.9224 |  |  | -27.6649 |  |  | -54.8921 |  |  | -88.7953 |  |  | -122.2701 |  |  | -152.3102 |  |  | -189.7016
[13 empty] | Delta P at this iteration flow rate |  |  | -6.4471 |  |  | -42.458 |  |  | -518.1772 |  |  | -2106.9599 |  |  | -5785.0661 |  |  | -11429.3772 |  |  | -18457.6714 |  |  | -25397.1463 |  |  | -31624.5945 |  |  | -39375.9981
[13 empty] | Press drop ratio this iteration |  |  | -0.14803 |  |  | -5.6295 |  |  | 1.1068 |  |  | 1.0243 |  |  | 1.0087 |  |  | 1.0044 |  |  | 1.0027 |  |  | 1.002 |  |  | 1.0016 |  |  | 1.0013
[13 empty] | Expansion factor | 12 |  | 1.0771 |  |  | 3.9313 |  |  | 0.41505 |  |  | 0.45122 |  |  | 0.44476 |  |  | 0.4156 |  |  | 0.37631 |  |  | 0.31906 |  |  | 0.4375 |  |  | 0.14634
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 42.1429 |  |  | 17.9663 |  |  | 10.9637 |  |  | 8.4909 |  |  | 7.6197 |  |  | 8.1258 |  |  | 6.0302 |  |  | 21.2223
[13 empty] | C Choked w/ reducers | 5 |  | 116.9972 |  |  | 863.5795 |  |  | 34.7391 |  |  | 15.5949 |  |  | 9.4353 |  |  | 7.0052 |  |  | 5.8804 |  |  | 5.5556 |  |  | 5.1381 |  |  | 7.4513
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 34.7391 |  |  | 15.5949 |  |  | 9.4353 |  |  | 7.0052 |  |  | 5.8804 |  |  | 5.5556 |  |  | 5.1381 |  |  | 7.4513
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 11952.6933 |  | 7174 | 15270.027 |  | 7174 | 37764.5938 |  | 7174 | 73555.7895 |  | 7174 | 120972.1922 |  | 7174 | 169672.8127 |  | 7174 | 215439.4492 |  | 7174 | 252619.6974 |  | 7174 | 281839.8001 |  | 7174 | 314439.7438
[13 empty] | Next iteration flow rate |  |  | 12191.7471 | Abs Value of | Flow this | 15422.7272 | Abs Value of | Flow this | 38142.2398 | Abs Value of | Flow this | 74291.3474 | Abs Value of | Flow this | 122181.9141 | Abs Value of | Flow this | 171369.5408 | Abs Value of | Flow this | 217593.8437 | Abs Value of | Flow this | 255145.8944 | Abs Value of | Flow this | 284658.1981 | Abs Value of | Flow this | 317584.1413 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 41.2513 |  |  | 5.6731 |  |  | -479.6081 |  |  | -2100.3253 |  |  | -5852.3614 |  |  | -11610.1232 |  |  | -18779.6861 |  |  | -25858.6444 |  |  | -32211.2644 |  |  | -40118.4711
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.19899 |  |  | 0.027366 |  |  | -2.3135 |  |  | -10.1316 |  |  | -28.2307 |  |  | -56.0052 |  |  | -90.5899 |  |  | -124.7375 |  |  | -155.3814 |  |  | -193.5244
[13 empty] | Delta P at this iteration flow rate |  |  | -8.7487 |  |  | -44.3269 |  |  | -529.6081 |  |  | -2150.3253 |  |  | -5902.3614 |  |  | -11660.1232 |  |  | -18829.6861 |  |  | -25908.6444 |  |  | -32261.2644 |  |  | -40168.4711
[13 empty] | Press drop ratio this iteration |  |  | -0.21208 |  |  | -7.8135 |  |  | 1.1043 |  |  | 1.0238 |  |  | 1.0085 |  |  | 1.0043 |  |  | 1.0027 |  |  | 1.0019 |  |  | 1.0016 |  |  | 1.0012
[13 empty] | Expansion factor | 12 |  | 1.1105 |  |  | 5.0685 |  |  | 0.41639 |  |  | 0.45149 |  |  | 0.44485 |  |  | 0.41565 |  |  | 0.37635 |  |  | 0.31909 |  |  | 0.43752 |  |  | 0.14636
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 41.4634 |  |  | 17.7651 |  |  | 10.85 |  |  | 8.4047 |  |  | 7.543 |  |  | 8.0442 |  |  | 5.97 |  |  | 21.0083
[13 empty] | C Choked w/ reducers | 5 |  | 125.9955 |  |  | 1159.5534 |  |  | 34.2503 |  |  | 15.4257 |  |  | 9.3387 |  |  | 6.9346 |  |  | 5.8215 |  |  | 5.5002 |  |  | 5.0869 |  |  | 7.3772
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 34.2503 |  |  | 15.4257 |  |  | 9.3387 |  |  | 6.9346 |  |  | 5.8215 |  |  | 5.5002 |  |  | 5.0869 |  |  | 7.3772
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 12191.7471 |  | 7174 | 15422.7272 |  | 7174 | 38142.2398 |  | 7174 | 74291.3474 |  | 7174 | 122181.9141 |  | 7174 | 171369.5408 |  | 7174 | 217593.8437 |  | 7174 | 255145.8944 |  | 7174 | 284658.1981 |  | 7174 | 317584.1413
[13 empty] | Next iteration flow rate |  |  | 12435.5821 | Abs Value of | Flow this | 15576.9545 | Abs Value of | Flow this | 38523.6622 | Abs Value of | Flow this | 75034.2609 | Abs Value of | Flow this | 123403.7332 | Abs Value of | Flow this | 173083.2362 | Abs Value of | Flow this | 219769.7821 | Abs Value of | Flow this | 257697.3533 | Abs Value of | Flow this | 287504.7801 | Abs Value of | Flow this | 320759.9827 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 38.8568 |  |  | 3.7666 |  |  | -491.2687 |  |  | -2144.5623 |  |  | -5972.0144 |  |  | -11845.5072 |  |  | -19159.1783 |  |  | -26380.4237 |  |  | -32860.7313 |  |  | -40926.8729
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.18744 |  |  | 0.018169 |  |  | -2.3698 |  |  | -10.345 |  |  | -28.8079 |  |  | -57.1406 |  |  | -92.4205 |  |  | -127.2545 |  |  | -158.5143 |  |  | -197.4239
[13 empty] | Delta P at this iteration flow rate |  |  | -11.1432 |  |  | -46.2334 |  |  | -541.2687 |  |  | -2194.5623 |  |  | -6022.0144 |  |  | -11895.5072 |  |  | -19209.1783 |  |  | -26430.4237 |  |  | -32910.7313 |  |  | -40976.8729
[13 empty] | Press drop ratio this iteration |  |  | -0.28678 |  |  | -12.2745 |  |  | 1.1018 |  |  | 1.0233 |  |  | 1.0084 |  |  | 1.0042 |  |  | 1.0026 |  |  | 1.0019 |  |  | 1.0015 |  |  | 1.0012
[13 empty] | Expansion factor | 12 |  | 1.1494 |  |  | 7.3913 |  |  | 0.4177 |  |  | 0.45175 |  |  | 0.44495 |  |  | 0.4157 |  |  | 0.37638 |  |  | 0.31912 |  |  | 0.43753 |  |  | 0.14638
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 40.8017 |  |  | 17.5666 |  |  | 10.7376 |  |  | 8.3194 |  |  | 7.467 |  |  | 7.9634 |  |  | 5.9104 |  |  | 20.7965
[13 empty] | C Choked w/ reducers | 5 |  | 136.4352 |  |  | 1763.9286 |  |  | 33.7717 |  |  | 15.2585 |  |  | 9.2431 |  |  | 6.8648 |  |  | 5.7633 |  |  | 5.4453 |  |  | 5.0363 |  |  | 7.3038
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 33.7717 |  |  | 15.2585 |  |  | 9.2431 |  |  | 6.8648 |  |  | 5.7633 |  |  | 5.4453 |  |  | 5.0363 |  |  | 7.3038
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 12435.5821 |  | 7174 | 15576.9545 |  | 7174 | 38523.6622 |  | 7174 | 75034.2609 |  | 7174 | 123403.7332 |  | 7174 | 173083.2362 |  | 7174 | 219769.7821 |  | 7174 | 257697.3533 |  | 7174 | 287504.7801 |  | 7174 | 320759.9827
[13 empty] | Next iteration flow rate |  |  | 12684.2937 | Abs Value of | Flow this | 15732.724 | Abs Value of | Flow this | 38908.8988 | Abs Value of | Flow this | 75784.6035 | Abs Value of | Flow this | 124637.7706 | Abs Value of | Flow this | 174814.0686 | Abs Value of | Flow this | 221967.4799 | Abs Value of | Flow this | 260274.3268 | Abs Value of | Flow this | 290379.8279 | Abs Value of | Flow this | 323967.5825 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 36.3655 |  |  | 1.8218 |  |  | -503.1637 |  |  | -2189.6885 |  |  | -6094.0724 |  |  | -12085.6224 |  |  | -19546.2983 |  |  | -26912.6907 |  |  | -33523.2525 |  |  | -41751.5236
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.17542 |  |  | 0.0087881 |  |  | -2.4272 |  |  | -10.5627 |  |  | -29.3967 |  |  | -58.2989 |  |  | -94.2879 |  |  | -129.822 |  |  | -161.7102 |  |  | -201.4019
[13 empty] | Delta P at this iteration flow rate |  |  | -13.6345 |  |  | -48.1782 |  |  | -553.1637 |  |  | -2239.6885 |  |  | -6144.0724 |  |  | -12135.6224 |  |  | -19596.2983 |  |  | -26962.6907 |  |  | -33573.2525 |  |  | -41801.5236
[13 empty] | Press drop ratio this iteration |  |  | -0.37493 |  |  | -26.4452 |  |  | 1.0994 |  |  | 1.0228 |  |  | 1.0082 |  |  | 1.0041 |  |  | 1.0026 |  |  | 1.0019 |  |  | 1.0015 |  |  | 1.0012
[13 empty] | Expansion factor | 12 |  | 1.1953 |  |  | 14.7699 |  |  | 0.41897 |  |  | 0.45201 |  |  | 0.44504 |  |  | 0.41575 |  |  | 0.37641 |  |  | 0.31914 |  |  | 0.43755 |  |  | 0.1464
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 40.1573 |  |  | 17.3708 |  |  | 10.6264 |  |  | 8.2351 |  |  | 7.3919 |  |  | 7.8835 |  |  | 5.8513 |  |  | 20.587
[13 empty] | C Choked w/ reducers | 5 |  | 148.6977 |  |  | 3683.4051 |  |  | 33.303 |  |  | 15.0935 |  |  | 9.1485 |  |  | 6.7957 |  |  | 5.7056 |  |  | 5.391 |  |  | 4.9861 |  |  | 7.2311
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 33.303 |  |  | 15.0935 |  |  | 9.1485 |  |  | 6.7957 |  |  | 5.7056 |  |  | 5.391 |  |  | 4.9861 |  |  | 7.2311
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 12684.2937 |  | 7174 | 15732.724 |  | 7174 | 38908.8988 |  | 7174 | 75784.6035 |  | 7174 | 124637.7706 |  | 7174 | 174814.0686 |  | 7174 | 221967.4799 |  | 7174 | 260274.3268 |  | 7174 | 290379.8279 |  | 7174 | 323967.5825
[13 empty] | Next iteration flow rate |  |  | 12937.9796 | Abs Value of | Flow this | 15890.0513 | Abs Value of | Flow this | 39297.9878 | Abs Value of | Flow this | 76542.4496 | Abs Value of | Flow this | 125884.1483 | Abs Value of | Flow this | 176562.2093 | Abs Value of | Flow this | 224187.1547 | Abs Value of | Flow this | 262877.0701 | Abs Value of | Flow this | 293283.6262 | Abs Value of | Flow this | 327207.2583 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 33.7735 |  |  | -0.16208 |  |  | -515.2978 |  |  | -2235.7218 |  |  | -6218.5838 |  |  | -12330.5639 |  |  | -19941.1994 |  |  | -27455.6563 |  |  | -34199.0904 |  |  | -42592.7497
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.16292 |  |  | -0.00078183 |  |  | -2.4857 |  |  | -10.7847 |  |  | -29.9973 |  |  | -59.4804 |  |  | -96.1928 |  |  | -132.4412 |  |  | -164.9703 |  |  | -205.4598
[13 empty] | Delta P at this iteration flow rate |  |  | -16.2265 |  |  | -50.1621 |  |  | -565.2978 |  |  | -2285.7218 |  |  | -6268.5838 |  |  | -12380.5639 |  |  | -19991.1994 |  |  | -27505.6563 |  |  | -34249.0904 |  |  | -42642.7497
[13 empty] | Press drop ratio this iteration |  |  | -0.48045 |  |  | 309.4959 |  |  | 1.097 |  |  | 1.0224 |  |  | 1.008 |  |  | 1.0041 |  |  | 1.0025 |  |  | 1.0018 |  |  | 1.0015 |  |  | 1.0012
[13 empty] | Expansion factor | 12 |  | 1.2502 |  |  | -160.1535 |  |  | 0.42021 |  |  | 0.45226 |  |  | 0.44513 |  |  | 0.4158 |  |  | 0.37644 |  |  | 0.31917 |  |  | 0.43757 |  |  | 0.14642
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | -7.9207 |  |  | 39.5293 |  |  | 17.1777 |  |  | 10.5165 |  |  | 8.1516 |  |  | 7.3175 |  |  | 7.8044 |  |  | 5.7929 |  |  | 20.3796
[13 empty] | C Choked w/ reducers | 5 |  | 163.3117 |  |  | 41817.1037 |  |  | 32.844 |  |  | 14.9306 |  |  | 9.055 |  |  | 6.7273 |  |  | 5.6486 |  |  | 5.3372 |  |  | 4.9364 |  |  | 7.1592
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | 41817.1037 |  |  | 32.844 |  |  | 14.9306 |  |  | 9.055 |  |  | 6.7273 |  |  | 5.6486 |  |  | 5.3372 |  |  | 4.9364 |  |  | 7.1592
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 12937.9796 |  | 7174 | 15890.0513 |  | 7174 | 39297.9878 |  | 7174 | 76542.4496 |  | 7174 | 125884.1483 |  | 7174 | 176562.2093 |  | 7174 | 224187.1547 |  | 7174 | 262877.0701 |  | 7174 | 293283.6262 |  | 7174 | 327207.2583
[13 empty] | Next iteration flow rate |  |  | 13196.7392 | Abs Value of | Flow this | 16048.9518 | Abs Value of | Flow this | 39690.9677 | Abs Value of | Flow this | 77307.8741 | Abs Value of | Flow this | 127142.9897 | Abs Value of | Flow this | 178327.8314 | Abs Value of | Flow this | 226429.0263 | Abs Value of | Flow this | 265505.8408 | Abs Value of | Flow this | 296216.4624 | Abs Value of | Flow this | 330479.3309 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 31.0768 |  |  | -2.1858 |  |  | -527.6758 |  |  | -2282.6803 |  |  | -6345.5978 |  |  | -12580.4288 |  |  | -20344.038 |  |  | -28009.5355 |  |  | -34888.5126 |  |  | -43450.8845
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.14991 |  |  | -0.010544 |  |  | -2.5454 |  |  | -11.0112 |  |  | -30.61 |  |  | -60.6857 |  |  | -98.136 |  |  | -135.113 |  |  | -168.296 |  |  | -209.5993
[13 empty] | Delta P at this iteration flow rate |  |  | -18.9232 |  |  | -52.1858 |  |  | -577.6758 |  |  | -2332.6803 |  |  | -6395.5978 |  |  | -12630.4288 |  |  | -20394.038 |  |  | -28059.5355 |  |  | -34938.5126 |  |  | -43500.8845
[13 empty] | Press drop ratio this iteration |  |  | -0.60891 |  |  | 23.8745 |  |  | 1.0948 |  |  | 1.0219 |  |  | 1.0079 |  |  | 1.004 |  |  | 1.0025 |  |  | 1.0018 |  |  | 1.0014 |  |  | 1.0012
[13 empty] | Expansion factor | 12 |  | 1.3171 |  |  | -11.4314 |  |  | 0.42141 |  |  | 0.45251 |  |  | 0.44522 |  |  | 0.41585 |  |  | 0.37647 |  |  | 0.31919 |  |  | 0.43758 |  |  | 0.14644
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | -29.9216 |  |  | 38.9172 |  |  | 16.9871 |  |  | 10.4078 |  |  | 8.069 |  |  | 7.244 |  |  | 7.7261 |  |  | 5.7351 |  |  | 20.1744
[13 empty] | C Choked w/ reducers | 5 |  | 181.0326 |  |  | 3131.6782 |  |  | 32.3943 |  |  | 14.7697 |  |  | 8.9625 |  |  | 6.6596 |  |  | 5.5921 |  |  | 5.284 |  |  | 4.8873 |  |  | 7.088
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | 3131.6782 |  |  | 32.3943 |  |  | 14.7697 |  |  | 8.9625 |  |  | 6.6596 |  |  | 5.5921 |  |  | 5.284 |  |  | 4.8873 |  |  | 7.088
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 13196.7392 |  | 7174 | 16048.9518 |  | 7174 | 39690.9677 |  | 7174 | 77307.8741 |  | 7174 | 127142.9897 |  | 7174 | 178327.8314 |  | 7174 | 226429.0263 |  | 7174 | 265505.8408 |  | 7174 | 296216.4624 |  | 7174 | 330479.3309
[13 empty] | Next iteration flow rate |  |  | 13460.674 | Abs Value of | Flow this | 16209.4413 | Abs Value of | Flow this | 40087.8773 | Abs Value of | Flow this | 78080.9528 | Abs Value of | Flow this | 128414.4196 | Abs Value of | Flow this | 180111.1097 | Abs Value of | Flow this | 228693.3165 | Abs Value of | Flow this | 268160.8992 | Abs Value of | Flow this | 299178.6271 | Abs Value of | Flow this | 333784.1242 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 28.2712 |  |  | -4.2503 |  |  | -540.3026 |  |  | -2330.5827 |  |  | -6475.1648 |  |  | -12835.3159 |  |  | -20754.9737 |  |  | -28574.5477 |  |  | -35591.7922 |  |  | -44326.2678
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.13638 |  |  | -0.020503 |  |  | -2.6063 |  |  | -11.2423 |  |  | -31.235 |  |  | -61.9153 |  |  | -100.1183 |  |  | -137.8385 |  |  | -171.6885 |  |  | -213.822
[13 empty] | Delta P at this iteration flow rate |  |  | -21.7288 |  |  | -54.2503 |  |  | -590.3026 |  |  | -2380.5827 |  |  | -6525.1648 |  |  | -12885.3159 |  |  | -20804.9737 |  |  | -28624.5477 |  |  | -35641.7922 |  |  | -44376.2678
[13 empty] | Press drop ratio this iteration |  |  | -0.76858 |  |  | 12.7639 |  |  | 1.0925 |  |  | 1.0215 |  |  | 1.0077 |  |  | 1.0039 |  |  | 1.0024 |  |  | 1.0017 |  |  | 1.0014 |  |  | 1.0011
[13 empty] | Expansion factor | 12 |  | 1.4003 |  |  | -5.6461 |  |  | 0.42258 |  |  | 0.45275 |  |  | 0.44531 |  |  | 0.41589 |  |  | 0.3765 |  |  | 0.31922 |  |  | 0.4376 |  |  | 0.14646
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | -43.0357 |  |  | 38.3202 |  |  | 16.7991 |  |  | 10.3004 |  |  | 7.9873 |  |  | 7.1711 |  |  | 7.6487 |  |  | 5.6779 |  |  | 19.9713
[13 empty] | C Choked w/ reducers | 5 |  | 202.9781 |  |  | 1626.6691 |  |  | 31.9536 |  |  | 14.6107 |  |  | 8.871 |  |  | 6.5927 |  |  | 5.5362 |  |  | 5.2313 |  |  | 4.8386 |  |  | 7.0175
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | 1626.6691 |  |  | 31.9536 |  |  | 14.6107 |  |  | 8.871 |  |  | 6.5927 |  |  | 5.5362 |  |  | 5.2313 |  |  | 4.8386 |  |  | 7.0175
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 13460.674 |  | 7174 | 16209.4413 |  | 7174 | 40087.8773 |  | 7174 | 78080.9528 |  | 7174 | 128414.4196 |  | 7174 | 180111.1097 |  | 7174 | 228693.3165 |  | 7174 | 268160.8992 |  | 7174 | 299178.6271 |  | 7174 | 333784.1242
[13 empty] | Next iteration flow rate |  |  | 13729.8875 | Abs Value of | Flow this | 16371.5357 | Abs Value of | Flow this | 40488.7561 | Abs Value of | Flow this | 78861.7623 | Abs Value of | Flow this | 129698.5638 | Abs Value of | Flow this | 181912.2208 | Abs Value of | Flow this | 230980.2497 | Abs Value of | Flow this | 270842.5082 | Abs Value of | Flow this | 302170.4133 | Abs Value of | Flow this | 337121.9655 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 25.3523 |  |  | -6.3562 |  |  | -553.1832 |  |  | -2379.4479 |  |  | -6607.3362 |  |  | -13095.3263 |  |  | -21174.1692 |  |  | -29150.9166 |  |  | -36309.2078 |  |  | -45219.2463
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.12229 |  |  | -0.030661 |  |  | -2.6685 |  |  | -11.478 |  |  | -31.8726 |  |  | -63.1695 |  |  | -102.1404 |  |  | -140.6188 |  |  | -175.1492 |  |  | -218.1296
[13 empty] | Delta P at this iteration flow rate |  |  | -24.6477 |  |  | -56.3562 |  |  | -603.1832 |  |  | -2429.4479 |  |  | -6657.3362 |  |  | -13145.3263 |  |  | -21224.1692 |  |  | -29200.9166 |  |  | -36359.2078 |  |  | -45269.2463
[13 empty] | Press drop ratio this iteration |  |  | -0.97221 |  |  | 8.8663 |  |  | 1.0904 |  |  | 1.021 |  |  | 1.0076 |  |  | 1.0038 |  |  | 1.0024 |  |  | 1.0017 |  |  | 1.0014 |  |  | 1.0011
[13 empty] | Expansion factor | 12 |  | 1.5063 |  |  | -3.6167 |  |  | 0.42372 |  |  | 0.45299 |  |  | 0.44539 |  |  | 0.41594 |  |  | 0.37653 |  |  | 0.31924 |  |  | 0.43761 |  |  | 0.14648
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | -54.442 |  |  | 37.7379 |  |  | 16.6136 |  |  | 10.1941 |  |  | 7.9064 |  |  | 7.0991 |  |  | 7.572 |  |  | 5.6212 |  |  | 19.7704
[13 empty] | C Choked w/ reducers | 5 |  | 230.8752 |  |  | 1098.5998 |  |  | 31.5217 |  |  | 14.4538 |  |  | 8.7805 |  |  | 6.5264 |  |  | 5.4808 |  |  | 5.1791 |  |  | 4.7904 |  |  | 6.9477
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | 1098.5998 |  |  | 31.5217 |  |  | 14.4538 |  |  | 8.7805 |  |  | 6.5264 |  |  | 5.4808 |  |  | 5.1791 |  |  | 4.7904 |  |  | 6.9477
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 13729.8875 |  | 7174 | 16371.5357 |  | 7174 | 40488.7561 |  | 7174 | 78861.7623 |  | 7174 | 129698.5638 |  | 7174 | 181912.2208 |  | 7174 | 230980.2497 |  | 7174 | 270842.5082 |  | 7174 | 302170.4133 |  | 7174 | 337121.9655
[13 empty] | Next iteration flow rate |  |  | 14004.4852 | Abs Value of | Flow this | 16535.2511 | Abs Value of | Flow this | 40893.6437 | Abs Value of | Flow this | 79650.3799 | Abs Value of | Flow this | 130995.5495 | Abs Value of | Flow this | 183731.343 | Abs Value of | Flow this | 233290.0522 | Abs Value of | Flow this | 273550.9333 | Abs Value of | Flow this | 305192.1175 | Abs Value of | Flow this | 340493.1851 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 22.3154 |  |  | -8.5045 |  |  | -566.3227 |  |  | -2429.2953 |  |  | -6742.1641 |  |  | -13360.5628 |  |  | -21601.7905 |  |  | -29738.8705 |  |  | -37041.0433 |  |  | -46130.1736
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.10765 |  |  | -0.041024 |  |  | -2.7318 |  |  | -11.7185 |  |  | -32.523 |  |  | -64.449 |  |  | -104.2032 |  |  | -143.455 |  |  | -178.6794 |  |  | -222.5237
[13 empty] | Delta P at this iteration flow rate |  |  | -27.6846 |  |  | -58.5045 |  |  | -616.3227 |  |  | -2479.2953 |  |  | -6792.1641 |  |  | -13410.5628 |  |  | -21651.7905 |  |  | -29788.8705 |  |  | -37091.0433 |  |  | -46180.1736
[13 empty] | Press drop ratio this iteration |  |  | -1.2406 |  |  | 6.8792 |  |  | 1.0883 |  |  | 1.0206 |  |  | 1.0074 |  |  | 1.0037 |  |  | 1.0023 |  |  | 1.0017 |  |  | 1.0013 |  |  | 1.0011
[13 empty] | Expansion factor | 12 |  | 1.6461 |  |  | -2.582 |  |  | 0.42483 |  |  | 0.45322 |  |  | 0.44547 |  |  | 0.41598 |  |  | 0.37656 |  |  | 0.31926 |  |  | 0.43763 |  |  | 0.1465
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | -65.3518 |  |  | 37.1696 |  |  | 16.4305 |  |  | 10.089 |  |  | 7.8264 |  |  | 7.0277 |  |  | 7.4961 |  |  | 5.5652 |  |  | 19.5715
[13 empty] | C Choked w/ reducers | 5 |  | 267.5408 |  |  | 829.3001 |  |  | 31.0983 |  |  | 14.2988 |  |  | 8.691 |  |  | 6.4608 |  |  | 5.4261 |  |  | 5.1275 |  |  | 4.7428 |  |  | 6.8786
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | 829.3001 |  |  | 31.0983 |  |  | 14.2988 |  |  | 8.691 |  |  | 6.4608 |  |  | 5.4261 |  |  | 5.1275 |  |  | 4.7428 |  |  | 6.8786
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 14004.4852 |  | 7174 | 16535.2511 |  | 7174 | 40893.6437 |  | 7174 | 79650.3799 |  | 7174 | 130995.5495 |  | 7174 | 183731.343 |  | 7174 | 233290.0522 |  | 7174 | 273550.9333 |  | 7174 | 305192.1175 |  | 7174 | 340493.1851
[13 empty] | Next iteration flow rate |  |  | 14284.5749 | Abs Value of | Flow this | 16700.6036 | Abs Value of | Flow this | 41302.5801 | Abs Value of | Flow this | 80446.8837 | Abs Value of | Flow this | 132305.505 | Abs Value of | Flow this | 185568.6564 | Abs Value of | Flow this | 235622.9527 | Abs Value of | Flow this | 276286.4426 | Abs Value of | Flow this | 308244.0386 | Abs Value of | Flow this | 343898.117 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 19.1558 |  |  | -10.6959 |  |  | -579.7263 |  |  | -2480.1446 |  |  | -6879.7021 |  |  | -13631.1307 |  |  | -22038.007 |  |  | -30338.6423 |  |  | -37787.5888 |  |  | -47059.4106
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.092404 |  |  | -0.051595 |  |  | -2.7965 |  |  | -11.9638 |  |  | -33.1865 |  |  | -65.7541 |  |  | -106.3074 |  |  | -146.3482 |  |  | -182.2806 |  |  | -227.0062
[13 empty] | Delta P at this iteration flow rate |  |  | -30.8442 |  |  | -60.6959 |  |  | -629.7263 |  |  | -2530.1446 |  |  | -6929.7021 |  |  | -13681.1307 |  |  | -22088.007 |  |  | -30388.6423 |  |  | -37837.5888 |  |  | -47109.4106
[13 empty] | Press drop ratio this iteration |  |  | -1.6102 |  |  | 5.6747 |  |  | 1.0862 |  |  | 1.0202 |  |  | 1.0073 |  |  | 1.0037 |  |  | 1.0023 |  |  | 1.0016 |  |  | 1.0013 |  |  | 1.0011
[13 empty] | Expansion factor | 12 |  | 1.8386 |  |  | -1.9548 |  |  | 0.42591 |  |  | 0.45344 |  |  | 0.44556 |  |  | 0.41602 |  |  | 0.37659 |  |  | 0.31928 |  |  | 0.43765 |  |  | 0.14652
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | -76.3249 |  |  | 36.6148 |  |  | 16.2498 |  |  | 9.9851 |  |  | 7.7473 |  |  | 6.9572 |  |  | 7.421 |  |  | 5.5096 |  |  | 19.3747
[13 empty] | C Choked w/ reducers | 5 |  | 317.9027 |  |  | 665.982 |  |  | 30.683 |  |  | 14.1457 |  |  | 8.6024 |  |  | 6.3959 |  |  | 5.3718 |  |  | 5.0764 |  |  | 4.6955 |  |  | 6.8102
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | 665.982 |  |  | 30.683 |  |  | 14.1457 |  |  | 8.6024 |  |  | 6.3959 |  |  | 5.3718 |  |  | 5.0764 |  |  | 4.6955 |  |  | 6.8102
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 14284.5749 |  | 7174 | 16700.6036 |  | 7174 | 41302.5801 |  | 7174 | 80446.8837 |  | 7174 | 132305.505 |  | 7174 | 185568.6564 |  | 7174 | 235622.9527 |  | 7174 | 276286.4426 |  | 7174 | 308244.0386 |  | 7174 | 343898.117
[13 empty] | Next iteration flow rate |  |  | 14570.2664 | Abs Value of | Flow this | 16867.6096 | Abs Value of | Flow this | 41715.6059 | Abs Value of | Flow this | 81251.3526 | Abs Value of | Flow this | 133628.56 | Abs Value of | Flow this | 187424.343 | Abs Value of | Flow this | 237979.1823 | Abs Value of | Flow this | 279049.3071 | Abs Value of | Flow this | 311326.479 | Abs Value of | Flow this | 347337.0981 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 15.8686 |  |  | -12.9314 |  |  | -593.3993 |  |  | -2532.016 |  |  | -7020.0047 |  |  | -13907.1369 |  |  | -22482.9914 |  |  | -30950.4696 |  |  | -38549.1399 |  |  | -48007.3253
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.076547 |  |  | -0.062379 |  |  | -2.8625 |  |  | -12.214 |  |  | -33.8633 |  |  | -67.0856 |  |  | -108.4539 |  |  | -149.2996 |  |  | -185.9542 |  |  | -231.5788
[13 empty] | Delta P at this iteration flow rate |  |  | -34.1314 |  |  | -62.9314 |  |  | -643.3993 |  |  | -2582.016 |  |  | -7070.0047 |  |  | -13957.1369 |  |  | -22532.9914 |  |  | -31000.4696 |  |  | -38599.1399 |  |  | -48057.3253
[13 empty] | Press drop ratio this iteration |  |  | -2.1509 |  |  | 4.8665 |  |  | 1.0843 |  |  | 1.0197 |  |  | 1.0071 |  |  | 1.0036 |  |  | 1.0022 |  |  | 1.0016 |  |  | 1.0013 |  |  | 1.001
[13 empty] | Expansion factor | 12 |  | 2.1202 |  |  | -1.534 |  |  | 0.42696 |  |  | 0.45367 |  |  | 0.44564 |  |  | 0.41607 |  |  | 0.37662 |  |  | 0.31931 |  |  | 0.43766 |  |  | 0.14654
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | -87.7394 |  |  | 36.0729 |  |  | 16.0715 |  |  | 9.8823 |  |  | 7.669 |  |  | 6.8873 |  |  | 7.3466 |  |  | 5.4547 |  |  | 19.1799
[13 empty] | C Choked w/ reducers | 5 |  | 391.4324 |  |  | 556.3602 |  |  | 30.2758 |  |  | 13.9945 |  |  | 8.5148 |  |  | 6.3316 |  |  | 5.3182 |  |  | 5.0258 |  |  | 4.6488 |  |  | 6.7425
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | 556.3602 |  |  | 30.2758 |  |  | 13.9945 |  |  | 8.5148 |  |  | 6.3316 |  |  | 5.3182 |  |  | 5.0258 |  |  | 4.6488 |  |  | 6.7425
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 14570.2664 |  | 7174 | 16867.6096 |  | 7174 | 41715.6059 |  | 7174 | 81251.3526 |  | 7174 | 133628.56 |  | 7174 | 187424.343 |  | 7174 | 237979.1823 |  | 7174 | 279049.3071 |  | 7174 | 311326.479 |  | 7174 | 347337.0981
[13 empty] | Next iteration flow rate |  |  | 14861.6717 | Abs Value of | Flow this | 17036.2857 | Abs Value of | Flow this | 42132.762 | Abs Value of | Flow this | 82063.8661 | Abs Value of | Flow this | 134964.8456 | Abs Value of | Flow this | 189298.5864 | Abs Value of | Flow this | 240358.9741 | Abs Value of | Flow this | 281839.8001 | Abs Value of | Flow this | 314439.7438 | Abs Value of | Flow this | 350810.4691 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 12.4485 |  |  | -15.2119 |  |  | -607.3471 |  |  | -2584.9301 |  |  | -7163.1273 |  |  | -14188.6908 |  |  | -22936.9201 |  |  | -31574.5945 |  |  | -39325.9981 |  |  | -48974.293
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.06005 |  |  | -0.073379 |  |  | -2.9297 |  |  | -12.4692 |  |  | -34.5537 |  |  | -68.4437 |  |  | -110.6436 |  |  | -152.3102 |  |  | -189.7016 |  |  | -236.2433
[13 empty] | Delta P at this iteration flow rate |  |  | -37.5515 |  |  | -65.2119 |  |  | -657.3471 |  |  | -2634.9301 |  |  | -7213.1273 |  |  | -14238.6908 |  |  | -22986.9201 |  |  | -31624.5945 |  |  | -39375.9981 |  |  | -49024.293
[13 empty] | Press drop ratio this iteration |  |  | -3.0165 |  |  | 4.2869 |  |  | 1.0823 |  |  | 1.0193 |  |  | 1.007 |  |  | 1.0035 |  |  | 1.0022 |  |  | 1.0016 |  |  | 1.0013 |  |  | 1.001
[13 empty] | Expansion factor | 12 |  | 2.571 |  |  | -1.2322 |  |  | 0.42798 |  |  | 0.45388 |  |  | 0.44571 |  |  | 0.41611 |  |  | 0.37665 |  |  | 0.31933 |  |  | 0.43767 |  |  | 0.14655
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | -99.9237 |  |  | 35.5436 |  |  | 15.8955 |  |  | 9.7807 |  |  | 7.5915 |  |  | 6.8182 |  |  | 7.273 |  |  | 5.4003 |  |  | 18.9872
[13 empty] | C Choked w/ reducers | 5 |  | 508.9513 |  |  | 477.6851 |  |  | 29.8763 |  |  | 13.8451 |  |  | 8.4281 |  |  | 6.268 |  |  | 5.2651 |  |  | 4.9757 |  |  | 4.6025 |  |  | 6.6754
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | 477.6851 |  |  | 29.8763 |  |  | 13.8451 |  |  | 8.4281 |  |  | 6.268 |  |  | 5.2651 |  |  | 4.9757 |  |  | 4.6025 |  |  | 6.6754
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 14861.6717 |  | 7174 | 17036.2857 |  | 7174 | 42132.762 |  | 7174 | 82063.8661 |  | 7174 | 134964.8456 |  | 7174 | 189298.5864 |  | 7174 | 240358.9741 |  | 7174 | 281839.8001 |  | 7174 | 314439.7438 |  | 7174 | 350810.4691
[13 empty] | Next iteration flow rate |  |  | 15158.9052 | Abs Value of | Flow this | 17206.6486 | Abs Value of | Flow this | 42554.0896 | Abs Value of | Flow this | 82884.5048 | Abs Value of | Flow this | 136314.4941 | Abs Value of | Flow this | 191191.5723 | Abs Value of | Flow this | 242762.5638 | Abs Value of | Flow this | 284658.1981 | Abs Value of | Flow this | 317584.1413 | Abs Value of | Flow this | 354318.5738 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 8.8903 |  |  | -17.5381 |  |  | -621.5753 |  |  | -2638.9077 |  |  | -7309.1266 |  |  | -14475.904 |  |  | -23399.9727 |  |  | -32211.2644 |  |  | -40118.4711 |  |  | -49960.6968
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.042885 |  |  | -0.084601 |  |  | -2.9984 |  |  | -12.7296 |  |  | -35.2579 |  |  | -69.8292 |  |  | -112.8773 |  |  | -155.3814 |  |  | -193.5244 |  |  | -241.0015
[13 empty] | Delta P at this iteration flow rate |  |  | -41.1097 |  |  | -67.5381 |  |  | -671.5753 |  |  | -2688.9077 |  |  | -7359.1266 |  |  | -14525.904 |  |  | -23449.9727 |  |  | -32261.2644 |  |  | -40168.4711 |  |  | -50010.6968
[13 empty] | Press drop ratio this iteration |  |  | -4.6241 |  |  | 3.8509 |  |  | 1.0804 |  |  | 1.0189 |  |  | 1.0068 |  |  | 1.0035 |  |  | 1.0021 |  |  | 1.0016 |  |  | 1.0012 |  |  | 1.001
[13 empty] | Expansion factor | 12 |  | 3.4083 |  |  | -1.0052 |  |  | 0.42898 |  |  | 0.45409 |  |  | 0.44579 |  |  | 0.41615 |  |  | 0.37667 |  |  | 0.31935 |  |  | 0.43769 |  |  | 0.14657
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | -113.2176 |  |  | 35.0264 |  |  | 15.7218 |  |  | 9.6802 |  |  | 7.5148 |  |  | 6.7497 |  |  | 7.2002 |  |  | 5.3465 |  |  | 18.7964
[13 empty] | C Choked w/ reducers | 5 |  | 726.9029 |  |  | 418.468 |  |  | 29.4844 |  |  | 13.6975 |  |  | 8.3423 |  |  | 6.2051 |  |  | 5.2125 |  |  | 4.9262 |  |  | 4.5567 |  |  | 6.6091
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | 418.468 |  |  | 29.4844 |  |  | 13.6975 |  |  | 8.3423 |  |  | 6.2051 |  |  | 5.2125 |  |  | 4.9262 |  |  | 4.5567 |  |  | 6.6091
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 15158.9052 |  | 7174 | 17206.6486 |  | 7174 | 42554.0896 |  | 7174 | 82884.5048 |  | 7174 | 136314.4941 |  | 7174 | 191191.5723 |  | 7174 | 242762.5638 |  | 7174 | 284658.1981 |  | 7174 | 317584.1413 |  | 7174 | 354318.5738
[13 empty] | Next iteration flow rate |  |  | 15462.0833 | Abs Value of | Flow this | 17378.7151 | Abs Value of | Flow this | 42979.6305 | Abs Value of | Flow this | 83713.3498 | Abs Value of | Flow this | 137677.639 | Abs Value of | Flow this | 193103.488 | Abs Value of | Flow this | 245190.1895 | Abs Value of | Flow this | 287504.7801 | Abs Value of | Flow this | 320759.9827 | Abs Value of | Flow this | 357861.7596 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 5.1884 |  |  | -19.9112 |  |  | -636.0895 |  |  | -2693.9702 |  |  | -7458.0606 |  |  | -14768.8902 |  |  | -23872.3326 |  |  | -32860.7313 |  |  | -40926.8729 |  |  | -50966.9273
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.025028 |  |  | -0.096048 |  |  | -3.0684 |  |  | -12.9952 |  |  | -35.9764 |  |  | -71.2425 |  |  | -115.1559 |  |  | -158.5143 |  |  | -197.4239 |  |  | -245.8554
[13 empty] | Delta P at this iteration flow rate |  |  | -44.8116 |  |  | -69.9112 |  |  | -686.0895 |  |  | -2743.9702 |  |  | -7508.0606 |  |  | -14818.8902 |  |  | -23922.3326 |  |  | -32910.7313 |  |  | -40976.8729 |  |  | -51016.9273
[13 empty] | Press drop ratio this iteration |  |  | -8.6369 |  |  | 3.5112 |  |  | 1.0786 |  |  | 1.0186 |  |  | 1.0067 |  |  | 1.0034 |  |  | 1.0021 |  |  | 1.0015 |  |  | 1.0012 |  |  | 1.001
[13 empty] | Expansion factor | 12 |  | 5.4982 |  |  | -0.82825 |  |  | 0.42995 |  |  | 0.4543 |  |  | 0.44587 |  |  | 0.41619 |  |  | 0.3767 |  |  | 0.31937 |  |  | 0.4377 |  |  | 0.14659
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | -128.0143 |  |  | 34.5208 |  |  | 15.5503 |  |  | 9.5808 |  |  | 7.4389 |  |  | 6.682 |  |  | 7.1281 |  |  | 5.2932 |  |  | 18.6076
[13 empty] | C Choked w/ reducers | 5 |  | 1270.4636 |  |  | 372.2806 |  |  | 29.0997 |  |  | 13.5517 |  |  | 8.2575 |  |  | 6.1428 |  |  | 5.1604 |  |  | 4.8771 |  |  | 4.5114 |  |  | 6.5434
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | 372.2806 |  |  | 29.0997 |  |  | 13.5517 |  |  | 8.2575 |  |  | 6.1428 |  |  | 5.1604 |  |  | 4.8771 |  |  | 4.5114 |  |  | 6.5434
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 15462.0833 |  | 7174 | 17378.7151 |  | 7174 | 42979.6305 |  | 7174 | 83713.3498 |  | 7174 | 137677.639 |  | 7174 | 193103.488 |  | 7174 | 245190.1895 |  | 7174 | 287504.7801 |  | 7174 | 320759.9827 |  | 7174 | 357861.7596
[13 empty] | Next iteration flow rate |  |  | 15771.3249 | Abs Value of | Flow this | 17552.5022 | Abs Value of | Flow this | 43409.4268 | Abs Value of | Flow this | 84550.4833 | Abs Value of | Flow this | 139054.4154 | Abs Value of | Flow this | 195034.5229 | Abs Value of | Flow this | 247642.0914 | Abs Value of | Flow this | 290379.8279 | Abs Value of | Flow this | 323967.5825 | Abs Value of | Flow this | 361440.3771 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 1.3369 |  |  | -22.3319 |  |  | -650.8954 |  |  | -2750.1395 |  |  | -7609.9881 |  |  | -15067.7654 |  |  | -24354.187 |  |  | -33523.2525 |  |  | -41751.5236 |  |  | -51993.3831
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | 0.0064489 |  |  | -0.10773 |  |  | -3.1398 |  |  | -13.2662 |  |  | -36.7092 |  |  | -72.6842 |  |  | -117.4803 |  |  | -161.7102 |  |  | -201.4019 |  |  | -250.8068
[13 empty] | Delta P at this iteration flow rate |  |  | -48.6631 |  |  | -72.3319 |  |  | -700.8954 |  |  | -2800.1395 |  |  | -7659.9881 |  |  | -15117.7654 |  |  | -24404.187 |  |  | -33573.2525 |  |  | -41801.5236 |  |  | -52043.3831
[13 empty] | Press drop ratio this iteration |  |  | -36.4004 |  |  | 3.239 |  |  | 1.0768 |  |  | 1.0182 |  |  | 1.0066 |  |  | 1.0033 |  |  | 1.0021 |  |  | 1.0015 |  |  | 1.0012 |  |  | 1.001
[13 empty] | Expansion factor | 12 |  | 19.9577 |  |  | -0.68651 |  |  | 0.43089 |  |  | 0.4545 |  |  | 0.44594 |  |  | 0.41623 |  |  | 0.37673 |  |  | 0.31939 |  |  | 0.43772 |  |  | 0.1466
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | -144.8057 |  |  | 34.0264 |  |  | 15.381 |  |  | 9.4825 |  |  | 7.3638 |  |  | 6.615 |  |  | 7.0568 |  |  | 5.2404 |  |  | 18.4207
[13 empty] | C Choked w/ reducers | 5 |  | 5029.2286 |  |  | 335.2456 |  |  | 28.7222 |  |  | 13.4077 |  |  | 8.1736 |  |  | 6.0812 |  |  | 5.1089 |  |  | 4.8285 |  |  | 4.4665 |  |  | 6.4784
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | 335.2456 |  |  | 28.7222 |  |  | 13.4077 |  |  | 8.1736 |  |  | 6.0812 |  |  | 5.1089 |  |  | 4.8285 |  |  | 4.4665 |  |  | 6.4784
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 15771.3249 |  | 7174 | 17552.5022 |  | 7174 | 43409.4268 |  | 7174 | 84550.4833 |  | 7174 | 139054.4154 |  | 7174 | 195034.5229 |  | 7174 | 247642.0914 |  | 7174 | 290379.8279 |  | 7174 | 323967.5825 |  | 7174 | 361440.3771
[13 empty] | Next iteration flow rate |  |  | 16086.7514 | Abs Value of | Flow this | 17728.0272 | Abs Value of | Flow this | 43843.521 | Abs Value of | Flow this | 85395.9881 | Abs Value of | Flow this | 140444.9596 | Abs Value of | Flow this | 196984.8681 | Abs Value of | Flow this | 250118.5123 | Abs Value of | Flow this | 293283.6262 | Abs Value of | Flow this | 327207.2583 | Abs Value of | Flow this | 365054.7809 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -2.6702 |  |  | -24.8013 |  |  | -665.9989 |  |  | -2807.4379 |  |  | -7764.9694 |  |  | -15372.648 |  |  | -24845.7267 |  |  | -34199.0904 |  |  | -42592.7497 |  |  | -53040.4706
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.012881 |  |  | -0.11964 |  |  | -3.2127 |  |  | -13.5426 |  |  | -37.4568 |  |  | -74.1549 |  |  | -119.8514 |  |  | -164.9703 |  |  | -205.4598 |  |  | -255.8578
[13 empty] | Delta P at this iteration flow rate |  |  | -52.6702 |  |  | -74.8013 |  |  | -715.9989 |  |  | -2857.4379 |  |  | -7814.9694 |  |  | -15422.648 |  |  | -24895.7267 |  |  | -34249.0904 |  |  | -42642.7497 |  |  | -53090.4706
[13 empty] | Press drop ratio this iteration |  |  | 19.725 |  |  | 3.016 |  |  | 1.0751 |  |  | 1.0178 |  |  | 1.0064 |  |  | 1.0033 |  |  | 1.002 |  |  | 1.0015 |  |  | 1.0012 |  |  | 1.0009
[13 empty] | Expansion factor | 12 |  | -9.273 |  |  | -0.57044 |  |  | 0.43181 |  |  | 0.4547 |  |  | 0.44601 |  |  | 0.41627 |  |  | 0.37675 |  |  | 0.31941 |  |  | 0.43773 |  |  | 0.14662
[13 empty] | C Non choked w/ reducers | 5 |  | -33.2769 |  |  | -164.2422 |  |  | 33.5428 |  |  | 15.2139 |  |  | 9.3852 |  |  | 7.2895 |  |  | 6.5487 |  |  | 6.9862 |  |  | 5.1882 |  |  | 18.2358
[13 empty] | C Choked w/ reducers | 5 |  | 2568.3107 |  |  | 304.885 |  |  | 28.3515 |  |  | 13.2654 |  |  | 8.0905 |  |  | 6.0202 |  |  | 5.0579 |  |  | 4.7804 |  |  | 4.4221 |  |  | 6.414
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 2568.3107 |  |  | 304.885 |  |  | 28.3515 |  |  | 13.2654 |  |  | 8.0905 |  |  | 6.0202 |  |  | 5.0579 |  |  | 4.7804 |  |  | 4.4221 |  |  | 6.414
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 16086.7514 |  | 7174 | 17728.0272 |  | 7174 | 43843.521 |  | 7174 | 85395.9881 |  | 7174 | 140444.9596 |  | 7174 | 196984.8681 |  | 7174 | 250118.5123 |  | 7174 | 293283.6262 |  | 7174 | 327207.2583 |  | 7174 | 365054.7809
[13 empty] | Next iteration flow rate |  |  | 16408.4865 | Abs Value of | Flow this | 17905.3075 | Abs Value of | Flow this | 44281.9563 | Abs Value of | Flow this | 86249.948 | Abs Value of | Flow this | 141849.4092 | Abs Value of | Flow this | 198954.7168 | Abs Value of | Flow this | 252619.6974 | Abs Value of | Flow this | 296216.4624 | Abs Value of | Flow this | 330479.3309 | Abs Value of | Flow this | 368705.3287 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -6.8392 |  |  | -27.3203 |  |  | -681.406 |  |  | -2865.8879 |  |  | -7923.0658 |  |  | -15683.6587 |  |  | -25347.1463 |  |  | -34888.5126 |  |  | -43450.8845 |  |  | -54108.6046
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.032991 |  |  | -0.13179 |  |  | -3.287 |  |  | -13.8245 |  |  | -38.2195 |  |  | -75.6552 |  |  | -122.2701 |  |  | -168.296 |  |  | -209.5993 |  |  | -261.0103
[13 empty] | Delta P at this iteration flow rate |  |  | -56.8392 |  |  | -77.3203 |  |  | -731.406 |  |  | -2915.8879 |  |  | -7973.0658 |  |  | -15733.6587 |  |  | -25397.1463 |  |  | -34938.5126 |  |  | -43500.8845 |  |  | -54158.6046
[13 empty] | Press drop ratio this iteration |  |  | 8.3108 |  |  | 2.8301 |  |  | 1.0734 |  |  | 1.0174 |  |  | 1.0063 |  |  | 1.0032 |  |  | 1.002 |  |  | 1.0014 |  |  | 1.0012 |  |  | 1.0009
[13 empty] | Expansion factor | 12 |  | -3.3283 |  |  | -0.47365 |  |  | 0.43271 |  |  | 0.4549 |  |  | 0.44608 |  |  | 0.4163 |  |  | 0.37678 |  |  | 0.31943 |  |  | 0.43774 |  |  | 0.14664
[13 empty] | C Non choked w/ reducers | 5 |  | -56.8807 |  |  | -187.2236 |  |  | 33.0697 |  |  | 15.0489 |  |  | 9.2891 |  |  | 7.216 |  |  | 6.483 |  |  | 6.9163 |  |  | 5.1365 |  |  | 18.0528
[13 empty] | C Choked w/ reducers | 5 |  | 1022.7957 |  |  | 279.5414 |  |  | 27.9876 |  |  | 13.1248 |  |  | 8.0084 |  |  | 5.9598 |  |  | 5.0074 |  |  | 4.7328 |  |  | 4.3781 |  |  | 6.3502
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 1022.7957 |  |  | 279.5414 |  |  | 27.9876 |  |  | 13.1248 |  |  | 8.0084 |  |  | 5.9598 |  |  | 5.0074 |  |  | 4.7328 |  |  | 4.3781 |  |  | 6.3502
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 16408.4865 |  | 7174 | 17905.3075 |  | 7174 | 44281.9563 |  | 7174 | 86249.948 |  | 7174 | 141849.4092 |  | 7174 | 198954.7168 |  | 7174 | 252619.6974 |  | 7174 | 296216.4624 |  | 7174 | 330479.3309 |  | 7174 | 368705.3287
[13 empty] | Next iteration flow rate |  |  | 16736.6562 | Abs Value of | Flow this | 18084.3606 | Abs Value of | Flow this | 44724.7758 | Abs Value of | Flow this | 87112.4475 | Abs Value of | Flow this | 143267.9032 | Abs Value of | Flow this | 200944.264 | Abs Value of | Flow this | 255145.8944 | Abs Value of | Flow this | 299178.6271 | Abs Value of | Flow this | 333784.1242 | Abs Value of | Flow this | 372392.382 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -11.1766 |  |  | -29.8899 |  |  | -697.1227 |  |  | -2925.5127 |  |  | -8084.3399 |  |  | -16000.9208 |  |  | -25858.6444 |  |  | -35591.7922 |  |  | -44326.2678 |  |  | -55198.208
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.053914 |  |  | -0.14418 |  |  | -3.3628 |  |  | -14.1122 |  |  | -38.9974 |  |  | -77.1856 |  |  | -124.7375 |  |  | -171.6885 |  |  | -213.822 |  |  | -266.2663
[13 empty] | Delta P at this iteration flow rate |  |  | -61.1766 |  |  | -79.8899 |  |  | -747.1227 |  |  | -2975.5127 |  |  | -8134.3399 |  |  | -16050.9208 |  |  | -25908.6444 |  |  | -35641.7922 |  |  | -44376.2678 |  |  | -55248.208
[13 empty] | Press drop ratio this iteration |  |  | 5.4736 |  |  | 2.6728 |  |  | 1.0717 |  |  | 1.0171 |  |  | 1.0062 |  |  | 1.0031 |  |  | 1.0019 |  |  | 1.0014 |  |  | 1.0011 |  |  | 1.0009
[13 empty] | Expansion factor | 12 |  | -1.8507 |  |  | -0.39172 |  |  | 0.43359 |  |  | 0.45509 |  |  | 0.44615 |  |  | 0.41634 |  |  | 0.3768 |  |  | 0.31945 |  |  | 0.43775 |  |  | 0.14665
[13 empty] | C Non choked w/ reducers | 5 |  | -78.674 |  |  | -215.0503 |  |  | 32.6067 |  |  | 14.8859 |  |  | 9.1939 |  |  | 7.1432 |  |  | 6.418 |  |  | 6.8471 |  |  | 5.0853 |  |  | 17.8717
[13 empty] | C Choked w/ reducers | 5 |  | 638.3873 |  |  | 258.0642 |  |  | 27.6301 |  |  | 12.9858 |  |  | 7.9271 |  |  | 5.9001 |  |  | 4.9575 |  |  | 4.6857 |  |  | 4.3346 |  |  | 6.2871
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 638.3873 |  |  | 258.0642 |  |  | 27.6301 |  |  | 12.9858 |  |  | 7.9271 |  |  | 5.9001 |  |  | 4.9575 |  |  | 4.6857 |  |  | 4.3346 |  |  | 6.2871
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 16736.6562 |  | 7174 | 18084.3606 |  | 7174 | 44724.7758 |  | 7174 | 87112.4475 |  | 7174 | 143267.9032 |  | 7174 | 200944.264 |  | 7174 | 255145.8944 |  | 7174 | 299178.6271 |  | 7174 | 333784.1242 |  | 7174 | 372392.382
[13 empty] | Next iteration flow rate |  |  | 17071.3893 | Abs Value of | Flow this | 18265.2042 | Abs Value of | Flow this | 45172.0236 | Abs Value of | Flow this | 87983.572 | Abs Value of | Flow this | 144700.5823 | Abs Value of | Flow this | 202953.7066 | Abs Value of | Flow this | 257697.3533 | Abs Value of | Flow this | 302170.4133 | Abs Value of | Flow this | 337121.9655 | Abs Value of | Flow this | 376116.3058 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -15.6893 |  |  | -32.5112 |  |  | -713.1554 |  |  | -2986.336 |  |  | -8248.8556 |  |  | -16324.5598 |  |  | -26380.4237 |  |  | -36309.2078 |  |  | -45219.2463 |  |  | -56309.7125
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.075682 |  |  | -0.15683 |  |  | -3.4401 |  |  | -14.4056 |  |  | -39.791 |  |  | -78.7468 |  |  | -127.2545 |  |  | -175.1492 |  |  | -218.1296 |  |  | -271.628
[13 empty] | Delta P at this iteration flow rate |  |  | -65.6893 |  |  | -82.5112 |  |  | -763.1554 |  |  | -3036.336 |  |  | -8298.8556 |  |  | -16374.5598 |  |  | -26430.4237 |  |  | -36359.2078 |  |  | -45269.2463 |  |  | -56359.7125
[13 empty] | Press drop ratio this iteration |  |  | 4.1869 |  |  | 2.5379 |  |  | 1.0701 |  |  | 1.0167 |  |  | 1.0061 |  |  | 1.0031 |  |  | 1.0019 |  |  | 1.0014 |  |  | 1.0011 |  |  | 1.0009
[13 empty] | Expansion factor | 12 |  | -1.1806 |  |  | -0.32149 |  |  | 0.43444 |  |  | 0.45528 |  |  | 0.44622 |  |  | 0.41638 |  |  | 0.37682 |  |  | 0.31947 |  |  | 0.43777 |  |  | 0.14667
[13 empty] | C Non choked w/ reducers | 5 |  | -102.4654 |  |  | -249.6909 |  |  | 32.1534 |  |  | 14.7251 |  |  | 9.0999 |  |  | 7.0712 |  |  | 6.3537 |  |  | 6.7786 |  |  | 5.0346 |  |  | 17.6924
[13 empty] | C Choked w/ reducers | 5 |  | 463.8658 |  |  | 239.6297 |  |  | 27.2791 |  |  | 12.8486 |  |  | 7.8467 |  |  | 5.8409 |  |  | 4.908 |  |  | 4.639 |  |  | 4.2915 |  |  | 6.2246
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 463.8658 |  |  | 239.6297 |  |  | 27.2791 |  |  | 12.8486 |  |  | 7.8467 |  |  | 5.8409 |  |  | 4.908 |  |  | 4.639 |  |  | 4.2915 |  |  | 6.2246
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 17071.3893 |  | 7174 | 18265.2042 |  | 7174 | 45172.0236 |  | 7174 | 87983.572 |  | 7174 | 144700.5823 |  | 7174 | 202953.7066 |  | 7174 | 257697.3533 |  | 7174 | 302170.4133 |  | 7174 | 337121.9655 |  | 7174 | 376116.3058
[13 empty] | Next iteration flow rate |  |  | 17412.8171 | Abs Value of | Flow this | 18447.8562 | Abs Value of | Flow this | 45623.7438 | Abs Value of | Flow this | 88863.4077 | Abs Value of | Flow this | 146147.5881 | Abs Value of | Flow this | 204983.2437 | Abs Value of | Flow this | 260274.3268 | Abs Value of | Flow this | 305192.1175 | Abs Value of | Flow this | 340493.1851 | Abs Value of | Flow this | 379877.4689 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -20.3843 |  |  | -35.1852 |  |  | -729.5103 |  |  | -3048.3819 |  |  | -8416.6781 |  |  | -16654.704 |  |  | -26912.6907 |  |  | -37041.0433 |  |  | -46130.1736 |  |  | -57443.5582
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.09833 |  |  | -0.16973 |  |  | -3.519 |  |  | -14.7049 |  |  | -40.6006 |  |  | -80.3393 |  |  | -129.822 |  |  | -178.6794 |  |  | -222.5237 |  |  | -277.0975
[13 empty] | Delta P at this iteration flow rate |  |  | -70.3843 |  |  | -85.1852 |  |  | -779.5103 |  |  | -3098.3819 |  |  | -8466.6781 |  |  | -16704.704 |  |  | -26962.6907 |  |  | -37091.0433 |  |  | -46180.1736 |  |  | -57493.5582
[13 empty] | Press drop ratio this iteration |  |  | 3.4529 |  |  | 2.4211 |  |  | 1.0685 |  |  | 1.0164 |  |  | 1.0059 |  |  | 1.003 |  |  | 1.0019 |  |  | 1.0013 |  |  | 1.0011 |  |  | 1.0009
[13 empty] | Expansion factor | 12 |  | -0.79829 |  |  | -0.26063 |  |  | 0.43527 |  |  | 0.45546 |  |  | 0.44629 |  |  | 0.41641 |  |  | 0.37685 |  |  | 0.31949 |  |  | 0.43778 |  |  | 0.14668
[13 empty] | C Non choked w/ reducers | 5 |  | -131.0003 |  |  | -294.2895 |  |  | 31.7096 |  |  | 14.5662 |  |  | 9.0068 |  |  | 7 |  |  | 6.2901 |  |  | 6.7108 |  |  | 4.9845 |  |  | 17.515
[13 empty] | C Choked w/ reducers | 5 |  | 364.1673 |  |  | 223.6327 |  |  | 26.9342 |  |  | 12.7129 |  |  | 7.7671 |  |  | 5.7824 |  |  | 4.8591 |  |  | 4.5929 |  |  | 4.2488 |  |  | 6.1628
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 364.1673 |  |  | 223.6327 |  |  | 26.9342 |  |  | 12.7129 |  |  | 7.7671 |  |  | 5.7824 |  |  | 4.8591 |  |  | 4.5929 |  |  | 4.2488 |  |  | 6.1628
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 17412.8171 |  | 7174 | 18447.8562 |  | 7174 | 45623.7438 |  | 7174 | 88863.4077 |  | 7174 | 146147.5881 |  | 7174 | 204983.2437 |  | 7174 | 260274.3268 |  | 7174 | 305192.1175 |  | 7174 | 340493.1851 |  | 7174 | 379877.4689
[13 empty] | Next iteration flow rate |  |  | 17761.0735 | Abs Value of | Flow this | 18632.3348 | Abs Value of | Flow this | 46079.9813 | Abs Value of | Flow this | 89752.0418 | Abs Value of | Flow this | 147609.064 | Abs Value of | Flow this | 207033.0761 | Abs Value of | Flow this | 262877.0701 | Abs Value of | Flow this | 308244.0386 | Abs Value of | Flow this | 343898.117 | Abs Value of | Flow this | 383676.2436 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -25.2689 |  |  | -37.9129 |  |  | -746.194 |  |  | -3111.6749 |  |  | -8587.8739 |  |  | -16991.484 |  |  | -27455.6563 |  |  | -37787.5888 |  |  | -47059.4106 |  |  | -58600.1943
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.12189 |  |  | -0.18289 |  |  | -3.5995 |  |  | -15.0102 |  |  | -41.4264 |  |  | -81.9639 |  |  | -132.4412 |  |  | -182.2806 |  |  | -227.0062 |  |  | -282.6769
[13 empty] | Delta P at this iteration flow rate |  |  | -75.2689 |  |  | -87.9129 |  |  | -796.194 |  |  | -3161.6749 |  |  | -8637.8739 |  |  | -17041.484 |  |  | -27505.6563 |  |  | -37837.5888 |  |  | -47109.4106 |  |  | -58650.1943
[13 empty] | Press drop ratio this iteration |  |  | 2.9787 |  |  | 2.3188 |  |  | 1.067 |  |  | 1.0161 |  |  | 1.0058 |  |  | 1.0029 |  |  | 1.0018 |  |  | 1.0013 |  |  | 1.0011 |  |  | 1.0009
[13 empty] | Expansion factor | 12 |  | -0.55135 |  |  | -0.2074 |  |  | 0.43608 |  |  | 0.45564 |  |  | 0.44635 |  |  | 0.41645 |  |  | 0.37687 |  |  | 0.31951 |  |  | 0.43779 |  |  | 0.1467
[13 empty] | C Non choked w/ reducers | 5 |  | -168.0326 |  |  | -354.2138 |  |  | 31.2749 |  |  | 14.4093 |  |  | 8.9147 |  |  | 6.9295 |  |  | 6.2271 |  |  | 6.6437 |  |  | 4.9348 |  |  | 17.3394
[13 empty] | C Choked w/ reducers | 5 |  | 299.6468 |  |  | 209.6183 |  |  | 26.5953 |  |  | 12.5789 |  |  | 7.6884 |  |  | 5.7245 |  |  | 4.8106 |  |  | 4.5471 |  |  | 4.2065 |  |  | 6.1016
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 299.6468 |  |  | 209.6183 |  |  | 26.5953 |  |  | 12.5789 |  |  | 7.6884 |  |  | 5.7245 |  |  | 4.8106 |  |  | 4.5471 |  |  | 4.2065 |  |  | 6.1016
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 17761.0735 |  | 7174 | 18632.3348 |  | 7174 | 46079.9813 |  | 7174 | 89752.0418 |  | 7174 | 147609.064 |  | 7174 | 207033.0761 |  | 7174 | 262877.0701 |  | 7174 | 308244.0386 |  | 7174 | 343898.117 |  | 7174 | 383676.2436
[13 empty] | Next iteration flow rate |  |  | 18116.2949 | Abs Value of | Flow this | 18818.6582 | Abs Value of | Flow this | 46540.7811 | Abs Value of | Flow this | 90649.5622 | Abs Value of | Flow this | 149085.1546 | Abs Value of | Flow this | 209103.4069 | Abs Value of | Flow this | 265505.8408 | Abs Value of | Flow this | 311326.479 | Abs Value of | Flow this | 347337.0981 | Abs Value of | Flow this | 387513.006 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -30.3509 |  |  | -40.6955 |  |  | -763.213 |  |  | -3176.24 |  |  | -8762.5106 |  |  | -17335.0334 |  |  | -28009.5355 |  |  | -38549.1399 |  |  | -48007.3253 |  |  | -59780.0787
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.14641 |  |  | -0.19631 |  |  | -3.6816 |  |  | -15.3216 |  |  | -42.2688 |  |  | -83.6211 |  |  | -135.113 |  |  | -185.9542 |  |  | -231.5788 |  |  | -288.3685
[13 empty] | Delta P at this iteration flow rate |  |  | -80.3509 |  |  | -90.6955 |  |  | -813.213 |  |  | -3226.24 |  |  | -8812.5106 |  |  | -17385.0334 |  |  | -28059.5355 |  |  | -38599.1399 |  |  | -48057.3253 |  |  | -59830.0787
[13 empty] | Press drop ratio this iteration |  |  | 2.6474 |  |  | 2.2286 |  |  | 1.0655 |  |  | 1.0157 |  |  | 1.0057 |  |  | 1.0029 |  |  | 1.0018 |  |  | 1.0013 |  |  | 1.001 |  |  | 1.0008
[13 empty] | Expansion factor | 12 |  | -0.37879 |  |  | -0.16044 |  |  | 0.43687 |  |  | 0.45581 |  |  | 0.44642 |  |  | 0.41648 |  |  | 0.37689 |  |  | 0.31952 |  |  | 0.4378 |  |  | 0.14671
[13 empty] | C Non choked w/ reducers | 5 |  | -220.311 |  |  | -439.4609 |  |  | 30.8491 |  |  | 14.2544 |  |  | 8.8237 |  |  | 6.8597 |  |  | 6.1647 |  |  | 6.5773 |  |  | 4.8857 |  |  | 17.1656
[13 empty] | C Choked w/ reducers | 5 |  | 254.4632 |  |  | 197.2385 |  |  | 26.2623 |  |  | 12.4464 |  |  | 7.6105 |  |  | 5.6671 |  |  | 4.7626 |  |  | 4.5019 |  |  | 4.1647 |  |  | 6.041
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 254.4632 |  |  | 197.2385 |  |  | 26.2623 |  |  | 12.4464 |  |  | 7.6105 |  |  | 5.6671 |  |  | 4.7626 |  |  | 4.5019 |  |  | 4.1647 |  |  | 6.041
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 18116.2949 |  | 7174 | 18818.6582 |  | 7174 | 46540.7811 |  | 7174 | 90649.5622 |  | 7174 | 149085.1546 |  | 7174 | 209103.4069 |  | 7174 | 265505.8408 |  | 7174 | 311326.479 |  | 7174 | 347337.0981 |  | 7174 | 387513.006
[13 empty] | Next iteration flow rate |  |  | 18478.6208 | Abs Value of | Flow this | 19006.8447 | Abs Value of | Flow this | 47006.1889 | Abs Value of | Flow this | 91556.0578 | Abs Value of | Flow this | 150576.0062 | Abs Value of | Flow this | 211194.4409 | Abs Value of | Flow this | 268160.8992 | Abs Value of | Flow this | 314439.7438 | Abs Value of | Flow this | 350810.4691 | Abs Value of | Flow this | 391388.1361 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -35.6382 |  |  | -43.534 |  |  | -780.5741 |  |  | -3242.103 |  |  | -8940.6576 |  |  | -17685.488 |  |  | -28574.5477 |  |  | -39325.9981 |  |  | -48974.293 |  |  | -60983.6788
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.17191 |  |  | -0.21 |  |  | -3.7654 |  |  | -15.6393 |  |  | -43.1281 |  |  | -85.3116 |  |  | -137.8385 |  |  | -189.7016 |  |  | -236.2433 |  |  | -294.1744
[13 empty] | Delta P at this iteration flow rate |  |  | -85.6382 |  |  | -93.534 |  |  | -830.5741 |  |  | -3292.103 |  |  | -8990.6576 |  |  | -17735.488 |  |  | -28624.5477 |  |  | -39375.9981 |  |  | -49024.293 |  |  | -61033.6788
[13 empty] | Press drop ratio this iteration |  |  | 2.403 |  |  | 2.1485 |  |  | 1.0641 |  |  | 1.0154 |  |  | 1.0056 |  |  | 1.0028 |  |  | 1.0017 |  |  | 1.0013 |  |  | 1.001 |  |  | 1.0008
[13 empty] | Expansion factor | 12 |  | -0.2515 |  |  | -0.11873 |  |  | 0.43764 |  |  | 0.45598 |  |  | 0.44648 |  |  | 0.41651 |  |  | 0.37691 |  |  | 0.31954 |  |  | 0.43781 |  |  | 0.14673
[13 empty] | C Non choked w/ reducers | 5 |  | -302.5414 |  |  | -571.0396 |  |  | 30.4318 |  |  | 14.1014 |  |  | 8.7336 |  |  | 6.7907 |  |  | 6.103 |  |  | 6.5116 |  |  | 4.837 |  |  | 16.9936
[13 empty] | C Choked w/ reducers | 5 |  | 221.0451 |  |  | 186.222 |  |  | 25.9349 |  |  | 12.3155 |  |  | 7.5335 |  |  | 5.6104 |  |  | 4.7151 |  |  | 4.4571 |  |  | 4.1233 |  |  | 5.9809
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 221.0451 |  |  | 186.222 |  |  | 25.9349 |  |  | 12.3155 |  |  | 7.5335 |  |  | 5.6104 |  |  | 4.7151 |  |  | 4.4571 |  |  | 4.1233 |  |  | 5.9809
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 18478.6208 |  | 7174 | 19006.8447 |  | 7174 | 47006.1889 |  | 7174 | 91556.0578 |  | 7174 | 150576.0062 |  | 7174 | 211194.4409 |  | 7174 | 268160.8992 |  | 7174 | 314439.7438 |  | 7174 | 350810.4691 |  | 7174 | 391388.1361
[13 empty] | Next iteration flow rate |  |  | 18848.1932 | Abs Value of | Flow this | 19196.9132 | Abs Value of | Flow this | 47476.2508 | Abs Value of | Flow this | 92471.6184 | Abs Value of | Flow this | 152081.7662 | Abs Value of | Flow this | 213306.3853 | Abs Value of | Flow this | 270842.5082 | Abs Value of | Flow this | 317584.1413 | Abs Value of | Flow this | 354318.5738 | Abs Value of | Flow this | 395302.0174 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -41.1391 |  |  | -46.4295 |  |  | -798.2842 |  |  | -3309.2898 |  |  | -9122.3853 |  |  | -18042.9869 |  |  | -29150.9166 |  |  | -40118.4711 |  |  | -49960.6968 |  |  | -62211.4712
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.19845 |  |  | -0.22397 |  |  | -3.8508 |  |  | -15.9634 |  |  | -44.0048 |  |  | -87.0362 |  |  | -140.6188 |  |  | -193.5244 |  |  | -241.0015 |  |  | -300.0971
[13 empty] | Delta P at this iteration flow rate |  |  | -91.1391 |  |  | -96.4295 |  |  | -848.2842 |  |  | -3359.2898 |  |  | -9172.3853 |  |  | -18092.9869 |  |  | -29200.9166 |  |  | -40168.4711 |  |  | -50010.6968 |  |  | -62261.4712
[13 empty] | Press drop ratio this iteration |  |  | 2.2154 |  |  | 2.0769 |  |  | 1.0626 |  |  | 1.0151 |  |  | 1.0055 |  |  | 1.0028 |  |  | 1.0017 |  |  | 1.0012 |  |  | 1.001 |  |  | 1.0008
[13 empty] | Expansion factor | 12 |  | -0.1538 |  |  | -0.081436 |  |  | 0.43839 |  |  | 0.45615 |  |  | 0.44654 |  |  | 0.41655 |  |  | 0.37694 |  |  | 0.31956 |  |  | 0.43783 |  |  | 0.14674
[13 empty] | C Non choked w/ reducers | 5 |  | -455.2882 |  |  | -801.9293 |  |  | 30.0228 |  |  | 13.9503 |  |  | 8.6445 |  |  | 6.7224 |  |  | 6.0419 |  |  | 6.4466 |  |  | 4.7889 |  |  | 16.8234
[13 empty] | C Choked w/ reducers | 5 |  | 195.3179 |  |  | 176.3545 |  |  | 25.6132 |  |  | 12.1861 |  |  | 7.4573 |  |  | 5.5542 |  |  | 4.6681 |  |  | 4.4127 |  |  | 4.0823 |  |  | 5.9215
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 195.3179 |  |  | 176.3545 |  |  | 25.6132 |  |  | 12.1861 |  |  | 7.4573 |  |  | 5.5542 |  |  | 4.6681 |  |  | 4.4127 |  |  | 4.0823 |  |  | 5.9215
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 18848.1932 |  | 7174 | 19196.9132 |  | 7174 | 47476.2508 |  | 7174 | 92471.6184 |  | 7174 | 152081.7662 |  | 7174 | 213306.3853 |  | 7174 | 270842.5082 |  | 7174 | 317584.1413 |  | 7174 | 354318.5738 |  | 7174 | 395302.0174
[13 empty] | Next iteration flow rate |  |  | 19225.1571 | Abs Value of | Flow this | 19388.8823 | Abs Value of | Flow this | 47951.0133 | Abs Value of | Flow this | 93396.3346 | Abs Value of | Flow this | 153602.5839 | Abs Value of | Flow this | 215439.4492 | Abs Value of | Flow this | 273550.9333 | Abs Value of | Flow this | 320759.9827 | Abs Value of | Flow this | 357861.7596 | Abs Value of | Flow this | 399255.0376 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -46.8622 |  |  | -49.3833 |  |  | -816.3502 |  |  | -3377.827 |  |  | -9307.7658 |  |  | -18407.6714 |  |  | -29738.8705 |  |  | -40926.8729 |  |  | -50966.9273 |  |  | -63463.9423
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.22606 |  |  | -0.23822 |  |  | -3.9379 |  |  | -16.294 |  |  | -44.899 |  |  | -88.7953 |  |  | -143.455 |  |  | -197.4239 |  |  | -245.8554 |  |  | -306.1388
[13 empty] | Delta P at this iteration flow rate |  |  | -96.8622 |  |  | -99.3833 |  |  | -866.3502 |  |  | -3427.827 |  |  | -9357.7658 |  |  | -18457.6714 |  |  | -29788.8705 |  |  | -40976.8729 |  |  | -51016.9273 |  |  | -63513.9423
[13 empty] | Press drop ratio this iteration |  |  | 2.067 |  |  | 2.0125 |  |  | 1.0612 |  |  | 1.0148 |  |  | 1.0054 |  |  | 1.0027 |  |  | 1.0017 |  |  | 1.0012 |  |  | 1.001 |  |  | 1.0008
[13 empty] | Expansion factor | 12 |  | -0.076495 |  |  | -0.047897 |  |  | 0.43912 |  |  | 0.45631 |  |  | 0.4466 |  |  | 0.41658 |  |  | 0.37696 |  |  | 0.31957 |  |  | 0.43784 |  |  | 0.14675
[13 empty] | C Non choked w/ reducers | 5 |  | -848.5958 |  |  | -1315.2984 |  |  | 29.6218 |  |  | 13.801 |  |  | 8.5564 |  |  | 6.6547 |  |  | 5.9814 |  |  | 6.3822 |  |  | 4.7412 |  |  | 16.6549
[13 empty] | C Choked w/ reducers | 5 |  | 174.8936 |  |  | 167.4644 |  |  | 25.2968 |  |  | 12.0582 |  |  | 7.3818 |  |  | 5.4986 |  |  | 4.6216 |  |  | 4.3688 |  |  | 4.0417 |  |  | 5.8627
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 174.8936 |  |  | 167.4644 |  |  | 25.2968 |  |  | 12.0582 |  |  | 7.3818 |  |  | 5.4986 |  |  | 4.6216 |  |  | 4.3688 |  |  | 4.0417 |  |  | 5.8627
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 19225.1571 |  | 7174 | 19388.8823 |  | 7174 | 47951.0133 |  | 7174 | 93396.3346 |  | 7174 | 153602.5839 |  | 7174 | 215439.4492 |  | 7174 | 273550.9333 |  | 7174 | 320759.9827 |  | 7174 | 357861.7596 |  | 7174 | 399255.0376
[13 empty] | Next iteration flow rate |  |  | 19609.6602 | Abs Value of | Flow this | 19582.7711 | Abs Value of | Flow this | 48430.5234 | Abs Value of | Flow this | 94330.2979 | Abs Value of | Flow this | 155138.6097 | Abs Value of | Flow this | 217593.8437 | Abs Value of | Flow this | 276286.4426 | Abs Value of | Flow this | 323967.5825 | Abs Value of | Flow this | 361440.3771 | Abs Value of | Flow this | 403247.588 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -52.8166 |  |  | -52.3964 |  |  | -834.7793 |  |  | -3447.7418 |  |  | -9496.8724 |  |  | -18779.6861 |  |  | -30338.6423 |  |  | -41751.5236 |  |  | -51993.3831 |  |  | -64741.588
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.25478 |  |  | -0.25275 |  |  | -4.0268 |  |  | -16.6313 |  |  | -45.8112 |  |  | -90.5899 |  |  | -146.3482 |  |  | -201.4019 |  |  | -250.8068 |  |  | -312.3019
[13 empty] | Delta P at this iteration flow rate |  |  | -102.8166 |  |  | -102.3964 |  |  | -884.7793 |  |  | -3497.7418 |  |  | -9546.8724 |  |  | -18829.6861 |  |  | -30388.6423 |  |  | -41801.5236 |  |  | -52043.3831 |  |  | -64791.588
[13 empty] | Press drop ratio this iteration |  |  | 1.9467 |  |  | 1.9543 |  |  | 1.0599 |  |  | 1.0145 |  |  | 1.0053 |  |  | 1.0027 |  |  | 1.0016 |  |  | 1.0012 |  |  | 1.001 |  |  | 1.0008
[13 empty] | Expansion factor | 12 |  | -0.013849 |  |  | -0.017579 |  |  | 0.43984 |  |  | 0.45648 |  |  | 0.44666 |  |  | 0.41661 |  |  | 0.37698 |  |  | 0.31959 |  |  | 0.43785 |  |  | 0.14677
[13 empty] | C Non choked w/ reducers | 5 |  | -4371.0274 |  |  | -3461.7934 |  |  | 29.2286 |  |  | 13.6536 |  |  | 8.4692 |  |  | 6.5878 |  |  | 5.9216 |  |  | 6.3184 |  |  | 4.694 |  |  | 16.4881
[13 empty] | C Choked w/ reducers | 5 |  | 158.2803 |  |  | 159.4125 |  |  | 24.9857 |  |  | 11.9319 |  |  | 7.3072 |  |  | 5.4436 |  |  | 4.5755 |  |  | 4.3254 |  |  | 4.0016 |  |  | 5.8045
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 158.2803 |  |  | 159.4125 |  |  | 24.9857 |  |  | 11.9319 |  |  | 7.3072 |  |  | 5.4436 |  |  | 4.5755 |  |  | 4.3254 |  |  | 4.0016 |  |  | 5.8045
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 19609.6602 |  | 7174 | 19582.7711 |  | 7174 | 48430.5234 |  | 7174 | 94330.2979 |  | 7174 | 155138.6097 |  | 7174 | 217593.8437 |  | 7174 | 276286.4426 |  | 7174 | 323967.5825 |  | 7174 | 361440.3771 |  | 7174 | 403247.588
[13 empty] | Next iteration flow rate |  |  | 20001.8534 | Abs Value of | Flow this | 19778.5989 | Abs Value of | Flow this | 48914.8286 | Abs Value of | Flow this | 95273.6009 | Abs Value of | Flow this | 156689.9958 | Abs Value of | Flow this | 219769.7821 | Abs Value of | Flow this | 279049.3071 | Abs Value of | Flow this | 327207.2583 | Abs Value of | Flow this | 365054.7809 | Abs Value of | Flow this | 407280.0639 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -59.0115 |  |  | -55.47 |  |  | -853.5789 |  |  | -3519.0619 |  |  | -9689.78 |  |  | -19159.1783 |  |  | -30950.4696 |  |  | -42592.7497 |  |  | -53040.4706 |  |  | -66044.9145
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.28466 |  |  | -0.26758 |  |  | -4.1175 |  |  | -16.9753 |  |  | -46.7418 |  |  | -92.4205 |  |  | -149.2996 |  |  | -205.4598 |  |  | -255.8578 |  |  | -318.5889
[13 empty] | Delta P at this iteration flow rate |  |  | -109.0115 |  |  | -105.47 |  |  | -903.5789 |  |  | -3569.0619 |  |  | -9739.78 |  |  | -19209.1783 |  |  | -31000.4696 |  |  | -42642.7497 |  |  | -53090.4706 |  |  | -66094.9145
[13 empty] | Press drop ratio this iteration |  |  | 1.8473 |  |  | 1.9014 |  |  | 1.0586 |  |  | 1.0142 |  |  | 1.0052 |  |  | 1.0026 |  |  | 1.0016 |  |  | 1.0012 |  |  | 1.0009 |  |  | 1.0008
[13 empty] | Expansion factor | 12 |  | 0.037909 |  |  | 0.0099537 |  |  | 0.44053 |  |  | 0.45663 |  |  | 0.44672 |  |  | 0.41664 |  |  | 0.377 |  |  | 0.31961 |  |  | 0.43786 |  |  | 0.14678
[13 empty] | C Non choked w/ reducers | 5 |  | 1496.4955 |  |  | 5913.4558 |  |  | 28.843 |  |  | 13.5079 |  |  | 8.383 |  |  | 6.5216 |  |  | 5.8624 |  |  | 6.2553 |  |  | 4.6473 |  |  | 16.323
[13 empty] | C Choked w/ reducers | 5 |  | 144.4976 |  |  | 152.085 |  |  | 24.6798 |  |  | 11.8069 |  |  | 7.2333 |  |  | 5.3891 |  |  | 4.5299 |  |  | 4.2823 |  |  | 3.9618 |  |  | 5.7468
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 144.4976 |  |  | 152.085 |  |  | 24.6798 |  |  | 11.8069 |  |  | 7.2333 |  |  | 5.3891 |  |  | 4.5299 |  |  | 4.2823 |  |  | 3.9618 |  |  | 5.7468
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 20001.8534 |  | 7174 | 19778.5989 |  | 7174 | 48914.8286 |  | 7174 | 95273.6009 |  | 7174 | 156689.9958 |  | 7174 | 219769.7821 |  | 7174 | 279049.3071 |  | 7174 | 327207.2583 |  | 7174 | 365054.7809 |  | 7174 | 407280.0639
[13 empty] | Next iteration flow rate |  |  | 20401.8905 | Abs Value of | Flow this | 19976.3848 | Abs Value of | Flow this | 49403.9769 | Abs Value of | Flow this | 96226.3369 | Abs Value of | Flow this | 158256.8958 | Abs Value of | Flow this | 221967.4799 | Abs Value of | Flow this | 281839.8001 | Abs Value of | Flow this | 330479.3309 | Abs Value of | Flow this | 368705.3287 | Abs Value of | Flow this | 411352.8645 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -65.4567 |  |  | -58.6055 |  |  | -872.7563 |  |  | -3591.8156 |  |  | -9886.5651 |  |  | -19546.2983 |  |  | -31574.5945 |  |  | -43450.8845 |  |  | -54108.6046 |  |  | -67374.4378
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.31575 |  |  | -0.2827 |  |  | -4.21 |  |  | -17.3263 |  |  | -47.691 |  |  | -94.2879 |  |  | -152.3102 |  |  | -209.5993 |  |  | -261.0103 |  |  | -325.0023
[13 empty] | Delta P at this iteration flow rate |  |  | -115.4567 |  |  | -108.6055 |  |  | -922.7563 |  |  | -3641.8156 |  |  | -9936.5651 |  |  | -19596.2983 |  |  | -31624.5945 |  |  | -43500.8845 |  |  | -54158.6046 |  |  | -67424.4378
[13 empty] | Press drop ratio this iteration |  |  | 1.7639 |  |  | 1.8532 |  |  | 1.0573 |  |  | 1.0139 |  |  | 1.0051 |  |  | 1.0026 |  |  | 1.0016 |  |  | 1.0012 |  |  | 1.0009 |  |  | 1.0007
[13 empty] | Expansion factor | 12 |  | 0.08136 |  |  | 0.035064 |  |  | 0.44121 |  |  | 0.45679 |  |  | 0.44677 |  |  | 0.41667 |  |  | 0.37702 |  |  | 0.31962 |  |  | 0.43787 |  |  | 0.14679
[13 empty] | C Non choked w/ reducers | 5 |  | 656.1867 |  |  | 1625.4669 |  |  | 28.4647 |  |  | 13.364 |  |  | 8.2976 |  |  | 6.4561 |  |  | 5.8037 |  |  | 6.1929 |  |  | 4.601 |  |  | 16.1596
[13 empty] | C Choked w/ reducers | 5 |  | 132.8751 |  |  | 145.3878 |  |  | 24.3788 |  |  | 11.6835 |  |  | 7.1602 |  |  | 5.3352 |  |  | 4.4848 |  |  | 4.2397 |  |  | 3.9224 |  |  | 5.6898
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 132.8751 |  |  | 145.3878 |  |  | 24.3788 |  |  | 11.6835 |  |  | 7.1602 |  |  | 5.3352 |  |  | 4.4848 |  |  | 4.2397 |  |  | 3.9224 |  |  | 5.6898
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 20401.8905 |  | 7174 | 19976.3848 |  | 7174 | 49403.9769 |  | 7174 | 96226.3369 |  | 7174 | 158256.8958 |  | 7174 | 221967.4799 |  | 7174 | 281839.8001 |  | 7174 | 330479.3309 |  | 7174 | 368705.3287 |  | 7174 | 411352.8645
[13 empty] | Next iteration flow rate |  |  | 20809.9283 | Abs Value of | Flow this | 20176.1487 | Abs Value of | Flow this | 49898.0167 | Abs Value of | Flow this | 97188.6003 | Abs Value of | Flow this | 159839.4647 | Abs Value of | Flow this | 224187.1547 | Abs Value of | Flow this | 284658.1981 | Abs Value of | Flow this | 333784.1242 | Abs Value of | Flow this | 372392.382 | Abs Value of | Flow this | 415466.3932 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -72.1623 |  |  | -61.804 |  |  | -892.3192 |  |  | -3666.0316 |  |  | -10087.3056 |  |  | -19941.1994 |  |  | -32211.2644 |  |  | -44326.2678 |  |  | -55198.208 |  |  | -68730.6845
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.3481 |  |  | -0.29813 |  |  | -4.3044 |  |  | -17.6843 |  |  | -48.6594 |  |  | -96.1928 |  |  | -155.3814 |  |  | -213.822 |  |  | -266.2663 |  |  | -331.5446
[13 empty] | Delta P at this iteration flow rate |  |  | -122.1623 |  |  | -111.804 |  |  | -942.3192 |  |  | -3716.0316 |  |  | -10137.3056 |  |  | -19991.1994 |  |  | -32261.2644 |  |  | -44376.2678 |  |  | -55248.208 |  |  | -68780.6845
[13 empty] | Press drop ratio this iteration |  |  | 1.6929 |  |  | 1.809 |  |  | 1.056 |  |  | 1.0136 |  |  | 1.005 |  |  | 1.0025 |  |  | 1.0016 |  |  | 1.0011 |  |  | 1.0009 |  |  | 1.0007
[13 empty] | Expansion factor | 12 |  | 0.11833 |  |  | 0.058055 |  |  | 0.44188 |  |  | 0.45694 |  |  | 0.44683 |  |  | 0.4167 |  |  | 0.37704 |  |  | 0.31964 |  |  | 0.43788 |  |  | 0.1468
[13 empty] | C Non choked w/ reducers | 5 |  | 426.1029 |  |  | 951.6712 |  |  | 28.0935 |  |  | 13.2219 |  |  | 8.2132 |  |  | 6.3912 |  |  | 5.7457 |  |  | 6.131 |  |  | 4.5552 |  |  | 15.9979
[13 empty] | C Choked w/ reducers | 5 |  | 122.9384 |  |  | 139.2423 |  |  | 24.0828 |  |  | 11.5614 |  |  | 7.0879 |  |  | 5.2819 |  |  | 4.4401 |  |  | 4.1976 |  |  | 3.8834 |  |  | 5.6333
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 122.9384 |  |  | 139.2423 |  |  | 24.0828 |  |  | 11.5614 |  |  | 7.0879 |  |  | 5.2819 |  |  | 4.4401 |  |  | 4.1976 |  |  | 3.8834 |  |  | 5.6333
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 20809.9283 |  | 7174 | 20176.1487 |  | 7174 | 49898.0167 |  | 7174 | 97188.6003 |  | 7174 | 159839.4647 |  | 7174 | 224187.1547 |  | 7174 | 284658.1981 |  | 7174 | 333784.1242 |  | 7174 | 372392.382 |  | 7174 | 415466.3932
[13 empty] | Next iteration flow rate |  |  | 21226.1269 | Abs Value of | Flow this | 20377.9102 | Abs Value of | Flow this | 50396.9969 | Abs Value of | Flow this | 98160.4863 | Abs Value of | Flow this | 161437.8594 | Abs Value of | Flow this | 226429.0263 | Abs Value of | Flow this | 287504.7801 | Abs Value of | Flow this | 337121.9655 | Abs Value of | Flow this | 376116.3058 | Abs Value of | Flow this | 419621.0571 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -79.1387 |  |  | -65.0667 |  |  | -912.2754 |  |  | -3741.7393 |  |  | -10292.0809 |  |  | -20344.038 |  |  | -32860.7313 |  |  | -45219.2463 |  |  | -56309.7125 |  |  | -70114.1917
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.38175 |  |  | -0.31387 |  |  | -4.4007 |  |  | -18.0495 |  |  | -49.6472 |  |  | -98.136 |  |  | -158.5143 |  |  | -218.1296 |  |  | -271.628 |  |  | -338.2184
[13 empty] | Delta P at this iteration flow rate |  |  | -129.1387 |  |  | -115.0667 |  |  | -962.2754 |  |  | -3791.7393 |  |  | -10342.0809 |  |  | -20394.038 |  |  | -32910.7313 |  |  | -45269.2463 |  |  | -56359.7125 |  |  | -70164.1917
[13 empty] | Press drop ratio this iteration |  |  | 1.6318 |  |  | 1.7684 |  |  | 1.0548 |  |  | 1.0134 |  |  | 1.0049 |  |  | 1.0025 |  |  | 1.0015 |  |  | 1.0011 |  |  | 1.0009 |  |  | 1.0007
[13 empty] | Expansion factor | 12 |  | 0.15014 |  |  | 0.079178 |  |  | 0.44253 |  |  | 0.45709 |  |  | 0.44688 |  |  | 0.41673 |  |  | 0.37706 |  |  | 0.31965 |  |  | 0.43789 |  |  | 0.14682
[13 empty] | C Non choked w/ reducers | 5 |  | 318.1315 |  |  | 677.0525 |  |  | 27.7292 |  |  | 13.0815 |  |  | 8.1297 |  |  | 6.327 |  |  | 5.6883 |  |  | 6.0698 |  |  | 4.5099 |  |  | 15.8379
[13 empty] | C Choked w/ reducers | 5 |  | 114.3428 |  |  | 133.5826 |  |  | 23.7916 |  |  | 11.4408 |  |  | 7.0164 |  |  | 5.229 |  |  | 4.3959 |  |  | 4.1558 |  |  | 3.8448 |  |  | 5.5773
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 114.3428 |  |  | 133.5826 |  |  | 23.7916 |  |  | 11.4408 |  |  | 7.0164 |  |  | 5.229 |  |  | 4.3959 |  |  | 4.1558 |  |  | 3.8448 |  |  | 5.5773
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 21226.1269 |  | 7174 | 20377.9102 |  | 7174 | 50396.9969 |  | 7174 | 98160.4863 |  | 7174 | 161437.8594 |  | 7174 | 226429.0263 |  | 7174 | 287504.7801 |  | 7174 | 337121.9655 |  | 7174 | 376116.3058 |  | 7174 | 419621.0571
[13 empty] | Next iteration flow rate |  |  | 21650.6494 | Abs Value of | Flow this | 20581.6893 | Abs Value of | Flow this | 50900.9668 | Abs Value of | Flow this | 99142.0911 | Abs Value of | Flow this | 163052.238 | Abs Value of | Flow this | 228693.3165 | Abs Value of | Flow this | 290379.8279 | Abs Value of | Flow this | 340493.1851 | Abs Value of | Flow this | 379877.4689 | Abs Value of | Flow this | 423817.2677 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -86.3971 |  |  | -68.3951 |  |  | -932.6326 |  |  | -3818.9688 |  |  | -10500.9723 |  |  | -20754.9737 |  |  | -33523.2525 |  |  | -46130.1736 |  |  | -57443.5582 |  |  | -71525.5075
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.41676 |  |  | -0.32993 |  |  | -4.4989 |  |  | -18.422 |  |  | -50.6548 |  |  | -100.1183 |  |  | -161.7102 |  |  | -222.5237 |  |  | -277.0975 |  |  | -345.0263
[13 empty] | Delta P at this iteration flow rate |  |  | -136.3971 |  |  | -118.3951 |  |  | -982.6326 |  |  | -3868.9688 |  |  | -10550.9723 |  |  | -20804.9737 |  |  | -33573.2525 |  |  | -46180.1736 |  |  | -57493.5582 |  |  | -71575.5075
[13 empty] | Press drop ratio this iteration |  |  | 1.5787 |  |  | 1.731 |  |  | 1.0536 |  |  | 1.0131 |  |  | 1.0048 |  |  | 1.0024 |  |  | 1.0015 |  |  | 1.0011 |  |  | 1.0009 |  |  | 1.0007
[13 empty] | Expansion factor | 12 |  | 0.17778 |  |  | 0.09865 |  |  | 0.44316 |  |  | 0.45723 |  |  | 0.44694 |  |  | 0.41676 |  |  | 0.37708 |  |  | 0.31967 |  |  | 0.4379 |  |  | 0.14683
[13 empty] | C Non choked w/ reducers | 5 |  | 255.2003 |  |  | 527.7503 |  |  | 27.3716 |  |  | 12.9427 |  |  | 8.0471 |  |  | 6.2635 |  |  | 5.6314 |  |  | 6.0093 |  |  | 4.4651 |  |  | 15.6794
[13 empty] | C Choked w/ reducers | 5 |  | 106.8314 |  |  | 128.3528 |  |  | 23.505 |  |  | 11.3215 |  |  | 6.9456 |  |  | 5.1768 |  |  | 4.3521 |  |  | 4.1145 |  |  | 3.8066 |  |  | 5.522
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 106.8314 |  |  | 128.3528 |  |  | 23.505 |  |  | 11.3215 |  |  | 6.9456 |  |  | 5.1768 |  |  | 4.3521 |  |  | 4.1145 |  |  | 3.8066 |  |  | 5.522
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 21650.6494 |  | 7174 | 20581.6893 |  | 7174 | 50900.9668 |  | 7174 | 99142.0911 |  | 7174 | 163052.238 |  | 7174 | 228693.3165 |  | 7174 | 290379.8279 |  | 7174 | 340493.1851 |  | 7174 | 379877.4689 |  | 7174 | 423817.2677
[13 empty] | Next iteration flow rate |  |  | 22083.6624 | Abs Value of | Flow this | 20787.5062 | Abs Value of | Flow this | 51409.9765 | Abs Value of | Flow this | 100133.5121 | Abs Value of | Flow this | 164682.7604 | Abs Value of | Flow this | 230980.2497 | Abs Value of | Flow this | 293283.6262 | Abs Value of | Flow this | 343898.117 | Abs Value of | Flow this | 383676.2436 | Abs Value of | Flow this | 428055.4403 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -93.9486 |  |  | -71.7903 |  |  | -953.399 |  |  | -3897.7506 |  |  | -10714.0623 |  |  | -21174.1692 |  |  | -34199.0904 |  |  | -47059.4106 |  |  | -58600.1943 |  |  | -72965.1907
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.45319 |  |  | -0.3463 |  |  | -4.599 |  |  | -18.8021 |  |  | -51.6827 |  |  | -102.1404 |  |  | -164.9703 |  |  | -227.0062 |  |  | -282.6769 |  |  | -351.9711
[13 empty] | Delta P at this iteration flow rate |  |  | -143.9486 |  |  | -121.7903 |  |  | -1003.399 |  |  | -3947.7506 |  |  | -10764.0623 |  |  | -21224.1692 |  |  | -34249.0904 |  |  | -47109.4106 |  |  | -58650.1943 |  |  | -73015.1907
[13 empty] | Press drop ratio this iteration |  |  | 1.5322 |  |  | 1.6965 |  |  | 1.0524 |  |  | 1.0128 |  |  | 1.0047 |  |  | 1.0024 |  |  | 1.0015 |  |  | 1.0011 |  |  | 1.0009 |  |  | 1.0007
[13 empty] | Expansion factor | 12 |  | 0.20201 |  |  | 0.11665 |  |  | 0.44377 |  |  | 0.45737 |  |  | 0.44699 |  |  | 0.41678 |  |  | 0.37709 |  |  | 0.31968 |  |  | 0.43791 |  |  | 0.14684
[13 empty] | C Non choked w/ reducers | 5 |  | 213.8464 |  |  | 433.8025 |  |  | 27.0205 |  |  | 12.8056 |  |  | 7.9654 |  |  | 6.2006 |  |  | 5.5751 |  |  | 5.9493 |  |  | 4.4206 |  |  | 15.5226
[13 empty] | C Choked w/ reducers | 5 |  | 100.2092 |  |  | 123.5053 |  |  | 23.2229 |  |  | 11.2036 |  |  | 6.8755 |  |  | 5.125 |  |  | 4.3087 |  |  | 4.0736 |  |  | 3.7688 |  |  | 5.4671
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 100.2092 |  |  | 123.5053 |  |  | 23.2229 |  |  | 11.2036 |  |  | 6.8755 |  |  | 5.125 |  |  | 4.3087 |  |  | 4.0736 |  |  | 3.7688 |  |  | 5.4671
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 22083.6624 |  | 7174 | 20787.5062 |  | 7174 | 51409.9765 |  | 7174 | 100133.5121 |  | 7174 | 164682.7604 |  | 7174 | 230980.2497 |  | 7174 | 293283.6262 |  | 7174 | 343898.117 |  | 7174 | 383676.2436 |  | 7174 | 428055.4403
[13 empty] | Next iteration flow rate |  |  | 22525.3357 | Abs Value of | Flow this | 20995.3812 | Abs Value of | Flow this | 51924.0763 | Abs Value of | Flow this | 101134.8472 | Abs Value of | Flow this | 166329.588 | Abs Value of | Flow this | 233290.0522 | Abs Value of | Flow this | 296216.4624 | Abs Value of | Flow this | 347337.0981 | Abs Value of | Flow this | 387513.006 | Abs Value of | Flow this | 432335.9947 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -101.8053 |  |  | -75.2538 |  |  | -974.5829 |  |  | -3978.1159 |  |  | -10931.4355 |  |  | -21601.7905 |  |  | -34888.5126 |  |  | -48007.3253 |  |  | -59780.0787 |  |  | -74433.8116
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.49109 |  |  | -0.36301 |  |  | -4.7012 |  |  | -19.1897 |  |  | -52.7313 |  |  | -104.2032 |  |  | -168.296 |  |  | -231.5788 |  |  | -288.3685 |  |  | -359.0555
[13 empty] | Delta P at this iteration flow rate |  |  | -151.8053 |  |  | -125.2538 |  |  | -1024.5829 |  |  | -4028.1159 |  |  | -10981.4355 |  |  | -21651.7905 |  |  | -34938.5126 |  |  | -48057.3253 |  |  | -59830.0787 |  |  | -74483.8116
[13 empty] | Press drop ratio this iteration |  |  | 1.4911 |  |  | 1.6644 |  |  | 1.0513 |  |  | 1.0126 |  |  | 1.0046 |  |  | 1.0023 |  |  | 1.0014 |  |  | 1.001 |  |  | 1.0008 |  |  | 1.0007
[13 empty] | Expansion factor | 12 |  | 0.2234 |  |  | 0.13334 |  |  | 0.44438 |  |  | 0.45751 |  |  | 0.44704 |  |  | 0.41681 |  |  | 0.37711 |  |  | 0.3197 |  |  | 0.43792 |  |  | 0.14685
[13 empty] | C Non choked w/ reducers | 5 |  | 184.5061 |  |  | 369.1612 |  |  | 26.6758 |  |  | 12.6702 |  |  | 7.8845 |  |  | 6.1384 |  |  | 5.5194 |  |  | 5.89 |  |  | 4.3767 |  |  | 15.3674
[13 empty] | C Choked w/ reducers | 5 |  | 94.3253 |  |  | 118.9993 |  |  | 22.9453 |  |  | 11.087 |  |  | 6.8062 |  |  | 5.0738 |  |  | 4.2658 |  |  | 4.0331 |  |  | 3.7314 |  |  | 5.4129
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 94.3253 |  |  | 118.9993 |  |  | 22.9453 |  |  | 11.087 |  |  | 6.8062 |  |  | 5.0738 |  |  | 4.2658 |  |  | 4.0331 |  |  | 3.7314 |  |  | 5.4129
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 22525.3357 |  | 7174 | 20995.3812 |  | 7174 | 51924.0763 |  | 7174 | 101134.8472 |  | 7174 | 166329.588 |  | 7174 | 233290.0522 |  | 7174 | 296216.4624 |  | 7174 | 347337.0981 |  | 7174 | 387513.006 |  | 7174 | 432335.9947
[13 empty] | Next iteration flow rate |  |  | 22975.8424 | Abs Value of | Flow this | 21205.335 | Abs Value of | Flow this | 52443.317 | Abs Value of | Flow this | 102146.1957 | Abs Value of | Flow this | 167992.8839 | Abs Value of | Flow this | 235622.9527 | Abs Value of | Flow this | 299178.6271 | Abs Value of | Flow this | 350810.4691 | Abs Value of | Flow this | 391388.1361 | Abs Value of | Flow this | 436659.3547 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -109.9793 |  |  | -78.7869 |  |  | -996.1925 |  |  | -4060.0965 |  |  | -11153.1779 |  |  | -22038.007 |  |  | -35591.7922 |  |  | -48974.293 |  |  | -60983.6788 |  |  | -75931.9517
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.53052 |  |  | -0.38005 |  |  | -4.8055 |  |  | -19.5852 |  |  | -53.8009 |  |  | -106.3074 |  |  | -171.6885 |  |  | -236.2433 |  |  | -294.1744 |  |  | -366.2822
[13 empty] | Delta P at this iteration flow rate |  |  | -159.9793 |  |  | -128.7869 |  |  | -1046.1925 |  |  | -4110.0965 |  |  | -11203.1779 |  |  | -22088.007 |  |  | -35641.7922 |  |  | -49024.293 |  |  | -61033.6788 |  |  | -75981.9517
[13 empty] | Press drop ratio this iteration |  |  | 1.4546 |  |  | 1.6346 |  |  | 1.0502 |  |  | 1.0123 |  |  | 1.0045 |  |  | 1.0023 |  |  | 1.0014 |  |  | 1.001 |  |  | 1.0008 |  |  | 1.0007
[13 empty] | Expansion factor | 12 |  | 0.24241 |  |  | 0.14886 |  |  | 0.44497 |  |  | 0.45765 |  |  | 0.44709 |  |  | 0.41684 |  |  | 0.37713 |  |  | 0.31971 |  |  | 0.43793 |  |  | 0.14686
[13 empty] | C Non choked w/ reducers | 5 |  | 162.5484 |  |  | 321.9101 |  |  | 26.3372 |  |  | 12.5363 |  |  | 7.8045 |  |  | 6.0768 |  |  | 5.4643 |  |  | 5.8312 |  |  | 4.3331 |  |  | 15.2138
[13 empty] | C Choked w/ reducers | 5 |  | 89.061 |  |  | 114.7996 |  |  | 22.6721 |  |  | 10.9718 |  |  | 6.7376 |  |  | 5.0231 |  |  | 4.2234 |  |  | 3.993 |  |  | 3.6943 |  |  | 5.3591
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 89.061 |  |  | 114.7996 |  |  | 22.6721 |  |  | 10.9718 |  |  | 6.7376 |  |  | 5.0231 |  |  | 4.2234 |  |  | 3.993 |  |  | 3.6943 |  |  | 5.3591
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 22975.8424 |  | 7174 | 21205.335 |  | 7174 | 52443.317 |  | 7174 | 102146.1957 |  | 7174 | 167992.8839 |  | 7174 | 235622.9527 |  | 7174 | 299178.6271 |  | 7174 | 350810.4691 |  | 7174 | 391388.1361 |  | 7174 | 436659.3547
[13 empty] | Next iteration flow rate |  |  | 23435.3592 | Abs Value of | Flow this | 21417.3884 | Abs Value of | Flow this | 52967.7502 | Abs Value of | Flow this | 103167.6576 | Abs Value of | Flow this | 169672.8127 | Abs Value of | Flow this | 237979.1823 | Abs Value of | Flow this | 302170.4133 | Abs Value of | Flow this | 354318.5738 | Abs Value of | Flow this | 395302.0174 | Abs Value of | Flow this | 441025.9482 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -118.4836 |  |  | -82.3911 |  |  | -1018.2365 |  |  | -4143.725 |  |  | -11379.3772 |  |  | -22482.9914 |  |  | -36309.2078 |  |  | -49960.6968 |  |  | -62211.4712 |  |  | -77460.2044
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.57154 |  |  | -0.39744 |  |  | -4.9118 |  |  | -19.9886 |  |  | -54.8921 |  |  | -108.4539 |  |  | -175.1492 |  |  | -241.0015 |  |  | -300.0971 |  |  | -373.6542
[13 empty] | Delta P at this iteration flow rate |  |  | -168.4836 |  |  | -132.3911 |  |  | -1068.2365 |  |  | -4193.725 |  |  | -11429.3772 |  |  | -22532.9914 |  |  | -36359.2078 |  |  | -50010.6968 |  |  | -62261.4712 |  |  | -77510.2044
[13 empty] | Press drop ratio this iteration |  |  | 1.422 |  |  | 1.6069 |  |  | 1.0491 |  |  | 1.0121 |  |  | 1.0044 |  |  | 1.0022 |  |  | 1.0014 |  |  | 1.001 |  |  | 1.0008 |  |  | 1.0006
[13 empty] | Expansion factor | 12 |  | 0.25941 |  |  | 0.16331 |  |  | 0.44554 |  |  | 0.45778 |  |  | 0.44714 |  |  | 0.41686 |  |  | 0.37715 |  |  | 0.31972 |  |  | 0.43794 |  |  | 0.14687
[13 empty] | C Non choked w/ reducers | 5 |  | 145.4571 |  |  | 285.8252 |  |  | 26.0046 |  |  | 12.4041 |  |  | 7.7254 |  |  | 6.0159 |  |  | 5.4097 |  |  | 5.773 |  |  | 4.29 |  |  | 15.0617
[13 empty] | C Choked w/ reducers | 5 |  | 84.3219 |  |  | 110.8755 |  |  | 22.403 |  |  | 10.8579 |  |  | 6.6697 |  |  | 4.9729 |  |  | 4.1813 |  |  | 3.9533 |  |  | 3.6576 |  |  | 5.3059
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 84.3219 |  |  | 110.8755 |  |  | 22.403 |  |  | 10.8579 |  |  | 6.6697 |  |  | 4.9729 |  |  | 4.1813 |  |  | 3.9533 |  |  | 3.6576 |  |  | 5.3059
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 23435.3592 |  | 7174 | 21417.3884 |  | 7174 | 52967.7502 |  | 7174 | 103167.6576 |  | 7174 | 169672.8127 |  | 7174 | 237979.1823 |  | 7174 | 302170.4133 |  | 7174 | 354318.5738 |  | 7174 | 395302.0174 |  | 7174 | 441025.9482
[13 empty] | Next iteration flow rate |  |  | 23904.0664 | Abs Value of | Flow this | 21631.5623 | Abs Value of | Flow this | 53497.4277 | Abs Value of | Flow this | 104199.3342 | Abs Value of | Flow this | 171369.5408 | Abs Value of | Flow this | 240358.9741 | Abs Value of | Flow this | 305192.1175 | Abs Value of | Flow this | 357861.7596 | Abs Value of | Flow this | 399255.0376 | Abs Value of | Flow this | 445436.2077 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -127.3315 |  |  | -86.0676 |  |  | -1040.7235 |  |  | -4229.0343 |  |  | -11610.1232 |  |  | -22936.9201 |  |  | -37041.0433 |  |  | -50966.9273 |  |  | -63463.9423 |  |  | -79019.175
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.61422 |  |  | -0.41517 |  |  | -5.0203 |  |  | -20.4001 |  |  | -56.0052 |  |  | -110.6436 |  |  | -178.6794 |  |  | -245.8554 |  |  | -306.1388 |  |  | -381.1744
[13 empty] | Delta P at this iteration flow rate |  |  | -177.3315 |  |  | -136.0676 |  |  | -1090.7235 |  |  | -4279.0343 |  |  | -11660.1232 |  |  | -22986.9201 |  |  | -37091.0433 |  |  | -51016.9273 |  |  | -63513.9423 |  |  | -79069.175
[13 empty] | Press drop ratio this iteration |  |  | 1.3927 |  |  | 1.5809 |  |  | 1.048 |  |  | 1.0118 |  |  | 1.0043 |  |  | 1.0022 |  |  | 1.0013 |  |  | 1.001 |  |  | 1.0008 |  |  | 1.0006
[13 empty] | Expansion factor | 12 |  | 0.27468 |  |  | 0.17681 |  |  | 0.4461 |  |  | 0.45791 |  |  | 0.44719 |  |  | 0.41689 |  |  | 0.37716 |  |  | 0.31974 |  |  | 0.43795 |  |  | 0.14689
[13 empty] | C Non choked w/ reducers | 5 |  | 131.7463 |  |  | 257.3385 |  |  | 25.6778 |  |  | 12.2734 |  |  | 7.6471 |  |  | 5.9555 |  |  | 5.3557 |  |  | 5.7155 |  |  | 4.2474 |  |  | 14.9112
[13 empty] | C Choked w/ reducers | 5 |  | 80.0319 |  |  | 107.2006 |  |  | 22.1382 |  |  | 10.7452 |  |  | 6.6025 |  |  | 4.9233 |  |  | 4.1397 |  |  | 3.914 |  |  | 3.6213 |  |  | 5.2533
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 80.0319 |  |  | 107.2006 |  |  | 22.1382 |  |  | 10.7452 |  |  | 6.6025 |  |  | 4.9233 |  |  | 4.1397 |  |  | 3.914 |  |  | 3.6213 |  |  | 5.2533
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 23904.0664 |  | 7174 | 21631.5623 |  | 7174 | 53497.4277 |  | 7174 | 104199.3342 |  | 7174 | 171369.5408 |  | 7174 | 240358.9741 |  | 7174 | 305192.1175 |  | 7174 | 357861.7596 |  | 7174 | 399255.0376 |  | 7174 | 445436.2077
[13 empty] | Next iteration flow rate |  |  | 24382.1477 | Abs Value of | Flow this | 21847.8779 | Abs Value of | Flow this | 54032.402 | Abs Value of | Flow this | 105241.3275 | Abs Value of | Flow this | 173083.2362 | Abs Value of | Flow this | 242762.5638 | Abs Value of | Flow this | 308244.0386 | Abs Value of | Flow this | 361440.3771 | Abs Value of | Flow this | 403247.588 | Abs Value of | Flow this | 449890.5698 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -136.5368 |  |  | -89.8181 |  |  | -1063.6626 |  |  | -4316.0584 |  |  | -11845.5072 |  |  | -23399.9727 |  |  | -37787.5888 |  |  | -51993.3831 |  |  | -64741.588 |  |  | -80609.481
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.65863 |  |  | -0.43327 |  |  | -5.1309 |  |  | -20.8199 |  |  | -57.1406 |  |  | -112.8773 |  |  | -182.2806 |  |  | -250.8068 |  |  | -312.3019 |  |  | -388.8458
[13 empty] | Delta P at this iteration flow rate |  |  | -186.5368 |  |  | -139.8181 |  |  | -1113.6626 |  |  | -4366.0584 |  |  | -11895.5072 |  |  | -23449.9727 |  |  | -37837.5888 |  |  | -52043.3831 |  |  | -64791.588 |  |  | -80659.481
[13 empty] | Press drop ratio this iteration |  |  | 1.3662 |  |  | 1.5567 |  |  | 1.047 |  |  | 1.0116 |  |  | 1.0042 |  |  | 1.0021 |  |  | 1.0013 |  |  | 1.001 |  |  | 1.0008 |  |  | 1.0006
[13 empty] | Expansion factor | 12 |  | 0.28847 |  |  | 0.18944 |  |  | 0.44665 |  |  | 0.45804 |  |  | 0.44723 |  |  | 0.41691 |  |  | 0.37718 |  |  | 0.31975 |  |  | 0.43795 |  |  | 0.1469
[13 empty] | C Non choked w/ reducers | 5 |  | 120.4818 |  |  | 234.2571 |  |  | 25.3567 |  |  | 12.1442 |  |  | 7.5696 |  |  | 5.8958 |  |  | 5.3022 |  |  | 5.6585 |  |  | 4.2051 |  |  | 14.7622
[13 empty] | C Choked w/ reducers | 5 |  | 76.1289 |  |  | 103.7516 |  |  | 21.8773 |  |  | 10.6339 |  |  | 6.536 |  |  | 4.8741 |  |  | 4.0985 |  |  | 3.8751 |  |  | 3.5853 |  |  | 5.2011
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 76.1289 |  |  | 103.7516 |  |  | 21.8773 |  |  | 10.6339 |  |  | 6.536 |  |  | 4.8741 |  |  | 4.0985 |  |  | 3.8751 |  |  | 3.5853 |  |  | 5.2011
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 24382.1477 |  | 7174 | 21847.8779 |  | 7174 | 54032.402 |  | 7174 | 105241.3275 |  | 7174 | 173083.2362 |  | 7174 | 242762.5638 |  | 7174 | 308244.0386 |  | 7174 | 361440.3771 |  | 7174 | 403247.588 |  | 7174 | 449890.5698
[13 empty] | Next iteration flow rate |  |  | 24869.7907 | Abs Value of | Flow this | 22066.3567 | Abs Value of | Flow this | 54572.726 | Abs Value of | Flow this | 106293.7408 | Abs Value of | Flow this | 174814.0686 | Abs Value of | Flow this | 245190.1895 | Abs Value of | Flow this | 311326.479 | Abs Value of | Flow this | 365054.7809 | Abs Value of | Flow this | 407280.0639 | Abs Value of | Flow this | 454389.4755 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -146.114 |  |  | -93.644 |  |  | -1087.0627 |  |  | -4404.8317 |  |  | -12085.6224 |  |  | -23872.3326 |  |  | -38549.1399 |  |  | -53040.4706 |  |  | -66044.9145 |  |  | -82231.752
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.70483 |  |  | -0.45172 |  |  | -5.2438 |  |  | -21.2481 |  |  | -58.2989 |  |  | -115.1559 |  |  | -185.9542 |  |  | -255.8578 |  |  | -318.5889 |  |  | -396.6713
[13 empty] | Delta P at this iteration flow rate |  |  | -196.114 |  |  | -143.644 |  |  | -1137.0627 |  |  | -4454.8317 |  |  | -12135.6224 |  |  | -23922.3326 |  |  | -38599.1399 |  |  | -53090.4706 |  |  | -66094.9145 |  |  | -82281.752
[13 empty] | Press drop ratio this iteration |  |  | 1.3422 |  |  | 1.5339 |  |  | 1.046 |  |  | 1.0114 |  |  | 1.0041 |  |  | 1.0021 |  |  | 1.0013 |  |  | 1.0009 |  |  | 1.0008 |  |  | 1.0006
[13 empty] | Expansion factor | 12 |  | 0.30097 |  |  | 0.20128 |  |  | 0.44718 |  |  | 0.45816 |  |  | 0.44728 |  |  | 0.41694 |  |  | 0.3772 |  |  | 0.31976 |  |  | 0.43796 |  |  | 0.14691
[13 empty] | C Non choked w/ reducers | 5 |  | 111.0463 |  |  | 215.1594 |  |  | 25.0412 |  |  | 12.0166 |  |  | 7.4929 |  |  | 5.8367 |  |  | 5.2493 |  |  | 5.6021 |  |  | 4.1633 |  |  | 14.6148
[13 empty] | C Choked w/ reducers | 5 |  | 72.5617 |  |  | 100.5079 |  |  | 21.6205 |  |  | 10.5237 |  |  | 6.4702 |  |  | 4.8254 |  |  | 4.0577 |  |  | 3.8366 |  |  | 3.5497 |  |  | 5.1495
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 72.5617 |  |  | 100.5079 |  |  | 21.6205 |  |  | 10.5237 |  |  | 6.4702 |  |  | 4.8254 |  |  | 4.0577 |  |  | 3.8366 |  |  | 3.5497 |  |  | 5.1495
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 24869.7907 |  | 7174 | 22066.3567 |  | 7174 | 54572.726 |  | 7174 | 106293.7408 |  | 7174 | 174814.0686 |  | 7174 | 245190.1895 |  | 7174 | 311326.479 |  | 7174 | 365054.7809 |  | 7174 | 407280.0639 |  | 7174 | 454389.4755
[13 empty] | Next iteration flow rate |  |  | 25367.1865 | Abs Value of | Flow this | 22287.0202 | Abs Value of | Flow this | 55118.4533 | Abs Value of | Flow this | 107356.6782 | Abs Value of | Flow this | 176562.2093 | Abs Value of | Flow this | 247642.0914 | Abs Value of | Flow this | 314439.7438 | Abs Value of | Flow this | 368705.3287 | Abs Value of | Flow this | 411352.8645 | Abs Value of | Flow this | 458933.3702 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -156.0781 |  |  | -97.5467 |  |  | -1110.9332 |  |  | -4495.3894 |  |  | -12330.5639 |  |  | -24354.187 |  |  | -39325.9981 |  |  | -54108.6046 |  |  | -67374.4378 |  |  | -83886.6308
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.75289 |  |  | -0.47055 |  |  | -5.3589 |  |  | -21.685 |  |  | -59.4804 |  |  | -117.4803 |  |  | -189.7016 |  |  | -261.0103 |  |  | -325.0023 |  |  | -404.6542
[13 empty] | Delta P at this iteration flow rate |  |  | -206.0781 |  |  | -147.5467 |  |  | -1160.9332 |  |  | -4545.3894 |  |  | -12380.5639 |  |  | -24404.187 |  |  | -39375.9981 |  |  | -54158.6046 |  |  | -67424.4378 |  |  | -83936.6308
[13 empty] | Press drop ratio this iteration |  |  | 1.3204 |  |  | 1.5126 |  |  | 1.045 |  |  | 1.0111 |  |  | 1.0041 |  |  | 1.0021 |  |  | 1.0013 |  |  | 1.0009 |  |  | 1.0007 |  |  | 1.0006
[13 empty] | Expansion factor | 12 |  | 0.31235 |  |  | 0.21241 |  |  | 0.44771 |  |  | 0.45829 |  |  | 0.44732 |  |  | 0.41696 |  |  | 0.37721 |  |  | 0.31978 |  |  | 0.43797 |  |  | 0.14692
[13 empty] | C Non choked w/ reducers | 5 |  | 103.0155 |  |  | 199.0829 |  |  | 24.7309 |  |  | 11.8904 |  |  | 7.4171 |  |  | 5.7783 |  |  | 5.1969 |  |  | 5.5462 |  |  | 4.1219 |  |  | 14.4688
[13 empty] | C Choked w/ reducers | 5 |  | 69.2879 |  |  | 97.4515 |  |  | 21.3675 |  |  | 10.4149 |  |  | 6.4051 |  |  | 4.7772 |  |  | 4.0173 |  |  | 3.7984 |  |  | 3.5145 |  |  | 5.0984
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 69.2879 |  |  | 97.4515 |  |  | 21.3675 |  |  | 10.4149 |  |  | 6.4051 |  |  | 4.7772 |  |  | 4.0173 |  |  | 3.7984 |  |  | 3.5145 |  |  | 5.0984
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 25367.1865 |  | 7174 | 22287.0202 |  | 7174 | 55118.4533 |  | 7174 | 107356.6782 |  | 7174 | 176562.2093 |  | 7174 | 247642.0914 |  | 7174 | 314439.7438 |  | 7174 | 368705.3287 |  | 7174 | 411352.8645 |  | 7174 | 458933.3702
[13 empty] | Next iteration flow rate |  |  | 25874.5302 | Abs Value of | Flow this | 22509.8904 | Abs Value of | Flow this | 55669.6378 | Abs Value of | Flow this | 108430.245 | Abs Value of | Flow this | 178327.8314 | Abs Value of | Flow this | 250118.5123 | Abs Value of | Flow this | 317584.1413 | Abs Value of | Flow this | 372392.382 | Abs Value of | Flow this | 415466.3932 | Abs Value of | Flow this | 463522.7039 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -166.4448 |  |  | -101.5279 |  |  | -1135.2834 |  |  | -4587.7672 |  |  | -12580.4288 |  |  | -24845.7267 |  |  | -40118.4711 |  |  | -55198.208 |  |  | -68730.6845 |  |  | -85574.7725
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.8029 |  |  | -0.48975 |  |  | -5.4764 |  |  | -22.1306 |  |  | -60.6857 |  |  | -119.8514 |  |  | -193.5244 |  |  | -266.2663 |  |  | -331.5446 |  |  | -412.7975
[13 empty] | Delta P at this iteration flow rate |  |  | -216.4448 |  |  | -151.5279 |  |  | -1185.2834 |  |  | -4637.7672 |  |  | -12630.4288 |  |  | -24895.7267 |  |  | -40168.4711 |  |  | -55248.208 |  |  | -68780.6845 |  |  | -85624.7725
[13 empty] | Press drop ratio this iteration |  |  | 1.3004 |  |  | 1.4925 |  |  | 1.044 |  |  | 1.0109 |  |  | 1.004 |  |  | 1.002 |  |  | 1.0012 |  |  | 1.0009 |  |  | 1.0007 |  |  | 1.0006
[13 empty] | Expansion factor | 12 |  | 0.32274 |  |  | 0.22287 |  |  | 0.44822 |  |  | 0.45841 |  |  | 0.44737 |  |  | 0.41699 |  |  | 0.37723 |  |  | 0.31979 |  |  | 0.43798 |  |  | 0.14693
[13 empty] | C Non choked w/ reducers | 5 |  | 96.0876 |  |  | 185.3529 |  |  | 24.426 |  |  | 11.7657 |  |  | 7.342 |  |  | 5.7204 |  |  | 5.145 |  |  | 5.491 |  |  | 4.0809 |  |  | 14.3243
[13 empty] | C Choked w/ reducers | 5 |  | 66.2719 |  |  | 94.5665 |  |  | 21.1183 |  |  | 10.3072 |  |  | 6.3406 |  |  | 4.7296 |  |  | 3.9773 |  |  | 3.7607 |  |  | 3.4796 |  |  | 5.0478
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 66.2719 |  |  | 94.5665 |  |  | 21.1183 |  |  | 10.3072 |  |  | 6.3406 |  |  | 4.7296 |  |  | 3.9773 |  |  | 3.7607 |  |  | 3.4796 |  |  | 5.0478
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 25874.5302 |  | 7174 | 22509.8904 |  | 7174 | 55669.6378 |  | 7174 | 108430.245 |  | 7174 | 178327.8314 |  | 7174 | 250118.5123 |  | 7174 | 317584.1413 |  | 7174 | 372392.382 |  | 7174 | 415466.3932 |  | 7174 | 463522.7039
[13 empty] | Next iteration flow rate |  |  | 26392.0208 | Abs Value of | Flow this | 22734.9894 | Abs Value of | Flow this | 56226.3342 | Abs Value of | Flow this | 109514.5474 | Abs Value of | Flow this | 180111.1097 | Abs Value of | Flow this | 252619.6974 | Abs Value of | Flow this | 320759.9827 | Abs Value of | Flow this | 376116.3058 | Abs Value of | Flow this | 419621.0571 | Abs Value of | Flow this | 468157.931 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -177.2303 |  |  | -105.5891 |  |  | -1160.1231 |  |  | -4682.0018 |  |  | -12835.3159 |  |  | -25347.1463 |  |  | -40926.8729 |  |  | -56309.7125 |  |  | -70114.1917 |  |  | -87296.846
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.85493 |  |  | -0.50934 |  |  | -5.5962 |  |  | -22.5851 |  |  | -61.9153 |  |  | -122.2701 |  |  | -197.4239 |  |  | -271.628 |  |  | -338.2184 |  |  | -421.1044
[13 empty] | Delta P at this iteration flow rate |  |  | -227.2303 |  |  | -155.5891 |  |  | -1210.1231 |  |  | -4732.0018 |  |  | -12885.3159 |  |  | -25397.1463 |  |  | -40976.8729 |  |  | -56359.7125 |  |  | -70164.1917 |  |  | -87346.846
[13 empty] | Press drop ratio this iteration |  |  | 1.2821 |  |  | 1.4735 |  |  | 1.0431 |  |  | 1.0107 |  |  | 1.0039 |  |  | 1.002 |  |  | 1.0012 |  |  | 1.0009 |  |  | 1.0007 |  |  | 1.0006
[13 empty] | Expansion factor | 12 |  | 0.33226 |  |  | 0.23274 |  |  | 0.44871 |  |  | 0.45852 |  |  | 0.44741 |  |  | 0.41701 |  |  | 0.37724 |  |  | 0.3198 |  |  | 0.43799 |  |  | 0.14694
[13 empty] | C Non choked w/ reducers | 5 |  | 90.0425 |  |  | 173.482 |  |  | 24.1261 |  |  | 11.6425 |  |  | 7.2678 |  |  | 5.6631 |  |  | 5.0937 |  |  | 5.4362 |  |  | 4.0404 |  |  | 14.1813
[13 empty] | C Choked w/ reducers | 5 |  | 63.4836 |  |  | 91.8385 |  |  | 20.8728 |  |  | 10.2007 |  |  | 6.2769 |  |  | 4.6824 |  |  | 3.9378 |  |  | 3.7233 |  |  | 3.445 |  |  | 4.9977
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 63.4836 |  |  | 91.8385 |  |  | 20.8728 |  |  | 10.2007 |  |  | 6.2769 |  |  | 4.6824 |  |  | 3.9378 |  |  | 3.7233 |  |  | 3.445 |  |  | 4.9977
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 26392.0208 |  | 7174 | 22734.9894 |  | 7174 | 56226.3342 |  | 7174 | 109514.5474 |  | 7174 | 180111.1097 |  | 7174 | 252619.6974 |  | 7174 | 320759.9827 |  | 7174 | 376116.3058 |  | 7174 | 419621.0571 |  | 7174 | 468157.931
[13 empty] | Next iteration flow rate |  |  | 26919.8613 | Abs Value of | Flow this | 22962.3392 | Abs Value of | Flow this | 56788.5975 | Abs Value of | Flow this | 110609.6929 | Abs Value of | Flow this | 181912.2208 | Abs Value of | Flow this | 255145.8944 | Abs Value of | Flow this | 323967.5825 | Abs Value of | Flow this | 379877.4689 | Abs Value of | Flow this | 423817.2677 | Abs Value of | Flow this | 472839.5103 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -188.4515 |  |  | -109.732 |  |  | -1185.4621 |  |  | -4778.1306 |  |  | -13095.3263 |  |  | -25858.6444 |  |  | -41751.5236 |  |  | -57443.5582 |  |  | -71525.5075 |  |  | -89053.5331
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.90906 |  |  | -0.52933 |  |  | -5.7185 |  |  | -23.0489 |  |  | -63.1695 |  |  | -124.7375 |  |  | -201.4019 |  |  | -277.0975 |  |  | -345.0263 |  |  | -429.5784
[13 empty] | Delta P at this iteration flow rate |  |  | -238.4515 |  |  | -159.732 |  |  | -1235.4621 |  |  | -4828.1306 |  |  | -13145.3263 |  |  | -25908.6444 |  |  | -41801.5236 |  |  | -57493.5582 |  |  | -71575.5075 |  |  | -89103.5331
[13 empty] | Press drop ratio this iteration |  |  | 1.2653 |  |  | 1.4557 |  |  | 1.0422 |  |  | 1.0105 |  |  | 1.0038 |  |  | 1.0019 |  |  | 1.0012 |  |  | 1.0009 |  |  | 1.0007 |  |  | 1.0006
[13 empty] | Expansion factor | 12 |  | 0.34101 |  |  | 0.24204 |  |  | 0.4492 |  |  | 0.45864 |  |  | 0.44745 |  |  | 0.41703 |  |  | 0.37726 |  |  | 0.31981 |  |  | 0.438 |  |  | 0.14695
[13 empty] | C Non choked w/ reducers | 5 |  | 84.7154 |  |  | 163.1098 |  |  | 23.8312 |  |  | 11.5207 |  |  | 7.1943 |  |  | 5.6064 |  |  | 5.0429 |  |  | 5.3821 |  |  | 4.0002 |  |  | 14.0397
[13 empty] | C Choked w/ reducers | 5 |  | 60.8976 |  |  | 89.2549 |  |  | 20.6309 |  |  | 10.0955 |  |  | 6.2138 |  |  | 4.6356 |  |  | 3.8986 |  |  | 3.6863 |  |  | 3.4108 |  |  | 4.9481
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 60.8976 |  |  | 89.2549 |  |  | 20.6309 |  |  | 10.0955 |  |  | 6.2138 |  |  | 4.6356 |  |  | 3.8986 |  |  | 3.6863 |  |  | 3.4108 |  |  | 4.9481
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 26919.8613 |  | 7174 | 22962.3392 |  | 7174 | 56788.5975 |  | 7174 | 110609.6929 |  | 7174 | 181912.2208 |  | 7174 | 255145.8944 |  | 7174 | 323967.5825 |  | 7174 | 379877.4689 |  | 7174 | 423817.2677 |  | 7174 | 472839.5103
[13 empty] | Next iteration flow rate |  |  | 27458.2585 | Abs Value of | Flow this | 23191.9626 | Abs Value of | Flow this | 57356.4835 | Abs Value of | Flow this | 111715.7898 | Abs Value of | Flow this | 183731.343 | Abs Value of | Flow this | 257697.3533 | Abs Value of | Flow this | 327207.2583 | Abs Value of | Flow this | 383676.2436 | Abs Value of | Flow this | 428055.4403 | Abs Value of | Flow this | 477567.9054 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -200.1261 |  |  | -113.9581 |  |  | -1211.3104 |  |  | -4876.1915 |  |  | -13360.5628 |  |  | -26380.4237 |  |  | -42592.7497 |  |  | -58600.1943 |  |  | -72965.1907 |  |  | -90845.5296
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -0.96537 |  |  | -0.54971 |  |  | -5.8431 |  |  | -23.5219 |  |  | -64.449 |  |  | -127.2545 |  |  | -205.4598 |  |  | -282.6769 |  |  | -351.9711 |  |  | -438.2227
[13 empty] | Delta P at this iteration flow rate |  |  | -250.1261 |  |  | -163.9581 |  |  | -1261.3104 |  |  | -4926.1915 |  |  | -13410.5628 |  |  | -26430.4237 |  |  | -42642.7497 |  |  | -58650.1943 |  |  | -73015.1907 |  |  | -90895.5296
[13 empty] | Press drop ratio this iteration |  |  | 1.2498 |  |  | 1.4388 |  |  | 1.0413 |  |  | 1.0103 |  |  | 1.0037 |  |  | 1.0019 |  |  | 1.0012 |  |  | 1.0009 |  |  | 1.0007 |  |  | 1.0006
[13 empty] | Expansion factor | 12 |  | 0.34907 |  |  | 0.25084 |  |  | 0.44968 |  |  | 0.45875 |  |  | 0.4475 |  |  | 0.41706 |  |  | 0.37727 |  |  | 0.31983 |  |  | 0.438 |  |  | 0.14696
[13 empty] | C Non choked w/ reducers | 5 |  | 79.9805 |  |  | 153.9635 |  |  | 23.5411 |  |  | 11.4003 |  |  | 7.1216 |  |  | 5.5503 |  |  | 4.9926 |  |  | 5.3285 |  |  | 3.9605 |  |  | 13.8996
[13 empty] | C Choked w/ reducers | 5 |  | 58.492 |  |  | 86.8044 |  |  | 20.3925 |  |  | 9.9914 |  |  | 6.1513 |  |  | 4.5894 |  |  | 3.8598 |  |  | 3.6497 |  |  | 3.377 |  |  | 4.899
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 58.492 |  |  | 86.8044 |  |  | 20.3925 |  |  | 9.9914 |  |  | 6.1513 |  |  | 4.5894 |  |  | 3.8598 |  |  | 3.6497 |  |  | 3.377 |  |  | 4.899
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 27458.2585 |  | 7174 | 23191.9626 |  | 7174 | 57356.4835 |  | 7174 | 111715.7898 |  | 7174 | 183731.343 |  | 7174 | 257697.3533 |  | 7174 | 327207.2583 |  | 7174 | 383676.2436 |  | 7174 | 428055.4403 |  | 7174 | 477567.9054
[13 empty] | Next iteration flow rate |  |  | 28007.4237 | Abs Value of | Flow this | 23423.8823 | Abs Value of | Flow this | 57930.0483 | Abs Value of | Flow this | 112832.9477 | Abs Value of | Flow this | 185568.6564 | Abs Value of | Flow this | 260274.3268 | Abs Value of | Flow this | 330479.3309 | Abs Value of | Flow this | 387513.006 | Abs Value of | Flow this | 432335.9947 | Abs Value of | Flow this | 482343.5844 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -212.2723 |  |  | -118.2692 |  |  | -1237.6783 |  |  | -4976.2235 |  |  | -13631.1307 |  |  | -26912.6907 |  |  | -43450.8845 |  |  | -59780.0787 |  |  | -74433.8116 |  |  | -92673.5453
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -1.024 |  |  | -0.57051 |  |  | -5.9703 |  |  | -24.0044 |  |  | -65.7541 |  |  | -129.822 |  |  | -209.5993 |  |  | -288.3685 |  |  | -359.0555 |  |  | -447.0407
[13 empty] | Delta P at this iteration flow rate |  |  | -262.2723 |  |  | -168.2692 |  |  | -1287.6783 |  |  | -5026.2235 |  |  | -13681.1307 |  |  | -26962.6907 |  |  | -43500.8845 |  |  | -59830.0787 |  |  | -74483.8116 |  |  | -92723.5453
[13 empty] | Press drop ratio this iteration |  |  | 1.2355 |  |  | 1.4228 |  |  | 1.0404 |  |  | 1.01 |  |  | 1.0037 |  |  | 1.0019 |  |  | 1.0012 |  |  | 1.0008 |  |  | 1.0007 |  |  | 1.0005
[13 empty] | Expansion factor | 12 |  | 0.35651 |  |  | 0.25917 |  |  | 0.45014 |  |  | 0.45886 |  |  | 0.44754 |  |  | 0.41708 |  |  | 0.37729 |  |  | 0.31984 |  |  | 0.43801 |  |  | 0.14696
[13 empty] | C Non choked w/ reducers | 5 |  | 75.7403 |  |  | 145.8332 |  |  | 23.2558 |  |  | 11.2812 |  |  | 7.0496 |  |  | 5.4947 |  |  | 4.9428 |  |  | 5.2754 |  |  | 3.9211 |  |  | 13.7609
[13 empty] | C Choked w/ reducers | 5 |  | 56.248 |  |  | 84.4766 |  |  | 20.1577 |  |  | 9.8884 |  |  | 6.0895 |  |  | 4.5436 |  |  | 3.8214 |  |  | 3.6135 |  |  | 3.3434 |  |  | 4.8504
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 56.248 |  |  | 84.4766 |  |  | 20.1577 |  |  | 9.8884 |  |  | 6.0895 |  |  | 4.5436 |  |  | 3.8214 |  |  | 3.6135 |  |  | 3.3434 |  |  | 4.8504
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 28007.4237 |  | 7174 | 23423.8823 |  | 7174 | 57930.0483 |  | 7174 | 112832.9477 |  | 7174 | 185568.6564 |  | 7174 | 260274.3268 |  | 7174 | 330479.3309 |  | 7174 | 387513.006 |  | 7174 | 432335.9947 |  | 7174 | 482343.5844
[13 empty] | Next iteration flow rate |  |  | 28567.5721 | Abs Value of | Flow this | 23658.1211 | Abs Value of | Flow this | 58509.3488 | Abs Value of | Flow this | 113961.2772 | Abs Value of | Flow this | 187424.343 | Abs Value of | Flow this | 262877.0701 | Abs Value of | Flow this | 333784.1242 | Abs Value of | Flow this | 391388.1361 | Abs Value of | Flow this | 436659.3547 | Abs Value of | Flow this | 487167.0203 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -224.9092 |  |  | -122.6669 |  |  | -1264.5761 |  |  | -5078.2661 |  |  | -13907.1369 |  |  | -27455.6563 |  |  | -44326.2678 |  |  | -60983.6788 |  |  | -75931.9517 |  |  | -94538.304
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -1.0849 |  |  | -0.59172 |  |  | -6.1001 |  |  | -24.4967 |  |  | -67.0856 |  |  | -132.4412 |  |  | -213.822 |  |  | -294.1744 |  |  | -366.2822 |  |  | -456.0359
[13 empty] | Delta P at this iteration flow rate |  |  | -274.9092 |  |  | -172.6669 |  |  | -1314.5761 |  |  | -5128.2661 |  |  | -13957.1369 |  |  | -27505.6563 |  |  | -44376.2678 |  |  | -61033.6788 |  |  | -75981.9517 |  |  | -94588.304
[13 empty] | Press drop ratio this iteration |  |  | 1.2223 |  |  | 1.4076 |  |  | 1.0395 |  |  | 1.0098 |  |  | 1.0036 |  |  | 1.0018 |  |  | 1.0011 |  |  | 1.0008 |  |  | 1.0007 |  |  | 1.0005
[13 empty] | Expansion factor | 12 |  | 0.36341 |  |  | 0.26706 |  |  | 0.4506 |  |  | 0.45897 |  |  | 0.44758 |  |  | 0.4171 |  |  | 0.3773 |  |  | 0.31985 |  |  | 0.43802 |  |  | 0.14697
[13 empty] | C Non choked w/ reducers | 5 |  | 71.9176 |  |  | 138.5544 |  |  | 22.9751 |  |  | 11.1636 |  |  | 6.9785 |  |  | 5.4397 |  |  | 4.8935 |  |  | 5.2228 |  |  | 3.8821 |  |  | 13.6236
[13 empty] | C Choked w/ reducers | 5 |  | 54.1494 |  |  | 82.2626 |  |  | 19.9262 |  |  | 9.7866 |  |  | 6.0283 |  |  | 4.4983 |  |  | 3.7834 |  |  | 3.5776 |  |  | 3.3102 |  |  | 4.8023
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 54.1494 |  |  | 82.2626 |  |  | 19.9262 |  |  | 9.7866 |  |  | 6.0283 |  |  | 4.4983 |  |  | 3.7834 |  |  | 3.5776 |  |  | 3.3102 |  |  | 4.8023
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 28567.5721 |  | 7174 | 23658.1211 |  | 7174 | 58509.3488 |  | 7174 | 113961.2772 |  | 7174 | 187424.343 |  | 7174 | 262877.0701 |  | 7174 | 333784.1242 |  | 7174 | 391388.1361 |  | 7174 | 436659.3547 |  | 7174 | 487167.0203
[13 empty] | Next iteration flow rate |  |  | 29138.9236 | Abs Value of | Flow this | 23894.7023 | Abs Value of | Flow this | 59094.4423 | Abs Value of | Flow this | 115100.89 | Abs Value of | Flow this | 189298.5864 | Abs Value of | Flow this | 265505.8408 | Abs Value of | Flow this | 337121.9655 | Abs Value of | Flow this | 395302.0174 | Abs Value of | Flow this | 441025.9482 | Abs Value of | Flow this | 492038.6905 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -238.0567 |  |  | -127.153 |  |  | -1292.0146 |  |  | -5182.3597 |  |  | -14188.6908 |  |  | -28009.5355 |  |  | -45219.2463 |  |  | -62211.4712 |  |  | -77460.2044 |  |  | -96440.5444
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -1.1483 |  |  | -0.61336 |  |  | -6.2324 |  |  | -24.9988 |  |  | -68.4437 |  |  | -135.113 |  |  | -218.1296 |  |  | -300.0971 |  |  | -373.6542 |  |  | -465.212
[13 empty] | Delta P at this iteration flow rate |  |  | -288.0567 |  |  | -177.153 |  |  | -1342.0146 |  |  | -5232.3597 |  |  | -14238.6908 |  |  | -28059.5355 |  |  | -45269.2463 |  |  | -62261.4712 |  |  | -77510.2044 |  |  | -96490.5444
[13 empty] | Press drop ratio this iteration |  |  | 1.21 |  |  | 1.3932 |  |  | 1.0387 |  |  | 1.0096 |  |  | 1.0035 |  |  | 1.0018 |  |  | 1.0011 |  |  | 1.0008 |  |  | 1.0006 |  |  | 1.0005
[13 empty] | Expansion factor | 12 |  | 0.3698 |  |  | 0.27455 |  |  | 0.45104 |  |  | 0.45908 |  |  | 0.44762 |  |  | 0.41712 |  |  | 0.37732 |  |  | 0.31986 |  |  | 0.43803 |  |  | 0.14698
[13 empty] | C Non choked w/ reducers | 5 |  | 68.4509 |  |  | 131.9967 |  |  | 22.6988 |  |  | 11.0473 |  |  | 6.908 |  |  | 5.3853 |  |  | 4.8447 |  |  | 5.1708 |  |  | 3.8436 |  |  | 13.4877
[13 empty] | C Choked w/ reducers | 5 |  | 52.182 |  |  | 80.1538 |  |  | 19.6981 |  |  | 9.686 |  |  | 5.9678 |  |  | 4.4534 |  |  | 3.7458 |  |  | 3.542 |  |  | 3.2774 |  |  | 4.7546
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 52.182 |  |  | 80.1538 |  |  | 19.6981 |  |  | 9.686 |  |  | 5.9678 |  |  | 4.4534 |  |  | 3.7458 |  |  | 3.542 |  |  | 3.2774 |  |  | 4.7546
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 29138.9236 |  | 7174 | 23894.7023 |  | 7174 | 59094.4423 |  | 7174 | 115100.89 |  | 7174 | 189298.5864 |  | 7174 | 265505.8408 |  | 7174 | 337121.9655 |  | 7174 | 395302.0174 |  | 7174 | 441025.9482 |  | 7174 | 492038.6905
[13 empty] | Next iteration flow rate |  |  | 29721.702 | Abs Value of | Flow this | 24133.6493 | Abs Value of | Flow this | 59685.3867 | Abs Value of | Flow this | 116251.8989 | Abs Value of | Flow this | 191191.5723 | Abs Value of | Flow this | 268160.8992 | Abs Value of | Flow this | 340493.1851 | Abs Value of | Flow this | 399255.0376 | Abs Value of | Flow this | 445436.2077 | Abs Value of | Flow this | 496959.0774 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -251.7353 |  |  | -131.7293 |  |  | -1320.0046 |  |  | -5288.5456 |  |  | -14475.904 |  |  | -28574.5477 |  |  | -46130.1736 |  |  | -63463.9423 |  |  | -79019.175 |  |  | -98381.0199
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -1.2143 |  |  | -0.63544 |  |  | -6.3675 |  |  | -25.511 |  |  | -69.8292 |  |  | -137.8385 |  |  | -222.5237 |  |  | -306.1388 |  |  | -381.1744 |  |  | -474.5725
[13 empty] | Delta P at this iteration flow rate |  |  | -301.7353 |  |  | -181.7293 |  |  | -1370.0046 |  |  | -5338.5456 |  |  | -14525.904 |  |  | -28624.5477 |  |  | -46180.1736 |  |  | -63513.9423 |  |  | -79069.175 |  |  | -98431.0199
[13 empty] | Press drop ratio this iteration |  |  | 1.1986 |  |  | 1.3796 |  |  | 1.0379 |  |  | 1.0095 |  |  | 1.0035 |  |  | 1.0017 |  |  | 1.0011 |  |  | 1.0008 |  |  | 1.0006 |  |  | 1.0005
[13 empty] | Expansion factor | 12 |  | 0.37574 |  |  | 0.28166 |  |  | 0.45147 |  |  | 0.45918 |  |  | 0.44765 |  |  | 0.41714 |  |  | 0.37733 |  |  | 0.31987 |  |  | 0.43803 |  |  | 0.14699
[13 empty] | C Non choked w/ reducers | 5 |  | 65.2903 |  |  | 126.0549 |  |  | 22.427 |  |  | 10.9323 |  |  | 6.8383 |  |  | 5.3314 |  |  | 4.7964 |  |  | 5.1193 |  |  | 3.8054 |  |  | 13.3531
[13 empty] | C Choked w/ reducers | 5 |  | 50.3335 |  |  | 78.143 |  |  | 19.4732 |  |  | 9.5864 |  |  | 5.9079 |  |  | 4.409 |  |  | 3.7085 |  |  | 3.5068 |  |  | 3.2448 |  |  | 4.7074
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 50.3335 |  |  | 78.143 |  |  | 19.4732 |  |  | 9.5864 |  |  | 5.9079 |  |  | 4.409 |  |  | 3.7085 |  |  | 3.5068 |  |  | 3.2448 |  |  | 4.7074
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 29721.702 |  | 7174 | 24133.6493 |  | 7174 | 59685.3867 |  | 7174 | 116251.8989 |  | 7174 | 191191.5723 |  | 7174 | 268160.8992 |  | 7174 | 340493.1851 |  | 7174 | 399255.0376 |  | 7174 | 445436.2077 |  | 7174 | 496959.0774
[13 empty] | Next iteration flow rate |  |  | 30316.1361 | Abs Value of | Flow this | 24374.9858 | Abs Value of | Flow this | 60282.2406 | Abs Value of | Flow this | 117414.4179 | Abs Value of | Flow this | 193103.488 | Abs Value of | Flow this | 270842.5082 | Abs Value of | Flow this | 343898.117 | Abs Value of | Flow this | 403247.588 | Abs Value of | Flow this | 449890.5698 | Abs Value of | Flow this | 501928.6682 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -265.9665 |  |  | -136.3975 |  |  | -1348.5572 |  |  | -5396.8659 |  |  | -14768.8902 |  |  | -29150.9166 |  |  | -47059.4106 |  |  | -64741.588 |  |  | -80609.481 |  |  | -100360.4989
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -1.283 |  |  | -0.65796 |  |  | -6.5052 |  |  | -26.0335 |  |  | -71.2425 |  |  | -140.6188 |  |  | -227.0062 |  |  | -312.3019 |  |  | -388.8458 |  |  | -484.1212
[13 empty] | Delta P at this iteration flow rate |  |  | -315.9665 |  |  | -186.3975 |  |  | -1398.5572 |  |  | -5446.8659 |  |  | -14818.8902 |  |  | -29200.9166 |  |  | -47109.4106 |  |  | -64791.588 |  |  | -80659.481 |  |  | -100410.4989
[13 empty] | Press drop ratio this iteration |  |  | 1.188 |  |  | 1.3666 |  |  | 1.0371 |  |  | 1.0093 |  |  | 1.0034 |  |  | 1.0017 |  |  | 1.0011 |  |  | 1.0008 |  |  | 1.0006 |  |  | 1.0005
[13 empty] | Expansion factor | 12 |  | 0.38128 |  |  | 0.28843 |  |  | 0.4519 |  |  | 0.45928 |  |  | 0.44769 |  |  | 0.41716 |  |  | 0.37734 |  |  | 0.31988 |  |  | 0.43804 |  |  | 0.147
[13 empty] | C Non choked w/ reducers | 5 |  | 62.3948 |  |  | 120.6438 |  |  | 22.1595 |  |  | 10.8186 |  |  | 6.7694 |  |  | 5.2781 |  |  | 4.7486 |  |  | 5.0684 |  |  | 3.7676 |  |  | 13.2199
[13 empty] | C Choked w/ reducers | 5 |  | 48.593 |  |  | 76.2232 |  |  | 19.2515 |  |  | 9.4879 |  |  | 5.8486 |  |  | 4.3651 |  |  | 3.6717 |  |  | 3.472 |  |  | 3.2126 |  |  | 4.6607
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 48.593 |  |  | 76.2232 |  |  | 19.2515 |  |  | 9.4879 |  |  | 5.8486 |  |  | 4.3651 |  |  | 3.6717 |  |  | 3.472 |  |  | 3.2126 |  |  | 4.6607
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 30316.1361 |  | 7174 | 24374.9858 |  | 7174 | 60282.2406 |  | 7174 | 117414.4179 |  | 7174 | 193103.488 |  | 7174 | 270842.5082 |  | 7174 | 343898.117 |  | 7174 | 403247.588 |  | 7174 | 449890.5698 |  | 7174 | 501928.6682
[13 empty] | Next iteration flow rate |  |  | 30922.4588 | Abs Value of | Flow this | 24618.7357 | Abs Value of | Flow this | 60885.063 | Abs Value of | Flow this | 118588.5621 | Abs Value of | Flow this | 195034.5229 | Abs Value of | Flow this | 273550.9333 | Abs Value of | Flow this | 347337.0981 | Abs Value of | Flow this | 407280.0639 | Abs Value of | Flow this | 454389.4755 | Abs Value of | Flow this | 506947.9549 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -280.7727 |  |  | -141.1596 |  |  | -1377.6837 |  |  | -5507.3634 |  |  | -15067.7654 |  |  | -29738.8705 |  |  | -48007.3253 |  |  | -66044.9145 |  |  | -82231.752 |  |  | -102379.7654
[13 empty] | P2 at this iteration flow rate |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50 |  |  | 50
[13 empty] | Density at this iteration |  |  | -1.3544 |  |  | -0.68093 |  |  | -6.6457 |  |  | -26.5665 |  |  | -72.6842 |  |  | -143.455 |  |  | -231.5788 |  |  | -318.5889 |  |  | -396.6713 |  |  | -493.8618
[13 empty] | Delta P at this iteration flow rate |  |  | -330.7727 |  |  | -191.1596 |  |  | -1427.6837 |  |  | -5557.3634 |  |  | -15117.7654 |  |  | -29788.8705 |  |  | -48057.3253 |  |  | -66094.9145 |  |  | -82281.752 |  |  | -102429.7654
[13 empty] | Press drop ratio this iteration |  |  | 1.1781 |  |  | 1.3542 |  |  | 1.0363 |  |  | 1.0091 |  |  | 1.0033 |  |  | 1.0017 |  |  | 1.001 |  |  | 1.0008 |  |  | 1.0006 |  |  | 1.0005
[13 empty] | Expansion factor | 12 |  | 0.38644 |  |  | 0.29487 |  |  | 0.45231 |  |  | 0.45938 |  |  | 0.44773 |  |  | 0.41718 |  |  | 0.37736 |  |  | 0.31989 |  |  | 0.43805 |  |  | 0.14701
[13 empty] | C Non choked w/ reducers | 5 |  | 59.7309 |  |  | 115.693 |  |  | 21.8961 |  |  | 10.7062 |  |  | 6.7011 |  |  | 5.2253 |  |  | 4.7013 |  |  | 5.0179 |  |  | 3.7301 |  |  | 13.0881
[13 empty] | C Choked w/ reducers | 5 |  | 46.9512 |  |  | 74.3883 |  |  | 19.0329 |  |  | 9.3905 |  |  | 5.7899 |  |  | 4.3216 |  |  | 3.6351 |  |  | 3.4375 |  |  | 3.1807 |  |  | 4.6145
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64017 |  |  | 0.63071 |  |  | 0.62218 |  |  | 0.60557 |  |  | 0.57289 |  |  | 0.53591 |  |  | 0.49049 |  |  | 0.59353 |  |  | 0.39097
[13 empty] | Selected C this iteration |  |  | 46.9512 |  |  | 74.3883 |  |  | 19.0329 |  |  | 9.3905 |  |  | 5.7899 |  |  | 4.3216 |  |  | 3.6351 |  |  | 3.4375 |  |  | 3.1807 |  |  | 4.6145
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7174 | 30922.4588 |  | 7174 | 24618.7357 |  | 7174 | 60885.063 |  | 7174 | 118588.5621 |  | 7174 | 195034.5229 |  | 7174 | 273550.9333 |  | 7174 | 347337.0981 |  | 7174 | 407280.0639 |  | 7174 | 454389.4755 |  | 7174 | 506947.9549

## Installed Gain
Neles RE
2 inch
PV123
Wmax = maximum
[8 empty] | design flow = | 7174
Wmin = minimum
[8 empty] | design flow = | 1145
[8 empty] | Flow units are | lbm/h
Graph Data
Valve relative travel, h | 0 | 0.05 | 0.1 | 0.15 | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.55 | 0.6 | 0.65 | 0.7 | 0.75 | 0.8 | 0.85 | 0.9 | 0.95 | 1
Relative flow Q/Qmax | 0 | 0.032378 | 0.064755 | 0.11245 | 0.16015 | 0.23604 | 0.31193 | 0.41247 | 0.51301 | 0.61627 | 0.71953 | 0.81657 | 0.91361 | 0.99245 | 1.0713 | 1.1332 | 1.1952 | 1.2643 | 1.3334 | 1.3605 | 1.3876 | 0.1596 | 0.1596 | 1 | 1
Gain = Delta Q / Delta h |  | 0.64755 | 0.80074 | 0.95392 | 1.2359 | 1.5178 | 1.7643 | 2.0108 | 2.038 | 2.0652 | 2.003 | 1.9408 | 1.7588 | 1.5767 | 1.4079 | 1.2391 | 1.3108 | 1.3825 | 0.96195 | 0.54143
Qmin vertical line | [21 empty] | 0 | 4
Qmax vertical line | [23 empty] | 0 | 4
Delta Q |  | 0.064755 | 0.080074 | 0.095392 | 0.12359 | 0.15178 | 0.17643 | 0.20108 | 0.2038 | 0.20652 | 0.2003 | 0.19408 | 0.17588 | 0.15767 | 0.14079 | 0.12391 | 0.13108 | 0.13825 | 0.096195 | 0.054143
Delta h |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1

## Typical xT
Typical xT values based on the Cv reported on Line 17 of the |  |  |  |  | For initial calculations (before |  |  | Intermediate calculations
Valve Sizing tab for the valve size entered in D14 of the Valve Sizing tab. |  |  |  |  | the Cv is known), consider using
[5 empty] | the xT values listed below. |  | DESCRIPTION OF VARIABLE | NAME OF VARIABLE | FORMULA
Flow | 1145 | 2060 | 4960 | 7174 | Minimum | Maximum | CALCULATED IN COLUMN "O" | CALCULATED IN COLUMN "O"
Valve type | Choked press drop ratio factor, xT |  |  |  | Flow | Flow
[7 empty] | Valve Cv/Valve size squared | Cv_over_d_Sq | 1.2458 | 2.5 | 6.6189 | 11.4284
Globe, 4 port cage | 0.73434 | 0.72475 | 0.7 | 0.7 | 0.79 | 0.71
The value of "Cv_over_d_Sq" is calculated from the Valve Sizing tab (S, T, U, V397)
Globe, Parabolic plug | 0.60857 | 0.6 | 0.6 | 0.6 | 0.77 | 0.65 | where Kv has been converted to Cv if the worksheet has been
configured for Kv and valve size (S414, which is named "d_in") in mm has been converted
Rotary eccentric plug | 0.62 | 0.62 | 0.60585 | 0.51544 | 0.62 | 0.52 | to inch if the worksheet has been configured for mm.
Segment ball | 0.64 | 0.63366 | 0.60257 | 0.53306 | 0.64 | 0.4
Butterfly | 0.693 | 0.69189 | 0.62677 | 0.55073 | 0.68 | 0.37
Full ball | 0.82 | 0.8111 | 0.7014 | 0.59192 | 0.82 | 0.3

## Density
This tab calculates Molecular mass from Specific gravity or from Valve Sizing tab process data. It also calculates Density from Valve Sizing tab data and Compressibility factor.
Conversion from specific gravity to Molecular Mass: |  |  |  | Case 1 | Case 2 | Case 3 | Case 4 |  | Intermediate Calculations
Inlet pressure converted to Pa (Pascal)
|  | Specific gravity | G_ | 1 | ======> | ======> | ======> | Inlet temperature coverted to Kelvin
|  | Molecular Mass |  | 28.97 | ======> | ======> | ======> | Pa | P_1..L | 689475.73 | 616391.3026 | 588812.2734 | 551580.584
[8 empty] | K | T_1..L | 310.9278 | 310.9278 | 310.9278 | 310.9278
Conversion from Molecular Mass, Inlet Pressure and Temperature given on the Valve Sizing tab to Density
|  | Compressibility factor (Z)* | Z_ | 1 | 1 | 1 | 1
|  | Density (kg/m3) |  | 7.7268 | 6.9077 | 6.5987 | 6.1814
|  | Density (lbm/ft3) |  | 0.48238 | 0.43125 | 0.41195 | 0.38591
Conversion from Density, Inlet Pressure and Temperature given in Column D on the Valve Sizing tab to Molecular Mass
|  | Compressibility factor (Z)* |  | 1
|  | Molecular mass |  | 28.9709
Data input
Final results
*Use 1.00 if compressibility factor is unknown. Using a compressibility factor of 1.0
will result in calculated density or molecular mass above to be an approximation.