## Valve Sizing
Unit selection: | 1 | 1 = US; 2 = SI (Cv, bar); 3 = SI (Cv, kPa); 4 = SI (Kv, bar); 5 = SI (Kv, kPa) | [6 empty] | Scroll to the right to view the intermediate calculations. | Valve sizing per ISA S75.01.01 2012
CONTROL VALVE SIZING: LIQUID |  |  | TAG: | PV123 |  |  | Valve type | Valve style SPL code |  | DESCRIPTION OF VARIABLE | Eqn. | NAME OF VARIABLE | FORMULA
Flow | gpm | Q | 80 | 213 | 423 | 550 | Globe | 0 |  | CALCULATED IN COLUMN "S" |  | CALCULATED IN COLUMN "S"
Inlet pressure | psiA | P_1 | 56.7 | 55.4 | 50.7 | 46.7 | Rotary eccentric plug | 1 |  | Critical pressure ratio factor | 4 | F_F | 0.95665 | 0.95665 | 0.95665 | 0.95665
Pressure drop | psi | DELTA_P | 32 | 30.4 | 24.9 | 20 | Segment ball | 2 |  | WITHOUT REDUCERS
Specific gravity (r1/r0) |  | G | 1 | 1 | 1 | 1 | Butterfly | 3 |  | Choked pressure drop | 3 | Delta_P_Ch | 47.6184 | 43.5338 | 34.6241 | 28.1445
Vapor pressure | psiA | P_V | 0.46 | 0.46 | 0.46 | 0.46 | Full ball | 4 |  | C Non choked | 1 | C_NonCh | 14.1421 | 38.6316 | 84.7697 | 122.9837
Critical pressure | psiA | P_C | 3208 | ======> | ======> | ======> | Milti-stage globe | 5 |  | C Choked | 1 | C_Ch | 11.5932 | 32.2824 | 71.8872 | 103.673
Recovery factor |  | F_L | 0.92 | 0.89 | 0.83 | 0.78 |  |  |  | Select C Non choked or C choked | 2 | Applicable_C_NonCh_or_Ch | 14.1421 | 38.6316 | 84.7697 | 122.9837
Inlet pipe diameter | inch | D_1 | 6 | ======> | ======> | ======> |  |  |  | (This is the initial guess for
Outlet pipe diameter | inch | D_2 | 6 | ======> | ======> | ======> |  |  |  | the following iterative calculations)
Valve size | inch | d | 3 | ======> | ======> | ======>
Valve style SPL code |  | VSC | 2 | ======> | ======> | ======> |  |  |  | WITH REDUCERS
Pipe wall correction | dB(A) | DeltaLp | -2 | ======> | ======> | ======> |  |  |  | Reducer velocity head coefficients | 18 | ZETA_1 | 0.28125
Turbulent flow coef. (Cv or Kv) | Cv | C_ | 14.1587 | 38.9735 | 88.5763 | 135.5671 |  |  |  |  | 17 | ZETA_B1 | 0.9375
Turbulent flow calc from Cv or Kv | gpm |  | 80 | 213 | 423 | 550 |  |  |  |  | 19 | ZETA_2 | 0.5625
Choked delta p | psi |  | 47.5936 | 43.4244 | 34.6384 | 28.7616 |  |  |  |  | 17 | ZETA_B2 | 0.9375
Sound pressure level | dB(A) |  | 66.2314 | 71.4645 | 74.7282 | 75.3717 |  |  |  | Sum of velocity head coefficients | 16 | SIGMA_ZETA | 0.84375
Valve inlet velocity | ft/s |  | 3.6311 | 9.6678 | 19.1995 | 24.9639 |  |  |  | Sum of upstream velocity head coef |  | SIGMA_ZETA_1 | 1.2188
Selected valve style (VSC) |  |  | Segment ball
For non-turbulent flow (valve Reynolds Number < 10,000) - Optional calculation if non-turbulent flow is suspected | [9 empty] | Beginning of iterative calculation |  | Total of 59 iterations
Kinematic viscosity | cS | n | 20 | 20 | 20 | 20 |  |  |  | Assumed C for this iteration |  | C_i | 14.1421 | 38.6316 | 84.7697 | 122.9837
Valve style modifier |  | F_D | 0.6 | 0.6 | 0.65 | 0.68 |  |  |  | Piping geometry factor | 15 | F_P | 0.99883 | 0.99138 | 0.96043 | 0.92174
Reduced trim? C(Rated)<N18*0.016 (yes or no) |  | RED_TRM | No | ======> | ======> | ======> |  |  |  | Combined liquid pressure recovery
Valve Reynolds Number |  |  | 11517.5627 | 18929.8207 | 28828.4485 | 34037.6701 |  |  |  | factor and piping geometry factor | 21 | F_LP | 0.91869 | 0.88124 | 0.79731 | 0.7256
Non-turb flow coef. (Cv or Kv) | Cv |  | Turbulent | Turbulent | Turbulent | Turbulent |  |  |  | C Non choked w/ reducers | 1 | C_NonCh_W_Reducers | 14.1587 | 38.9675 | 88.2625 | 133.426
Non-turb. Flow Calc from Cv or Kv | Cv | [8 empty] | C Choked w/ reducers | 1 | C_Ch_W_Reducers | 11.6098 | 32.6034 | 74.8349 | 111.4458
[6 empty] | Data input |  |  |  | Choked pressure drop w/ reducers | 3 | Delta_P_Ch_W_Reducers | 47.5937 | 43.4263 | 34.6373 | 28.6671
[6 empty] | Final results |  |  |  | Select C Non choked or C choked |  |  | 14.1587 | 38.9675 | 88.2625 | 133.426
[10 empty] | Ci/ C, this iteration |  | C_i divided by S29 | 0.99883 | 0.99138 | 0.96043 | 0.92174
This worksheet is distributed at no cost on an as-is basis.
The author does not assume any liability for its use. | [9 empty] | Assumed C for this iteration |  |  | 14.1587 | 38.9675 | 88.2625 | 133.426
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95731 | 0.90971
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88109 | 0.79473 | 0.7171
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9734 | 88.55 | 135.1905
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.609 | 75.0775 | 112.7659
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4245 | 34.6383 | 28.7453
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9734 | 88.55 | 135.1905
[10 empty] | Ci / C, this iteration |  |  | 1 | 0.99985 | 0.99675 | 0.98695
The cells below (Rows 52 & 54) detrmine if any input data is missing.
| If it is, error messages are blanked out of the calculated results. | [8 empty] | Assumed C for this iteration |  |  | 14.1587 | 38.9734 | 88.55 | 135.1905
| TURB1 | TURB2 | TURB3 | TURB4 | [5 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95705 | 0.90763
| -42565407355.6992 | -101765108709.4211 | -141277079531.2931 | -127717412359.68 | [5 empty] | Combined liquid pressure recovery
| N_TURB1 | N_TURB2 | N_TURB3 | N_TURB4 | [5 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79451 | 0.71563
| -510784888268.3904 | -1.2212e+12 | -1.8366e+12 | -1.737e+12 | [5 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5741 | 135.5005
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0979 | 112.998
These Numerical constants are set by the units choises set by the user above the user interface | [9 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7588
which incllude all the options for the ISA Standard | [9 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5741 | 135.5005
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 0.99973 | 0.99771
Numerical constants | [9 empty] | Assumed C for this iteration |  |  | 14.1587 | 38.9735 | 88.5741 | 135.5005
N_1 | 1 | [8 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95703 | 0.90726
N_2 * | 890 | [8 empty] | Combined liquid pressure recovery
N_4 | 17300 | [8 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.7945 | 0.71537
N_18 | 645 | [8 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5762 | 135.5553
N_32 | 17 | [8 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0996 | 113.0391
N_41 * | 12.1 | 12.1=density lbm/ft^3, pressure psia | [7 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7611
|  | 39.0 =density kg/m^3, barA | [7 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5762 | 135.5553
|  | 3.0=density kg/m^3, pressure kPaA | [7 empty] | Ci / C, this iteration |  |  | 1 | 1 | 0.99998 | 0.9996
FLAG_1 *** | 1 | 1=flow coef is Cv 2=flow coef is Kv
FLAG_3** | 1 | 1=flow is gpm, valve size is inch, inlet velocity is ft/s | [7 empty] | Assumed C for this iteration |  |  | 14.1587 | 38.9735 | 88.5762 | 135.5553
|  | 2= flow is m^3/h, valve size is mm, inlet velocity is m/s | [7 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90719
NOTE: The constants in B53, 54, 55, 56, 57, 58, 61 and 62 are set by formulas in those cells and are based on the unit selection made in Cell B1. | [9 empty] | Combined liquid pressure recovery
FLAG_1 & N_41 only have an effect in the noise calculation | [9 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71533
FLAG_3 only has an effect of the Inlet velocity calculation | [9 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.565
N_41 is a constant added by the Author for setting the noise calculation to use the appropriate units. | [9 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0463
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
* Using anything other than the exact numeric values in Table 1 of ISA S75.01.01 or Table 1 of the author's instructions may result in a logic error in the Mach number calc. | [9 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.565
** Using anything other than the exact numeric values for FLAG_3 may result in a logic error in the velocity calculation. | [9 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 0.99993
*** Using anything other than the exact numeric values for FLAG_1 may result in a logic error in the noise calculation.
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.565
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5667
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0476
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5667
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 0.99999
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5667
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.567
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0478
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.567
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.567
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | CI / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor |  |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
[10 empty] | Combined liquid pressure recovery | 15
[10 empty] | factor and piping geometry factor |  |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 21 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 1 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked | 3 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | CI / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor |  |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
[10 empty] | Combined liquid pressure recovery | 15
[10 empty] | factor and piping geometry factor |  |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 21 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 1 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked | 3 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
[10 empty] | Assumed C for iterative purposes |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 |  | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 |  | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | C Non choked w/ reducers | 1 |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | C Choked w/ reducers | 1 |  | 11.6098 | 32.6091 | 75.0997 | 113.0479
[10 empty] | Choked pressure drop w/ reducers | 3 |  | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Select C Non choked or C choked |  |  | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Ci / C, this iteration |  |  | 1 | 1 | 1 | 1
Confirmation that the calculated C will
produce the given flow rate
[10 empty] | Final C calculated above |  | Final_Calculated_C | 14.1587 | 38.9735 | 88.5763 | 135.5671
[10 empty] | Piping geometry factor | 15 | Final_F_P | 0.99883 | 0.99123 | 0.95702 | 0.90718
Combined liquid pressure recovery
[10 empty] | factor and piping geometry factor | 21 | Final_F_LP | 0.91868 | 0.88108 | 0.79449 | 0.71532
[10 empty] | Flow Non choked w/ reducers | 1 | Final_Flow_NonCh_W_Reducers | 80 | 213 | 423 | 550
[10 empty] | Flow Choked w/ reducers | 1 | Final_Flow_Ch_W_Reducers | 97.5639 | 254.5716 | 498.9071 | 659.5603
[10 empty] | Choked pressure drop w/ reducers | 3 | Final_Delta_P_Ch_W_Reducers | 47.5936 | 43.4244 | 34.6384 | 28.7616
[10 empty] | Calculated flow from final calculated C |  | Calc_Flow_From_Final_ Calc_C | 80 | 213 | 423 | 550
Hydrodynamic noise calculation
Based on VDMA24422 1979
[10 empty] | Valve nominal size in inches |  | d_in | 3 | 3 | 3 | 3
[10 empty] | Cv/nominal size in inches squared |  | C_d | 1.5732 | 4.3304 | 9.8418 | 15.063
VALVE STYLE SPECIFIC
PRESSURE DROP RATIOS WHERE
CAVITATION NOISE IS FIRST
DETECTED
[10 empty] | For globe valves |  | z_0 | 0.55249 | 0.4336 | 0.30075 | 0.299
[10 empty] | For eccentric rotary plug valves |  | z_1 | 0.47973 | 0.38055 | 0.33092 | 0.22477
[10 empty] | For segment ball valves |  | z_2 | 0.42083 | 0.38889 | 0.33133 | 0.28453
[10 empty] | For butterfly valves |  | z_3 | 0.35391 | 0.32703 | 0.2783 | 0.2383
[10 empty] | For ball valves |  | z_4 | 0.48259 | 0.43507 | 0.35364 | 0.2906
[10 empty] | For multi-stage globe valves |  | z_5 | 0.86 | 0.86 | 0.86 | 0.86
[10 empty] | For selected valve based on VSC |  | z | 0.42083 | 0.38889 | 0.33133 | 0.28453
(Valve Style Code)
[10 empty] | Pressure drop ratio |  | x_F | 0.56899 | 0.55333 | 0.49562 | 0.43253
[10 empty] | Scaled pressure drop ratio |  | x_R | 0.25581 | 0.26908 | 0.2457 | 0.20685
VALVE STYLE SPECIFIC NOISE
COEFFICIENT
[10 empty] | For globe valves |  | DeltaLf_0 | -6.9724 | -7.1578 | -6.8232 | -6.1867
[10 empty] | For eccentric rotary plug valves |  | DeltaLf_1 | -6.9724 | -7.1578 | -6.8232 | -6.1867
[10 empty] | For segment ball valves |  | DeltaLf_2 | 0 | 0 | 0 | 0
[10 empty] | For butterfly valves |  | DeltaLf_3 | 2 | 2 | 2 | 2
[10 empty] | For ball valves |  | DeltaLf_4 | 1.5349 | 1.6145 | 1.4742 | 1.2411
[10 empty] | For multi-stage globe valves |  | DeltaLf_5 | -20 | -20 | -20 | -20
[10 empty] | For selected valve based on VSC |  | DeltaLf | 0 | 0 | 0 | 0
(Valve Style Code)
[10 empty] | Common portion of SPL Calculation |  | SPL_C | 44.1362 | 48.3508 | 51.2172 | 52.417
[10 empty] | SPL calculation if x_F is <=z |  | SPL_L | 46.4941 | 51.1076 | 54.3652 | 55.6909
[10 empty] | SPL calculation if x_F is >z |  | SPL_G | 66.2314 | 71.4645 | 74.7282 | 75.3717
[10 empty] | Selected SPL (SPL_L or SPL_G) |  | SPL_SELECTED | 66.2314 | 71.4645 | 74.7282 | 75.3717
[10 empty] | Non-Turbulent Calculation of C |  | Total of 12 iterations
[10 empty] | Initial value of C for Non-turb Calculations |  | C_i_NT | 14.1421 | 38.6316 | 84.7697 | 122.9837
[10 empty] | Valve Reynolds Number | 23 | Re_V | 11517.5627 | 18929.8207 | 28828.4485 | 34037.6701
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 360.45 | 48.3047 | 10.0321 | 4.7663
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 23.9772 | 45.9003 | 76.8195 | 98.1671
[10 empty] | Select Eta, full or reduced trim |  |  | 360.45 | 48.3047 | 10.0321 | 4.7663
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 1 | 1 | 1 | 1
[10 empty] | Selected based on actual Rev |  |  | 1 | 1 | 1 | 1
[10 empty] | Calculated flow from Initial Cv | A.2 |  | 80 | 213 | 423 | 550
[10 empty] | Assumed C for iterative purposes |  |  | 14.1421 | 38.6316 | 84.7697 | 122.9837
[10 empty] | Valve Reynolds Number | 23 |  | 11517.5627 | 18929.8207 | 28828.4485 | 34037.6701
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 360.45 | 48.3047 | 10.0321 | 4.7663
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 23.9772 | 45.9003 | 76.8195 | 98.1671
[10 empty] | Select Eta, full or reduced trim |  |  | 360.45 | 48.3047 | 10.0321 | 4.7663
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 1 | 1 | 1 | 1
[10 empty] | Selected based on actual Rev |  |  | 1 | 1 | 1 | 1
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 80 | 213 | 423 | 550
[10 empty] | Change from previouse iteration |  |  | -3.553e-14% | 2.669e-14% | -2.688e-14% | 0%
[10 empty] | Assumed C for iterative purposes |  |  | 14.1421 | 38.6316 | 84.7697 | 122.9837
[10 empty] | Valve Reynolds Number | 23 |  | 11517.5627 | 18929.8207 | 28828.4485 | 34037.6701
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 360.45 | 48.3047 | 10.0321 | 4.7663
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 23.9772 | 45.9003 | 76.8195 | 98.1671
[10 empty] | Select Eta, full or reduced trim |  |  | 360.45 | 48.3047 | 10.0321 | 4.7663
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 1 | 1 | 1 | 1
[10 empty] | Selected based on actual Rev |  |  | 1 | 1 | 1 | 1
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 80 | 213 | 423 | 550
[10 empty] | Change from previouse iteration |  |  | 0% | -2.669e-14% | 0% | 0%
[10 empty] | Assumed C for iterative purposes |  |  | 14.1421 | 38.6316 | 84.7697 | 122.9837
[10 empty] | Valve Reynolds Number | 23 |  | 11517.5627 | 18929.8207 | 28828.4485 | 34037.6701
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 360.45 | 48.3047 | 10.0321 | 4.7663
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 23.9772 | 45.9003 | 76.8195 | 98.1671
[10 empty] | Select Eta, full or reduced trim |  |  | 360.45 | 48.3047 | 10.0321 | 4.7663
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 1 | 1 | 1 | 1
[10 empty] | Selected based on actual Rev |  |  | 1 | 1 | 1 | 1
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 80 | 213 | 423 | 550
[10 empty] | Change from previouse iteration |  |  | 0% | 0% | 0% | 0%
[10 empty] | Assumed C for iterative purposes |  |  | 14.1421 | 38.6316 | 84.7697 | 122.9837
[10 empty] | Valve Reynolds Number | 23 |  | 11517.5627 | 18929.8207 | 28828.4485 | 34037.6701
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 360.45 | 48.3047 | 10.0321 | 4.7663
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 23.9772 | 45.9003 | 76.8195 | 98.1671
[10 empty] | Select Eta, full or reduced trim |  |  | 360.45 | 48.3047 | 10.0321 | 4.7663
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 1 | 1 | 1 | 1
[10 empty] | Selected based on actual Rev |  |  | 1 | 1 | 1 | 1
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 80 | 213 | 423 | 550
[10 empty] | Change from previouse iteration |  |  | 0% | 0% | 0% | 0%
[10 empty] | Assumed C for iterative purposes |  |  | 14.1421 | 38.6316 | 84.7697 | 122.9837
[10 empty] | Valve Reynolds Number | 23 |  | 11517.5627 | 18929.8207 | 28828.4485 | 34037.6701
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 360.45 | 48.3047 | 10.0321 | 4.7663
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 23.9772 | 45.9003 | 76.8195 | 98.1671
[10 empty] | Select Eta, full or reduced trim |  |  | 360.45 | 48.3047 | 10.0321 | 4.7663
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 1 | 1 | 1 | 1
[10 empty] | Selected based on actual Rev |  |  | 1 | 1 | 1 | 1
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 80 | 213 | 423 | 550
[10 empty] | Change from previouse iteration |  |  | 0% | 0% | 0% | 0%
[10 empty] | Assumed C for iterative purposes |  |  | 14.1421 | 38.6316 | 84.7697 | 122.9837
[10 empty] | Valve Reynolds Number | 23 |  | 11517.5627 | 18929.8207 | 28828.4485 | 34037.6701
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 360.45 | 48.3047 | 10.0321 | 4.7663
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 23.9772 | 45.9003 | 76.8195 | 98.1671
[10 empty] | Select Eta, full or reduced trim |  |  | 360.45 | 48.3047 | 10.0321 | 4.7663
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 1 | 1 | 1 | 1
[10 empty] | Selected based on actual Rev |  |  | 1 | 1 | 1 | 1
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 80 | 213 | 423 | 550
[10 empty] | Change from previouse iteration |  |  | 0% | 0% | 0% | 0%
[10 empty] | Assumed C for iterative purposes |  |  | 14.1421 | 38.6316 | 84.7697 | 122.9837
[10 empty] | Valve Reynolds Number | 23 |  | 11517.5627 | 18929.8207 | 28828.4485 | 34037.6701
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 360.45 | 48.3047 | 10.0321 | 4.7663
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 23.9772 | 45.9003 | 76.8195 | 98.1671
[10 empty] | Select Eta, full or reduced trim |  |  | 360.45 | 48.3047 | 10.0321 | 4.7663
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 1 | 1 | 1 | 1
[10 empty] | Selected based on actual Rev |  |  | 1 | 1 | 1 | 1
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 80 | 213 | 423 | 550
[10 empty] | Change from previouse iteration |  |  | 0% | 0% | 0% | 0%
[10 empty] | Assumed C for iterative purposes |  |  | 14.1421 | 38.6316 | 84.7697 | 122.9837
[10 empty] | Valve Reynolds Number | 23 |  | 11517.5627 | 18929.8207 | 28828.4485 | 34037.6701
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 360.45 | 48.3047 | 10.0321 | 4.7663
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 23.9772 | 45.9003 | 76.8195 | 98.1671
[10 empty] | Select Eta, full or reduced trim |  |  | 360.45 | 48.3047 | 10.0321 | 4.7663
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 1 | 1 | 1 | 1
[10 empty] | Selected based on actual Rev |  |  | 1 | 1 | 1 | 1
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 80 | 213 | 423 | 550
[10 empty] | Change from previouse iteration |  |  | 0% | 0% | 0% | 0%
[10 empty] | Assumed C for iterative purposes |  |  | 14.1421 | 38.6316 | 84.7697 | 122.9837
[10 empty] | Valve Reynolds Number | 23 |  | 11517.5627 | 18929.8207 | 28828.4485 | 34037.6701
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 360.45 | 48.3047 | 10.0321 | 4.7663
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 23.9772 | 45.9003 | 76.8195 | 98.1671
[10 empty] | Select Eta, full or reduced trim |  |  | 360.45 | 48.3047 | 10.0321 | 4.7663
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 1 | 1 | 1 | 1
[10 empty] | Selected based on actual Rev |  |  | 1 | 1 | 1 | 1
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 80 | 213 | 423 | 550
[10 empty] | Change from previouse iteration |  |  | 0% | 0% | 0% | 0%
[10 empty] | Assumed C for iterative purposes |  |  | 14.1421 | 38.6316 | 84.7697 | 122.9837
[10 empty] | Valve Reynolds Number | 23 |  | 11517.5627 | 18929.8207 | 28828.4485 | 34037.6701
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 360.45 | 48.3047 | 10.0321 | 4.7663
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 23.9772 | 45.9003 | 76.8195 | 98.1671
[10 empty] | Select Eta, full or reduced trim |  |  | 360.45 | 48.3047 | 10.0321 | 4.7663
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 1 | 1 | 1 | 1
[10 empty] | Selected based on actual Rev |  |  | 1 | 1 | 1 | 1
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 80 | 213 | 423 | 550
[10 empty] | Change from previouse iteration |  |  | 0% | 0% | 0% | 0%
[10 empty] | Assumed C for iterative purposes |  |  | 14.1421 | 38.6316 | 84.7697 | 122.9837
[10 empty] | Valve Reynolds Number | 23 |  | 11517.5627 | 18929.8207 | 28828.4485 | 34037.6701
[10 empty] | Eta, C/d2 >= 0.016 (Full area trim) | A.8a |  | 360.45 | 48.3047 | 10.0321 | 4.7663
[10 empty] | Eta, C/d2 < 0.016 (reduced trim) | A8.b |  | 23.9772 | 45.9003 | 76.8195 | 98.1671
[10 empty] | Select Eta, full or reduced trim |  |  | 360.45 | 48.3047 | 10.0321 | 4.7663
Reynolds Number Factor (FR)
[10 empty] | For laminar flow (Rev < 10) | A.6 |  | 1 | 1 | 1 | 1
[10 empty] | For transitional flow (Rev >= 10) | A.7 |  | 1 | 1 | 1 | 1
[10 empty] | Selected based on actual Rev |  |  | 1 | 1 | 1 | 1
[10 empty] | Non-turbulent flow this iteration | A.2 |  | 80 | 213 | 423 | 550
[10 empty] | Change from previouse iteration |  |  | 0% | 0% | 0% | 0%
[10 empty] | Final Reynolds Number with error hidden |  |  | 11517.5627 |  |  | 34037.6701

## Installed Flow
Intermediate Calculations
VALVE DATA | ` | [10 empty] | Scroll to the right to see the | DESCRIPTION OF VARIABLE | Eqn. | NAME OF VARIABLE | FORMULA
Valve style / model # | Neles RE | [10 empty] | intermediate calculations | CALCULATED IN COLUMN "P" |  | CALCULATED IN COLUMN "P"
Valve size | 3 inch
Relative travel, h | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 |  |  | CALCULATE PARAMETERS FOR UPSTREAM AND DOWNSTREAM PROCESS PRESSURE MODEL
C (Cv or Kv) | 5 | 12 | 23 | 39 | 61 | 88 | 121 | 165 | 246 | 420 |  |  | Minimum design flow (From Col D) |  | Q_min | 80
FL | 0.91 | 0.91 | 0.9 | 0.88 | 0.85 | 0.8 | 0.75 | 0.66 | 0.55 | 0.44 |  |  | Maximum design flow (From Col F) |  | Q_max | 550
[13 empty] | Valve inlet pressure at minimum des. Flow |  | P_1_minQ | 56.7
[12 empty] | Scroll down for instructions for the Installed flow and gain graphs and | Valve inlet pressure at maximum des. flow |  | P_1_maxQ | 46.7
[12 empty] | the calculation of the fully open flow, Qf. The accuracy of the calculations | Pressure drop at minimum des. flow |  | DELTA_P_minQ | 32
| 3 inch 0.7: Neles RE |  | on this and the Installed Gain tab depend on the accuracy of the process | Pressure drop at maximum des. flow |  | DELTA_P_maxQ | 20
| 3 inch 0.7: 3 inch |  | data. | Valve outlet pressure at minimum des. Flow |  | P_2_minQ | 24.7
| 3 inch 0.7: PV123 |  |  | Valve outlet pressure at maximum des. flow |  | P_2_maxQ | 26.7
[13 empty] | Upstream system drop |  | dp_up | 10
| 3 inch 0.7: Fully open Flow, Qf |  | INSTALED FLOW AND GAIN ERRORS | Upstream system resistance factor |  | R_up | 3.3772e-05 |  | FLOW AT EACH INCREMENT OF RELATIVE VALVE TRAVEL
| 3 inch 0.7: Qf=; 3 inch 0.8: 746.1959 |  | If there are any error messages below, the graphs and Qf are not valid | Downstream system drop |  | dp_dn | 2
[13 empty] | Downstream system resistance factor |  | R_dn | 6.7545e-06 | Relative Travel, h | 0.1 |  |  | 0.2 |  |  | 0.3 |  |  | 0.4 |  |  | 0.5 |  |  | 0.6 |  |  | 0.7 |  |  | 0.8 |  |  | 0.9 |  |  | 1
[13 empty] | Upstream system press drop an min flow |  | dpup_minQ | 0.21614 | Min C_h - Ci | 0.021776 |  |  | 0.013341 |  |  | 0.1168 |  |  | 0.041201 |  |  | 0.019779 |  |  | 0.38773 |  |  | 0.34093 |  |  | 1.3455 |  |  | 2.3398 |  |  | 0.43829
[13 empty] | Downstream system press drop an min flow |  | dpdn_minQ | 0.043229 | Flow at C_h | 28.2567 |  |  | 67.8269 |  |  | 129.5064 |  |  | 212.9903 |  |  | 317.1135 |  |  | 423.1892 |  |  | 516.3712 |  |  | 599.491 |  |  | 682.2767 |  |  | 746.1959
| 3 inch 0.7: Qmax = maximum | [6 empty] | Values found on Line | 2022 |  |  | 1010 |  |  | 757 |  |  | 592 |  |  | 482 |  |  | 361 |  |  | 262 |  |  | 207 |  |  | 185 |  |  | 141
[8 empty] | design flow = | 550
CALCULATE FLOW AT EACH INCREMENT OF h
[13 empty] | Valve C at travel h (Cv or Kv) |  | C_h | 5 |  |  | 12 |  |  | 23 |  |  | 39 |  |  | 61 |  |  | 88 |  |  | 121 |  |  | 165 |  |  | 246 |  |  | 420
Qmin = minimum
| 3 inch 0.8: design flow =; 3 inch 0.9: 80 |  |  | Caculation of flow conditions
[13 empty] | Piping geometry factor at relative travel, h | 15 | F_P_h | 0.99985 |  |  | 0.99916 |  |  | 0.99692 |  |  | 0.99122 |  |  | 0.97891 |  |  | 0.95755 |  |  | 0.92396 |  |  | 0.87084 |  |  | 0.7651 |  |  | 0.57123
Combined liquid pressure recovery factor
| 3 inch 0.8: Flow units are; 3 inch 0.9: gpm |  |  | and piping geometry factor at relative travel, h | 21 | F_LP_h | 0.90984 |  |  | 0.90908 |  |  | 0.89676 |  |  | 0.87137 |  |  | 0.83132 |  |  | 0.76845 |  |  | 0.70268 |  |  | 0.60237 |  |  | 0.48063 |  |  | 0.35034
Total iterations 421
[13 empty] | First iteration flow rate |  | Q_i | 0.8 | Abs Value of | Flow this | 28.2567 | Abs Value of | Flow this | 67.8269 | Abs Value of | Flow this | 129.5064 | Abs Value of | Flow this | 212.9903 | Abs Value of | Flow this | 317.1135 | Abs Value of | Flow this | 423.1892 | Abs Value of | Flow this | 516.3712 | Abs Value of | Flow this | 599.491 | Abs Value of | Flow this | 682.2767 | Abs Value of | Flow this
Valve relative travel, h | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | The cell below prevents an error in M20 above when viscosity and F_D are |  |  |  |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
Relative Flow Q/Qf | 0 | 0.037868 | 0.090897 | 0.17356 | 0.28543 | 0.42497 | 0.56713 | 0.692 | 0.8034 | 0.91434 | 1 | not entered in Columns D and G of the Valve Sizing tab. | P1 at this iteration flow rate |  | P1_Qi | 56.9161 |  |  | 56.8892 |  |  | 56.7608 |  |  | 56.3497 |  |  | 55.3841 |  |  | 53.52 |  |  | 50.8679 |  |  | 47.9111 |  |  | 44.7787 |  |  | 41.1951
Minimum Flow | 0.10721 | 0.10721 | 0.10721 | 0.10721 | 0.10721 | 0.10721 | 0.10721 | 0.10721 | 0.10721 | 0.10721 | 0.10721 |  | P2 at this iteration flow rate |  | P2_Qi | 24.6568 |  |  | 24.6622 |  |  | 24.6878 |  |  | 24.7701 |  |  | 24.9632 |  |  | 25.336 |  |  | 25.8664 |  |  | 26.4578 |  |  | 27.0843 |  |  | 27.801
Maximum Flow | 0.73707 | 0.73707 | 0.73707 | 0.73707 | 0.73707 | 0.73707 | 0.73707 | 0.73707 | 0.73707 | 0.73707 | 0.73707 |  | Delta P at this iteration flow rate |  | DELTA_P_Qi | 32.2593 |  |  | 32.227 |  |  | 32.0729 |  |  | 31.5797 |  |  | 30.4209 |  |  | 28.184 |  |  | 25.0015 |  |  | 21.4533 |  |  | 17.6945 |  |  | 13.3941
[13 empty] | Choked pressure drop w/ reducers | 3 | DELTA_P_CH_W_Reducers | 46.7651 |  |  | 46.7301 |  |  | 45.5721 |  |  | 43.2068 |  |  | 39.6249 |  |  | 34.1858 |  |  | 29.1657 |  |  | 22.7136 |  |  | 17.4972 |  |  | 15.3296
[13 empty] | C Non choked w/ reducers | 7 | C_N_Ch | 0.14087 |  |  | 4.9817 |  |  | 12.0136 |  |  | 23.2498 |  |  | 39.4485 |  |  | 62.3812 |  |  | 91.6003 |  |  | 128.0202 |  |  | 186.2707 |  |  | 326.3561
[13 empty] | C Choked w/ reducers | 7 | C_Ch | 0.117 |  |  | 4.137 |  |  | 10.0784 |  |  | 19.8768 |  |  | 34.5647 |  |  | 56.6411 |  |  | 84.8094 |  |  | 124.418 |  |  | 187.3176 |  |  | 305.0579
INSTRUCTIONS FOR THE OPTIONAL INSTALLED FLOW AND GAIN GRAPHS AND FULLY OPEN FLOW CALCULATION The process pressure model is a curve fit based on the Flow, P1 and Delta P in Columns D and G on the Valve Sizing tab. The curve fit is based on the principle that piping pressure losses are approximately proportional to flow squared. This model is only valid for fully turbulent flow. The Vapor pressure and specific gravity used in the installed flow calculation are the values entered in Column G on the Valve Sizing tab. To calculate the fully open flow, Qf, the installed flow and the installed gain, on the Valve Sizing tab, enter the minimum design flow along with its associated values of P1 and Delta P in Column D and the maximum design flow along with its associated values of P1 and Delta P in Column G. The accuracy of these calculations depends on the accuracy of the process data that is used. Any process conditions entered in Columns E and F are not used in the calculation of the fully open flow, the installed flow and the installed gain. The process model, Qf, and the graphs are only valid if: 1. The flow in G2 on the Valve Sizing tab is greater than the flow in D2 2. P1 is either constant or decreasing with increasing flow 3. P2 is either constant or increasing with increasing flow 4. Flow is turbulent. NOTE: Extrapolating curve-fit data beyond the limits for which the curve fit was established can be uncertain. The farther beyond the limits, the greater is the potential for uncertainty. As such, the fully open flow, the Installed Flow and the Installed Gain should be treated as approximations. | [12 empty] | Selected C this iteration |  | C_i | 0.14087 |  |  | 4.9817 |  |  | 12.0136 |  |  | 23.2498 |  |  | 39.4485 |  |  | 62.3812 |  |  | 91.6003 |  |  | 128.0202 |  |  | 187.3176 |  |  | 326.3561
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8591 | 0.8 |  | 7.0183 | 28.2567 |  | 10.9864 | 67.8269 |  | 15.7502 | 129.5064 |  | 21.5515 | 212.9903 |  | 25.6188 | 317.1135 |  | 29.3997 | 423.1892 |  | 36.9798 | 516.3712 |  | 58.6824 | 599.491 |  | 93.6439 | 682.2767
[13 empty] | Next iteration flow rate |  |  | 0.816 | Abs Value of | Flow this | 28.5392 | Abs Value of | Flow this | 68.5051 | Abs Value of | Flow this | 130.8014 | Abs Value of | Flow this | 215.1202 | Abs Value of | Flow this | 320.2846 | Abs Value of | Flow this | 427.4211 | Abs Value of | Flow this | 521.535 | Abs Value of | Flow this | 605.4859 | Abs Value of | Flow this | 689.0994 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8886 |  |  | 56.7577 |  |  | 56.3383 |  |  | 55.3533 |  |  | 53.4517 |  |  | 50.7463 |  |  | 47.7301 |  |  | 44.5347 |  |  | 40.8791
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6623 |  |  | 24.6885 |  |  | 24.7723 |  |  | 24.9693 |  |  | 25.3497 |  |  | 25.8907 |  |  | 26.494 |  |  | 27.1331 |  |  | 27.8642
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2264 |  |  | 32.0692 |  |  | 31.566 |  |  | 30.3839 |  |  | 28.102 |  |  | 24.8556 |  |  | 21.2361 |  |  | 17.4017 |  |  | 13.0149
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7296 |  |  | 45.5696 |  |  | 43.198 |  |  | 39.6027 |  |  | 34.1418 |  |  | 29.0953 |  |  | 22.627 |  |  | 17.4009 |  |  | 15.2108
[13 empty] | C Non choked w/ reducers | 7 |  | 0.14369 |  |  | 5.0316 |  |  | 12.1344 |  |  | 23.4874 |  |  | 39.8672 |  |  | 63.0968 |  |  | 92.7875 |  |  | 129.96 |  |  | 189.7093 |  |  | 334.3869
[13 empty] | C Choked w/ reducers | 7 |  | 0.11934 |  |  | 4.1784 |  |  | 10.1795 |  |  | 20.0776 |  |  | 34.9201 |  |  | 57.2444 |  |  | 85.7609 |  |  | 125.9024 |  |  | 189.7134 |  |  | 309.3099
[13 empty] | Selected C this iteration |  |  | 0.14369 |  |  | 5.0316 |  |  | 12.1344 |  |  | 23.4874 |  |  | 39.8672 |  |  | 63.0968 |  |  | 92.7875 |  |  | 129.96 |  |  | 189.7134 |  |  | 334.3869
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8563 | 0.816 |  | 6.9684 | 28.5392 |  | 10.8656 | 68.5051 |  | 15.5126 | 130.8014 |  | 21.1328 | 215.1202 |  | 24.9032 | 320.2846 |  | 28.2125 | 427.4211 |  | 35.04 | 521.535 |  | 56.2866 | 605.4859 |  | 85.6131 | 689.0994
[13 empty] | Next iteration flow rate |  |  | 0.83232 | Abs Value of | Flow this | 28.8246 | Abs Value of | Flow this | 69.1902 | Abs Value of | Flow this | 132.1094 | Abs Value of | Flow this | 217.2714 | Abs Value of | Flow this | 323.4875 | Abs Value of | Flow this | 431.6953 | Abs Value of | Flow this | 526.7503 | Abs Value of | Flow this | 611.5408 | Abs Value of | Flow this | 695.9904 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8881 |  |  | 56.7545 |  |  | 56.3267 |  |  | 55.3219 |  |  | 53.3821 |  |  | 50.6223 |  |  | 47.5455 |  |  | 44.2859 |  |  | 40.5567
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6624 |  |  | 24.6891 |  |  | 24.7747 |  |  | 24.9756 |  |  | 25.3636 |  |  | 25.9155 |  |  | 26.5309 |  |  | 27.1828 |  |  | 27.9287
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2257 |  |  | 32.0654 |  |  | 31.5521 |  |  | 30.3462 |  |  | 28.0185 |  |  | 24.7068 |  |  | 21.0146 |  |  | 17.1031 |  |  | 12.6281
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7292 |  |  | 45.567 |  |  | 43.1891 |  |  | 39.5801 |  |  | 34.097 |  |  | 29.0236 |  |  | 22.5386 |  |  | 17.3027 |  |  | 15.0895
[13 empty] | C Non choked w/ reducers | 7 |  | 0.14656 |  |  | 5.0819 |  |  | 12.2565 |  |  | 23.7275 |  |  | 40.2909 |  |  | 63.8227 |  |  | 93.9971 |  |  | 131.9498 |  |  | 193.272 |  |  | 342.8644
[13 empty] | C Choked w/ reducers | 7 |  | 0.12173 |  |  | 4.2202 |  |  | 10.2816 |  |  | 20.2805 |  |  | 35.2794 |  |  | 57.8548 |  |  | 86.7255 |  |  | 127.4104 |  |  | 192.1535 |  |  | 313.6556
[13 empty] | Selected C this iteration |  |  | 0.14656 |  |  | 5.0819 |  |  | 12.2565 |  |  | 23.7275 |  |  | 40.2909 |  |  | 63.8227 |  |  | 93.9971 |  |  | 131.9498 |  |  | 193.272 |  |  | 342.8644
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8534 | 0.83232 |  | 6.9181 | 28.8246 |  | 10.7435 | 69.1902 |  | 15.2725 | 132.1094 |  | 20.7091 | 217.2714 |  | 24.1773 | 323.4875 |  | 27.0029 | 431.6953 |  | 33.0502 | 526.7503 |  | 52.728 | 611.5408 |  | 77.1356 | 695.9904
[13 empty] | Next iteration flow rate |  |  | 0.84897 | Abs Value of | Flow this | 29.1129 | Abs Value of | Flow this | 69.8821 | Abs Value of | Flow this | 133.4305 | Abs Value of | Flow this | 219.4441 | Abs Value of | Flow this | 326.7224 | Abs Value of | Flow this | 436.0123 | Abs Value of | Flow this | 532.0178 | Abs Value of | Flow this | 617.6562 | Abs Value of | Flow this | 702.9503 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8875 |  |  | 56.7512 |  |  | 56.3149 |  |  | 55.2898 |  |  | 53.311 |  |  | 50.4958 |  |  | 47.3571 |  |  | 44.032 |  |  | 40.2279
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6625 |  |  | 24.6898 |  |  | 24.777 |  |  | 24.982 |  |  | 25.3778 |  |  | 25.9408 |  |  | 26.5686 |  |  | 27.2336 |  |  | 27.9944
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.225 |  |  | 32.0615 |  |  | 31.5378 |  |  | 30.3078 |  |  | 27.9332 |  |  | 24.5549 |  |  | 20.7885 |  |  | 16.7984 |  |  | 12.2335
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7287 |  |  | 45.5644 |  |  | 43.1799 |  |  | 39.557 |  |  | 34.0512 |  |  | 28.9504 |  |  | 22.4485 |  |  | 17.2026 |  |  | 14.9658
[13 empty] | C Non choked w/ reducers | 7 |  | 0.14949 |  |  | 5.1328 |  |  | 12.3798 |  |  | 23.9702 |  |  | 40.7196 |  |  | 64.5592 |  |  | 95.2301 |  |  | 133.9918 |  |  | 196.9668 |  |  | 351.8335
[13 empty] | C Choked w/ reducers | 7 |  | 0.12416 |  |  | 4.2624 |  |  | 10.3847 |  |  | 20.4855 |  |  | 35.6426 |  |  | 58.4726 |  |  | 87.7034 |  |  | 128.9426 |  |  | 194.6394 |  |  | 318.0985
[13 empty] | Selected C this iteration |  |  | 0.14949 |  |  | 5.1328 |  |  | 12.3798 |  |  | 23.9702 |  |  | 40.7196 |  |  | 64.5592 |  |  | 95.2301 |  |  | 133.9918 |  |  | 196.9668 |  |  | 351.8335
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8505 | 0.84897 |  | 6.8672 | 29.1129 |  | 10.6202 | 69.8821 |  | 15.0298 | 133.4305 |  | 20.2804 | 219.4441 |  | 23.4408 | 326.7224 |  | 25.7699 | 436.0123 |  | 31.0082 | 532.0178 |  | 49.0332 | 617.6562 |  | 68.1665 | 702.9503
[13 empty] | Next iteration flow rate |  |  | 0.86595 | Abs Value of | Flow this | 29.404 | Abs Value of | Flow this | 70.5809 | Abs Value of | Flow this | 134.7648 | Abs Value of | Flow this | 221.6385 | Abs Value of | Flow this | 329.9896 | Abs Value of | Flow this | 440.3724 | Abs Value of | Flow this | 537.338 | Abs Value of | Flow this | 623.8327 | Abs Value of | Flow this | 709.9798 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8869 |  |  | 56.7479 |  |  | 56.3028 |  |  | 55.2571 |  |  | 53.2386 |  |  | 50.3667 |  |  | 47.165 |  |  | 43.773 |  |  | 39.8925
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6626 |  |  | 24.6904 |  |  | 24.7794 |  |  | 24.9886 |  |  | 25.3923 |  |  | 25.9667 |  |  | 26.607 |  |  | 27.2854 |  |  | 28.0615
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2243 |  |  | 32.0575 |  |  | 31.5233 |  |  | 30.2685 |  |  | 27.8463 |  |  | 24.4001 |  |  | 20.558 |  |  | 16.4876 |  |  | 11.8309
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7282 |  |  | 45.5617 |  |  | 43.1706 |  |  | 39.5334 |  |  | 34.0046 |  |  | 28.8758 |  |  | 22.3566 |  |  | 17.1004 |  |  | 14.8397
[13 empty] | C Non choked w/ reducers | 7 |  | 0.15248 |  |  | 5.1842 |  |  | 12.5044 |  |  | 24.2154 |  |  | 41.1535 |  |  | 65.3065 |  |  | 96.4872 |  |  | 136.0885 |  |  | 200.8025 |  |  | 361.3463
[13 empty] | C Choked w/ reducers | 7 |  | 0.12665 |  |  | 4.3051 |  |  | 10.4888 |  |  | 20.6926 |  |  | 36.0098 |  |  | 59.0979 |  |  | 88.6948 |  |  | 130.4995 |  |  | 197.1723 |  |  | 322.6424
[13 empty] | Selected C this iteration |  |  | 0.15248 |  |  | 5.1842 |  |  | 12.5044 |  |  | 24.2154 |  |  | 41.1535 |  |  | 65.3065 |  |  | 96.4872 |  |  | 136.0885 |  |  | 200.8025 |  |  | 361.3463
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8475 | 0.86595 |  | 6.8158 | 29.404 |  | 10.4956 | 70.5809 |  | 14.7846 | 134.7648 |  | 19.8465 | 221.6385 |  | 22.6935 | 329.9896 |  | 24.5128 | 440.3724 |  | 28.9115 | 537.338 |  | 45.1975 | 623.8327 |  | 58.6537 | 709.9798
[13 empty] | Next iteration flow rate |  |  | 0.88326 | Abs Value of | Flow this | 29.698 | Abs Value of | Flow this | 71.2867 | Abs Value of | Flow this | 136.1125 | Abs Value of | Flow this | 223.8549 | Abs Value of | Flow this | 333.2895 | Abs Value of | Flow this | 444.7761 | Abs Value of | Flow this | 542.7114 | Abs Value of | Flow this | 630.071 | Abs Value of | Flow this | 717.0796 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8864 |  |  | 56.7445 |  |  | 56.2905 |  |  | 55.2238 |  |  | 53.1646 |  |  | 50.2351 |  |  | 46.969 |  |  | 43.5089 |  |  | 39.5503
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6627 |  |  | 24.6911 |  |  | 24.7819 |  |  | 24.9952 |  |  | 25.4071 |  |  | 25.993 |  |  | 26.6462 |  |  | 27.3382 |  |  | 28.1299
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2236 |  |  | 32.0534 |  |  | 31.5085 |  |  | 30.2285 |  |  | 27.7576 |  |  | 24.2421 |  |  | 20.3228 |  |  | 16.1706 |  |  | 11.4203
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7278 |  |  | 45.559 |  |  | 43.161 |  |  | 39.5093 |  |  | 33.957 |  |  | 28.7997 |  |  | 22.2628 |  |  | 16.9961 |  |  | 14.711
[13 empty] | C Non choked w/ reducers | 7 |  | 0.15553 |  |  | 5.2361 |  |  | 12.6302 |  |  | 24.4633 |  |  | 41.5925 |  |  | 66.0649 |  |  | 97.769 |  |  | 138.2424 |  |  | 204.7889 |  |  | 371.4628
[13 empty] | C Choked w/ reducers | 7 |  | 0.12918 |  |  | 4.3482 |  |  | 10.5941 |  |  | 20.9018 |  |  | 36.3809 |  |  | 59.7307 |  |  | 89.7001 |  |  | 132.0818 |  |  | 199.7538 |  |  | 327.2913
[13 empty] | Selected C this iteration |  |  | 0.15553 |  |  | 5.2361 |  |  | 12.6302 |  |  | 24.4633 |  |  | 41.5925 |  |  | 66.0649 |  |  | 97.769 |  |  | 138.2424 |  |  | 204.7889 |  |  | 371.4628
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8445 | 0.88326 |  | 6.7639 | 29.698 |  | 10.3698 | 71.2867 |  | 14.5367 | 136.1125 |  | 19.4075 | 223.8549 |  | 21.9351 | 333.2895 |  | 23.231 | 444.7761 |  | 26.7576 | 542.7114 |  | 41.2111 | 630.071 |  | 48.5372 | 717.0796
[13 empty] | Next iteration flow rate |  |  | 0.90093 | Abs Value of | Flow this | 29.995 | Abs Value of | Flow this | 71.9996 | Abs Value of | Flow this | 137.4736 | Abs Value of | Flow this | 226.0935 | Abs Value of | Flow this | 336.6224 | Abs Value of | Flow this | 449.2239 | Abs Value of | Flow this | 548.1385 | Abs Value of | Flow this | 636.3718 | Abs Value of | Flow this | 724.2504 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8858 |  |  | 56.7411 |  |  | 56.2779 |  |  | 55.1898 |  |  | 53.0892 |  |  | 50.1008 |  |  | 46.769 |  |  | 43.2394 |  |  | 39.2012
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6628 |  |  | 24.6918 |  |  | 24.7844 |  |  | 25.002 |  |  | 25.4222 |  |  | 26.0198 |  |  | 26.6862 |  |  | 27.3921 |  |  | 28.1998
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2229 |  |  | 32.0493 |  |  | 31.4935 |  |  | 30.1877 |  |  | 27.6671 |  |  | 24.081 |  |  | 20.0828 |  |  | 15.8473 |  |  | 11.0015
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7273 |  |  | 45.5562 |  |  | 43.1513 |  |  | 39.4848 |  |  | 33.9084 |  |  | 28.722 |  |  | 22.1671 |  |  | 16.8898 |  |  | 14.5797
[13 empty] | C Non choked w/ reducers | 7 |  | 0.15865 |  |  | 5.2885 |  |  | 12.7574 |  |  | 24.7139 |  |  | 42.0368 |  |  | 66.8346 |  |  | 99.0766 |  |  | 140.4564 |  |  | 208.9365 |  |  | 382.2528
[13 empty] | C Choked w/ reducers | 7 |  | 0.13176 |  |  | 4.3917 |  |  | 10.7003 |  |  | 21.1132 |  |  | 36.7561 |  |  | 60.3712 |  |  | 90.7195 |  |  | 133.6902 |  |  | 202.3856 |  |  | 332.0492
[13 empty] | Selected C this iteration |  |  | 0.15865 |  |  | 5.2885 |  |  | 12.7574 |  |  | 24.7139 |  |  | 42.0368 |  |  | 66.8346 |  |  | 99.0766 |  |  | 140.4564 |  |  | 208.9365 |  |  | 382.2528
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8414 | 0.90093 |  | 6.7115 | 29.995 |  | 10.2426 | 71.9996 |  | 14.2861 | 137.4736 |  | 18.9632 | 226.0935 |  | 21.1654 | 336.6224 |  | 21.9234 | 449.2239 |  | 24.5436 | 548.1385 |  | 37.0635 | 636.3718 |  | 37.7472 | 724.2504
[13 empty] | Next iteration flow rate |  |  | 0.91895 | Abs Value of | Flow this | 30.295 | Abs Value of | Flow this | 72.7196 | Abs Value of | Flow this | 138.8483 | Abs Value of | Flow this | 228.3544 | Abs Value of | Flow this | 339.9886 | Abs Value of | Flow this | 453.7161 | Abs Value of | Flow this | 553.6199 | Abs Value of | Flow this | 642.7355 | Abs Value of | Flow this | 731.4929 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8851 |  |  | 56.7376 |  |  | 56.2651 |  |  | 55.1551 |  |  | 53.0123 |  |  | 49.9638 |  |  | 46.5651 |  |  | 42.9645 |  |  | 38.8452
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.663 |  |  | 24.6925 |  |  | 24.787 |  |  | 25.009 |  |  | 25.4375 |  |  | 26.0472 |  |  | 26.727 |  |  | 27.4471 |  |  | 28.271
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2222 |  |  | 32.0451 |  |  | 31.4781 |  |  | 30.1461 |  |  | 27.5748 |  |  | 23.9166 |  |  | 19.8381 |  |  | 15.5174 |  |  | 10.5742
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7268 |  |  | 45.5533 |  |  | 43.1414 |  |  | 39.4598 |  |  | 33.8588 |  |  | 28.6428 |  |  | 22.0695 |  |  | 16.7813 |  |  | 14.4457
[13 empty] | C Non choked w/ reducers | 7 |  | 0.16182 |  |  | 5.3414 |  |  | 12.8858 |  |  | 24.9671 |  |  | 42.4865 |  |  | 67.6158 |  |  | 100.4107 |  |  | 142.7334 |  |  | 213.2571 |  |  | 393.7984
[13 empty] | C Choked w/ reducers | 7 |  | 0.1344 |  |  | 4.4356 |  |  | 10.8077 |  |  | 21.3268 |  |  | 37.1355 |  |  | 61.0195 |  |  | 91.7533 |  |  | 135.3253 |  |  | 205.0691 |  |  | 336.9208
[13 empty] | Selected C this iteration |  |  | 0.16182 |  |  | 5.3414 |  |  | 12.8858 |  |  | 24.9671 |  |  | 42.4865 |  |  | 67.6158 |  |  | 100.4107 |  |  | 142.7334 |  |  | 213.2571 |  |  | 393.7984
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8382 | 0.91895 |  | 6.6586 | 30.295 |  | 10.1142 | 72.7196 |  | 14.0329 | 138.8483 |  | 18.5135 | 228.3544 |  | 20.3842 | 339.9886 |  | 20.5893 | 453.7161 |  | 22.2666 | 553.6199 |  | 32.7429 | 642.7355 |  | 26.2016 | 731.4929
[13 empty] | Next iteration flow rate |  |  | 0.93733 | Abs Value of | Flow this | 30.5979 | Abs Value of | Flow this | 73.4468 | Abs Value of | Flow this | 140.2368 | Abs Value of | Flow this | 230.638 | Abs Value of | Flow this | 343.3885 | Abs Value of | Flow this | 458.2533 | Abs Value of | Flow this | 559.1561 | Abs Value of | Flow this | 649.1628 | Abs Value of | Flow this | 738.8079 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8845 |  |  | 56.734 |  |  | 56.252 |  |  | 55.1197 |  |  | 52.9339 |  |  | 49.8241 |  |  | 46.357 |  |  | 42.684 |  |  | 38.4819
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6631 |  |  | 24.6932 |  |  | 24.7896 |  |  | 25.0161 |  |  | 25.4532 |  |  | 26.0752 |  |  | 26.7686 |  |  | 27.5032 |  |  | 28.3436
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2214 |  |  | 32.0408 |  |  | 31.4624 |  |  | 30.1036 |  |  | 27.4806 |  |  | 23.7489 |  |  | 19.5884 |  |  | 15.1809 |  |  | 10.1383
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7262 |  |  | 45.5504 |  |  | 43.1313 |  |  | 39.4342 |  |  | 33.8083 |  |  | 28.562 |  |  | 21.97 |  |  | 16.6706 |  |  | 14.3091
[13 empty] | C Non choked w/ reducers | 7 |  | 0.16505 |  |  | 5.3949 |  |  | 13.0155 |  |  | 25.2231 |  |  | 42.9416 |  |  | 68.4089 |  |  | 101.7722 |  |  | 145.0765 |  |  | 217.7639 |  |  | 406.1963
[13 empty] | C Choked w/ reducers | 7 |  | 0.13709 |  |  | 4.48 |  |  | 10.9161 |  |  | 21.5426 |  |  | 37.519 |  |  | 61.6757 |  |  | 92.8019 |  |  | 136.9878 |  |  | 207.8061 |  |  | 341.9107
[13 empty] | Selected C this iteration |  |  | 0.16505 |  |  | 5.3949 |  |  | 13.0155 |  |  | 25.2231 |  |  | 42.9416 |  |  | 68.4089 |  |  | 101.7722 |  |  | 145.0765 |  |  | 217.7639 |  |  | 406.1963
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8349 | 0.93733 |  | 6.6051 | 30.5979 |  | 9.9845 | 73.4468 |  | 13.7769 | 140.2368 |  | 18.0584 | 230.638 |  | 19.5911 | 343.3885 |  | 19.2278 | 458.2533 |  | 19.9235 | 559.1561 |  | 28.2361 | 649.1628 |  | 13.8037 | 738.8079
[13 empty] | Next iteration flow rate |  |  | 0.95607 | Abs Value of | Flow this | 30.9039 | Abs Value of | Flow this | 74.1813 | Abs Value of | Flow this | 141.6392 | Abs Value of | Flow this | 232.9443 | Abs Value of | Flow this | 346.8224 | Abs Value of | Flow this | 462.8358 | Abs Value of | Flow this | 564.7476 | Abs Value of | Flow this | 655.6545 | Abs Value of | Flow this | 746.1959 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8839 |  |  | 56.7303 |  |  | 56.2386 |  |  | 55.0836 |  |  | 52.8538 |  |  | 49.6815 |  |  | 46.1448 |  |  | 42.398 |  |  | 38.1114
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6632 |  |  | 24.6939 |  |  | 24.7923 |  |  | 25.0233 |  |  | 25.4692 |  |  | 26.1037 |  |  | 26.811 |  |  | 27.5604 |  |  | 28.4177
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2207 |  |  | 32.0364 |  |  | 31.4463 |  |  | 30.0603 |  |  | 27.3846 |  |  | 23.5778 |  |  | 19.3337 |  |  | 14.8376 |  |  | 9.6937
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7257 |  |  | 45.5474 |  |  | 43.121 |  |  | 39.4082 |  |  | 33.7568 |  |  | 28.4795 |  |  | 21.8684 |  |  | 16.5577 |  |  | 14.1697
[13 empty] | C Non choked w/ reducers | 7 |  | 0.16836 |  |  | 5.4489 |  |  | 13.1466 |  |  | 25.4818 |  |  | 43.4023 |  |  | 69.214 |  |  | 103.1621 |  |  | 147.4892 |  |  | 222.4712 |  |  | 419.5617
[13 empty] | C Choked w/ reducers | 7 |  | 0.13983 |  |  | 4.5248 |  |  | 11.0256 |  |  | 21.7606 |  |  | 37.9067 |  |  | 62.34 |  |  | 93.8655 |  |  | 138.6786 |  |  | 210.5984 |  |  | 347.024
[13 empty] | Selected C this iteration |  |  | 0.16836 |  |  | 5.4489 |  |  | 13.1466 |  |  | 25.4818 |  |  | 43.4023 |  |  | 69.214 |  |  | 103.1621 |  |  | 147.4892 |  |  | 222.4712 |  |  | 419.5617
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8316 | 0.95607 |  | 6.5511 | 30.9039 |  | 9.8534 | 74.1813 |  | 13.5182 | 141.6392 |  | 17.5977 | 232.9443 |  | 18.786 | 346.8224 |  | 17.8379 | 462.8358 |  | 17.5108 | 564.7476 |  | 23.5288 | 655.6545 |  | 0.43829 | 746.1959
[13 empty] | Next iteration flow rate |  |  | 0.9752 | Abs Value of | Flow this | 31.2129 | Abs Value of | Flow this | 74.9231 | Abs Value of | Flow this | 143.0556 | Abs Value of | Flow this | 235.2738 | Abs Value of | Flow this | 350.2906 | Abs Value of | Flow this | 467.4642 | Abs Value of | Flow this | 570.3951 | Abs Value of | Flow this | 662.211 | Abs Value of | Flow this | 753.6579 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8832 |  |  | 56.7266 |  |  | 56.225 |  |  | 55.0467 |  |  | 52.7722 |  |  | 49.5361 |  |  | 45.9283 |  |  | 42.1062 |  |  | 37.7334
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6634 |  |  | 24.6947 |  |  | 24.795 |  |  | 25.0307 |  |  | 25.4856 |  |  | 26.1328 |  |  | 26.8543 |  |  | 27.6188 |  |  | 28.4933
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2199 |  |  | 32.0319 |  |  | 31.43 |  |  | 30.0161 |  |  | 27.2866 |  |  | 23.4033 |  |  | 19.0739 |  |  | 14.4874 |  |  | 9.2401
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7252 |  |  | 45.5444 |  |  | 43.1104 |  |  | 39.3816 |  |  | 33.7042 |  |  | 28.3954 |  |  | 21.7648 |  |  | 16.4426 |  |  | 14.0276
[13 empty] | C Non choked w/ reducers | 7 |  | 0.17172 |  |  | 5.5035 |  |  | 13.279 |  |  | 25.7433 |  |  | 43.8686 |  |  | 70.0316 |  |  | 104.5814 |  |  | 149.9752 |  |  | 227.3953 |  |  | 434.0332
[13 empty] | C Choked w/ reducers | 7 |  | 0.14262 |  |  | 4.5701 |  |  | 11.1362 |  |  | 21.9809 |  |  | 38.2987 |  |  | 63.0125 |  |  | 94.9444 |  |  | 140.3983 |  |  | 213.4479 |  |  | 352.2659
[13 empty] | Selected C this iteration |  |  | 0.17172 |  |  | 5.5035 |  |  | 13.279 |  |  | 25.7433 |  |  | 43.8686 |  |  | 70.0316 |  |  | 104.5814 |  |  | 149.9752 |  |  | 227.3953 |  |  | 434.0332
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8283 | 0.9752 |  | 6.4965 | 31.2129 |  | 9.721 | 74.9231 |  | 13.2567 | 143.0556 |  | 17.1314 | 235.2738 |  | 17.9684 | 350.2906 |  | 16.4186 | 467.4642 |  | 15.0248 | 570.3951 |  | 18.6047 | 662.211 |  | 14.0332 | 753.6579
[13 empty] | Next iteration flow rate |  |  | 0.9947 | Abs Value of | Flow this | 31.5251 | Abs Value of | Flow this | 75.6723 | Abs Value of | Flow this | 144.4861 | Abs Value of | Flow this | 237.6265 | Abs Value of | Flow this | 353.7935 | Abs Value of | Flow this | 472.1388 | Abs Value of | Flow this | 576.0991 | Abs Value of | Flow this | 668.8331 | Abs Value of | Flow this | 761.1945 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8826 |  |  | 56.7228 |  |  | 56.2111 |  |  | 55.0091 |  |  | 52.6889 |  |  | 49.3878 |  |  | 45.7074 |  |  | 41.8085 |  |  | 37.3479
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6635 |  |  | 24.6954 |  |  | 24.7978 |  |  | 25.0382 |  |  | 25.5022 |  |  | 26.1624 |  |  | 26.8985 |  |  | 27.6783 |  |  | 28.5704
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2191 |  |  | 32.0273 |  |  | 31.4133 |  |  | 29.971 |  |  | 27.1866 |  |  | 23.2253 |  |  | 18.8089 |  |  | 14.1302 |  |  | 8.7774
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7246 |  |  | 45.5413 |  |  | 43.0997 |  |  | 39.3545 |  |  | 33.6505 |  |  | 28.3096 |  |  | 21.6592 |  |  | 16.3251 |  |  | 13.8825
[13 empty] | C Non choked w/ reducers | 7 |  | 0.17516 |  |  | 5.5586 |  |  | 13.4127 |  |  | 26.0076 |  |  | 44.3406 |  |  | 70.8618 |  |  | 106.0313 |  |  | 152.5384 |  |  | 232.5542 |  |  | 449.7793
[13 empty] | C Choked w/ reducers | 7 |  | 0.14548 |  |  | 4.6158 |  |  | 11.248 |  |  | 22.2035 |  |  | 38.695 |  |  | 63.6933 |  |  | 96.0391 |  |  | 142.1478 |  |  | 216.3567 |  |  | 357.6422
[13 empty] | Selected C this iteration |  |  | 0.17516 |  |  | 5.5586 |  |  | 13.4127 |  |  | 26.0076 |  |  | 44.3406 |  |  | 70.8618 |  |  | 106.0313 |  |  | 152.5384 |  |  | 232.5542 |  |  | 449.7793
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8248 | 0.9947 |  | 6.4414 | 31.5251 |  | 9.5873 | 75.6723 |  | 12.9924 | 144.4861 |  | 16.6594 | 237.6265 |  | 17.1382 | 353.7935 |  | 14.9687 | 472.1388 |  | 12.4616 | 576.0991 |  | 13.4458 | 668.8331 |  | 29.7793 | 761.1945
[13 empty] | Next iteration flow rate |  |  | 1.0146 | Abs Value of | Flow this | 31.8403 | Abs Value of | Flow this | 76.429 | Abs Value of | Flow this | 145.931 | Abs Value of | Flow this | 240.0028 | Abs Value of | Flow this | 357.3314 | Abs Value of | Flow this | 476.8602 | Abs Value of | Flow this | 581.86 | Abs Value of | Flow this | 675.5214 | Abs Value of | Flow this | 768.8064 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8819 |  |  | 56.7189 |  |  | 56.1969 |  |  | 54.9708 |  |  | 52.6039 |  |  | 49.2365 |  |  | 45.4821 |  |  | 41.5048 |  |  | 36.9545
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6636 |  |  | 24.6962 |  |  | 24.8006 |  |  | 25.0458 |  |  | 25.5192 |  |  | 26.1927 |  |  | 26.9436 |  |  | 27.739 |  |  | 28.6491
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2183 |  |  | 32.0226 |  |  | 31.3963 |  |  | 29.925 |  |  | 27.0847 |  |  | 23.0437 |  |  | 18.5386 |  |  | 13.7658 |  |  | 8.3054
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7241 |  |  | 45.5382 |  |  | 43.0888 |  |  | 39.3269 |  |  | 33.5958 |  |  | 28.2221 |  |  | 21.5514 |  |  | 16.2053 |  |  | 13.7346
[13 empty] | C Non choked w/ reducers | 7 |  | 0.17866 |  |  | 5.6143 |  |  | 13.5478 |  |  | 26.2748 |  |  | 44.8184 |  |  | 71.705 |  |  | 107.5127 |  |  | 155.1831 |  |  | 237.9682 |  |  | 467.0067
[13 empty] | C Choked w/ reducers | 7 |  | 0.14839 |  |  | 4.662 |  |  | 11.3608 |  |  | 22.4283 |  |  | 39.0956 |  |  | 64.3826 |  |  | 97.1497 |  |  | 143.9279 |  |  | 219.3267 |  |  | 363.1588
[13 empty] | Selected C this iteration |  |  | 0.17866 |  |  | 5.6143 |  |  | 13.5478 |  |  | 26.2748 |  |  | 44.8184 |  |  | 71.705 |  |  | 107.5127 |  |  | 155.1831 |  |  | 237.9682 |  |  | 467.0067
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8213 | 1.0146 |  | 6.3857 | 31.8403 |  | 9.4522 | 76.429 |  | 12.7252 | 145.931 |  | 16.1816 | 240.0028 |  | 16.295 | 357.3314 |  | 13.4873 | 476.8602 |  | 9.8169 | 581.86 |  | 8.0318 | 675.5214 |  | 47.0067 | 768.8064
[13 empty] | Next iteration flow rate |  |  | 1.0349 | Abs Value of | Flow this | 32.1587 | Abs Value of | Flow this | 77.1933 | Abs Value of | Flow this | 147.3903 | Abs Value of | Flow this | 242.4028 | Abs Value of | Flow this | 360.9047 | Abs Value of | Flow this | 481.6288 | Abs Value of | Flow this | 587.6786 | Abs Value of | Flow this | 682.2767 | Abs Value of | Flow this | 776.4945 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8812 |  |  | 56.7149 |  |  | 56.1825 |  |  | 54.9317 |  |  | 52.5172 |  |  | 49.0821 |  |  | 45.2523 |  |  | 41.1951 |  |  | 36.5533
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6638 |  |  | 24.697 |  |  | 24.8035 |  |  | 25.0537 |  |  | 25.5366 |  |  | 26.2236 |  |  | 26.9895 |  |  | 27.801 |  |  | 28.7293
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2175 |  |  | 32.0179 |  |  | 31.379 |  |  | 29.878 |  |  | 26.9807 |  |  | 22.8585 |  |  | 18.2628 |  |  | 13.3941 |  |  | 7.824
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7235 |  |  | 45.535 |  |  | 43.0776 |  |  | 39.2987 |  |  | 33.54 |  |  | 28.1328 |  |  | 21.4414 |  |  | 16.083 |  |  | 13.5837
[13 empty] | C Non choked w/ reducers | 7 |  | 0.18223 |  |  | 5.6705 |  |  | 13.6843 |  |  | 26.5449 |  |  | 45.3021 |  |  | 72.5615 |  |  | 109.0269 |  |  | 157.9139 |  |  | 243.6602 |  |  | 485.9732
[13 empty] | C Choked w/ reducers | 7 |  | 0.15135 |  |  | 4.7087 |  |  | 11.4749 |  |  | 22.6556 |  |  | 39.5008 |  |  | 65.0806 |  |  | 98.2768 |  |  | 145.7394 |  |  | 222.3602 |  |  | 368.8224
[13 empty] | Selected C this iteration |  |  | 0.18223 |  |  | 5.6705 |  |  | 13.6843 |  |  | 26.5449 |  |  | 45.3021 |  |  | 72.5615 |  |  | 109.0269 |  |  | 157.9139 |  |  | 243.6602 |  |  | 485.9732
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8178 | 1.0349 |  | 6.3295 | 32.1587 |  | 9.3157 | 77.1933 |  | 12.4551 | 147.3903 |  | 15.6979 | 242.4028 |  | 15.4385 | 360.9047 |  | 11.9731 | 481.6288 |  | 7.0861 | 587.6786 |  | 2.3398 | 682.2767 |  | 65.9732 | 776.4945
[13 empty] | Next iteration flow rate |  |  | 1.0556 | Abs Value of | Flow this | 32.4803 | Abs Value of | Flow this | 77.9652 | Abs Value of | Flow this | 148.8642 | Abs Value of | Flow this | 244.8268 | Abs Value of | Flow this | 364.5138 | Abs Value of | Flow this | 486.4451 | Abs Value of | Flow this | 593.5554 | Abs Value of | Flow this | 689.0994 | Abs Value of | Flow this | 784.2594 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8805 |  |  | 56.7109 |  |  | 56.1677 |  |  | 54.8918 |  |  | 52.4288 |  |  | 48.9246 |  |  | 45.0179 |  |  | 40.8791 |  |  | 36.144
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6639 |  |  | 24.6978 |  |  | 24.8065 |  |  | 25.0616 |  |  | 25.5542 |  |  | 26.2551 |  |  | 27.0364 |  |  | 27.8642 |  |  | 28.8112
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2166 |  |  | 32.013 |  |  | 31.3613 |  |  | 29.8302 |  |  | 26.8746 |  |  | 22.6696 |  |  | 17.9814 |  |  | 13.0149 |  |  | 7.3328
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7229 |  |  | 45.5317 |  |  | 43.0662 |  |  | 39.2699 |  |  | 33.483 |  |  | 28.0417 |  |  | 21.3292 |  |  | 15.9583 |  |  | 13.4297
[13 empty] | C Non choked w/ reducers | 7 |  | 0.18588 |  |  | 5.7272 |  |  | 13.8222 |  |  | 26.8179 |  |  | 45.7918 |  |  | 73.4317 |  |  | 110.5751 |  |  | 160.7359 |  |  | 249.6562 |  |  | 507.0045
[13 empty] | C Choked w/ reducers | 7 |  | 0.15438 |  |  | 4.7558 |  |  | 11.59 |  |  | 22.8851 |  |  | 39.9104 |  |  | 65.7872 |  |  | 99.4206 |  |  | 147.5834 |  |  | 225.4596 |  |  | 374.6397
[13 empty] | Selected C this iteration |  |  | 0.18588 |  |  | 5.7272 |  |  | 13.8222 |  |  | 26.8179 |  |  | 45.7918 |  |  | 73.4317 |  |  | 110.5751 |  |  | 160.7359 |  |  | 249.6562 |  |  | 507.0045
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8141 | 1.0556 |  | 6.2728 | 32.4803 |  | 9.1778 | 77.9652 |  | 12.1821 | 148.8642 |  | 15.2082 | 244.8268 |  | 14.5683 | 364.5138 |  | 10.4249 | 486.4451 |  | 4.2641 | 593.5554 |  | 3.6562 | 689.0994 |  | 87.0045 | 784.2594
[13 empty] | Next iteration flow rate |  |  | 1.0767 | Abs Value of | Flow this | 32.8051 | Abs Value of | Flow this | 78.7449 | Abs Value of | Flow this | 150.3529 | Abs Value of | Flow this | 247.2751 | Abs Value of | Flow this | 368.1589 | Abs Value of | Flow this | 491.3095 | Abs Value of | Flow this | 599.491 | Abs Value of | Flow this | 695.9904 | Abs Value of | Flow this | 792.102 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8798 |  |  | 56.7067 |  |  | 56.1527 |  |  | 54.8511 |  |  | 52.3386 |  |  | 48.764 |  |  | 44.7787 |  |  | 40.5567 |  |  | 35.7265
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.664 |  |  | 24.6987 |  |  | 24.8095 |  |  | 25.0698 |  |  | 25.5723 |  |  | 26.2872 |  |  | 27.0843 |  |  | 27.9287 |  |  | 28.8947
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2158 |  |  | 32.0081 |  |  | 31.3432 |  |  | 29.7814 |  |  | 26.7663 |  |  | 22.4768 |  |  | 17.6945 |  |  | 12.6281 |  |  | 6.8318
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7223 |  |  | 45.5284 |  |  | 43.0546 |  |  | 39.2406 |  |  | 33.4249 |  |  | 27.9488 |  |  | 21.2148 |  |  | 15.8311 |  |  | 13.2727
[13 empty] | C Non choked w/ reducers | 7 |  | 0.1896 |  |  | 5.7846 |  |  | 13.9615 |  |  | 27.0939 |  |  | 46.2876 |  |  | 74.3158 |  |  | 112.1588 |  |  | 163.6545 |  |  | 255.9855 |  |  | 530.5194
[13 empty] | C Choked w/ reducers | 7 |  | 0.15747 |  |  | 4.8034 |  |  | 11.7064 |  |  | 23.1171 |  |  | 40.3245 |  |  | 66.5028 |  |  | 100.5816 |  |  | 149.4607 |  |  | 228.6272 |  |  | 380.6181
[13 empty] | Selected C this iteration |  |  | 0.1896 |  |  | 5.7846 |  |  | 13.9615 |  |  | 27.0939 |  |  | 46.2876 |  |  | 74.3158 |  |  | 112.1588 |  |  | 163.6545 |  |  | 255.9855 |  |  | 530.5194
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8104 | 1.0767 |  | 6.2154 | 32.8051 |  | 9.0385 | 78.7449 |  | 11.9061 | 150.3529 |  | 14.7124 | 247.2751 |  | 13.6842 | 368.1589 |  | 8.8412 | 491.3095 |  | 1.3455 | 599.491 |  | 9.9855 | 695.9904 |  | 110.5194 | 792.102
[13 empty] | Next iteration flow rate |  |  | 1.0982 | Abs Value of | Flow this | 33.1332 | Abs Value of | Flow this | 79.5323 | Abs Value of | Flow this | 151.8564 | Abs Value of | Flow this | 249.7479 | Abs Value of | Flow this | 371.8405 | Abs Value of | Flow this | 496.2226 | Abs Value of | Flow this | 605.4859 | Abs Value of | Flow this | 702.9503 | Abs Value of | Flow this | 800.023 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8791 |  |  | 56.7025 |  |  | 56.1373 |  |  | 54.8096 |  |  | 52.2466 |  |  | 48.6001 |  |  | 44.5347 |  |  | 40.2279 |  |  | 35.3006
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6642 |  |  | 24.6995 |  |  | 24.8125 |  |  | 25.0781 |  |  | 25.5907 |  |  | 26.32 |  |  | 27.1331 |  |  | 27.9944 |  |  | 28.9799
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2149 |  |  | 32.003 |  |  | 31.3248 |  |  | 29.7316 |  |  | 26.6559 |  |  | 22.2802 |  |  | 17.4017 |  |  | 12.2335 |  |  | 6.3207
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7217 |  |  | 45.525 |  |  | 43.0427 |  |  | 39.2106 |  |  | 33.3657 |  |  | 27.8541 |  |  | 21.0981 |  |  | 15.7013 |  |  | 13.1125
[13 empty] | C Non choked w/ reducers | 7 |  | 0.19339 |  |  | 5.8425 |  |  | 14.1023 |  |  | 27.3729 |  |  | 46.7897 |  |  | 75.2142 |  |  | 113.7791 |  |  | 166.6756 |  |  | 262.6819 |  |  | 557.0671
[13 empty] | C Choked w/ reducers | 7 |  | 0.16062 |  |  | 4.8514 |  |  | 11.8239 |  |  | 23.3515 |  |  | 40.7433 |  |  | 67.2275 |  |  | 101.7601 |  |  | 151.3723 |  |  | 231.8657 |  |  | 386.7655
[13 empty] | Selected C this iteration |  |  | 0.19339 |  |  | 5.8425 |  |  | 14.1023 |  |  | 27.3729 |  |  | 46.7897 |  |  | 75.2142 |  |  | 113.7791 |  |  | 166.6756 |  |  | 262.6819 |  |  | 557.0671
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8066 | 1.0982 |  | 6.1575 | 33.1332 |  | 8.8977 | 79.5323 |  | 11.6271 | 151.8564 |  | 14.2103 | 249.7479 |  | 12.7858 | 371.8405 |  | 7.2209 | 496.2226 |  | 1.6756 | 605.4859 |  | 16.6819 | 702.9503 |  | 137.0671 | 800.023
[13 empty] | Next iteration flow rate |  |  | 1.1202 | Abs Value of | Flow this | 33.4645 | Abs Value of | Flow this | 80.3277 | Abs Value of | Flow this | 153.375 | Abs Value of | Flow this | 252.2453 | Abs Value of | Flow this | 375.5589 | Abs Value of | Flow this | 501.1848 | Abs Value of | Flow this | 611.5408 | Abs Value of | Flow this | 709.9798 | Abs Value of | Flow this | 808.0233 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8783 |  |  | 56.6982 |  |  | 56.1217 |  |  | 54.7673 |  |  | 52.1527 |  |  | 48.433 |  |  | 44.2859 |  |  | 39.8925 |  |  | 34.8661
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6643 |  |  | 24.7004 |  |  | 24.8157 |  |  | 25.0865 |  |  | 25.6095 |  |  | 26.3534 |  |  | 27.1828 |  |  | 28.0615 |  |  | 29.0668
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.214 |  |  | 31.9979 |  |  | 31.306 |  |  | 29.6807 |  |  | 26.5433 |  |  | 22.0796 |  |  | 17.1031 |  |  | 11.8309 |  |  | 5.7993
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7211 |  |  | 45.5215 |  |  | 43.0306 |  |  | 39.1801 |  |  | 33.3052 |  |  | 27.7574 |  |  | 20.979 |  |  | 15.569 |  |  | 12.949
[13 empty] | C Non choked w/ reducers | 7 |  | 0.19726 |  |  | 5.901 |  |  | 14.2444 |  |  | 27.6549 |  |  | 47.298 |  |  | 76.1274 |  |  | 115.4377 |  |  | 169.8058 |  |  | 269.7843 |  |  | 587.3845
[13 empty] | C Choked w/ reducers | 7 |  | 0.16383 |  |  | 4.9 |  |  | 11.9426 |  |  | 23.5883 |  |  | 41.1668 |  |  | 67.9613 |  |  | 102.9565 |  |  | 153.3193 |  |  | 235.1778 |  |  | 393.0904
[13 empty] | Selected C this iteration |  |  | 0.19726 |  |  | 5.901 |  |  | 14.2444 |  |  | 27.6549 |  |  | 47.298 |  |  | 76.1274 |  |  | 115.4377 |  |  | 169.8058 |  |  | 269.7843 |  |  | 587.3845
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.8027 | 1.1202 |  | 6.099 | 33.4645 |  | 8.7556 | 80.3277 |  | 11.3451 | 153.375 |  | 13.702 | 252.2453 |  | 11.8726 | 375.5589 |  | 5.5623 | 501.1848 |  | 4.8058 | 611.5408 |  | 23.7843 | 709.9798 |  | 167.3845 | 808.0233
[13 empty] | Next iteration flow rate |  |  | 1.1426 | Abs Value of | Flow this | 33.7991 | Abs Value of | Flow this | 81.1309 | Abs Value of | Flow this | 154.9087 | Abs Value of | Flow this | 254.7678 | Abs Value of | Flow this | 379.3145 | Abs Value of | Flow this | 506.1967 | Abs Value of | Flow this | 617.6562 | Abs Value of | Flow this | 717.0796 | Abs Value of | Flow this | 816.1035 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8776 |  |  | 56.6938 |  |  | 56.1057 |  |  | 54.7241 |  |  | 52.057 |  |  | 48.2625 |  |  | 44.032 |  |  | 39.5503 |  |  | 34.4229
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6645 |  |  | 24.7012 |  |  | 24.8189 |  |  | 25.0952 |  |  | 25.6286 |  |  | 26.3875 |  |  | 27.2336 |  |  | 28.1299 |  |  | 29.1554
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2131 |  |  | 31.9926 |  |  | 31.2869 |  |  | 29.6289 |  |  | 26.4284 |  |  | 21.875 |  |  | 16.7984 |  |  | 11.4203 |  |  | 5.2675
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7205 |  |  | 45.518 |  |  | 43.0183 |  |  | 39.149 |  |  | 33.2436 |  |  | 27.6588 |  |  | 20.8575 |  |  | 15.4339 |  |  | 12.7823
[13 empty] | C Non choked w/ reducers | 7 |  | 0.2012 |  |  | 5.9601 |  |  | 14.3881 |  |  | 27.94 |  |  | 47.8127 |  |  | 77.0556 |  |  | 117.1361 |  |  | 173.052 |  |  | 277.3373 |  |  | 622.4883
[13 empty] | C Choked w/ reducers | 7 |  | 0.16711 |  |  | 4.949 |  |  | 12.0624 |  |  | 23.8276 |  |  | 41.595 |  |  | 68.7046 |  |  | 104.1713 |  |  | 155.3028 |  |  | 238.5664 |  |  | 399.6019
[13 empty] | Selected C this iteration |  |  | 0.2012 |  |  | 5.9601 |  |  | 14.3881 |  |  | 27.94 |  |  | 47.8127 |  |  | 77.0556 |  |  | 117.1361 |  |  | 173.052 |  |  | 277.3373 |  |  | 622.4883
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7988 | 1.1426 |  | 6.0399 | 33.7991 |  | 8.6119 | 81.1309 |  | 11.06 | 154.9087 |  | 13.1873 | 254.7678 |  | 10.9444 | 379.3145 |  | 3.8639 | 506.1967 |  | 8.052 | 617.6562 |  | 31.3373 | 717.0796 |  | 202.4883 | 816.1035
[13 empty] | Next iteration flow rate |  |  | 1.1654 | Abs Value of | Flow this | 34.1371 | Abs Value of | Flow this | 81.9423 | Abs Value of | Flow this | 156.4578 | Abs Value of | Flow this | 257.3155 | Abs Value of | Flow this | 383.1077 | Abs Value of | Flow this | 511.2587 | Abs Value of | Flow this | 623.8327 | Abs Value of | Flow this | 724.2504 | Abs Value of | Flow this | 824.2645 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8768 |  |  | 56.6894 |  |  | 56.0894 |  |  | 54.68 |  |  | 51.9593 |  |  | 48.0885 |  |  | 43.773 |  |  | 39.2012 |  |  | 33.9708
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6646 |  |  | 24.7021 |  |  | 24.8221 |  |  | 25.104 |  |  | 25.6481 |  |  | 26.4223 |  |  | 27.2854 |  |  | 28.1998 |  |  | 29.2458
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2121 |  |  | 31.9873 |  |  | 31.2673 |  |  | 29.576 |  |  | 26.3112 |  |  | 21.6662 |  |  | 16.4876 |  |  | 11.0015 |  |  | 4.7249
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7198 |  |  | 45.5143 |  |  | 43.0057 |  |  | 39.1172 |  |  | 33.1807 |  |  | 27.5582 |  |  | 20.7336 |  |  | 15.2962 |  |  | 12.6123
[13 empty] | C Non choked w/ reducers | 7 |  | 0.20522 |  |  | 6.0198 |  |  | 14.5331 |  |  | 28.2282 |  |  | 48.334 |  |  | 77.9993 |  |  | 118.876 |  |  | 176.422 |  |  | 285.3933 |  |  | 663.8282
[13 empty] | C Choked w/ reducers | 7 |  | 0.17045 |  |  | 4.9985 |  |  | 12.1836 |  |  | 24.0694 |  |  | 42.028 |  |  | 69.4574 |  |  | 105.4049 |  |  | 157.3238 |  |  | 242.0346 |  |  | 406.3098
[13 empty] | Selected C this iteration |  |  | 0.20522 |  |  | 6.0198 |  |  | 14.5331 |  |  | 28.2282 |  |  | 48.334 |  |  | 77.9993 |  |  | 118.876 |  |  | 176.422 |  |  | 285.3933 |  |  | 663.8282
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7948 | 1.1654 |  | 5.9802 | 34.1371 |  | 8.4669 | 81.9423 |  | 10.7718 | 156.4578 |  | 12.666 | 257.3155 |  | 10.0007 | 383.1077 |  | 2.124 | 511.2587 |  | 11.422 | 623.8327 |  | 39.3933 | 724.2504 |  | 243.8282 | 824.2645
[13 empty] | Next iteration flow rate |  |  | 1.1888 | Abs Value of | Flow this | 34.4785 | Abs Value of | Flow this | 82.7617 | Abs Value of | Flow this | 158.0224 | Abs Value of | Flow this | 259.8886 | Abs Value of | Flow this | 386.9387 | Abs Value of | Flow this | 516.3712 | Abs Value of | Flow this | 630.071 | Abs Value of | Flow this | 731.4929 | Abs Value of | Flow this | 832.5072 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.876 |  |  | 56.6848 |  |  | 56.0728 |  |  | 54.6351 |  |  | 51.8597 |  |  | 47.9111 |  |  | 43.5089 |  |  | 38.8452 |  |  | 33.5096
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6648 |  |  | 24.703 |  |  | 24.8254 |  |  | 25.113 |  |  | 25.6681 |  |  | 26.4578 |  |  | 27.3382 |  |  | 28.271 |  |  | 29.3381
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2112 |  |  | 31.9818 |  |  | 31.2474 |  |  | 29.5221 |  |  | 26.1916 |  |  | 21.4533 |  |  | 16.1706 |  |  | 10.5742 |  |  | 4.1715
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7192 |  |  | 45.5106 |  |  | 42.9928 |  |  | 39.0848 |  |  | 33.1165 |  |  | 27.4556 |  |  | 20.6072 |  |  | 15.1557 |  |  | 12.4388
[13 empty] | C Non choked w/ reducers | 7 |  | 0.20933 |  |  | 6.0801 |  |  | 14.6797 |  |  | 28.5196 |  |  | 48.8619 |  |  | 78.9589 |  |  | 120.6591 |  |  | 179.9243 |  |  | 294.0133 |  |  | 713.5579
[13 empty] | C Choked w/ reducers | 7 |  | 0.17386 |  |  | 5.0485 |  |  | 12.3059 |  |  | 24.3138 |  |  | 42.4659 |  |  | 70.2199 |  |  | 106.6577 |  |  | 159.3836 |  |  | 245.5855 |  |  | 413.2246
[13 empty] | Selected C this iteration |  |  | 0.20933 |  |  | 6.0801 |  |  | 14.6797 |  |  | 28.5196 |  |  | 48.8619 |  |  | 78.9589 |  |  | 120.6591 |  |  | 179.9243 |  |  | 294.0133 |  |  | 713.5579
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7907 | 1.1888 |  | 5.9199 | 34.4785 |  | 8.3203 | 82.7617 |  | 10.4804 | 158.0224 |  | 12.1381 | 259.8886 |  | 9.0411 | 386.9387 |  | 0.34093 | 516.3712 |  | 14.9243 | 630.071 |  | 48.0133 | 731.4929 |  | 293.5579 | 832.5072
[13 empty] | Next iteration flow rate |  |  | 1.2125 | Abs Value of | Flow this | 34.8233 | Abs Value of | Flow this | 83.5893 | Abs Value of | Flow this | 159.6026 | Abs Value of | Flow this | 262.4875 | Abs Value of | Flow this | 390.8081 | Abs Value of | Flow this | 521.535 | Abs Value of | Flow this | 636.3718 | Abs Value of | Flow this | 738.8079 | Abs Value of | Flow this | 840.8323 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8752 |  |  | 56.6802 |  |  | 56.0559 |  |  | 54.5892 |  |  | 51.7581 |  |  | 47.7301 |  |  | 43.2394 |  |  | 38.4819 |  |  | 33.0391
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.665 |  |  | 24.704 |  |  | 24.8288 |  |  | 25.1222 |  |  | 25.6884 |  |  | 26.494 |  |  | 27.3921 |  |  | 28.3436 |  |  | 29.4322
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2102 |  |  | 31.9762 |  |  | 31.227 |  |  | 29.4671 |  |  | 26.0697 |  |  | 21.2361 |  |  | 15.8473 |  |  | 10.1383 |  |  | 3.6069
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7185 |  |  | 45.5069 |  |  | 42.9797 |  |  | 39.0517 |  |  | 33.051 |  |  | 27.3509 |  |  | 20.4783 |  |  | 15.0123 |  |  | 12.2618
[13 empty] | C Non choked w/ reducers | 7 |  | 0.21352 |  |  | 6.141 |  |  | 14.8278 |  |  | 28.8142 |  |  | 49.3966 |  |  | 79.9348 |  |  | 122.4873 |  |  | 183.5683 |  |  | 303.2696 |  |  | 775.0462
[13 empty] | C Choked w/ reducers | 7 |  | 0.17734 |  |  | 5.0991 |  |  | 12.4295 |  |  | 24.5606 |  |  | 42.9087 |  |  | 70.9923 |  |  | 107.9302 |  |  | 161.4835 |  |  | 249.2227 |  |  | 420.3577
[13 empty] | Selected C this iteration |  |  | 0.21352 |  |  | 6.141 |  |  | 14.8278 |  |  | 28.8142 |  |  | 49.3966 |  |  | 79.9348 |  |  | 122.4873 |  |  | 183.5683 |  |  | 303.2696 |  |  | 775.0462
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7865 | 1.2125 |  | 5.859 | 34.8233 |  | 8.1722 | 83.5893 |  | 10.1858 | 159.6026 |  | 11.6034 | 262.4875 |  | 8.0652 | 390.8081 |  | 1.4873 | 521.535 |  | 18.5683 | 636.3718 |  | 57.2696 | 738.8079 |  | 355.0462 | 840.8323
[13 empty] | Next iteration flow rate |  |  | 1.2368 | Abs Value of | Flow this | 35.1715 | Abs Value of | Flow this | 84.4252 | Abs Value of | Flow this | 161.1986 | Abs Value of | Flow this | 265.1124 | Abs Value of | Flow this | 394.7162 | Abs Value of | Flow this | 526.7503 | Abs Value of | Flow this | 642.7355 | Abs Value of | Flow this | 746.1959 | Abs Value of | Flow this | 849.2406 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8744 |  |  | 56.6754 |  |  | 56.0386 |  |  | 54.5425 |  |  | 51.6544 |  |  | 47.5455 |  |  | 42.9645 |  |  | 38.1114 |  |  | 32.5592
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6651 |  |  | 24.7049 |  |  | 24.8323 |  |  | 25.1315 |  |  | 25.7091 |  |  | 26.5309 |  |  | 27.4471 |  |  | 28.4177 |  |  | 29.5282
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2092 |  |  | 31.9705 |  |  | 31.2063 |  |  | 29.411 |  |  | 25.9453 |  |  | 21.0146 |  |  | 15.5174 |  |  | 9.6937 |  |  | 3.031
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7178 |  |  | 45.503 |  |  | 42.9664 |  |  | 39.018 |  |  | 32.9843 |  |  | 27.2441 |  |  | 20.3467 |  |  | 14.8661 |  |  | 12.0813
[13 empty] | C Non choked w/ reducers | 7 |  | 0.21779 |  |  | 6.2025 |  |  | 14.9774 |  |  | 29.112 |  |  | 49.9381 |  |  | 80.9275 |  |  | 124.3626 |  |  | 187.3644 |  |  | 313.2484 |  |  | 853.9327
[13 empty] | C Choked w/ reducers | 7 |  | 0.18088 |  |  | 5.1501 |  |  | 12.5543 |  |  | 24.8101 |  |  | 43.3565 |  |  | 71.7747 |  |  | 109.2229 |  |  | 163.6246 |  |  | 252.9498 |  |  | 427.7215
[13 empty] | Selected C this iteration |  |  | 0.21779 |  |  | 6.2025 |  |  | 14.9774 |  |  | 29.112 |  |  | 49.9381 |  |  | 80.9275 |  |  | 124.3626 |  |  | 187.3644 |  |  | 313.2484 |  |  | 853.9327
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7822 | 1.2368 |  | 5.7975 | 35.1715 |  | 8.0226 | 84.4252 |  | 9.888 | 161.1986 |  | 11.0619 | 265.1124 |  | 7.0725 | 394.7162 |  | 3.3626 | 526.7503 |  | 22.3644 | 642.7355 |  | 67.2484 | 746.1959 |  | 433.9327 | 849.2406
[13 empty] | Next iteration flow rate |  |  | 1.2615 | Abs Value of | Flow this | 35.5232 | Abs Value of | Flow this | 85.2694 | Abs Value of | Flow this | 162.8106 | Abs Value of | Flow this | 267.7635 | Abs Value of | Flow this | 398.6634 | Abs Value of | Flow this | 532.0178 | Abs Value of | Flow this | 649.1628 | Abs Value of | Flow this | 753.6579 | Abs Value of | Flow this | 857.733 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8735 |  |  | 56.6706 |  |  | 56.0209 |  |  | 54.4948 |  |  | 51.5486 |  |  | 47.3571 |  |  | 42.684 |  |  | 37.7334 |  |  | 32.0696
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6653 |  |  | 24.7059 |  |  | 24.8358 |  |  | 25.141 |  |  | 25.7303 |  |  | 26.5686 |  |  | 27.5032 |  |  | 28.4933 |  |  | 29.6261
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2082 |  |  | 31.9647 |  |  | 31.1851 |  |  | 29.3537 |  |  | 25.8183 |  |  | 20.7885 |  |  | 15.1809 |  |  | 9.2401 |  |  | 2.4435
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7171 |  |  | 45.4991 |  |  | 42.9527 |  |  | 38.9836 |  |  | 32.9162 |  |  | 27.1352 |  |  | 20.2126 |  |  | 14.717 |  |  | 11.8972
[13 empty] | C Non choked w/ reducers | 7 |  | 0.22214 |  |  | 6.2646 |  |  | 15.1286 |  |  | 29.4131 |  |  | 50.4867 |  |  | 81.9374 |  |  | 126.2872 |  |  | 191.324 |  |  | 324.0529 |  |  | 960.5734
[13 empty] | C Choked w/ reducers | 7 |  | 0.1845 |  |  | 5.2016 |  |  | 12.6804 |  |  | 25.0622 |  |  | 43.8094 |  |  | 72.5674 |  |  | 110.5364 |  |  | 165.8085 |  |  | 256.7707 |  |  | 435.3292
[13 empty] | Selected C this iteration |  |  | 0.22214 |  |  | 6.2646 |  |  | 15.1286 |  |  | 29.4131 |  |  | 50.4867 |  |  | 81.9374 |  |  | 126.2872 |  |  | 191.324 |  |  | 324.0529 |  |  | 960.5734
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7779 | 1.2615 |  | 5.7354 | 35.5232 |  | 7.8714 | 85.2694 |  | 9.5869 | 162.8106 |  | 10.5133 | 267.7635 |  | 6.0626 | 398.6634 |  | 5.2872 | 532.0178 |  | 26.324 | 649.1628 |  | 78.0529 | 753.6579 |  | 540.5734 | 857.733
[13 empty] | Next iteration flow rate |  |  | 1.2867 | Abs Value of | Flow this | 35.8785 | Abs Value of | Flow this | 86.1221 | Abs Value of | Flow this | 164.4387 | Abs Value of | Flow this | 270.4411 | Abs Value of | Flow this | 402.65 | Abs Value of | Flow this | 537.338 | Abs Value of | Flow this | 655.6545 | Abs Value of | Flow this | 761.1945 | Abs Value of | Flow this | 866.3103 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8727 |  |  | 56.6657 |  |  | 56.0029 |  |  | 54.4461 |  |  | 51.4407 |  |  | 47.165 |  |  | 42.398 |  |  | 37.3479 |  |  | 31.5702
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6655 |  |  | 24.7069 |  |  | 24.8394 |  |  | 25.1508 |  |  | 25.7519 |  |  | 26.607 |  |  | 27.5604 |  |  | 28.5704 |  |  | 29.726
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2072 |  |  | 31.9588 |  |  | 31.1635 |  |  | 29.2953 |  |  | 25.6889 |  |  | 20.558 |  |  | 14.8376 |  |  | 8.7774 |  |  | 1.8442
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7164 |  |  | 45.4951 |  |  | 42.9388 |  |  | 38.9485 |  |  | 32.8467 |  |  | 27.024 |  |  | 20.0757 |  |  | 14.5648 |  |  | 11.7093
[13 empty] | C Non choked w/ reducers | 7 |  | 0.22658 |  |  | 6.3274 |  |  | 15.2813 |  |  | 29.7175 |  |  | 51.0423 |  |  | 82.9651 |  |  | 128.2634 |  |  | 195.4598 |  |  | 335.8091 |  |  | 1116.7424
[13 empty] | C Choked w/ reducers | 7 |  | 0.18819 |  |  | 5.2537 |  |  | 12.8077 |  |  | 25.3169 |  |  | 44.2674 |  |  | 73.3706 |  |  | 111.8711 |  |  | 168.0365 |  |  | 260.6895 |  |  | 443.1953
[13 empty] | Selected C this iteration |  |  | 0.22658 |  |  | 6.3274 |  |  | 15.2813 |  |  | 29.7175 |  |  | 51.0423 |  |  | 82.9651 |  |  | 128.2634 |  |  | 195.4598 |  |  | 335.8091 |  |  | 1116.7424
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7734 | 1.2867 |  | 5.6726 | 35.8785 |  | 7.7187 | 86.1221 |  | 9.2825 | 164.4387 |  | 9.9577 | 270.4411 |  | 5.0349 | 402.65 |  | 7.2634 | 537.338 |  | 30.4598 | 655.6545 |  | 89.8091 | 761.1945 |  | 696.7424 | 866.3103
[13 empty] | Next iteration flow rate |  |  | 1.3125 | Abs Value of | Flow this | 36.2373 | Abs Value of | Flow this | 86.9834 | Abs Value of | Flow this | 166.0831 | Abs Value of | Flow this | 273.1455 | Abs Value of | Flow this | 406.6765 | Abs Value of | Flow this | 542.7114 | Abs Value of | Flow this | 662.211 | Abs Value of | Flow this | 768.8064 | Abs Value of | Flow this | 874.9734 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8718 |  |  | 56.6606 |  |  | 55.9846 |  |  | 54.3964 |  |  | 51.3307 |  |  | 46.969 |  |  | 42.1062 |  |  | 36.9545 |  |  | 31.0607
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6656 |  |  | 24.7079 |  |  | 24.8431 |  |  | 25.1607 |  |  | 25.7739 |  |  | 26.6462 |  |  | 27.6188 |  |  | 28.6491 |  |  | 29.8279
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2062 |  |  | 31.9527 |  |  | 31.1415 |  |  | 29.2357 |  |  | 25.5568 |  |  | 20.3228 |  |  | 14.4874 |  |  | 8.3054 |  |  | 1.2329
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7157 |  |  | 45.4911 |  |  | 42.9247 |  |  | 38.9127 |  |  | 32.7758 |  |  | 26.9107 |  |  | 19.9361 |  |  | 14.4096 |  |  | 11.5177
[13 empty] | C Non choked w/ reducers | 7 |  | 0.23112 |  |  | 6.3907 |  |  | 15.4356 |  |  | 30.0253 |  |  | 51.6053 |  |  | 84.0109 |  |  | 130.2935 |  |  | 199.786 |  |  | 348.6712 |  |  | 1379.4958
[13 empty] | C Choked w/ reducers | 7 |  | 0.19195 |  |  | 5.3063 |  |  | 12.9364 |  |  | 25.5743 |  |  | 44.7307 |  |  | 74.1844 |  |  | 113.2275 |  |  | 170.3101 |  |  | 264.7107 |  |  | 451.3356
[13 empty] | Selected C this iteration |  |  | 0.23112 |  |  | 6.3907 |  |  | 15.4356 |  |  | 30.0253 |  |  | 51.6053 |  |  | 84.0109 |  |  | 130.2935 |  |  | 199.786 |  |  | 348.6712 |  |  | 1379.4958
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7689 | 1.3125 |  | 5.6093 | 36.2373 |  | 7.5644 | 86.9834 |  | 8.9747 | 166.0831 |  | 9.3947 | 273.1455 |  | 3.9891 | 406.6765 |  | 9.2935 | 542.7114 |  | 34.786 | 662.211 |  | 102.6712 | 768.8064 |  | 959.4958 | 874.9734
[13 empty] | Next iteration flow rate |  |  | 1.3387 | Abs Value of | Flow this | 36.5996 | Abs Value of | Flow this | 87.8532 | Abs Value of | Flow this | 167.7439 | Abs Value of | Flow this | 275.877 | Abs Value of | Flow this | 410.7433 | Abs Value of | Flow this | 548.1385 | Abs Value of | Flow this | 668.8331 | Abs Value of | Flow this | 776.4945 | Abs Value of | Flow this | 883.7232 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8709 |  |  | 56.6555 |  |  | 55.9659 |  |  | 54.3458 |  |  | 51.2184 |  |  | 46.769 |  |  | 41.8085 |  |  | 36.5533 |  |  | 30.541
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6658 |  |  | 24.7089 |  |  | 24.8468 |  |  | 25.1708 |  |  | 25.7963 |  |  | 26.6862 |  |  | 27.6783 |  |  | 28.7293 |  |  | 29.9318
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2051 |  |  | 31.9466 |  |  | 31.119 |  |  | 29.1749 |  |  | 25.4221 |  |  | 20.0828 |  |  | 14.1302 |  |  | 7.824 |  |  | 0.60926
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.715 |  |  | 45.4869 |  |  | 42.9102 |  |  | 38.8761 |  |  | 32.7035 |  |  | 26.795 |  |  | 19.7936 |  |  | 14.2513 |  |  | 11.3222
[13 empty] | C Non choked w/ reducers | 7 |  | 0.23574 |  |  | 6.4548 |  |  | 15.5914 |  |  | 30.3365 |  |  | 52.1756 |  |  | 85.0756 |  |  | 132.3801 |  |  | 204.3185 |  |  | 362.8318 |  |  | 1982.0003
[13 empty] | C Choked w/ reducers | 7 |  | 0.19579 |  |  | 5.3594 |  |  | 13.0664 |  |  | 25.8344 |  |  | 45.1992 |  |  | 75.009 |  |  | 114.6063 |  |  | 172.631 |  |  | 268.8389 |  |  | 459.7672
[13 empty] | Selected C this iteration |  |  | 0.23574 |  |  | 6.4548 |  |  | 15.5914 |  |  | 30.3365 |  |  | 52.1756 |  |  | 85.0756 |  |  | 132.3801 |  |  | 204.3185 |  |  | 362.8318 |  |  | 1982.0003
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7643 | 1.3387 |  | 5.5452 | 36.5996 |  | 7.4086 | 87.8532 |  | 8.6635 | 167.7439 |  | 8.8244 | 275.877 |  | 2.9244 | 410.7433 |  | 11.3801 | 548.1385 |  | 39.3185 | 668.8331 |  | 116.8318 | 776.4945 |  | 1562.0003 | 883.7232
[13 empty] | Next iteration flow rate |  |  | 1.3655 | Abs Value of | Flow this | 36.9656 | Abs Value of | Flow this | 88.7317 | Abs Value of | Flow this | 169.4214 | Abs Value of | Flow this | 278.6358 | Abs Value of | Flow this | 414.8507 | Abs Value of | Flow this | 553.6199 | Abs Value of | Flow this | 675.5214 | Abs Value of | Flow this | 784.2594 | Abs Value of | Flow this | 892.5604 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.87 |  |  | 56.6502 |  |  | 55.9468 |  |  | 54.2941 |  |  | 51.1039 |  |  | 46.5651 |  |  | 41.5048 |  |  | 36.144 |  |  | 30.0109
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.666 |  |  | 24.71 |  |  | 24.8506 |  |  | 25.1812 |  |  | 25.8192 |  |  | 26.727 |  |  | 27.739 |  |  | 28.8112 |  |  | 30.0378
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.204 |  |  | 31.9403 |  |  | 31.0961 |  |  | 29.113 |  |  | 25.2847 |  |  | 19.8381 |  |  | 13.7658 |  |  | 7.3328 |  |  | -0.026911
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7142 |  |  | 45.4827 |  |  | 42.8954 |  |  | 38.8389 |  |  | 32.6297 |  |  | 26.6771 |  |  | 19.6483 |  |  | 14.0897 |  |  | 11.1228
[13 empty] | C Non choked w/ reducers | 7 |  | 0.24045 |  |  | 6.5194 |  |  | 15.7489 |  |  | 30.6512 |  |  | 52.7534 |  |  | 86.1595 |  |  | 134.5262 |  |  | 209.0752 |  |  | 378.5339 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.19971 |  |  | 5.413 |  |  | 13.1976 |  |  | 26.0972 |  |  | 45.6731 |  |  | 75.8447 |  |  | 116.008 |  |  | 175.0008 |  |  | 273.0792 |  |  | 468.5089
[13 empty] | Selected C this iteration |  |  | 0.24045 |  |  | 6.5194 |  |  | 15.7489 |  |  | 30.6512 |  |  | 52.7534 |  |  | 86.1595 |  |  | 134.5262 |  |  | 209.0752 |  |  | 378.5339 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7595 | 1.3655 |  | 5.4806 | 36.9656 |  | 7.2511 | 88.7317 |  | 8.3488 | 169.4214 |  | 8.2466 | 278.6358 |  | 1.8405 | 414.8507 |  | 13.5262 | 553.6199 |  | 44.0752 | 675.5214 |  | 132.5339 | 784.2594 |  | 5500 | 892.5604
[13 empty] | Next iteration flow rate |  |  | 1.3928 | Abs Value of | Flow this | 37.3353 | Abs Value of | Flow this | 89.619 | Abs Value of | Flow this | 171.1156 | Abs Value of | Flow this | 281.4221 | Abs Value of | Flow this | 418.9992 | Abs Value of | Flow this | 559.1561 | Abs Value of | Flow this | 682.2767 | Abs Value of | Flow this | 792.102 | Abs Value of | Flow this | 901.486 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8691 |  |  | 56.6449 |  |  | 55.9273 |  |  | 54.2414 |  |  | 50.9871 |  |  | 46.357 |  |  | 41.1951 |  |  | 35.7265 |  |  | 29.4701
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6662 |  |  | 24.711 |  |  | 24.8545 |  |  | 25.1917 |  |  | 25.8426 |  |  | 26.7686 |  |  | 27.801 |  |  | 28.8947 |  |  | 30.146
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2029 |  |  | 31.9339 |  |  | 31.0727 |  |  | 29.0497 |  |  | 25.1445 |  |  | 19.5884 |  |  | 13.3941 |  |  | 6.8318 |  |  | -0.67587
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7134 |  |  | 45.4783 |  |  | 42.8804 |  |  | 38.8009 |  |  | 32.5545 |  |  | 26.5567 |  |  | 19.5001 |  |  | 13.925 |  |  | 10.9194
[13 empty] | C Non choked w/ reducers | 7 |  | 0.24526 |  |  | 6.5847 |  |  | 15.908 |  |  | 30.9693 |  |  | 53.3389 |  |  | 87.2634 |  |  | 136.7346 |  |  | 214.0761 |  |  | 396.0904 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.2037 |  |  | 5.4672 |  |  | 13.3302 |  |  | 26.3628 |  |  | 46.1524 |  |  | 76.6916 |  |  | 117.4332 |  |  | 177.4213 |  |  | 277.4369 |  |  | 477.5812
[13 empty] | Selected C this iteration |  |  | 0.24526 |  |  | 6.5847 |  |  | 15.908 |  |  | 30.9693 |  |  | 53.3389 |  |  | 87.2634 |  |  | 136.7346 |  |  | 214.0761 |  |  | 396.0904 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7547 | 1.3928 |  | 5.4153 | 37.3353 |  | 7.092 | 89.619 |  | 8.0307 | 171.1156 |  | 7.6611 | 281.4221 |  | 0.73661 | 418.9992 |  | 15.7346 | 559.1561 |  | 49.0761 | 682.2767 |  | 150.0904 | 792.102 |  | 5500 | 901.486
[13 empty] | Next iteration flow rate |  |  | 1.4207 | Abs Value of | Flow this | 37.7086 | Abs Value of | Flow this | 90.5152 | Abs Value of | Flow this | 172.8267 | Abs Value of | Flow this | 284.2364 | Abs Value of | Flow this | 423.1892 | Abs Value of | Flow this | 564.7476 | Abs Value of | Flow this | 689.0994 | Abs Value of | Flow this | 800.023 | Abs Value of | Flow this | 910.5008 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8681 |  |  | 56.6394 |  |  | 55.9074 |  |  | 54.1877 |  |  | 50.8679 |  |  | 46.1448 |  |  | 40.8791 |  |  | 35.3006 |  |  | 28.9184
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6664 |  |  | 24.7121 |  |  | 24.8585 |  |  | 25.2025 |  |  | 25.8664 |  |  | 26.811 |  |  | 27.8642 |  |  | 28.9799 |  |  | 30.2563
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2017 |  |  | 31.9273 |  |  | 31.0489 |  |  | 28.9852 |  |  | 25.0015 |  |  | 19.3337 |  |  | 13.0149 |  |  | 6.3207 |  |  | -1.3379
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7127 |  |  | 45.4739 |  |  | 42.865 |  |  | 38.7621 |  |  | 32.4777 |  |  | 26.434 |  |  | 19.3489 |  |  | 13.7569 |  |  | 10.7119
[13 empty] | C Non choked w/ reducers | 7 |  | 0.25017 |  |  | 6.6507 |  |  | 16.0687 |  |  | 31.291 |  |  | 53.9322 |  |  | 88.3877 |  |  | 139.0086 |  |  | 219.344 |  |  | 415.911 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.20778 |  |  | 5.5219 |  |  | 13.4642 |  |  | 26.6312 |  |  | 46.6372 |  |  | 77.55 |  |  | 118.8826 |  |  | 179.8942 |  |  | 281.9179 |  |  | 487.0066
[13 empty] | Selected C this iteration |  |  | 0.25017 |  |  | 6.6507 |  |  | 16.0687 |  |  | 31.291 |  |  | 53.9322 |  |  | 88.3877 |  |  | 139.0086 |  |  | 219.344 |  |  | 415.911 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7498 | 1.4207 |  | 5.3493 | 37.7086 |  | 6.9313 | 90.5152 |  | 7.709 | 172.8267 |  | 7.0678 | 284.2364 |  | 0.38773 | 423.1892 |  | 18.0086 | 564.7476 |  | 54.344 | 689.0994 |  | 169.911 | 800.023 |  | 5500 | 910.5008
[13 empty] | Next iteration flow rate |  |  | 1.4491 | Abs Value of | Flow this | 38.0857 | Abs Value of | Flow this | 91.4204 | Abs Value of | Flow this | 174.555 | Abs Value of | Flow this | 287.0787 | Abs Value of | Flow this | 427.4211 | Abs Value of | Flow this | 570.3951 | Abs Value of | Flow this | 695.9904 | Abs Value of | Flow this | 808.0233 | Abs Value of | Flow this | 919.6059 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8672 |  |  | 56.6339 |  |  | 55.8871 |  |  | 54.1328 |  |  | 50.7463 |  |  | 45.9283 |  |  | 40.5567 |  |  | 34.8661 |  |  | 28.3557
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6666 |  |  | 24.7132 |  |  | 24.8626 |  |  | 25.2134 |  |  | 25.8907 |  |  | 26.8543 |  |  | 27.9287 |  |  | 29.0668 |  |  | 30.3689
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.2006 |  |  | 31.9207 |  |  | 31.0245 |  |  | 28.9194 |  |  | 24.8556 |  |  | 19.0739 |  |  | 12.6281 |  |  | 5.7993 |  |  | -2.0132
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7119 |  |  | 45.4694 |  |  | 42.8493 |  |  | 38.7225 |  |  | 32.3994 |  |  | 26.3088 |  |  | 19.1947 |  |  | 13.5854 |  |  | 10.5002
[13 empty] | C Non choked w/ reducers | 7 |  | 0.25517 |  |  | 6.7173 |  |  | 16.2311 |  |  | 31.6163 |  |  | 54.5335 |  |  | 89.5332 |  |  | 141.3516 |  |  | 224.9049 |  |  | 438.5463 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.21193 |  |  | 5.5772 |  |  | 13.5995 |  |  | 26.9025 |  |  | 47.1277 |  |  | 78.4201 |  |  | 120.3568 |  |  | 182.4217 |  |  | 286.5282 |  |  | 496.8098
[13 empty] | Selected C this iteration |  |  | 0.25517 |  |  | 6.7173 |  |  | 16.2311 |  |  | 31.6163 |  |  | 54.5335 |  |  | 89.5332 |  |  | 141.3516 |  |  | 224.9049 |  |  | 438.5463 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7448 | 1.4491 |  | 5.2827 | 38.0857 |  | 6.7689 | 91.4204 |  | 7.3837 | 174.555 |  | 6.4665 | 287.0787 |  | 1.5332 | 427.4211 |  | 20.3516 | 570.3951 |  | 59.9049 | 695.9904 |  | 192.5463 | 808.0233 |  | 5500 | 919.6059
[13 empty] | Next iteration flow rate |  |  | 1.4781 | Abs Value of | Flow this | 38.4666 | Abs Value of | Flow this | 92.3346 | Abs Value of | Flow this | 176.3006 | Abs Value of | Flow this | 289.9495 | Abs Value of | Flow this | 431.6953 | Abs Value of | Flow this | 576.0991 | Abs Value of | Flow this | 702.9503 | Abs Value of | Flow this | 816.1035 | Abs Value of | Flow this | 928.8019 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8662 |  |  | 56.6282 |  |  | 55.8664 |  |  | 54.0769 |  |  | 50.6223 |  |  | 45.7074 |  |  | 40.2279 |  |  | 34.4229 |  |  | 27.7816
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6668 |  |  | 24.7144 |  |  | 24.8667 |  |  | 25.2246 |  |  | 25.9155 |  |  | 26.8985 |  |  | 27.9944 |  |  | 29.1554 |  |  | 30.4837
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.1994 |  |  | 31.9139 |  |  | 30.9997 |  |  | 28.8523 |  |  | 24.7068 |  |  | 18.8089 |  |  | 12.2335 |  |  | 5.2675 |  |  | -2.702
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.711 |  |  | 45.4648 |  |  | 42.8333 |  |  | 38.6822 |  |  | 32.3196 |  |  | 26.181 |  |  | 19.0374 |  |  | 13.4105 |  |  | 10.2843
[13 empty] | C Non choked w/ reducers | 7 |  | 0.26027 |  |  | 6.7846 |  |  | 16.3951 |  |  | 31.9453 |  |  | 55.1429 |  |  | 90.7005 |  |  | 143.7674 |  |  | 230.7883 |  |  | 464.7551 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.21617 |  |  | 5.633 |  |  | 13.7362 |  |  | 27.1765 |  |  | 47.6238 |  |  | 79.3021 |  |  | 121.8566 |  |  | 185.0057 |  |  | 291.2745 |  |  | 507.0182
[13 empty] | Selected C this iteration |  |  | 0.26027 |  |  | 6.7846 |  |  | 16.3951 |  |  | 31.9453 |  |  | 55.1429 |  |  | 90.7005 |  |  | 143.7674 |  |  | 230.7883 |  |  | 464.7551 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7397 | 1.4781 |  | 5.2154 | 38.4666 |  | 6.6049 | 92.3346 |  | 7.0547 | 176.3006 |  | 5.8571 | 289.9495 |  | 2.7005 | 431.6953 |  | 22.7674 | 576.0991 |  | 65.7883 | 702.9503 |  | 218.7551 | 816.1035 |  | 5500 | 928.8019
[13 empty] | Next iteration flow rate |  |  | 1.5076 | Abs Value of | Flow this | 38.8512 | Abs Value of | Flow this | 93.2579 | Abs Value of | Flow this | 178.0636 | Abs Value of | Flow this | 292.849 | Abs Value of | Flow this | 436.0123 | Abs Value of | Flow this | 581.86 | Abs Value of | Flow this | 709.9798 | Abs Value of | Flow this | 824.2645 | Abs Value of | Flow this | 938.0899 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8652 |  |  | 56.6224 |  |  | 55.8453 |  |  | 54.0198 |  |  | 50.4958 |  |  | 45.4821 |  |  | 39.8925 |  |  | 33.9708 |  |  | 27.196
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.667 |  |  | 24.7155 |  |  | 24.8709 |  |  | 25.236 |  |  | 25.9408 |  |  | 26.9436 |  |  | 28.0615 |  |  | 29.2458 |  |  | 30.6008
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.1982 |  |  | 31.9069 |  |  | 30.9744 |  |  | 28.7838 |  |  | 24.5549 |  |  | 18.5386 |  |  | 11.8309 |  |  | 4.7249 |  |  | -3.4048
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7102 |  |  | 45.4602 |  |  | 42.817 |  |  | 38.641 |  |  | 32.2381 |  |  | 26.0507 |  |  | 18.8769 |  |  | 13.2321 |  |  | 10.064
[13 empty] | C Non choked w/ reducers | 7 |  | 0.26548 |  |  | 6.8526 |  |  | 16.5609 |  |  | 32.2779 |  |  | 55.7605 |  |  | 91.8902 |  |  | 146.2601 |  |  | 237.0283 |  |  | 495.6198 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.22049 |  |  | 5.6894 |  |  | 13.8743 |  |  | 27.4535 |  |  | 48.1256 |  |  | 80.1963 |  |  | 123.3826 |  |  | 187.6484 |  |  | 296.1639 |  |  | 517.662
[13 empty] | Selected C this iteration |  |  | 0.26548 |  |  | 6.8526 |  |  | 16.5609 |  |  | 32.2779 |  |  | 55.7605 |  |  | 91.8902 |  |  | 146.2601 |  |  | 237.0283 |  |  | 495.6198 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7345 | 1.5076 |  | 5.1474 | 38.8512 |  | 6.4391 | 93.2579 |  | 6.7221 | 178.0636 |  | 5.2395 | 292.849 |  | 3.8902 | 436.0123 |  | 25.2601 | 581.86 |  | 72.0283 | 709.9798 |  | 249.6198 | 824.2645 |  | 5500 | 938.0899
[13 empty] | Next iteration flow rate |  |  | 1.5378 | Abs Value of | Flow this | 39.2398 | Abs Value of | Flow this | 94.1905 | Abs Value of | Flow this | 179.8442 | Abs Value of | Flow this | 295.7775 | Abs Value of | Flow this | 440.3724 | Abs Value of | Flow this | 587.6786 | Abs Value of | Flow this | 717.0796 | Abs Value of | Flow this | 832.5072 | Abs Value of | Flow this | 947.4708 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8641 |  |  | 56.6165 |  |  | 55.8238 |  |  | 53.9616 |  |  | 50.3667 |  |  | 45.2523 |  |  | 39.5503 |  |  | 33.5096 |  |  | 26.5986
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6672 |  |  | 24.7167 |  |  | 24.8752 |  |  | 25.2477 |  |  | 25.9667 |  |  | 26.9895 |  |  | 28.1299 |  |  | 29.3381 |  |  | 30.7203
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.197 |  |  | 31.8998 |  |  | 30.9486 |  |  | 28.7139 |  |  | 24.4001 |  |  | 18.2628 |  |  | 11.4203 |  |  | 4.1715 |  |  | -4.1216
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7094 |  |  | 45.4554 |  |  | 42.8004 |  |  | 38.5991 |  |  | 32.155 |  |  | 25.9178 |  |  | 18.7132 |  |  | 13.0501 |  |  | 9.8393
[13 empty] | C Non choked w/ reducers | 7 |  | 0.27079 |  |  | 6.9212 |  |  | 16.7284 |  |  | 32.6143 |  |  | 56.3866 |  |  | 93.1032 |  |  | 148.8339 |  |  | 243.6643 |  |  | 532.7484 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.2249 |  |  | 5.7463 |  |  | 14.0138 |  |  | 27.7335 |  |  | 48.6333 |  |  | 81.1028 |  |  | 124.9355 |  |  | 190.3522 |  |  | 301.2042 |  |  | 528.7749
[13 empty] | Selected C this iteration |  |  | 0.27079 |  |  | 6.9212 |  |  | 16.7284 |  |  | 32.6143 |  |  | 56.3866 |  |  | 93.1032 |  |  | 148.8339 |  |  | 243.6643 |  |  | 532.7484 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7292 | 1.5378 |  | 5.0788 | 39.2398 |  | 6.2716 | 94.1905 |  | 6.3857 | 179.8442 |  | 4.6134 | 295.7775 |  | 5.1032 | 440.3724 |  | 27.8339 | 587.6786 |  | 78.6643 | 717.0796 |  | 286.7484 | 832.5072 |  | 5500 | 947.4708
[13 empty] | Next iteration flow rate |  |  | 1.5685 | Abs Value of | Flow this | 39.6321 | Abs Value of | Flow this | 95.1324 | Abs Value of | Flow this | 181.6426 | Abs Value of | Flow this | 298.7353 | Abs Value of | Flow this | 444.7761 | Abs Value of | Flow this | 593.5554 | Abs Value of | Flow this | 724.2504 | Abs Value of | Flow this | 840.8323 | Abs Value of | Flow this | 956.9455 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8631 |  |  | 56.6105 |  |  | 55.8019 |  |  | 53.9022 |  |  | 50.2351 |  |  | 45.0179 |  |  | 39.2012 |  |  | 33.0391 |  |  | 25.9893
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6674 |  |  | 24.7179 |  |  | 24.8796 |  |  | 25.2596 |  |  | 25.993 |  |  | 27.0364 |  |  | 28.1998 |  |  | 29.4322 |  |  | 30.8421
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.1957 |  |  | 31.8926 |  |  | 30.9222 |  |  | 28.6426 |  |  | 24.2421 |  |  | 17.9814 |  |  | 11.0015 |  |  | 3.6069 |  |  | -4.8529
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7085 |  |  | 45.4505 |  |  | 42.7834 |  |  | 38.5562 |  |  | 32.0702 |  |  | 25.7822 |  |  | 18.5461 |  |  | 12.8645 |  |  | 9.6101
[13 empty] | C Non choked w/ reducers | 7 |  | 0.27621 |  |  | 6.9906 |  |  | 16.8976 |  |  | 32.9544 |  |  | 57.0213 |  |  | 94.3401 |  |  | 151.4936 |  |  | 250.7421 |  |  | 578.6562 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.2294 |  |  | 5.8038 |  |  | 14.1547 |  |  | 28.0164 |  |  | 49.1469 |  |  | 82.0221 |  |  | 126.5163 |  |  | 193.1194 |  |  | 306.4036 |  |  | 540.3941
[13 empty] | Selected C this iteration |  |  | 0.27621 |  |  | 6.9906 |  |  | 16.8976 |  |  | 32.9544 |  |  | 57.0213 |  |  | 94.3401 |  |  | 151.4936 |  |  | 250.7421 |  |  | 578.6562 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7238 | 1.5685 |  | 5.0094 | 39.6321 |  | 6.1024 | 95.1324 |  | 6.0456 | 181.6426 |  | 3.9787 | 298.7353 |  | 6.3401 | 444.7761 |  | 30.4936 | 593.5554 |  | 85.7421 | 724.2504 |  | 332.6562 | 840.8323 |  | 5500 | 956.9455
[13 empty] | Next iteration flow rate |  |  | 1.5999 | Abs Value of | Flow this | 40.0285 | Abs Value of | Flow this | 96.0837 | Abs Value of | Flow this | 183.4591 | Abs Value of | Flow this | 301.7226 | Abs Value of | Flow this | 449.2239 | Abs Value of | Flow this | 599.491 | Abs Value of | Flow this | 731.4929 | Abs Value of | Flow this | 849.2406 | Abs Value of | Flow this | 966.515 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.862 |  |  | 56.6044 |  |  | 55.7795 |  |  | 53.8416 |  |  | 50.1008 |  |  | 44.7787 |  |  | 38.8452 |  |  | 32.5592 |  |  | 25.3676
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6676 |  |  | 24.7191 |  |  | 24.8841 |  |  | 25.2717 |  |  | 26.0198 |  |  | 27.0843 |  |  | 28.271 |  |  | 29.5282 |  |  | 30.9665
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.1944 |  |  | 31.8852 |  |  | 30.8954 |  |  | 28.5699 |  |  | 24.081 |  |  | 17.6945 |  |  | 10.5742 |  |  | 3.031 |  |  | -5.5988
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7076 |  |  | 45.4455 |  |  | 42.7661 |  |  | 38.5125 |  |  | 31.9837 |  |  | 25.6439 |  |  | 18.3758 |  |  | 12.6751 |  |  | 9.3763
[13 empty] | C Non choked w/ reducers | 7 |  | 0.28173 |  |  | 7.0606 |  |  | 17.0685 |  |  | 33.2985 |  |  | 57.6647 |  |  | 95.6018 |  |  | 154.2444 |  |  | 258.3155 |  |  | 637.5535 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.23399 |  |  | 5.8619 |  |  | 14.297 |  |  | 28.3022 |  |  | 49.6665 |  |  | 82.9542 |  |  | 128.1256 |  |  | 195.9527 |  |  | 311.7712 |  |  | 552.5616
[13 empty] | Selected C this iteration |  |  | 0.28173 |  |  | 7.0606 |  |  | 17.0685 |  |  | 33.2985 |  |  | 57.6647 |  |  | 95.6018 |  |  | 154.2444 |  |  | 258.3155 |  |  | 637.5535 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7183 | 1.5999 |  | 4.9394 | 40.0285 |  | 5.9315 | 96.0837 |  | 5.7015 | 183.4591 |  | 3.3353 | 301.7226 |  | 7.6018 | 449.2239 |  | 33.2444 | 599.491 |  | 93.3155 | 731.4929 |  | 391.5535 | 849.2406 |  | 5500 | 966.515
[13 empty] | Next iteration flow rate |  |  | 1.6319 | Abs Value of | Flow this | 40.4288 | Abs Value of | Flow this | 97.0446 | Abs Value of | Flow this | 185.2937 | Abs Value of | Flow this | 304.7398 | Abs Value of | Flow this | 453.7161 | Abs Value of | Flow this | 605.4859 | Abs Value of | Flow this | 738.8079 | Abs Value of | Flow this | 857.733 | Abs Value of | Flow this | 976.1801 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9161 |  |  | 56.8609 |  |  | 56.5981 |  |  | 55.7566 |  |  | 53.7798 |  |  | 49.9638 |  |  | 44.5347 |  |  | 38.4819 |  |  | 32.0696 |  |  | 24.7335
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6678 |  |  | 24.7204 |  |  | 24.8887 |  |  | 25.284 |  |  | 26.0472 |  |  | 27.1331 |  |  | 28.3436 |  |  | 29.6261 |  |  | 31.0933
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.1931 |  |  | 31.8777 |  |  | 30.8679 |  |  | 28.4958 |  |  | 23.9166 |  |  | 17.4017 |  |  | 10.1383 |  |  | 2.4435 |  |  | -6.3598
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7067 |  |  | 45.4405 |  |  | 42.7485 |  |  | 38.468 |  |  | 31.8955 |  |  | 25.5028 |  |  | 18.202 |  |  | 12.4819 |  |  | 9.1378
[13 empty] | C Non choked w/ reducers | 7 |  | 0.28736 |  |  | 7.1314 |  |  | 17.2412 |  |  | 33.6464 |  |  | 58.3171 |  |  | 96.889 |  |  | 157.0918 |  |  | 266.448 |  |  | 717.1724 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.23867 |  |  | 5.9206 |  |  | 14.4408 |  |  | 28.5912 |  |  | 50.1922 |  |  | 83.8996 |  |  | 129.7643 |  |  | 198.8548 |  |  | 317.3165 |  |  | 565.3241
[13 empty] | Selected C this iteration |  |  | 0.28736 |  |  | 7.1314 |  |  | 17.2412 |  |  | 33.6464 |  |  | 58.3171 |  |  | 96.889 |  |  | 157.0918 |  |  | 266.448 |  |  | 717.1724 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7126 | 1.6319 |  | 4.8686 | 40.4288 |  | 5.7588 | 97.0446 |  | 5.3536 | 185.2937 |  | 2.6829 | 304.7398 |  | 8.889 | 453.7161 |  | 36.0918 | 605.4859 |  | 101.448 | 738.8079 |  | 471.1724 | 857.733 |  | 5500 | 976.1801
[13 empty] | Next iteration flow rate |  |  | 1.6645 | Abs Value of | Flow this | 40.833 | Abs Value of | Flow this | 98.015 | Abs Value of | Flow this | 187.1466 | Abs Value of | Flow this | 307.7872 | Abs Value of | Flow this | 458.2533 | Abs Value of | Flow this | 611.5408 | Abs Value of | Flow this | 746.1959 | Abs Value of | Flow this | 866.3103 | Abs Value of | Flow this | 985.9419 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8598 |  |  | 56.5917 |  |  | 55.7333 |  |  | 53.7168 |  |  | 49.8241 |  |  | 44.2859 |  |  | 38.1114 |  |  | 31.5702 |  |  | 24.0866
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.668 |  |  | 24.7217 |  |  | 24.8933 |  |  | 25.2966 |  |  | 26.0752 |  |  | 27.1828 |  |  | 28.4177 |  |  | 29.726 |  |  | 31.2227
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.1918 |  |  | 31.87 |  |  | 30.84 |  |  | 28.4201 |  |  | 23.7489 |  |  | 17.1031 |  |  | 9.6937 |  |  | 1.8442 |  |  | -7.136
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7058 |  |  | 45.4353 |  |  | 42.7305 |  |  | 38.4225 |  |  | 31.8055 |  |  | 25.3589 |  |  | 18.0247 |  |  | 12.2848 |  |  | 8.8944
[13 empty] | C Non choked w/ reducers | 7 |  | 0.29311 |  |  | 7.2029 |  |  | 17.4157 |  |  | 33.9983 |  |  | 58.9786 |  |  | 98.2028 |  |  | 160.0419 |  |  | 275.2152 |  |  | 833.7695 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.24344 |  |  | 5.9799 |  |  | 14.586 |  |  | 28.8832 |  |  | 50.7241 |  |  | 84.8584 |  |  | 131.4334 |  |  | 201.8287 |  |  | 323.0502 |  |  | 578.7344
[13 empty] | Selected C this iteration |  |  | 0.29311 |  |  | 7.2029 |  |  | 17.4157 |  |  | 33.9983 |  |  | 58.9786 |  |  | 98.2028 |  |  | 160.0419 |  |  | 275.2152 |  |  | 833.7695 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7069 | 1.6645 |  | 4.7971 | 40.833 |  | 5.5843 | 98.015 |  | 5.0017 | 187.1466 |  | 2.0214 | 307.7872 |  | 10.2028 | 458.2533 |  | 39.0419 | 611.5408 |  | 110.2152 | 746.1959 |  | 587.7695 | 866.3103 |  | 5500 | 985.9419
[13 empty] | Next iteration flow rate |  |  | 1.6978 | Abs Value of | Flow this | 41.2414 | Abs Value of | Flow this | 98.9952 | Abs Value of | Flow this | 189.0181 | Abs Value of | Flow this | 310.8651 | Abs Value of | Flow this | 462.8358 | Abs Value of | Flow this | 617.6562 | Abs Value of | Flow this | 753.6579 | Abs Value of | Flow this | 874.9734 | Abs Value of | Flow this | 995.8014 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8587 |  |  | 56.5852 |  |  | 55.7095 |  |  | 53.6525 |  |  | 49.6815 |  |  | 44.032 |  |  | 37.7334 |  |  | 31.0607 |  |  | 23.4268
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6683 |  |  | 24.723 |  |  | 24.8981 |  |  | 25.3095 |  |  | 26.1037 |  |  | 27.2336 |  |  | 28.4933 |  |  | 29.8279 |  |  | 31.3546
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.1904 |  |  | 31.8622 |  |  | 30.8114 |  |  | 28.343 |  |  | 23.5778 |  |  | 16.7984 |  |  | 9.2401 |  |  | 1.2329 |  |  | -7.9279
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7049 |  |  | 45.43 |  |  | 42.7121 |  |  | 38.3761 |  |  | 31.7137 |  |  | 25.212 |  |  | 17.8438 |  |  | 12.0837 |  |  | 8.6462
[13 empty] | C Non choked w/ reducers | 7 |  | 0.29897 |  |  | 7.275 |  |  | 17.592 |  |  | 34.3541 |  |  | 59.6494 |  |  | 99.544 |  |  | 163.1015 |  |  | 284.7079 |  |  | 1029.9434 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.24831 |  |  | 6.0397 |  |  | 14.7327 |  |  | 29.1783 |  |  | 51.2623 |  |  | 85.8309 |  |  | 133.1337 |  |  | 204.8774 |  |  | 328.9838 |  |  | 592.8522
[13 empty] | Selected C this iteration |  |  | 0.29897 |  |  | 7.275 |  |  | 17.592 |  |  | 34.3541 |  |  | 59.6494 |  |  | 99.544 |  |  | 163.1015 |  |  | 284.7079 |  |  | 1029.9434 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.701 | 1.6978 |  | 4.725 | 41.2414 |  | 5.408 | 98.9952 |  | 4.6459 | 189.0181 |  | 1.3506 | 310.8651 |  | 11.544 | 462.8358 |  | 42.1015 | 617.6562 |  | 119.7079 | 753.6579 |  | 783.9434 | 874.9734 |  | 5500 | 995.8014
[13 empty] | Next iteration flow rate |  |  | 1.7318 | Abs Value of | Flow this | 41.6538 | Abs Value of | Flow this | 99.9851 | Abs Value of | Flow this | 190.9082 | Abs Value of | Flow this | 313.9738 | Abs Value of | Flow this | 467.4642 | Abs Value of | Flow this | 623.8327 | Abs Value of | Flow this | 761.1945 | Abs Value of | Flow this | 883.7232 | Abs Value of | Flow this | 1005.7594 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8575 |  |  | 56.5785 |  |  | 55.6853 |  |  | 53.5869 |  |  | 49.5361 |  |  | 43.773 |  |  | 37.3479 |  |  | 30.541 |  |  | 22.7536
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6685 |  |  | 24.7243 |  |  | 24.9029 |  |  | 25.3226 |  |  | 26.1328 |  |  | 27.2854 |  |  | 28.5704 |  |  | 29.9318 |  |  | 31.4893
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2593 |  |  | 32.1891 |  |  | 31.8542 |  |  | 30.7823 |  |  | 28.2643 |  |  | 23.4033 |  |  | 16.4876 |  |  | 8.7774 |  |  | 0.60926 |  |  | -8.7356
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7039 |  |  | 45.4246 |  |  | 42.6934 |  |  | 38.3288 |  |  | 31.62 |  |  | 25.0623 |  |  | 17.6594 |  |  | 11.8787 |  |  | 8.393
[13 empty] | C Non choked w/ reducers | 7 |  | 0.30495 |  |  | 7.3479 |  |  | 17.7702 |  |  | 34.7141 |  |  | 60.3297 |  |  | 100.9136 |  |  | 166.2777 |  |  | 295.0366 |  |  | 1479.7785 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.25328 |  |  | 6.1002 |  |  | 14.8809 |  |  | 29.4765 |  |  | 51.8069 |  |  | 86.8175 |  |  | 134.8663 |  |  | 208.0042 |  |  | 335.1297 |  |  | 607.7454
[13 empty] | Selected C this iteration |  |  | 0.30495 |  |  | 7.3479 |  |  | 17.7702 |  |  | 34.7141 |  |  | 60.3297 |  |  | 100.9136 |  |  | 166.2777 |  |  | 295.0366 |  |  | 1479.7785 |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.695 | 1.7318 |  | 4.6521 | 41.6538 |  | 5.2298 | 99.9851 |  | 4.2859 | 190.9082 |  | 0.67026 | 313.9738 |  | 12.9136 | 467.4642 |  | 45.2777 | 623.8327 |  | 130.0366 | 761.1945 |  | 1233.7785 | 883.7232 |  | 5500 | 1005.7594
[13 empty] | Next iteration flow rate |  |  | 1.7664 | Abs Value of | Flow this | 42.0703 | Abs Value of | Flow this | 100.985 | Abs Value of | Flow this | 192.8173 | Abs Value of | Flow this | 317.1135 | Abs Value of | Flow this | 472.1388 | Abs Value of | Flow this | 630.071 | Abs Value of | Flow this | 768.8064 | Abs Value of | Flow this | 892.5604 | Abs Value of | Flow this | 1015.817 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8564 |  |  | 56.5717 |  |  | 55.6605 |  |  | 53.52 |  |  | 49.3878 |  |  | 43.5089 |  |  | 36.9545 |  |  | 30.0109 |  |  | 22.067
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6687 |  |  | 24.7257 |  |  | 24.9079 |  |  | 25.336 |  |  | 26.1624 |  |  | 27.3382 |  |  | 28.6491 |  |  | 30.0378 |  |  | 31.6266
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1876 |  |  | 31.8461 |  |  | 30.7526 |  |  | 28.184 |  |  | 23.2253 |  |  | 16.1706 |  |  | 8.3054 |  |  | -0.026911 |  |  | -9.5596
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7029 |  |  | 45.4191 |  |  | 42.6742 |  |  | 38.2806 |  |  | 31.5245 |  |  | 24.9095 |  |  | 17.4712 |  |  | 11.6695 |  |  | 8.1348
[13 empty] | C Non choked w/ reducers | 7 |  | 0.31105 |  |  | 7.4216 |  |  | 17.9502 |  |  | 35.0781 |  |  | 61.0198 |  |  | 102.3125 |  |  | 169.5786 |  |  | 306.3371 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.25834 |  |  | 6.1613 |  |  | 15.0306 |  |  | 29.778 |  |  | 52.3579 |  |  | 87.8185 |  |  | 136.632 |  |  | 211.2127 |  |  | 341.5016 |  |  | 623.4913
[13 empty] | Selected C this iteration |  |  | 0.31105 |  |  | 7.4216 |  |  | 17.9502 |  |  | 35.0781 |  |  | 61.0198 |  |  | 102.3125 |  |  | 169.5786 |  |  | 306.3371 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6889 | 1.7664 |  | 4.5784 | 42.0703 |  | 5.0498 | 100.985 |  | 3.9219 | 192.8173 |  | 0.019779 | 317.1135 |  | 14.3125 | 472.1388 |  | 48.5786 | 630.071 |  | 141.3371 | 768.8064 |  | 5500 | 892.5604 |  | 5500 | 1015.817
[13 empty] | Next iteration flow rate |  |  | 1.8018 | Abs Value of | Flow this | 42.491 | Abs Value of | Flow this | 101.9948 | Abs Value of | Flow this | 194.7455 | Abs Value of | Flow this | 320.2846 | Abs Value of | Flow this | 476.8602 | Abs Value of | Flow this | 636.3718 | Abs Value of | Flow this | 776.4945 | Abs Value of | Flow this | 901.486 | Abs Value of | Flow this | 1025.9751 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8552 |  |  | 56.5648 |  |  | 55.6353 |  |  | 53.4517 |  |  | 49.2365 |  |  | 43.2394 |  |  | 36.5533 |  |  | 29.4701 |  |  | 21.3665
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.669 |  |  | 24.727 |  |  | 24.9129 |  |  | 25.3497 |  |  | 26.1927 |  |  | 27.3921 |  |  | 28.7293 |  |  | 30.146 |  |  | 31.7667
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1862 |  |  | 31.8378 |  |  | 30.7224 |  |  | 28.102 |  |  | 23.0437 |  |  | 15.8473 |  |  | 7.824 |  |  | -0.67587 |  |  | -10.4002
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7019 |  |  | 45.4135 |  |  | 42.6547 |  |  | 38.2313 |  |  | 31.427 |  |  | 24.7536 |  |  | 17.2792 |  |  | 11.456 |  |  | 7.8713
[13 empty] | C Non choked w/ reducers | 7 |  | 0.31727 |  |  | 7.496 |  |  | 18.1321 |  |  | 35.4464 |  |  | 61.7197 |  |  | 103.742 |  |  | 173.0131 |  |  | 318.7784 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.26351 |  |  | 6.2229 |  |  | 15.1819 |  |  | 30.0826 |  |  | 52.9155 |  |  | 88.8341 |  |  | 138.4321 |  |  | 214.5066 |  |  | 348.1145 |  |  | 640.1788
[13 empty] | Selected C this iteration |  |  | 0.31727 |  |  | 7.496 |  |  | 18.1321 |  |  | 35.4464 |  |  | 61.7197 |  |  | 103.742 |  |  | 173.0131 |  |  | 318.7784 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6827 | 1.8018 |  | 4.504 | 42.491 |  | 4.8679 | 101.9948 |  | 3.5536 | 194.7455 |  | 0.71974 | 320.2846 |  | 15.742 | 476.8602 |  | 52.0131 | 636.3718 |  | 153.7784 | 776.4945 |  | 5500 | 901.486 |  | 5500 | 1025.9751
[13 empty] | Next iteration flow rate |  |  | 1.8378 | Abs Value of | Flow this | 42.9159 | Abs Value of | Flow this | 103.0148 | Abs Value of | Flow this | 196.6929 | Abs Value of | Flow this | 323.4875 | Abs Value of | Flow this | 481.6288 | Abs Value of | Flow this | 642.7355 | Abs Value of | Flow this | 784.2594 | Abs Value of | Flow this | 910.5008 | Abs Value of | Flow this | 1036.2349 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8539 |  |  | 56.5577 |  |  | 55.6096 |  |  | 53.3821 |  |  | 49.0821 |  |  | 42.9645 |  |  | 36.144 |  |  | 28.9184 |  |  | 20.652
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6692 |  |  | 24.7285 |  |  | 24.9181 |  |  | 25.3636 |  |  | 26.2236 |  |  | 27.4471 |  |  | 28.8112 |  |  | 30.2563 |  |  | 31.9096
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1847 |  |  | 31.8293 |  |  | 30.6915 |  |  | 28.0185 |  |  | 22.8585 |  |  | 15.5174 |  |  | 7.3328 |  |  | -1.3379 |  |  | -11.2577
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.7009 |  |  | 45.4078 |  |  | 42.6348 |  |  | 38.1811 |  |  | 31.3276 |  |  | 24.5946 |  |  | 17.0833 |  |  | 11.2383 |  |  | 7.6025
[13 empty] | C Non choked w/ reducers | 7 |  | 0.32362 |  |  | 7.5711 |  |  | 18.3158 |  |  | 35.8188 |  |  | 62.4298 |  |  | 105.2031 |  |  | 176.5909 |  |  | 332.574 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.26878 |  |  | 6.2852 |  |  | 15.3347 |  |  | 30.3905 |  |  | 53.4798 |  |  | 89.8646 |  |  | 140.2677 |  |  | 217.8899 |  |  | 354.9848 |  |  | 657.9106
[13 empty] | Selected C this iteration |  |  | 0.32362 |  |  | 7.5711 |  |  | 18.3158 |  |  | 35.8188 |  |  | 62.4298 |  |  | 105.2031 |  |  | 176.5909 |  |  | 332.574 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6764 | 1.8378 |  | 4.4289 | 42.9159 |  | 4.6842 | 103.0148 |  | 3.1812 | 196.6929 |  | 1.4298 | 323.4875 |  | 17.2031 | 481.6288 |  | 55.5909 | 642.7355 |  | 167.574 | 784.2594 |  | 5500 | 910.5008 |  | 5500 | 1036.2349
[13 empty] | Next iteration flow rate |  |  | 1.8746 | Abs Value of | Flow this | 43.3451 | Abs Value of | Flow this | 104.0449 | Abs Value of | Flow this | 198.6599 | Abs Value of | Flow this | 326.7224 | Abs Value of | Flow this | 486.4451 | Abs Value of | Flow this | 649.1628 | Abs Value of | Flow this | 792.102 | Abs Value of | Flow this | 919.6059 | Abs Value of | Flow this | 1046.5972 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8527 |  |  | 56.5505 |  |  | 55.5833 |  |  | 53.311 |  |  | 48.9246 |  |  | 42.684 |  |  | 35.7265 |  |  | 28.3557 |  |  | 19.923
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6695 |  |  | 24.7299 |  |  | 24.9233 |  |  | 25.3778 |  |  | 26.2551 |  |  | 27.5032 |  |  | 28.8947 |  |  | 30.3689 |  |  | 32.0554
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1832 |  |  | 31.8207 |  |  | 30.6599 |  |  | 27.9332 |  |  | 22.6696 |  |  | 15.1809 |  |  | 6.8318 |  |  | -2.0132 |  |  | -12.1324
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.6999 |  |  | 45.402 |  |  | 42.6145 |  |  | 38.1299 |  |  | 31.2262 |  |  | 24.4324 |  |  | 16.8836 |  |  | 11.0163 |  |  | 7.3283
[13 empty] | C Non choked w/ reducers | 7 |  | 0.33009 |  |  | 7.647 |  |  | 18.5015 |  |  | 36.1956 |  |  | 63.1503 |  |  | 106.697 |  |  | 180.3228 |  |  | 347.9988 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.27416 |  |  | 6.3482 |  |  | 15.489 |  |  | 30.7017 |  |  | 54.0509 |  |  | 90.9106 |  |  | 142.1398 |  |  | 221.367 |  |  | 362.1304 |  |  | 676.8057
[13 empty] | Selected C this iteration |  |  | 0.33009 |  |  | 7.647 |  |  | 18.5015 |  |  | 36.1956 |  |  | 63.1503 |  |  | 106.697 |  |  | 180.3228 |  |  | 347.9988 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6699 | 1.8746 |  | 4.353 | 43.3451 |  | 4.4985 | 104.0449 |  | 2.8044 | 198.6599 |  | 2.1503 | 326.7224 |  | 18.697 | 486.4451 |  | 59.3228 | 649.1628 |  | 182.9988 | 792.102 |  | 5500 | 919.6059 |  | 5500 | 1046.5972
[13 empty] | Next iteration flow rate |  |  | 1.912 | Abs Value of | Flow this | 43.7785 | Abs Value of | Flow this | 105.0854 | Abs Value of | Flow this | 200.6465 | Abs Value of | Flow this | 329.9896 | Abs Value of | Flow this | 491.3095 | Abs Value of | Flow this | 655.6545 | Abs Value of | Flow this | 800.023 | Abs Value of | Flow this | 928.8019 | Abs Value of | Flow this | 1057.0632 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8514 |  |  | 56.5432 |  |  | 55.5565 |  |  | 53.2386 |  |  | 48.764 |  |  | 42.398 |  |  | 35.3006 |  |  | 27.7816 |  |  | 19.1795
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6697 |  |  | 24.7314 |  |  | 24.9287 |  |  | 25.3923 |  |  | 26.2872 |  |  | 27.5604 |  |  | 28.9799 |  |  | 30.4837 |  |  | 32.2041
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1817 |  |  | 31.8118 |  |  | 30.6278 |  |  | 27.8463 |  |  | 22.4768 |  |  | 14.8376 |  |  | 6.3207 |  |  | -2.702 |  |  | -13.0246
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.6988 |  |  | 45.3961 |  |  | 42.5938 |  |  | 38.0776 |  |  | 31.1227 |  |  | 24.267 |  |  | 16.6798 |  |  | 10.7897 |  |  | 7.0487
[13 empty] | C Non choked w/ reducers | 7 |  | 0.33669 |  |  | 7.7236 |  |  | 18.6891 |  |  | 36.5768 |  |  | 63.8813 |  |  | 108.2251 |  |  | 184.2208 |  |  | 365.413 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.27964 |  |  | 6.4117 |  |  | 15.6449 |  |  | 31.0163 |  |  | 54.6289 |  |  | 91.9721 |  |  | 144.0497 |  |  | 224.9423 |  |  | 369.5715 |  |  | 697.0036
[13 empty] | Selected C this iteration |  |  | 0.33669 |  |  | 7.7236 |  |  | 18.6891 |  |  | 36.5768 |  |  | 63.8813 |  |  | 108.2251 |  |  | 184.2208 |  |  | 365.413 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6633 | 1.912 |  | 4.2764 | 43.7785 |  | 4.3109 | 105.0854 |  | 2.4232 | 200.6465 |  | 2.8813 | 329.9896 |  | 20.2251 | 491.3095 |  | 63.2208 | 655.6545 |  | 200.413 | 800.023 |  | 5500 | 928.8019 |  | 5500 | 1057.0632
[13 empty] | Next iteration flow rate |  |  | 1.9503 | Abs Value of | Flow this | 44.2163 | Abs Value of | Flow this | 106.1362 | Abs Value of | Flow this | 202.6529 | Abs Value of | Flow this | 333.2895 | Abs Value of | Flow this | 496.2226 | Abs Value of | Flow this | 662.211 | Abs Value of | Flow this | 808.0233 | Abs Value of | Flow this | 938.0899 | Abs Value of | Flow this | 1067.6338 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8501 |  |  | 56.5357 |  |  | 55.5292 |  |  | 53.1646 |  |  | 48.6001 |  |  | 42.1062 |  |  | 34.8661 |  |  | 27.196 |  |  | 18.421
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.67 |  |  | 24.7329 |  |  | 24.9342 |  |  | 25.4071 |  |  | 26.32 |  |  | 27.6188 |  |  | 29.0668 |  |  | 30.6008 |  |  | 32.3558
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1801 |  |  | 31.8028 |  |  | 30.595 |  |  | 27.7576 |  |  | 22.2802 |  |  | 14.4874 |  |  | 5.7993 |  |  | -3.4048 |  |  | -13.9348
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.6978 |  |  | 45.39 |  |  | 42.5727 |  |  | 38.0243 |  |  | 31.0172 |  |  | 24.0982 |  |  | 16.4719 |  |  | 10.5586 |  |  | 6.7634
[13 empty] | C Non choked w/ reducers | 7 |  | 0.34343 |  |  | 7.8011 |  |  | 18.8787 |  |  | 36.9623 |  |  | 64.6231 |  |  | 109.7886 |  |  | 188.2983 |  |  | 385.3 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.28523 |  |  | 6.4759 |  |  | 15.8024 |  |  | 31.3342 |  |  | 55.2138 |  |  | 93.0498 |  |  | 145.9988 |  |  | 228.6209 |  |  | 377.3299 |  |  | 718.6685
[13 empty] | Selected C this iteration |  |  | 0.34343 |  |  | 7.8011 |  |  | 18.8787 |  |  | 36.9623 |  |  | 64.6231 |  |  | 109.7886 |  |  | 188.2983 |  |  | 385.3 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6566 | 1.9503 |  | 4.1989 | 44.2163 |  | 4.1213 | 106.1362 |  | 2.0377 | 202.6529 |  | 3.6231 | 333.2895 |  | 21.7886 | 496.2226 |  | 67.2983 | 662.211 |  | 220.3 | 808.0233 |  | 5500 | 938.0899 |  | 5500 | 1067.6338
[13 empty] | Next iteration flow rate |  |  | 1.9893 | Abs Value of | Flow this | 44.6585 | Abs Value of | Flow this | 107.1976 | Abs Value of | Flow this | 204.6795 | Abs Value of | Flow this | 336.6224 | Abs Value of | Flow this | 501.1848 | Abs Value of | Flow this | 668.8331 | Abs Value of | Flow this | 816.1035 | Abs Value of | Flow this | 947.4708 | Abs Value of | Flow this | 1078.3102 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8488 |  |  | 56.5281 |  |  | 55.5013 |  |  | 53.0892 |  |  | 48.433 |  |  | 41.8085 |  |  | 34.4229 |  |  | 26.5986 |  |  | 17.6472
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6702 |  |  | 24.7344 |  |  | 24.9397 |  |  | 25.4222 |  |  | 26.3534 |  |  | 27.6783 |  |  | 29.1554 |  |  | 30.7203 |  |  | 32.5106
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1785 |  |  | 31.7937 |  |  | 30.5616 |  |  | 27.6671 |  |  | 22.0796 |  |  | 14.1302 |  |  | 5.2675 |  |  | -4.1216 |  |  | -14.8633
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7651 |  |  | 46.6967 |  |  | 45.3838 |  |  | 42.5512 |  |  | 37.9699 |  |  | 30.9096 |  |  | 23.926 |  |  | 16.2598 |  |  | 10.3229 |  |  | 6.4723
[13 empty] | C Non choked w/ reducers | 7 |  | 0.3503 |  |  | 7.8793 |  |  | 19.0702 |  |  | 37.3524 |  |  | 65.376 |  |  | 111.3891 |  |  | 192.5702 |  |  | 408.3266 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.29094 |  |  | 6.5407 |  |  | 15.9615 |  |  | 31.6556 |  |  | 55.8059 |  |  | 94.1438 |  |  | 147.9884 |  |  | 232.4079 |  |  | 385.4302 |  |  | 741.9955
[13 empty] | Selected C this iteration |  |  | 0.3503 |  |  | 7.8793 |  |  | 19.0702 |  |  | 37.3524 |  |  | 65.376 |  |  | 111.3891 |  |  | 192.5702 |  |  | 408.3266 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6497 | 1.9893 |  | 4.1207 | 44.6585 |  | 3.9298 | 107.1976 |  | 1.6476 | 204.6795 |  | 4.376 | 336.6224 |  | 23.3891 | 501.1848 |  | 71.5702 | 668.8331 |  | 243.3266 | 816.1035 |  | 5500 | 947.4708 |  | 5500 | 1078.3102
[13 empty] | Next iteration flow rate |  |  | 2.0291 | Abs Value of | Flow this | 45.1051 | Abs Value of | Flow this | 108.2696 | Abs Value of | Flow this | 206.7263 | Abs Value of | Flow this | 339.9886 | Abs Value of | Flow this | 506.1967 | Abs Value of | Flow this | 675.5214 | Abs Value of | Flow this | 824.2645 | Abs Value of | Flow this | 956.9455 | Abs Value of | Flow this | 1089.0933 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8474 |  |  | 56.5203 |  |  | 55.4729 |  |  | 53.0123 |  |  | 48.2625 |  |  | 41.5048 |  |  | 33.9708 |  |  | 25.9893 |  |  | 16.8579
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6705 |  |  | 24.7359 |  |  | 24.9454 |  |  | 25.4375 |  |  | 26.3875 |  |  | 27.739 |  |  | 29.2458 |  |  | 30.8421 |  |  | 32.6684
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1769 |  |  | 31.7843 |  |  | 30.5274 |  |  | 27.5748 |  |  | 21.875 |  |  | 13.7658 |  |  | 4.7249 |  |  | -4.8529 |  |  | -15.8105
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.6955 |  |  | 45.3775 |  |  | 42.5292 |  |  | 37.9145 |  |  | 30.7997 |  |  | 23.7504 |  |  | 16.0435 |  |  | 10.0824 |  |  | 6.1754
[13 empty] | C Non choked w/ reducers | 7 |  | 0.3573 |  |  | 7.9583 |  |  | 19.2637 |  |  | 37.747 |  |  | 66.1401 |  |  | 113.0279 |  |  | 197.0534 |  |  | 435.4439 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.29676 |  |  | 6.6062 |  |  | 16.1223 |  |  | 31.9804 |  |  | 56.4052 |  |  | 95.2546 |  |  | 150.0199 |  |  | 236.3092 |  |  | 393.8996 |  |  | 767.2184
[13 empty] | Selected C this iteration |  |  | 0.3573 |  |  | 7.9583 |  |  | 19.2637 |  |  | 37.747 |  |  | 66.1401 |  |  | 113.0279 |  |  | 197.0534 |  |  | 435.4439 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6427 | 2.0291 |  | 4.0417 | 45.1051 |  | 3.7363 | 108.2696 |  | 1.253 | 206.7263 |  | 5.1401 | 339.9886 |  | 25.0279 | 506.1967 |  | 76.0534 | 675.5214 |  | 270.4439 | 824.2645 |  | 5500 | 956.9455 |  | 5500 | 1089.0933
[13 empty] | Next iteration flow rate |  |  | 2.0697 | Abs Value of | Flow this | 45.5561 | Abs Value of | Flow this | 109.3523 | Abs Value of | Flow this | 208.7935 | Abs Value of | Flow this | 343.3885 | Abs Value of | Flow this | 511.2587 | Abs Value of | Flow this | 682.2767 | Abs Value of | Flow this | 832.5072 | Abs Value of | Flow this | 966.515 | Abs Value of | Flow this | 1099.9842 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8461 |  |  | 56.5123 |  |  | 55.4438 |  |  | 52.9339 |  |  | 48.0885 |  |  | 41.1951 |  |  | 33.5096 |  |  | 25.3676 |  |  | 16.0527
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6708 |  |  | 24.7375 |  |  | 24.9512 |  |  | 25.4532 |  |  | 26.4223 |  |  | 27.801 |  |  | 29.3381 |  |  | 30.9665 |  |  | 32.8295
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1753 |  |  | 31.7748 |  |  | 30.4926 |  |  | 27.4806 |  |  | 21.6662 |  |  | 13.3941 |  |  | 4.1715 |  |  | -5.5988 |  |  | -16.7767
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.6944 |  |  | 45.3711 |  |  | 42.5068 |  |  | 37.8579 |  |  | 30.6877 |  |  | 23.5712 |  |  | 15.8228 |  |  | 9.8371 |  |  | 5.8726
[13 empty] | C Non choked w/ reducers | 7 |  | 0.36445 |  |  | 8.0381 |  |  | 19.4593 |  |  | 38.1462 |  |  | 66.9159 |  |  | 114.7067 |  |  | 201.7667 |  |  | 468.0645 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.30269 |  |  | 6.6724 |  |  | 16.2847 |  |  | 32.3087 |  |  | 57.0118 |  |  | 96.3826 |  |  | 152.0949 |  |  | 240.3309 |  |  | 402.7686 |  |  | 794.6206
[13 empty] | Selected C this iteration |  |  | 0.36445 |  |  | 8.0381 |  |  | 19.4593 |  |  | 38.1462 |  |  | 66.9159 |  |  | 114.7067 |  |  | 201.7667 |  |  | 468.0645 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6356 | 2.0697 |  | 3.9619 | 45.5561 |  | 3.5407 | 109.3523 |  | 0.85379 | 208.7935 |  | 5.9159 | 343.3885 |  | 26.7067 | 511.2587 |  | 80.7667 | 682.2767 |  | 303.0645 | 832.5072 |  | 5500 | 966.515 |  | 5500 | 1099.9842
[13 empty] | Next iteration flow rate |  |  | 2.111 | Abs Value of | Flow this | 46.0117 | Abs Value of | Flow this | 110.4458 | Abs Value of | Flow this | 210.8815 | Abs Value of | Flow this | 346.8224 | Abs Value of | Flow this | 516.3712 | Abs Value of | Flow this | 689.0994 | Abs Value of | Flow this | 840.8323 | Abs Value of | Flow this | 976.1801 | Abs Value of | Flow this | 1110.9841 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8446 |  |  | 56.5042 |  |  | 55.4143 |  |  | 52.8538 |  |  | 47.9111 |  |  | 40.8791 |  |  | 33.0391 |  |  | 24.7335 |  |  | 15.2314
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6711 |  |  | 24.7392 |  |  | 24.9571 |  |  | 25.4692 |  |  | 26.4578 |  |  | 27.8642 |  |  | 29.4322 |  |  | 31.0933 |  |  | 32.9937
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1736 |  |  | 31.765 |  |  | 30.4571 |  |  | 27.3846 |  |  | 21.4533 |  |  | 13.0149 |  |  | 3.6069 |  |  | -6.3598 |  |  | -17.7623
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.6932 |  |  | 45.3645 |  |  | 42.4839 |  |  | 37.8001 |  |  | 30.5734 |  |  | 23.3885 |  |  | 15.5977 |  |  | 9.5868 |  |  | 5.5636
[13 empty] | C Non choked w/ reducers | 7 |  | 0.37174 |  |  | 8.1187 |  |  | 19.6569 |  |  | 38.5501 |  |  | 67.7035 |  |  | 116.4273 |  |  | 206.7317 |  |  | 508.3983 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.30875 |  |  | 6.7392 |  |  | 16.4487 |  |  | 32.6406 |  |  | 57.6258 |  |  | 97.5281 |  |  | 154.2148 |  |  | 244.4795 |  |  | 412.0713 |  |  | 824.5488
[13 empty] | Selected C this iteration |  |  | 0.37174 |  |  | 8.1187 |  |  | 19.6569 |  |  | 38.5501 |  |  | 67.7035 |  |  | 116.4273 |  |  | 206.7317 |  |  | 508.3983 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6283 | 2.111 |  | 3.8813 | 46.0117 |  | 3.3431 | 110.4458 |  | 0.44988 | 210.8815 |  | 6.7035 | 346.8224 |  | 28.4273 | 516.3712 |  | 85.7317 | 689.0994 |  | 343.3983 | 840.8323 |  | 5500 | 976.1801 |  | 5500 | 1110.9841
[13 empty] | Next iteration flow rate |  |  | 2.1533 | Abs Value of | Flow this | 46.4718 | Abs Value of | Flow this | 111.5502 | Abs Value of | Flow this | 212.9903 | Abs Value of | Flow this | 350.2906 | Abs Value of | Flow this | 521.535 | Abs Value of | Flow this | 695.9904 | Abs Value of | Flow this | 849.2406 | Abs Value of | Flow this | 985.9419 | Abs Value of | Flow this | 1122.0939 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8432 |  |  | 56.4959 |  |  | 55.3841 |  |  | 52.7722 |  |  | 47.7301 |  |  | 40.5567 |  |  | 32.5592 |  |  | 24.0866 |  |  | 14.3935
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6714 |  |  | 24.7408 |  |  | 24.9632 |  |  | 25.4856 |  |  | 26.494 |  |  | 27.9287 |  |  | 29.5282 |  |  | 31.2227 |  |  | 33.1613
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1718 |  |  | 31.7551 |  |  | 30.4209 |  |  | 27.2866 |  |  | 21.2361 |  |  | 12.6281 |  |  | 3.031 |  |  | -7.136 |  |  | -18.7678
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.692 |  |  | 45.3578 |  |  | 42.4606 |  |  | 37.7412 |  |  | 30.4569 |  |  | 23.202 |  |  | 15.3681 |  |  | 9.3316 |  |  | 5.2485
[13 empty] | C Non choked w/ reducers | 7 |  | 0.37917 |  |  | 8.2001 |  |  | 19.8566 |  |  | 38.9588 |  |  | 68.5032 |  |  | 118.1914 |  |  | 211.9728 |  |  | 560.1446 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.31492 |  |  | 6.8067 |  |  | 16.6144 |  |  | 32.976 |  |  | 58.2475 |  |  | 98.6918 |  |  | 156.3815 |  |  | 248.7622 |  |  | 421.8462 |  |  | 857.4332
[13 empty] | Selected C this iteration |  |  | 0.37917 |  |  | 8.2001 |  |  | 19.8566 |  |  | 38.9588 |  |  | 68.5032 |  |  | 118.1914 |  |  | 211.9728 |  |  | 560.1446 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6208 | 2.1533 |  | 3.7999 | 46.4718 |  | 3.1434 | 111.5502 |  | 0.041201 | 212.9903 |  | 7.5032 | 350.2906 |  | 30.1914 | 521.535 |  | 90.9728 | 695.9904 |  | 395.1446 | 849.2406 |  | 5500 | 985.9419 |  | 5500 | 1122.0939
[13 empty] | Next iteration flow rate |  |  | 2.1963 | Abs Value of | Flow this | 46.9365 | Abs Value of | Flow this | 112.6657 | Abs Value of | Flow this | 215.1202 | Abs Value of | Flow this | 353.7935 | Abs Value of | Flow this | 526.7503 | Abs Value of | Flow this | 702.9503 | Abs Value of | Flow this | 857.733 | Abs Value of | Flow this | 995.8014 | Abs Value of | Flow this | 1133.3148 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8417 |  |  | 56.4875 |  |  | 55.3533 |  |  | 52.6889 |  |  | 47.5455 |  |  | 40.2279 |  |  | 32.0696 |  |  | 23.4268 |  |  | 13.5388
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6717 |  |  | 24.7425 |  |  | 24.9693 |  |  | 25.5022 |  |  | 26.5309 |  |  | 27.9944 |  |  | 29.6261 |  |  | 31.3546 |  |  | 33.3322
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1701 |  |  | 31.7449 |  |  | 30.3839 |  |  | 27.1866 |  |  | 21.0146 |  |  | 12.2335 |  |  | 2.4435 |  |  | -7.9279 |  |  | -19.7934
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.6908 |  |  | 45.3509 |  |  | 42.4368 |  |  | 37.6812 |  |  | 30.338 |  |  | 23.0119 |  |  | 15.1339 |  |  | 9.0712 |  |  | 4.927
[13 empty] | C Non choked w/ reducers | 7 |  | 0.38675 |  |  | 8.2823 |  |  | 20.0583 |  |  | 39.3723 |  |  | 69.3153 |  |  | 120.001 |  |  | 217.5179 |  |  | 630.0965 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.32122 |  |  | 6.8748 |  |  | 16.7818 |  |  | 33.3151 |  |  | 58.8768 |  |  | 99.8738 |  |  | 158.5966 |  |  | 253.1869 |  |  | 432.1369 |  |  | 893.8149
[13 empty] | Selected C this iteration |  |  | 0.38675 |  |  | 8.2823 |  |  | 20.0583 |  |  | 39.3723 |  |  | 69.3153 |  |  | 120.001 |  |  | 217.5179 |  |  | 630.0965 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6132 | 2.1963 |  | 3.7177 | 46.9365 |  | 2.9417 | 112.6657 |  | 0.37231 | 215.1202 |  | 8.3153 | 353.7935 |  | 32.001 | 526.7503 |  | 96.5179 | 702.9503 |  | 465.0965 | 857.733 |  | 5500 | 995.8014 |  | 5500 | 1133.3148
[13 empty] | Next iteration flow rate |  |  | 2.2403 | Abs Value of | Flow this | 47.4059 | Abs Value of | Flow this | 113.7924 | Abs Value of | Flow this | 217.2714 | Abs Value of | Flow this | 357.3314 | Abs Value of | Flow this | 532.0178 | Abs Value of | Flow this | 709.9798 | Abs Value of | Flow this | 866.3103 | Abs Value of | Flow this | 1005.7594 | Abs Value of | Flow this | 1144.648 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8402 |  |  | 56.4788 |  |  | 55.3219 |  |  | 52.6039 |  |  | 47.3571 |  |  | 39.8925 |  |  | 31.5702 |  |  | 22.7536 |  |  | 12.6669
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.672 |  |  | 24.7442 |  |  | 24.9756 |  |  | 25.5192 |  |  | 26.5686 |  |  | 28.0615 |  |  | 29.726 |  |  | 31.4893 |  |  | 33.5066
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1683 |  |  | 31.7346 |  |  | 30.3462 |  |  | 27.0847 |  |  | 20.7885 |  |  | 11.8309 |  |  | 1.8442 |  |  | -8.7356 |  |  | -20.8397
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.6896 |  |  | 45.344 |  |  | 42.4125 |  |  | 37.6199 |  |  | 30.2166 |  |  | 22.8179 |  |  | 14.8949 |  |  | 8.8055 |  |  | 4.599
[13 empty] | C Non choked w/ reducers | 7 |  | 0.39449 |  |  | 8.3653 |  |  | 20.2622 |  |  | 39.7907 |  |  | 70.1401 |  |  | 121.8581 |  |  | 223.3991 |  |  | 732.5369 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.32764 |  |  | 6.9437 |  |  | 16.9509 |  |  | 33.6579 |  |  | 59.514 |  |  | 101.0749 |  |  | 160.8621 |  |  | 257.7618 |  |  | 442.9927 |  |  | 934.386
[13 empty] | Selected C this iteration |  |  | 0.39449 |  |  | 8.3653 |  |  | 20.2622 |  |  | 39.7907 |  |  | 70.1401 |  |  | 121.8581 |  |  | 223.3991 |  |  | 732.5369 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.6055 | 2.2403 |  | 3.6347 | 47.4059 |  | 2.7378 | 113.7924 |  | 0.79072 | 217.2714 |  | 9.1401 | 357.3314 |  | 33.8581 | 532.0178 |  | 102.3991 | 709.9798 |  | 567.5369 | 866.3103 |  | 5500 | 1005.7594 |  | 5500 | 1144.648
[13 empty] | Next iteration flow rate |  |  | 2.2851 | Abs Value of | Flow this | 47.88 | Abs Value of | Flow this | 114.9303 | Abs Value of | Flow this | 219.4441 | Abs Value of | Flow this | 360.9047 | Abs Value of | Flow this | 537.338 | Abs Value of | Flow this | 717.0796 | Abs Value of | Flow this | 874.9734 | Abs Value of | Flow this | 1015.817 | Abs Value of | Flow this | 1156.0945 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8387 |  |  | 56.47 |  |  | 55.2898 |  |  | 52.5172 |  |  | 47.165 |  |  | 39.5503 |  |  | 31.0607 |  |  | 22.067 |  |  | 11.7775
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6723 |  |  | 24.746 |  |  | 24.982 |  |  | 25.5366 |  |  | 26.607 |  |  | 28.1299 |  |  | 29.8279 |  |  | 31.6266 |  |  | 33.6845
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1665 |  |  | 31.7241 |  |  | 30.3078 |  |  | 26.9807 |  |  | 20.558 |  |  | 11.4203 |  |  | 1.2329 |  |  | -9.5596 |  |  | -21.907
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.6883 |  |  | 45.3369 |  |  | 42.3877 |  |  | 37.5574 |  |  | 30.0929 |  |  | 22.62 |  |  | 14.6511 |  |  | 8.5346 |  |  | 4.2645
[13 empty] | C Non choked w/ reducers | 7 |  | 0.40238 |  |  | 8.4492 |  |  | 20.4682 |  |  | 40.2141 |  |  | 70.9779 |  |  | 123.7649 |  |  | 229.6535 |  |  | 904.8923 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.3342 |  |  | 7.0132 |  |  | 17.1218 |  |  | 34.0044 |  |  | 60.1592 |  |  | 102.2953 |  |  | 163.1799 |  |  | 262.4962 |  |  | 454.4701 |  |  | 980.0482
[13 empty] | Selected C this iteration |  |  | 0.40238 |  |  | 8.4492 |  |  | 20.4682 |  |  | 40.2141 |  |  | 70.9779 |  |  | 123.7649 |  |  | 229.6535 |  |  | 904.8923 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5976 | 2.2851 |  | 3.5508 | 47.88 |  | 2.5318 | 114.9303 |  | 1.2141 | 219.4441 |  | 9.9779 | 360.9047 |  | 35.7649 | 537.338 |  | 108.6535 | 717.0796 |  | 739.8923 | 874.9734 |  | 5500 | 1015.817 |  | 5500 | 1156.0945
[13 empty] | Next iteration flow rate |  |  | 2.3308 | Abs Value of | Flow this | 48.3588 | Abs Value of | Flow this | 116.0796 | Abs Value of | Flow this | 221.6385 | Abs Value of | Flow this | 364.5138 | Abs Value of | Flow this | 542.7114 | Abs Value of | Flow this | 724.2504 | Abs Value of | Flow this | 883.7232 | Abs Value of | Flow this | 1025.9751 | Abs Value of | Flow this | 1167.6554 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8372 |  |  | 56.4611 |  |  | 55.2571 |  |  | 52.4288 |  |  | 46.969 |  |  | 39.2012 |  |  | 30.541 |  |  | 21.3665 |  |  | 10.8702
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6726 |  |  | 24.7478 |  |  | 24.9886 |  |  | 25.5542 |  |  | 26.6462 |  |  | 28.1998 |  |  | 29.9318 |  |  | 31.7667 |  |  | 33.866
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2592 |  |  | 32.1646 |  |  | 31.7133 |  |  | 30.2685 |  |  | 26.8746 |  |  | 20.3228 |  |  | 11.0015 |  |  | 0.60926 |  |  | -10.4002 |  |  | -22.9957
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.687 |  |  | 45.3296 |  |  | 42.3625 |  |  | 37.4936 |  |  | 29.9667 |  |  | 22.4181 |  |  | 14.4025 |  |  | 8.2581 |  |  | 3.9232
[13 empty] | C Non choked w/ reducers | 7 |  | 0.41043 |  |  | 8.534 |  |  | 20.6764 |  |  | 40.6426 |  |  | 71.8291 |  |  | 125.7238 |  |  | 236.3244 |  |  | 1300.1104 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.34088 |  |  | 7.0834 |  |  | 17.2944 |  |  | 34.3547 |  |  | 60.8124 |  |  | 103.5356 |  |  | 165.5521 |  |  | 267.4 |  |  | 466.6338 |  |  | 1032.0028
[13 empty] | Selected C this iteration |  |  | 0.41043 |  |  | 8.534 |  |  | 20.6764 |  |  | 40.6426 |  |  | 71.8291 |  |  | 125.7238 |  |  | 236.3244 |  |  | 1300.1104 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5896 | 2.3308 |  | 3.466 | 48.3588 |  | 2.3236 | 116.0796 |  | 1.6426 | 221.6385 |  | 10.8291 | 364.5138 |  | 37.7238 | 542.7114 |  | 115.3244 | 724.2504 |  | 1135.1104 | 883.7232 |  | 5500 | 1025.9751 |  | 5500 | 1167.6554
[13 empty] | Next iteration flow rate |  |  | 2.3774 | Abs Value of | Flow this | 48.8423 | Abs Value of | Flow this | 117.2404 | Abs Value of | Flow this | 223.8549 | Abs Value of | Flow this | 368.1589 | Abs Value of | Flow this | 548.1385 | Abs Value of | Flow this | 731.4929 | Abs Value of | Flow this | 892.5604 | Abs Value of | Flow this | 1036.2349 | Abs Value of | Flow this | 1179.332 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.916 |  |  | 56.8356 |  |  | 56.4519 |  |  | 55.2238 |  |  | 52.3386 |  |  | 46.769 |  |  | 38.8452 |  |  | 30.0109 |  |  | 20.652 |  |  | 9.9447
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6729 |  |  | 24.7496 |  |  | 24.9952 |  |  | 25.5723 |  |  | 26.6862 |  |  | 28.271 |  |  | 30.0378 |  |  | 31.9096 |  |  | 34.0511
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1627 |  |  | 31.7023 |  |  | 30.2285 |  |  | 26.7663 |  |  | 20.0828 |  |  | 10.5742 |  |  | -0.026911 |  |  | -11.2577 |  |  | -24.1063
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.6857 |  |  | 45.3222 |  |  | 42.3367 |  |  | 37.4286 |  |  | 29.8379 |  |  | 22.2121 |  |  | 14.1488 |  |  | 7.9762 |  |  | 3.5751
[13 empty] | C Non choked w/ reducers | 7 |  | 0.41864 |  |  | 8.6196 |  |  | 20.8868 |  |  | 41.0762 |  |  | 72.6939 |  |  | 127.7373 |  |  | 243.4623 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.3477 |  |  | 7.1543 |  |  | 17.4688 |  |  | 34.7088 |  |  | 61.4739 |  |  | 104.7964 |  |  | 167.981 |  |  | 272.4842 |  |  | 479.5587 |  |  | 1091.8926
[13 empty] | Selected C this iteration |  |  | 0.41864 |  |  | 8.6196 |  |  | 20.8868 |  |  | 41.0762 |  |  | 72.6939 |  |  | 127.7373 |  |  | 243.4623 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5814 | 2.3774 |  | 3.3804 | 48.8423 |  | 2.1132 | 117.2404 |  | 2.0762 | 223.8549 |  | 11.6939 | 368.1589 |  | 39.7373 | 548.1385 |  | 122.4623 | 731.4929 |  | 5500 | 892.5604 |  | 5500 | 1036.2349 |  | 5500 | 1179.332
[13 empty] | Next iteration flow rate |  |  | 2.4249 | Abs Value of | Flow this | 49.3308 | Abs Value of | Flow this | 118.4128 | Abs Value of | Flow this | 226.0935 | Abs Value of | Flow this | 371.8405 | Abs Value of | Flow this | 553.6199 | Abs Value of | Flow this | 738.8079 | Abs Value of | Flow this | 901.486 | Abs Value of | Flow this | 1046.5972 | Abs Value of | Flow this | 1191.1253 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.834 |  |  | 56.4426 |  |  | 55.1898 |  |  | 52.2466 |  |  | 46.5651 |  |  | 38.4819 |  |  | 29.4701 |  |  | 19.923 |  |  | 9.0006
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6732 |  |  | 24.7515 |  |  | 25.002 |  |  | 25.5907 |  |  | 26.727 |  |  | 28.3436 |  |  | 30.146 |  |  | 32.0554 |  |  | 34.2399
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1607 |  |  | 31.6911 |  |  | 30.1877 |  |  | 26.6559 |  |  | 19.8381 |  |  | 10.1383 |  |  | -0.67587 |  |  | -12.1324 |  |  | -25.2393
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.6844 |  |  | 45.3147 |  |  | 42.3104 |  |  | 37.3622 |  |  | 29.7065 |  |  | 22.0021 |  |  | 13.8901 |  |  | 7.6885 |  |  | 3.22
[13 empty] | C Non choked w/ reducers | 7 |  | 0.42701 |  |  | 8.706 |  |  | 21.0994 |  |  | 41.515 |  |  | 73.5727 |  |  | 129.8081 |  |  | 251.1272 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.35465 |  |  | 7.226 |  |  | 17.6449 |  |  | 35.0668 |  |  | 62.1437 |  |  | 106.0781 |  |  | 170.4688 |  |  | 277.7606 |  |  | 493.3316 |  |  | 1162.0349
[13 empty] | Selected C this iteration |  |  | 0.42701 |  |  | 8.706 |  |  | 21.0994 |  |  | 41.515 |  |  | 73.5727 |  |  | 129.8081 |  |  | 251.1272 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.573 | 2.4249 |  | 3.294 | 49.3308 |  | 1.9006 | 118.4128 |  | 2.515 | 226.0935 |  | 12.5727 | 371.8405 |  | 41.8081 | 553.6199 |  | 130.1272 | 738.8079 |  | 5500 | 901.486 |  | 5500 | 1046.5972 |  | 5500 | 1191.1253
[13 empty] | Next iteration flow rate |  |  | 2.4734 | Abs Value of | Flow this | 49.8241 | Abs Value of | Flow this | 119.5969 | Abs Value of | Flow this | 228.3544 | Abs Value of | Flow this | 375.5589 | Abs Value of | Flow this | 559.1561 | Abs Value of | Flow this | 746.1959 | Abs Value of | Flow this | 910.5008 | Abs Value of | Flow this | 1057.0632 | Abs Value of | Flow this | 1203.0365 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8323 |  |  | 56.4331 |  |  | 55.1551 |  |  | 52.1527 |  |  | 46.357 |  |  | 38.1114 |  |  | 28.9184 |  |  | 19.1795 |  |  | 8.0375
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6735 |  |  | 24.7534 |  |  | 25.009 |  |  | 25.6095 |  |  | 26.7686 |  |  | 28.4177 |  |  | 30.2563 |  |  | 32.2041 |  |  | 34.4325
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1588 |  |  | 31.6797 |  |  | 30.1461 |  |  | 26.5433 |  |  | 19.5884 |  |  | 9.6937 |  |  | -1.3379 |  |  | -13.0246 |  |  | -26.395
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.683 |  |  | 45.307 |  |  | 42.2836 |  |  | 37.2945 |  |  | 29.5725 |  |  | 21.7878 |  |  | 13.6261 |  |  | 7.3951 |  |  | 2.8577
[13 empty] | C Non choked w/ reducers | 7 |  | 0.43555 |  |  | 8.7934 |  |  | 21.3142 |  |  | 41.9591 |  |  | 74.4659 |  |  | 131.939 |  |  | 259.3903 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.36175 |  |  | 7.2984 |  |  | 17.8229 |  |  | 35.4287 |  |  | 62.8221 |  |  | 107.3813 |  |  | 173.0182 |  |  | 283.2424 |  |  | 508.0541 |  |  | 1245.8265
[13 empty] | Selected C this iteration |  |  | 0.43555 |  |  | 8.7934 |  |  | 21.3142 |  |  | 41.9591 |  |  | 74.4659 |  |  | 131.939 |  |  | 259.3903 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5645 | 2.4734 |  | 3.2066 | 49.8241 |  | 1.6858 | 119.5969 |  | 2.9591 | 228.3544 |  | 13.4659 | 375.5589 |  | 43.939 | 559.1561 |  | 138.3903 | 746.1959 |  | 5500 | 910.5008 |  | 5500 | 1057.0632 |  | 5500 | 1203.0365
[13 empty] | Next iteration flow rate |  |  | 2.5229 | Abs Value of | Flow this | 50.3223 | Abs Value of | Flow this | 120.7929 | Abs Value of | Flow this | 230.638 | Abs Value of | Flow this | 379.3145 | Abs Value of | Flow this | 564.7476 | Abs Value of | Flow this | 753.6579 | Abs Value of | Flow this | 919.6059 | Abs Value of | Flow this | 1067.6338 | Abs Value of | Flow this | 1215.0669 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8306 |  |  | 56.4234 |  |  | 55.1197 |  |  | 52.057 |  |  | 46.1448 |  |  | 37.7334 |  |  | 28.3557 |  |  | 18.421 |  |  | 7.055
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6739 |  |  | 24.7553 |  |  | 25.0161 |  |  | 25.6286 |  |  | 26.811 |  |  | 28.4933 |  |  | 30.3689 |  |  | 32.3558 |  |  | 34.629
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1567 |  |  | 31.668 |  |  | 30.1036 |  |  | 26.4284 |  |  | 19.3337 |  |  | 9.2401 |  |  | -2.0132 |  |  | -13.9348 |  |  | -27.574
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.6816 |  |  | 45.2991 |  |  | 42.2562 |  |  | 37.2255 |  |  | 29.4359 |  |  | 21.5692 |  |  | 13.3569 |  |  | 7.0958 |  |  | 2.4882
[13 empty] | C Non choked w/ reducers | 7 |  | 0.44426 |  |  | 8.8816 |  |  | 21.5313 |  |  | 42.4085 |  |  | 75.3739 |  |  | 134.1333 |  |  | 268.3372 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.36898 |  |  | 7.3715 |  |  | 18.0027 |  |  | 35.7946 |  |  | 63.5091 |  |  | 108.7067 |  |  | 175.6317 |  |  | 288.9439 |  |  | 523.8459 |  |  | 1348.492
[13 empty] | Selected C this iteration |  |  | 0.44426 |  |  | 8.8816 |  |  | 21.5313 |  |  | 42.4085 |  |  | 75.3739 |  |  | 134.1333 |  |  | 268.3372 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5557 | 2.5229 |  | 3.1184 | 50.3223 |  | 1.4687 | 120.7929 |  | 3.4085 | 230.638 |  | 14.3739 | 379.3145 |  | 46.1333 | 564.7476 |  | 147.3372 | 753.6579 |  | 5500 | 919.6059 |  | 5500 | 1067.6338 |  | 5500 | 1215.0669
[13 empty] | Next iteration flow rate |  |  | 2.5734 | Abs Value of | Flow this | 50.8255 | Abs Value of | Flow this | 122.0008 | Abs Value of | Flow this | 232.9443 | Abs Value of | Flow this | 383.1077 | Abs Value of | Flow this | 570.3951 | Abs Value of | Flow this | 761.1945 | Abs Value of | Flow this | 928.8019 | Abs Value of | Flow this | 1078.3102 | Abs Value of | Flow this | 1227.2176 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8289 |  |  | 56.4135 |  |  | 55.0836 |  |  | 51.9593 |  |  | 45.9283 |  |  | 37.3479 |  |  | 27.7816 |  |  | 17.6472 |  |  | 6.0528
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6742 |  |  | 24.7573 |  |  | 25.0233 |  |  | 25.6481 |  |  | 26.8543 |  |  | 28.5704 |  |  | 30.4837 |  |  | 32.5106 |  |  | 34.8294
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1547 |  |  | 31.6562 |  |  | 30.0603 |  |  | 26.3112 |  |  | 19.0739 |  |  | 8.7774 |  |  | -2.702 |  |  | -14.8633 |  |  | -28.7766
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.6802 |  |  | 45.2911 |  |  | 42.2283 |  |  | 37.155 |  |  | 29.2964 |  |  | 21.3462 |  |  | 13.0822 |  |  | 6.7904 |  |  | 2.1112
[13 empty] | C Non choked w/ reducers | 7 |  | 0.45315 |  |  | 8.9707 |  |  | 21.7507 |  |  | 42.8635 |  |  | 76.297 |  |  | 136.3941 |  |  | 278.072 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.37636 |  |  | 7.4453 |  |  | 18.1843 |  |  | 36.1644 |  |  | 64.205 |  |  | 110.0547 |  |  | 178.3122 |  |  | 294.8811 |  |  | 540.8492 |  |  | 1478.5819
[13 empty] | Selected C this iteration |  |  | 0.45315 |  |  | 8.9707 |  |  | 21.7507 |  |  | 42.8635 |  |  | 76.297 |  |  | 136.3941 |  |  | 278.072 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5469 | 2.5734 |  | 3.0293 | 50.8255 |  | 1.2493 | 122.0008 |  | 3.8635 | 232.9443 |  | 15.297 | 383.1077 |  | 48.3941 | 570.3951 |  | 157.072 | 761.1945 |  | 5500 | 928.8019 |  | 5500 | 1078.3102 |  | 5500 | 1227.2176
[13 empty] | Next iteration flow rate |  |  | 2.6248 | Abs Value of | Flow this | 51.3338 | Abs Value of | Flow this | 123.2209 | Abs Value of | Flow this | 235.2738 | Abs Value of | Flow this | 386.9387 | Abs Value of | Flow this | 576.0991 | Abs Value of | Flow this | 768.8064 | Abs Value of | Flow this | 938.0899 | Abs Value of | Flow this | 1089.0933 | Abs Value of | Flow this | 1239.4898 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8271 |  |  | 56.4034 |  |  | 55.0467 |  |  | 51.8597 |  |  | 45.7074 |  |  | 36.9545 |  |  | 27.196 |  |  | 16.8579 |  |  | 5.0305
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6746 |  |  | 24.7593 |  |  | 25.0307 |  |  | 25.6681 |  |  | 26.8985 |  |  | 28.6491 |  |  | 30.6008 |  |  | 32.6684 |  |  | 35.0339
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1526 |  |  | 31.644 |  |  | 30.0161 |  |  | 26.1916 |  |  | 18.8089 |  |  | 8.3054 |  |  | -3.4048 |  |  | -15.8105 |  |  | -30.0034
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.6787 |  |  | 45.2829 |  |  | 42.1999 |  |  | 37.0832 |  |  | 29.1542 |  |  | 21.1187 |  |  | 12.802 |  |  | 6.4789 |  |  | 1.7266
[13 empty] | C Non choked w/ reducers | 7 |  | 0.46221 |  |  | 9.0607 |  |  | 21.9725 |  |  | 43.324 |  |  | 77.2357 |  |  | 138.7252 |  |  | 288.7227 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.38389 |  |  | 7.5199 |  |  | 18.3678 |  |  | 36.5384 |  |  | 64.9098 |  |  | 111.4261 |  |  | 181.0627 |  |  | 301.0715 |  |  | 559.2345 |  |  | 1651.3129
[13 empty] | Selected C this iteration |  |  | 0.46221 |  |  | 9.0607 |  |  | 21.9725 |  |  | 43.324 |  |  | 77.2357 |  |  | 138.7252 |  |  | 288.7227 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5378 | 2.6248 |  | 2.9393 | 51.3338 |  | 1.0275 | 123.2209 |  | 4.324 | 235.2738 |  | 16.2357 | 386.9387 |  | 50.7252 | 576.0991 |  | 167.7227 | 768.8064 |  | 5500 | 938.0899 |  | 5500 | 1089.0933 |  | 5500 | 1239.4898
[13 empty] | Next iteration flow rate |  |  | 2.6773 | Abs Value of | Flow this | 51.8471 | Abs Value of | Flow this | 124.4531 | Abs Value of | Flow this | 237.6265 | Abs Value of | Flow this | 390.8081 | Abs Value of | Flow this | 581.86 | Abs Value of | Flow this | 776.4945 | Abs Value of | Flow this | 947.4708 | Abs Value of | Flow this | 1099.9842 | Abs Value of | Flow this | 1251.8847 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8254 |  |  | 56.3931 |  |  | 55.0091 |  |  | 51.7581 |  |  | 45.4821 |  |  | 36.5533 |  |  | 26.5986 |  |  | 16.0527 |  |  | 3.9876
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6749 |  |  | 24.7614 |  |  | 25.0382 |  |  | 25.6884 |  |  | 26.9436 |  |  | 28.7293 |  |  | 30.7203 |  |  | 32.8295 |  |  | 35.2425
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1504 |  |  | 31.6317 |  |  | 29.971 |  |  | 26.0697 |  |  | 18.5386 |  |  | 7.824 |  |  | -4.1216 |  |  | -16.7767 |  |  | -31.2549
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.6773 |  |  | 45.2746 |  |  | 42.1708 |  |  | 37.0099 |  |  | 29.0091 |  |  | 20.8866 |  |  | 12.5162 |  |  | 6.1612 |  |  | 1.3344
[13 empty] | C Non choked w/ reducers | 7 |  | 0.47145 |  |  | 9.1516 |  |  | 22.1965 |  |  | 43.7901 |  |  | 78.1903 |  |  | 141.1304 |  |  | 300.4486 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.39156 |  |  | 7.5952 |  |  | 18.5532 |  |  | 36.9165 |  |  | 65.6238 |  |  | 112.8214 |  |  | 183.8864 |  |  | 307.5348 |  |  | 579.2082 |  |  | 1897.2073
[13 empty] | Selected C this iteration |  |  | 0.47145 |  |  | 9.1516 |  |  | 22.1965 |  |  | 43.7901 |  |  | 78.1903 |  |  | 141.1304 |  |  | 300.4486 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5285 | 2.6773 |  | 2.8484 | 51.8471 |  | 0.80348 | 124.4531 |  | 4.7901 | 237.6265 |  | 17.1903 | 390.8081 |  | 53.1304 | 581.86 |  | 179.4486 | 776.4945 |  | 5500 | 947.4708 |  | 5500 | 1099.9842 |  | 5500 | 1251.8847
[13 empty] | Next iteration flow rate |  |  | 2.7309 | Abs Value of | Flow this | 52.3656 | Abs Value of | Flow this | 125.6976 | Abs Value of | Flow this | 240.0028 | Abs Value of | Flow this | 394.7162 | Abs Value of | Flow this | 587.6786 | Abs Value of | Flow this | 784.2594 | Abs Value of | Flow this | 956.9455 | Abs Value of | Flow this | 1110.9841 | Abs Value of | Flow this | 1264.4035 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8235 |  |  | 56.3825 |  |  | 54.9708 |  |  | 51.6544 |  |  | 45.2523 |  |  | 36.144 |  |  | 25.9893 |  |  | 15.2314 |  |  | 2.9237
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6753 |  |  | 24.7635 |  |  | 25.0458 |  |  | 25.7091 |  |  | 26.9895 |  |  | 28.8112 |  |  | 30.8421 |  |  | 32.9937 |  |  | 35.4553
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.1482 |  |  | 31.6191 |  |  | 29.925 |  |  | 25.9453 |  |  | 18.2628 |  |  | 7.3328 |  |  | -4.8529 |  |  | -17.7623 |  |  | -32.5316
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.765 |  |  | 46.6758 |  |  | 45.2661 |  |  | 42.1412 |  |  | 36.9351 |  |  | 28.8611 |  |  | 20.6499 |  |  | 12.2246 |  |  | 5.8371 |  |  | 0.9342
[13 empty] | C Non choked w/ reducers | 7 |  | 0.48088 |  |  | 9.2434 |  |  | 22.423 |  |  | 44.262 |  |  | 79.1613 |  |  | 143.614 |  |  | 313.451 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.3994 |  |  | 7.6712 |  |  | 18.7405 |  |  | 37.2988 |  |  | 66.3471 |  |  | 114.2415 |  |  | 186.7867 |  |  | 314.2925 |  |  | 601.0232 |  |  | 2290.0935
[13 empty] | Selected C this iteration |  |  | 0.48088 |  |  | 9.2434 |  |  | 22.423 |  |  | 44.262 |  |  | 79.1613 |  |  | 143.614 |  |  | 313.451 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5191 | 2.7309 |  | 2.7566 | 52.3656 |  | 0.57704 | 125.6976 |  | 5.262 | 240.0028 |  | 18.1613 | 394.7162 |  | 55.614 | 587.6786 |  | 192.451 | 784.2594 |  | 5500 | 956.9455 |  | 5500 | 1110.9841 |  | 5500 | 1264.4035
[13 empty] | Next iteration flow rate |  |  | 2.7855 | Abs Value of | Flow this | 52.8893 | Abs Value of | Flow this | 126.9546 | Abs Value of | Flow this | 242.4028 | Abs Value of | Flow this | 398.6634 | Abs Value of | Flow this | 593.5554 | Abs Value of | Flow this | 792.102 | Abs Value of | Flow this | 966.515 | Abs Value of | Flow this | 1122.0939 | Abs Value of | Flow this | 1277.0475 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8217 |  |  | 56.3718 |  |  | 54.9317 |  |  | 51.5486 |  |  | 45.0179 |  |  | 35.7265 |  |  | 25.3676 |  |  | 14.3935 |  |  | 1.8385
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6757 |  |  | 24.7656 |  |  | 25.0537 |  |  | 25.7303 |  |  | 27.0364 |  |  | 28.8947 |  |  | 30.9665 |  |  | 33.1613 |  |  | 35.6723
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2591 |  |  | 32.146 |  |  | 31.6062 |  |  | 29.878 |  |  | 25.8183 |  |  | 17.9814 |  |  | 6.8318 |  |  | -5.5988 |  |  | -18.7678 |  |  | -33.8339
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7649 |  |  | 46.6742 |  |  | 45.2574 |  |  | 42.111 |  |  | 36.8588 |  |  | 28.7101 |  |  | 20.4084 |  |  | 11.9272 |  |  | 5.5064 |  |  | 0.52599
[13 empty] | C Non choked w/ reducers | 7 |  | 0.4905 |  |  | 9.3362 |  |  | 22.6518 |  |  | 44.7397 |  |  | 80.1492 |  |  | 146.1804 |  |  | 327.9889 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.40738 |  |  | 7.7481 |  |  | 18.9297 |  |  | 37.6853 |  |  | 67.0799 |  |  | 115.6869 |  |  | 189.7674 |  |  | 321.3691 |  |  | 624.9931 |  |  | 3082.5081
[13 empty] | Selected C this iteration |  |  | 0.4905 |  |  | 9.3362 |  |  | 22.6518 |  |  | 44.7397 |  |  | 80.1492 |  |  | 146.1804 |  |  | 327.9889 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5095 | 2.7855 |  | 2.6638 | 52.8893 |  | 0.3482 | 126.9546 |  | 5.7397 | 242.4028 |  | 19.1492 | 398.6634 |  | 58.1804 | 593.5554 |  | 206.9889 | 792.102 |  | 5500 | 966.515 |  | 5500 | 1122.0939 |  | 5500 | 1277.0475
[13 empty] | Next iteration flow rate |  |  | 2.8412 | Abs Value of | Flow this | 53.4181 | Abs Value of | Flow this | 128.2241 | Abs Value of | Flow this | 244.8268 | Abs Value of | Flow this | 402.65 | Abs Value of | Flow this | 599.491 | Abs Value of | Flow this | 800.023 | Abs Value of | Flow this | 976.1801 | Abs Value of | Flow this | 1133.3148 | Abs Value of | Flow this | 1289.818 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8198 |  |  | 56.3609 |  |  | 54.8918 |  |  | 51.4407 |  |  | 44.7787 |  |  | 35.3006 |  |  | 24.7335 |  |  | 13.5388 |  |  | 0.73139
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.676 |  |  | 24.7678 |  |  | 25.0616 |  |  | 25.7519 |  |  | 27.0843 |  |  | 28.9799 |  |  | 31.0933 |  |  | 33.3322 |  |  | 35.8937
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.1437 |  |  | 31.5931 |  |  | 29.8302 |  |  | 25.6889 |  |  | 17.6945 |  |  | 6.3207 |  |  | -6.3598 |  |  | -19.7934 |  |  | -35.1623
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7649 |  |  | 46.6726 |  |  | 45.2485 |  |  | 42.0802 |  |  | 36.781 |  |  | 28.556 |  |  | 20.1621 |  |  | 11.6237 |  |  | 5.1691 |  |  | 0.10958
[13 empty] | C Non choked w/ reducers | 7 |  | 0.50031 |  |  | 9.4299 |  |  | 22.8831 |  |  | 45.2233 |  |  | 81.1544 |  |  | 148.8347 |  |  | 344.4017 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.41553 |  |  | 7.8257 |  |  | 19.1209 |  |  | 38.0761 |  |  | 67.8223 |  |  | 117.1585 |  |  | 192.8324 |  |  | 328.7917 |  |  | 651.5121 |  |  | 6820.9544
[13 empty] | Selected C this iteration |  |  | 0.50031 |  |  | 9.4299 |  |  | 22.8831 |  |  | 45.2233 |  |  | 81.1544 |  |  | 148.8347 |  |  | 344.4017 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4997 | 2.8412 |  | 2.5701 | 53.4181 |  | 0.11693 | 128.2241 |  | 6.2233 | 244.8268 |  | 20.1544 | 402.65 |  | 60.8347 | 599.491 |  | 223.4017 | 800.023 |  | 5500 | 976.1801 |  | 5500 | 1133.3148 |  | 5500 | 1289.818
[13 empty] | Next iteration flow rate |  |  | 2.898 | Abs Value of | Flow this | 53.9523 | Abs Value of | Flow this | 129.5064 | Abs Value of | Flow this | 247.2751 | Abs Value of | Flow this | 406.6765 | Abs Value of | Flow this | 605.4859 | Abs Value of | Flow this | 808.0233 | Abs Value of | Flow this | 985.9419 | Abs Value of | Flow this | 1144.648 | Abs Value of | Flow this | 1302.7162 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9159 |  |  | 56.8178 |  |  | 56.3497 |  |  | 54.8511 |  |  | 51.3307 |  |  | 44.5347 |  |  | 34.8661 |  |  | 24.0866 |  |  | 12.6669 |  |  | -0.39792
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6764 |  |  | 24.7701 |  |  | 25.0698 |  |  | 25.7739 |  |  | 27.1331 |  |  | 29.0668 |  |  | 31.2227 |  |  | 33.5066 |  |  | 36.1196
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.1414 |  |  | 31.5797 |  |  | 29.7814 |  |  | 25.5568 |  |  | 17.4017 |  |  | 5.7993 |  |  | -7.136 |  |  | -20.8397 |  |  | -36.5175
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7649 |  |  | 46.671 |  |  | 45.2395 |  |  | 42.0487 |  |  | 36.7017 |  |  | 28.3989 |  |  | 19.9108 |  |  | 11.3142 |  |  | 4.8251 |  |  | -0.3152
[13 empty] | C Non choked w/ reducers | 7 |  | 0.51032 |  |  | 9.5245 |  |  | 23.1168 |  |  | 45.713 |  |  | 82.1774 |  |  | 151.5822 |  |  | 363.1452 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.42384 |  |  | 7.9041 |  |  | 19.314 |  |  | 38.4712 |  |  | 68.5746 |  |  | 118.657 |  |  | 195.9859 |  |  | 336.5912 |  |  | 681.0848 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.51032 |  |  | 9.5245 |  |  | 23.1168 |  |  | 45.713 |  |  | 82.1774 |  |  | 151.5822 |  |  | 363.1452 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4897 | 2.898 |  | 2.4755 | 53.9523 |  | 0.1168 | 129.5064 |  | 6.713 | 247.2751 |  | 21.1774 | 406.6765 |  | 63.5822 | 605.4859 |  | 242.1452 | 808.0233 |  | 5500 | 985.9419 |  | 5500 | 1144.648 |  | 5500 | 1302.7162
[13 empty] | Next iteration flow rate |  |  | 2.956 | Abs Value of | Flow this | 54.4919 | Abs Value of | Flow this | 130.8014 | Abs Value of | Flow this | 249.7479 | Abs Value of | Flow this | 410.7433 | Abs Value of | Flow this | 611.5408 | Abs Value of | Flow this | 816.1035 | Abs Value of | Flow this | 995.8014 | Abs Value of | Flow this | 1156.0945 | Abs Value of | Flow this | 1315.7434 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8159 |  |  | 56.3383 |  |  | 54.8096 |  |  | 51.2184 |  |  | 44.2859 |  |  | 34.4229 |  |  | 23.4268 |  |  | 11.7775 |  |  | -1.5499
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6768 |  |  | 24.7723 |  |  | 25.0781 |  |  | 25.7963 |  |  | 27.1828 |  |  | 29.1554 |  |  | 31.3546 |  |  | 33.6845 |  |  | 36.35
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.139 |  |  | 31.566 |  |  | 29.7316 |  |  | 25.4221 |  |  | 17.1031 |  |  | 5.2675 |  |  | -7.9279 |  |  | -21.907 |  |  | -37.8999
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7649 |  |  | 46.6694 |  |  | 45.2303 |  |  | 42.0167 |  |  | 36.6207 |  |  | 28.2386 |  |  | 19.6545 |  |  | 10.9985 |  |  | 4.4741 |  |  | -0.74852
[13 empty] | C Non choked w/ reducers | 7 |  | 0.52052 |  |  | 9.6201 |  |  | 23.353 |  |  | 46.2088 |  |  | 83.2188 |  |  | 154.4289 |  |  | 384.8478 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.43232 |  |  | 7.9833 |  |  | 19.5091 |  |  | 38.8707 |  |  | 69.3368 |  |  | 120.1832 |  |  | 199.2323 |  |  | 344.8021 |  |  | 714.3685 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.52052 |  |  | 9.6201 |  |  | 23.353 |  |  | 46.2088 |  |  | 83.2188 |  |  | 154.4289 |  |  | 384.8478 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4795 | 2.956 |  | 2.3799 | 54.4919 |  | 0.35302 | 130.8014 |  | 7.2088 | 249.7479 |  | 22.2188 | 410.7433 |  | 66.4289 | 611.5408 |  | 263.8478 | 816.1035 |  | 5500 | 995.8014 |  | 5500 | 1156.0945 |  | 5500 | 1315.7434
[13 empty] | Next iteration flow rate |  |  | 3.0151 | Abs Value of | Flow this | 55.0368 | Abs Value of | Flow this | 132.1094 | Abs Value of | Flow this | 252.2453 | Abs Value of | Flow this | 414.8507 | Abs Value of | Flow this | 617.6562 | Abs Value of | Flow this | 824.2645 | Abs Value of | Flow this | 1005.7594 | Abs Value of | Flow this | 1167.6554 | Abs Value of | Flow this | 1328.9008 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8138 |  |  | 56.3267 |  |  | 54.7673 |  |  | 51.1039 |  |  | 44.032 |  |  | 33.9708 |  |  | 22.7536 |  |  | 10.8702 |  |  | -2.7251
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6772 |  |  | 24.7747 |  |  | 25.0865 |  |  | 25.8192 |  |  | 27.2336 |  |  | 29.2458 |  |  | 31.4893 |  |  | 33.866 |  |  | 36.585
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.1366 |  |  | 31.5521 |  |  | 29.6807 |  |  | 25.2847 |  |  | 16.7984 |  |  | 4.7249 |  |  | -8.7356 |  |  | -22.9957 |  |  | -39.3101
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7649 |  |  | 46.6677 |  |  | 45.2209 |  |  | 41.9839 |  |  | 36.5381 |  |  | 28.0751 |  |  | 19.393 |  |  | 10.6764 |  |  | 4.116 |  |  | -1.1905
[13 empty] | C Non choked w/ reducers | 7 |  | 0.53093 |  |  | 9.7167 |  |  | 23.5918 |  |  | 46.7108 |  |  | 84.2791 |  |  | 157.3811 |  |  | 410.4058 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.44097 |  |  | 8.0633 |  |  | 19.7063 |  |  | 39.2747 |  |  | 70.1093 |  |  | 121.7379 |  |  | 202.5767 |  |  | 353.4639 |  |  | 752.2389 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.53093 |  |  | 9.7167 |  |  | 23.5918 |  |  | 46.7108 |  |  | 84.2791 |  |  | 157.3811 |  |  | 410.4058 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4691 | 3.0151 |  | 2.2833 | 55.0368 |  | 0.59176 | 132.1094 |  | 7.7108 | 252.2453 |  | 23.2791 | 414.8507 |  | 69.3811 | 617.6562 |  | 289.4058 | 824.2645 |  | 5500 | 1005.7594 |  | 5500 | 1167.6554 |  | 5500 | 1328.9008
[13 empty] | Next iteration flow rate |  |  | 3.0754 | Abs Value of | Flow this | 55.5871 | Abs Value of | Flow this | 133.4305 | Abs Value of | Flow this | 254.7678 | Abs Value of | Flow this | 418.9992 | Abs Value of | Flow this | 623.8327 | Abs Value of | Flow this | 832.5072 | Abs Value of | Flow this | 1015.817 | Abs Value of | Flow this | 1179.332 | Abs Value of | Flow this | 1342.1898 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8118 |  |  | 56.3149 |  |  | 54.7241 |  |  | 50.9871 |  |  | 43.773 |  |  | 33.5096 |  |  | 22.067 |  |  | 9.9447 |  |  | -3.9239
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6776 |  |  | 24.777 |  |  | 25.0952 |  |  | 25.8426 |  |  | 27.2854 |  |  | 29.3381 |  |  | 31.6266 |  |  | 34.0511 |  |  | 36.8248
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.1341 |  |  | 31.5378 |  |  | 29.6289 |  |  | 25.1445 |  |  | 16.4876 |  |  | 4.1715 |  |  | -9.5596 |  |  | -24.1063 |  |  | -40.7487
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7649 |  |  | 46.666 |  |  | 45.2113 |  |  | 41.9506 |  |  | 36.4539 |  |  | 27.9083 |  |  | 19.1262 |  |  | 10.3479 |  |  | 3.7508 |  |  | -1.6415
[13 empty] | C Non choked w/ reducers | 7 |  | 0.54155 |  |  | 9.8142 |  |  | 23.833 |  |  | 47.2192 |  |  | 85.3589 |  |  | 160.446 |  |  | 441.1507 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.44979 |  |  | 8.144 |  |  | 19.9055 |  |  | 39.6833 |  |  | 70.8922 |  |  | 123.3222 |  |  | 206.0243 |  |  | 362.6217 |  |  | 795.8933 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.54155 |  |  | 9.8142 |  |  | 23.833 |  |  | 47.2192 |  |  | 85.3589 |  |  | 160.446 |  |  | 441.1507 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4584 | 3.0754 |  | 2.1858 | 55.5871 |  | 0.83305 | 133.4305 |  | 8.2192 | 254.7678 |  | 24.3589 | 418.9992 |  | 72.446 | 623.8327 |  | 320.1507 | 832.5072 |  | 5500 | 1015.817 |  | 5500 | 1179.332 |  | 5500 | 1342.1898
[13 empty] | Next iteration flow rate |  |  | 3.1369 | Abs Value of | Flow this | 56.143 | Abs Value of | Flow this | 134.7648 | Abs Value of | Flow this | 257.3155 | Abs Value of | Flow this | 423.1892 | Abs Value of | Flow this | 630.071 | Abs Value of | Flow this | 840.8323 | Abs Value of | Flow this | 1025.9751 | Abs Value of | Flow this | 1191.1253 | Abs Value of | Flow this | 1355.6117 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8097 |  |  | 56.3028 |  |  | 54.68 |  |  | 50.8679 |  |  | 43.5089 |  |  | 33.0391 |  |  | 21.3665 |  |  | 9.0006 |  |  | -5.1468
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6781 |  |  | 24.7794 |  |  | 25.104 |  |  | 25.8664 |  |  | 27.3382 |  |  | 29.4322 |  |  | 31.7667 |  |  | 34.2399 |  |  | 37.0694
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.1316 |  |  | 31.5233 |  |  | 29.576 |  |  | 25.0015 |  |  | 16.1706 |  |  | 3.6069 |  |  | -10.4002 |  |  | -25.2393 |  |  | -42.2161
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7649 |  |  | 46.6643 |  |  | 45.2015 |  |  | 41.9165 |  |  | 36.3679 |  |  | 27.7382 |  |  | 18.8541 |  |  | 10.0127 |  |  | 3.3782 |  |  | -2.1014
[13 empty] | C Non choked w/ reducers | 7 |  | 0.55238 |  |  | 9.9128 |  |  | 24.0769 |  |  | 47.734 |  |  | 86.4587 |  |  | 163.6312 |  |  | 479.1654 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.45878 |  |  | 8.2256 |  |  | 20.1067 |  |  | 40.0964 |  |  | 71.6857 |  |  | 124.9368 |  |  | 209.5807 |  |  | 372.3272 |  |  | 847.0208 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.55238 |  |  | 9.9128 |  |  | 24.0769 |  |  | 47.734 |  |  | 86.4587 |  |  | 163.6312 |  |  | 479.1654 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4476 | 3.1369 |  | 2.0872 | 56.143 |  | 1.0769 | 134.7648 |  | 8.734 | 257.3155 |  | 25.4587 | 423.1892 |  | 75.6312 | 630.071 |  | 358.1654 | 840.8323 |  | 5500 | 1025.9751 |  | 5500 | 1191.1253 |  | 5500 | 1355.6117
[13 empty] | Next iteration flow rate |  |  | 3.1996 | Abs Value of | Flow this | 56.7044 | Abs Value of | Flow this | 136.1125 | Abs Value of | Flow this | 259.8886 | Abs Value of | Flow this | 427.4211 | Abs Value of | Flow this | 636.3718 | Abs Value of | Flow this | 849.2406 | Abs Value of | Flow this | 1036.2349 | Abs Value of | Flow this | 1203.0365 | Abs Value of | Flow this | 1369.1678 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8076 |  |  | 56.2905 |  |  | 54.6351 |  |  | 50.7463 |  |  | 43.2394 |  |  | 32.5592 |  |  | 20.652 |  |  | 8.0375 |  |  | -6.3942
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6785 |  |  | 24.7819 |  |  | 25.113 |  |  | 25.8907 |  |  | 27.3921 |  |  | 29.5282 |  |  | 31.9096 |  |  | 34.4325 |  |  | 37.3188
[13 empty] | Delta P at this iteration flow rate |  |  | 32.259 |  |  | 32.1291 |  |  | 31.5085 |  |  | 29.5221 |  |  | 24.8556 |  |  | 15.8473 |  |  | 3.031 |  |  | -11.2577 |  |  | -26.395 |  |  | -43.7131
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7649 |  |  | 46.6625 |  |  | 45.1915 |  |  | 41.8818 |  |  | 36.2802 |  |  | 27.5646 |  |  | 18.5766 |  |  | 9.6708 |  |  | 2.9982 |  |  | -2.5707
[13 empty] | C Non choked w/ reducers | 7 |  | 0.56343 |  |  | 10.0123 |  |  | 24.3234 |  |  | 48.2553 |  |  | 87.5792 |  |  | 166.9452 |  |  | 527.9362 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.46796 |  |  | 8.308 |  |  | 20.31 |  |  | 40.5141 |  |  | 72.4899 |  |  | 126.5828 |  |  | 213.2521 |  |  | 382.6399 |  |  | 908.0975 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.56343 |  |  | 10.0123 |  |  | 24.3234 |  |  | 48.2553 |  |  | 87.5792 |  |  | 166.9452 |  |  | 527.9362 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4366 | 3.1996 |  | 1.9877 | 56.7044 |  | 1.3234 | 136.1125 |  | 9.2553 | 259.8886 |  | 26.5792 | 427.4211 |  | 78.9452 | 636.3718 |  | 406.9362 | 849.2406 |  | 5500 | 1036.2349 |  | 5500 | 1203.0365 |  | 5500 | 1369.1678
[13 empty] | Next iteration flow rate |  |  | 3.2636 | Abs Value of | Flow this | 57.2715 | Abs Value of | Flow this | 137.4736 | Abs Value of | Flow this | 262.4875 | Abs Value of | Flow this | 431.6953 | Abs Value of | Flow this | 642.7355 | Abs Value of | Flow this | 857.733 | Abs Value of | Flow this | 1046.5972 | Abs Value of | Flow this | 1215.0669 | Abs Value of | Flow this | 1382.8595 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8054 |  |  | 56.2779 |  |  | 54.5892 |  |  | 50.6223 |  |  | 42.9645 |  |  | 32.0696 |  |  | 19.923 |  |  | 7.055 |  |  | -7.6668
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6789 |  |  | 24.7844 |  |  | 25.1222 |  |  | 25.9155 |  |  | 27.4471 |  |  | 29.6261 |  |  | 32.0554 |  |  | 34.629 |  |  | 37.5734
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2589 |  |  | 32.1264 |  |  | 31.4935 |  |  | 29.4671 |  |  | 24.7068 |  |  | 15.5174 |  |  | 2.4435 |  |  | -12.1324 |  |  | -27.574 |  |  | -45.2401
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7649 |  |  | 46.6607 |  |  | 45.1814 |  |  | 41.8463 |  |  | 36.1908 |  |  | 27.3876 |  |  | 18.2934 |  |  | 9.3221 |  |  | 2.6104 |  |  | -3.0493
[13 empty] | C Non choked w/ reducers | 7 |  | 0.5747 |  |  | 10.1128 |  |  | 24.5725 |  |  | 48.7834 |  |  | 88.721 |  |  | 170.3975 |  |  | 593.8659 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.47732 |  |  | 8.3913 |  |  | 20.5154 |  |  | 40.9366 |  |  | 73.3053 |  |  | 128.2612 |  |  | 217.0451 |  |  | 393.6293 |  |  | 982.9315 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.5747 |  |  | 10.1128 |  |  | 24.5725 |  |  | 48.7834 |  |  | 88.721 |  |  | 170.3975 |  |  | 593.8659 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4253 | 3.2636 |  | 1.8872 | 57.2715 |  | 1.5725 | 137.4736 |  | 9.7834 | 262.4875 |  | 27.721 | 431.6953 |  | 82.3975 | 642.7355 |  | 472.8659 | 857.733 |  | 5500 | 1046.5972 |  | 5500 | 1215.0669 |  | 5500 | 1382.8595
[13 empty] | Next iteration flow rate |  |  | 3.3289 | Abs Value of | Flow this | 57.8442 | Abs Value of | Flow this | 138.8483 | Abs Value of | Flow this | 265.1124 | Abs Value of | Flow this | 436.0123 | Abs Value of | Flow this | 649.1628 | Abs Value of | Flow this | 866.3103 | Abs Value of | Flow this | 1057.0632 | Abs Value of | Flow this | 1227.2176 | Abs Value of | Flow this | 1396.6881 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8031 |  |  | 56.2651 |  |  | 54.5425 |  |  | 50.4958 |  |  | 42.684 |  |  | 31.5702 |  |  | 19.1795 |  |  | 6.0528 |  |  | -8.9649
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6794 |  |  | 24.787 |  |  | 25.1315 |  |  | 25.9408 |  |  | 27.5032 |  |  | 29.726 |  |  | 32.2041 |  |  | 34.8294 |  |  | 37.833
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2589 |  |  | 32.1238 |  |  | 31.4781 |  |  | 29.411 |  |  | 24.5549 |  |  | 15.1809 |  |  | 1.8442 |  |  | -13.0246 |  |  | -28.7766 |  |  | -46.7979
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7649 |  |  | 46.6589 |  |  | 45.171 |  |  | 41.8102 |  |  | 36.0996 |  |  | 27.207 |  |  | 18.0046 |  |  | 8.9663 |  |  | 2.2149 |  |  | -3.5376
[13 empty] | C Non choked w/ reducers | 7 |  | 0.58619 |  |  | 10.2144 |  |  | 24.8243 |  |  | 49.3182 |  |  | 89.8848 |  |  | 173.9985 |  |  | 690.416 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.48686 |  |  | 8.4754 |  |  | 20.7229 |  |  | 41.3638 |  |  | 74.1318 |  |  | 129.9731 |  |  | 220.967 |  |  | 405.3764 |  |  | 1077.7556 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.58619 |  |  | 10.2144 |  |  | 24.8243 |  |  | 49.3182 |  |  | 89.8848 |  |  | 173.9985 |  |  | 690.416 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4138 | 3.3289 |  | 1.7856 | 57.8442 |  | 1.8243 | 138.8483 |  | 10.3182 | 265.1124 |  | 28.8848 | 436.0123 |  | 85.9985 | 649.1628 |  | 569.416 | 866.3103 |  | 5500 | 1057.0632 |  | 5500 | 1227.2176 |  | 5500 | 1396.6881
[13 empty] | Next iteration flow rate |  |  | 3.3955 | Abs Value of | Flow this | 58.4226 | Abs Value of | Flow this | 140.2368 | Abs Value of | Flow this | 267.7635 | Abs Value of | Flow this | 440.3724 | Abs Value of | Flow this | 655.6545 | Abs Value of | Flow this | 874.9734 | Abs Value of | Flow this | 1067.6338 | Abs Value of | Flow this | 1239.4898 | Abs Value of | Flow this | 1410.655 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9158 |  |  | 56.8009 |  |  | 56.252 |  |  | 54.4948 |  |  | 50.3667 |  |  | 42.398 |  |  | 31.0607 |  |  | 18.421 |  |  | 5.0305 |  |  | -10.2891
[13 empty] | P2 at this iteration flow rate |  |  | 24.6568 |  |  | 24.6798 |  |  | 24.7896 |  |  | 25.141 |  |  | 25.9667 |  |  | 27.5604 |  |  | 29.8279 |  |  | 32.3558 |  |  | 35.0339 |  |  | 38.0978
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2589 |  |  | 32.121 |  |  | 31.4624 |  |  | 29.3537 |  |  | 24.4001 |  |  | 14.8376 |  |  | 1.2329 |  |  | -13.9348 |  |  | -30.0034 |  |  | -48.3869
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7648 |  |  | 46.657 |  |  | 45.1604 |  |  | 41.7733 |  |  | 36.0065 |  |  | 27.0227 |  |  | 17.7099 |  |  | 8.6034 |  |  | 1.8115 |  |  | -4.0357
[13 empty] | C Non choked w/ reducers | 7 |  | 0.59792 |  |  | 10.317 |  |  | 25.0788 |  |  | 49.8599 |  |  | 91.0712 |  |  | 177.7598 |  |  | 852.8609 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.4966 |  |  | 8.5603 |  |  | 20.9326 |  |  | 41.7959 |  |  | 74.9698 |  |  | 131.7196 |  |  | 225.0256 |  |  | 417.9766 |  |  | 1203.6612 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.59792 |  |  | 10.317 |  |  | 25.0788 |  |  | 49.8599 |  |  | 91.0712 |  |  | 177.7598 |  |  | 852.8609 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.4021 | 3.3955 |  | 1.683 | 58.4226 |  | 2.0788 | 140.2368 |  | 10.8599 | 267.7635 |  | 30.0712 | 440.3724 |  | 89.7598 | 655.6545 |  | 731.8609 | 874.9734 |  | 5500 | 1067.6338 |  | 5500 | 1239.4898 |  | 5500 | 1410.655
[13 empty] | Next iteration flow rate |  |  | 3.4634 | Abs Value of | Flow this | 59.0069 | Abs Value of | Flow this | 141.6392 | Abs Value of | Flow this | 270.4411 | Abs Value of | Flow this | 444.7761 | Abs Value of | Flow this | 662.211 | Abs Value of | Flow this | 883.7232 | Abs Value of | Flow this | 1078.3102 | Abs Value of | Flow this | 1251.8847 | Abs Value of | Flow this | 1424.7615 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9157 |  |  | 56.7986 |  |  | 56.2386 |  |  | 54.4461 |  |  | 50.2351 |  |  | 42.1062 |  |  | 30.541 |  |  | 17.6472 |  |  | 3.9876 |  |  | -11.6399
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6803 |  |  | 24.7923 |  |  | 25.1508 |  |  | 25.993 |  |  | 27.6188 |  |  | 29.9318 |  |  | 32.5106 |  |  | 35.2425 |  |  | 38.368
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2589 |  |  | 32.1183 |  |  | 31.4463 |  |  | 29.2953 |  |  | 24.2421 |  |  | 14.4874 |  |  | 0.60926 |  |  | -14.8633 |  |  | -31.2549 |  |  | -50.0079
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7648 |  |  | 46.6551 |  |  | 45.1496 |  |  | 41.7357 |  |  | 35.9116 |  |  | 26.8348 |  |  | 17.4093 |  |  | 8.2331 |  |  | 1.3999 |  |  | -4.5438
[13 empty] | C Non choked w/ reducers | 7 |  | 0.60988 |  |  | 10.4206 |  |  | 25.336 |  |  | 50.4087 |  |  | 92.2812 |  |  | 181.6943 |  |  | 1225.3539 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.50653 |  |  | 8.6461 |  |  | 21.1445 |  |  | 42.2329 |  |  | 75.8195 |  |  | 133.5018 |  |  | 229.2294 |  |  | 431.5436 |  |  | 1382.8965 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.60988 |  |  | 10.4206 |  |  | 25.336 |  |  | 50.4087 |  |  | 92.2812 |  |  | 181.6943 |  |  | 1225.3539 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3901 | 3.4634 |  | 1.5794 | 59.0069 |  | 2.336 | 141.6392 |  | 11.4087 | 270.4411 |  | 31.2812 | 444.7761 |  | 93.6943 | 662.211 |  | 1104.3539 | 883.7232 |  | 5500 | 1078.3102 |  | 5500 | 1251.8847 |  | 5500 | 1424.7615
[13 empty] | Next iteration flow rate |  |  | 3.5327 | Abs Value of | Flow this | 59.5969 | Abs Value of | Flow this | 143.0556 | Abs Value of | Flow this | 273.1455 | Abs Value of | Flow this | 449.2239 | Abs Value of | Flow this | 668.8331 | Abs Value of | Flow this | 892.5604 | Abs Value of | Flow this | 1089.0933 | Abs Value of | Flow this | 1264.4035 | Abs Value of | Flow this | 1439.0091 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9157 |  |  | 56.7962 |  |  | 56.225 |  |  | 54.3964 |  |  | 50.1008 |  |  | 41.8085 |  |  | 30.0109 |  |  | 16.8579 |  |  | 2.9237 |  |  | -13.0179
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6808 |  |  | 24.795 |  |  | 25.1607 |  |  | 26.0198 |  |  | 27.6783 |  |  | 30.0378 |  |  | 32.6684 |  |  | 35.4553 |  |  | 38.6436
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2589 |  |  | 32.1154 |  |  | 31.43 |  |  | 29.2357 |  |  | 24.081 |  |  | 14.1302 |  |  | -0.026911 |  |  | -15.8105 |  |  | -32.5316 |  |  | -51.6615
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7648 |  |  | 46.6531 |  |  | 45.1386 |  |  | 41.6973 |  |  | 35.8147 |  |  | 26.6431 |  |  | 17.1027 |  |  | 7.8555 |  |  | 0.98011 |  |  | -5.0621
[13 empty] | C Non choked w/ reducers | 7 |  | 0.62207 |  |  | 10.5253 |  |  | 25.5961 |  |  | 50.9646 |  |  | 93.5153 |  |  | 185.8164 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.51666 |  |  | 8.7327 |  |  | 21.3585 |  |  | 42.6748 |  |  | 76.6812 |  |  | 135.3211 |  |  | 233.5878 |  |  | 446.2132 |  |  | 1669.2759 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.62207 |  |  | 10.5253 |  |  | 25.5961 |  |  | 50.9646 |  |  | 93.5153 |  |  | 185.8164 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3779 | 3.5327 |  | 1.4747 | 59.5969 |  | 2.5961 | 143.0556 |  | 11.9646 | 273.1455 |  | 32.5153 | 449.2239 |  | 97.8164 | 668.8331 |  | 5500 | 892.5604 |  | 5500 | 1089.0933 |  | 5500 | 1264.4035 |  | 5500 | 1439.0091
[13 empty] | Next iteration flow rate |  |  | 3.6033 | Abs Value of | Flow this | 60.1929 | Abs Value of | Flow this | 144.4861 | Abs Value of | Flow this | 275.877 | Abs Value of | Flow this | 453.7161 | Abs Value of | Flow this | 675.5214 | Abs Value of | Flow this | 901.486 | Abs Value of | Flow this | 1099.9842 | Abs Value of | Flow this | 1277.0475 | Abs Value of | Flow this | 1453.3992 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9157 |  |  | 56.7938 |  |  | 56.2111 |  |  | 54.3458 |  |  | 49.9638 |  |  | 41.5048 |  |  | 29.4701 |  |  | 16.0527 |  |  | 1.8385 |  |  | -14.4236
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6812 |  |  | 24.7978 |  |  | 25.1708 |  |  | 26.0472 |  |  | 27.739 |  |  | 30.146 |  |  | 32.8295 |  |  | 35.6723 |  |  | 38.9247
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2588 |  |  | 32.1125 |  |  | 31.4133 |  |  | 29.1749 |  |  | 23.9166 |  |  | 13.7658 |  |  | -0.67587 |  |  | -16.7767 |  |  | -33.8339 |  |  | -53.3483
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7648 |  |  | 46.6511 |  |  | 45.1273 |  |  | 41.6582 |  |  | 35.7159 |  |  | 26.4475 |  |  | 16.7899 |  |  | 7.4702 |  |  | 0.55184 |  |  | -5.5908
[13 empty] | C Non choked w/ reducers | 7 |  | 0.63452 |  |  | 10.631 |  |  | 25.8589 |  |  | 51.5279 |  |  | 94.7745 |  |  | 190.1423 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.527 |  |  | 8.8202 |  |  | 21.5748 |  |  | 43.1218 |  |  | 77.5551 |  |  | 137.1787 |  |  | 238.111 |  |  | 462.1503 |  |  | 2246.8761 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.63452 |  |  | 10.631 |  |  | 25.8589 |  |  | 51.5279 |  |  | 94.7745 |  |  | 190.1423 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3655 | 3.6033 |  | 1.369 | 60.1929 |  | 2.8589 | 144.4861 |  | 12.5279 | 275.877 |  | 33.7745 | 453.7161 |  | 102.1423 | 675.5214 |  | 5500 | 901.486 |  | 5500 | 1099.9842 |  | 5500 | 1277.0475 |  | 5500 | 1453.3992
[13 empty] | Next iteration flow rate |  |  | 3.6754 | Abs Value of | Flow this | 60.7948 | Abs Value of | Flow this | 145.931 | Abs Value of | Flow this | 278.6358 | Abs Value of | Flow this | 458.2533 | Abs Value of | Flow this | 682.2767 | Abs Value of | Flow this | 910.5008 | Abs Value of | Flow this | 1110.9841 | Abs Value of | Flow this | 1289.818 | Abs Value of | Flow this | 1467.9332 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9157 |  |  | 56.7913 |  |  | 56.1969 |  |  | 54.2941 |  |  | 49.8241 |  |  | 41.1951 |  |  | 28.9184 |  |  | 15.2314 |  |  | 0.73139 |  |  | -15.8575
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6817 |  |  | 24.8006 |  |  | 25.1812 |  |  | 26.0752 |  |  | 27.801 |  |  | 30.2563 |  |  | 32.9937 |  |  | 35.8937 |  |  | 39.2115
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2588 |  |  | 32.1096 |  |  | 31.3963 |  |  | 29.113 |  |  | 23.7489 |  |  | 13.3941 |  |  | -1.3379 |  |  | -17.7623 |  |  | -35.1623 |  |  | -55.069
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7648 |  |  | 46.6491 |  |  | 45.1159 |  |  | 41.6183 |  |  | 35.6151 |  |  | 26.248 |  |  | 16.4709 |  |  | 7.0772 |  |  | 0.11497 |  |  | -6.1302
[13 empty] | C Non choked w/ reducers | 7 |  | 0.64721 |  |  | 10.7378 |  |  | 26.1245 |  |  | 52.0985 |  |  | 96.0596 |  |  | 194.6903 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.53754 |  |  | 8.9086 |  |  | 21.7933 |  |  | 43.5739 |  |  | 78.4414 |  |  | 139.0761 |  |  | 242.8103 |  |  | 479.5565 |  |  | 4971.8731 |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.64721 |  |  | 10.7378 |  |  | 26.1245 |  |  | 52.0985 |  |  | 96.0596 |  |  | 194.6903 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3528 | 3.6754 |  | 1.2622 | 60.7948 |  | 3.1245 | 145.931 |  | 13.0985 | 278.6358 |  | 35.0596 | 458.2533 |  | 106.6903 | 682.2767 |  | 5500 | 910.5008 |  | 5500 | 1110.9841 |  | 5500 | 1289.818 |  | 5500 | 1467.9332
[13 empty] | Next iteration flow rate |  |  | 3.7489 | Abs Value of | Flow this | 61.4028 | Abs Value of | Flow this | 147.3903 | Abs Value of | Flow this | 281.4221 | Abs Value of | Flow this | 462.8358 | Abs Value of | Flow this | 689.0994 | Abs Value of | Flow this | 919.6059 | Abs Value of | Flow this | 1122.0939 | Abs Value of | Flow this | 1302.7162 | Abs Value of | Flow this | 1482.6125 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9157 |  |  | 56.7888 |  |  | 56.1825 |  |  | 54.2414 |  |  | 49.6815 |  |  | 40.8791 |  |  | 28.3557 |  |  | 14.3935 |  |  | -0.39792 |  |  | -17.3203
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6822 |  |  | 24.8035 |  |  | 25.1917 |  |  | 26.1037 |  |  | 27.8642 |  |  | 30.3689 |  |  | 33.1613 |  |  | 36.1196 |  |  | 39.5041
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2588 |  |  | 32.1066 |  |  | 31.379 |  |  | 29.0497 |  |  | 23.5778 |  |  | 13.0149 |  |  | -2.0132 |  |  | -18.7678 |  |  | -36.5175 |  |  | -56.8243
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7648 |  |  | 46.647 |  |  | 45.1042 |  |  | 41.5775 |  |  | 35.5123 |  |  | 26.0445 |  |  | 16.1454 |  |  | 6.6763 |  |  | -0.33069 |  |  | -6.6804
[13 empty] | C Non choked w/ reducers | 7 |  | 0.66015 |  |  | 10.8457 |  |  | 26.3931 |  |  | 52.6768 |  |  | 97.3715 |  |  | 199.4812 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.54829 |  |  | 8.9979 |  |  | 22.0141 |  |  | 44.0312 |  |  | 79.3404 |  |  | 141.0146 |  |  | 247.698 |  |  | 498.682 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.66015 |  |  | 10.8457 |  |  | 26.3931 |  |  | 52.6768 |  |  | 97.3715 |  |  | 199.4812 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3398 | 3.7489 |  | 1.1543 | 61.4028 |  | 3.3931 | 147.3903 |  | 13.6768 | 281.4221 |  | 36.3715 | 462.8358 |  | 111.4812 | 689.0994 |  | 5500 | 919.6059 |  | 5500 | 1122.0939 |  | 5500 | 1302.7162 |  | 5500 | 1482.6125
[13 empty] | Next iteration flow rate |  |  | 3.8239 | Abs Value of | Flow this | 62.0168 | Abs Value of | Flow this | 148.8642 | Abs Value of | Flow this | 284.2364 | Abs Value of | Flow this | 467.4642 | Abs Value of | Flow this | 695.9904 | Abs Value of | Flow this | 928.8019 | Abs Value of | Flow this | 1133.3148 | Abs Value of | Flow this | 1315.7434 | Abs Value of | Flow this | 1497.4387 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9156 |  |  | 56.7863 |  |  | 56.1677 |  |  | 54.1877 |  |  | 49.5361 |  |  | 40.5567 |  |  | 27.7816 |  |  | 13.5388 |  |  | -1.5499 |  |  | -18.8124
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6827 |  |  | 24.8065 |  |  | 25.2025 |  |  | 26.1328 |  |  | 27.9287 |  |  | 30.4837 |  |  | 33.3322 |  |  | 36.35 |  |  | 39.8025
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2588 |  |  | 32.1035 |  |  | 31.3613 |  |  | 28.9852 |  |  | 23.4033 |  |  | 12.6281 |  |  | -2.702 |  |  | -19.7934 |  |  | -37.8999 |  |  | -58.6149
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7648 |  |  | 46.6449 |  |  | 45.0922 |  |  | 41.536 |  |  | 35.4075 |  |  | 25.8369 |  |  | 15.8134 |  |  | 6.2674 |  |  | -0.7853 |  |  | -7.2416
[13 empty] | C Non choked w/ reducers | 7 |  | 0.67335 |  |  | 10.9547 |  |  | 26.6645 |  |  | 53.2627 |  |  | 98.7112 |  |  | 204.5385 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.55925 |  |  | 9.0881 |  |  | 22.2372 |  |  | 44.4937 |  |  | 80.2524 |  |  | 142.9958 |  |  | 252.7876 |  |  | 519.8416 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.67335 |  |  | 10.9547 |  |  | 26.6645 |  |  | 53.2627 |  |  | 98.7112 |  |  | 204.5385 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3266 | 3.8239 |  | 1.0453 | 62.0168 |  | 3.6645 | 148.8642 |  | 14.2627 | 284.2364 |  | 37.7112 | 467.4642 |  | 116.5385 | 695.9904 |  | 5500 | 928.8019 |  | 5500 | 1133.3148 |  | 5500 | 1315.7434 |  | 5500 | 1497.4387
[13 empty] | Next iteration flow rate |  |  | 3.9004 | Abs Value of | Flow this | 62.637 | Abs Value of | Flow this | 150.3529 | Abs Value of | Flow this | 287.0787 | Abs Value of | Flow this | 472.1388 | Abs Value of | Flow this | 702.9503 | Abs Value of | Flow this | 938.0899 | Abs Value of | Flow this | 1144.648 | Abs Value of | Flow this | 1328.9008 | Abs Value of | Flow this | 1512.4131 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9156 |  |  | 56.7836 |  |  | 56.1527 |  |  | 54.1328 |  |  | 49.3878 |  |  | 40.2279 |  |  | 27.196 |  |  | 12.6669 |  |  | -2.7251 |  |  | -20.3346
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6833 |  |  | 24.8095 |  |  | 25.2134 |  |  | 26.1624 |  |  | 27.9944 |  |  | 30.6008 |  |  | 33.5066 |  |  | 36.585 |  |  | 40.1069
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2588 |  |  | 32.1004 |  |  | 31.3432 |  |  | 28.9194 |  |  | 23.2253 |  |  | 12.2335 |  |  | -3.4048 |  |  | -20.8397 |  |  | -39.3101 |  |  | -60.4415
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7647 |  |  | 46.6427 |  |  | 45.0801 |  |  | 41.4936 |  |  | 35.3005 |  |  | 25.6251 |  |  | 15.4747 |  |  | 5.8502 |  |  | -1.2491 |  |  | -7.8142
[13 empty] | C Non choked w/ reducers | 7 |  | 0.68682 |  |  | 11.0647 |  |  | 26.9389 |  |  | 53.8565 |  |  | 100.0796 |  |  | 209.8891 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.57044 |  |  | 9.1792 |  |  | 22.4626 |  |  | 44.9616 |  |  | 81.1776 |  |  | 145.0213 |  |  | 258.0944 |  |  | 543.4376 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.68682 |  |  | 11.0647 |  |  | 26.9389 |  |  | 53.8565 |  |  | 100.0796 |  |  | 209.8891 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3132 | 3.9004 |  | 0.93525 | 62.637 |  | 3.9389 | 150.3529 |  | 14.8565 | 287.0787 |  | 39.0796 | 472.1388 |  | 121.8891 | 702.9503 |  | 5500 | 938.0899 |  | 5500 | 1144.648 |  | 5500 | 1328.9008 |  | 5500 | 1512.4131
[13 empty] | Next iteration flow rate |  |  | 3.9784 | Abs Value of | Flow this | 63.2633 | Abs Value of | Flow this | 151.8564 | Abs Value of | Flow this | 289.9495 | Abs Value of | Flow this | 476.8602 | Abs Value of | Flow this | 709.9798 | Abs Value of | Flow this | 947.4708 | Abs Value of | Flow this | 1156.0945 | Abs Value of | Flow this | 1342.1898 | Abs Value of | Flow this | 1527.5372 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9156 |  |  | 56.781 |  |  | 56.1373 |  |  | 54.0769 |  |  | 49.2365 |  |  | 39.8925 |  |  | 26.5986 |  |  | 11.7775 |  |  | -3.9239 |  |  | -21.8873
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6838 |  |  | 24.8125 |  |  | 25.2246 |  |  | 26.1927 |  |  | 28.0615 |  |  | 30.7203 |  |  | 33.6845 |  |  | 36.8248 |  |  | 40.4175
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2587 |  |  | 32.0972 |  |  | 31.3248 |  |  | 28.8523 |  |  | 23.0437 |  |  | 11.8309 |  |  | -4.1216 |  |  | -21.907 |  |  | -40.7487 |  |  | -62.3048
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7647 |  |  | 46.6405 |  |  | 45.0677 |  |  | 41.4504 |  |  | 35.1913 |  |  | 25.4091 |  |  | 15.1292 |  |  | 5.4247 |  |  | -1.7221 |  |  | -8.3982
[13 empty] | C Non choked w/ reducers | 7 |  | 0.70056 |  |  | 11.176 |  |  | 27.2163 |  |  | 54.4583 |  |  | 101.4779 |  |  | 215.564 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.58185 |  |  | 9.2712 |  |  | 22.6903 |  |  | 45.4349 |  |  | 82.1164 |  |  | 147.0929 |  |  | 263.635 |  |  | 569.9947 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.70056 |  |  | 11.176 |  |  | 27.2163 |  |  | 54.4583 |  |  | 101.4779 |  |  | 215.564 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2994 | 3.9784 |  | 0.82405 | 63.2633 |  | 4.2163 | 151.8564 |  | 15.4583 | 289.9495 |  | 40.4779 | 476.8602 |  | 127.564 | 709.9798 |  | 5500 | 947.4708 |  | 5500 | 1156.0945 |  | 5500 | 1342.1898 |  | 5500 | 1527.5372
[13 empty] | Next iteration flow rate |  |  | 4.0579 | Abs Value of | Flow this | 63.896 | Abs Value of | Flow this | 153.375 | Abs Value of | Flow this | 292.849 | Abs Value of | Flow this | 481.6288 | Abs Value of | Flow this | 717.0796 | Abs Value of | Flow this | 956.9455 | Abs Value of | Flow this | 1167.6554 | Abs Value of | Flow this | 1355.6117 | Abs Value of | Flow this | 1542.8126 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9156 |  |  | 56.7783 |  |  | 56.1217 |  |  | 54.0198 |  |  | 49.0821 |  |  | 39.5503 |  |  | 25.9893 |  |  | 10.8702 |  |  | -5.1468 |  |  | -23.4712
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6843 |  |  | 24.8157 |  |  | 25.236 |  |  | 26.2236 |  |  | 28.1299 |  |  | 30.8421 |  |  | 33.866 |  |  | 37.0694 |  |  | 40.7342
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2587 |  |  | 32.0939 |  |  | 31.306 |  |  | 28.7838 |  |  | 22.8585 |  |  | 11.4203 |  |  | -4.8529 |  |  | -22.9957 |  |  | -42.2161 |  |  | -64.2055
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7647 |  |  | 46.6383 |  |  | 45.055 |  |  | 41.4063 |  |  | 35.08 |  |  | 25.1887 |  |  | 14.7768 |  |  | 4.9906 |  |  | -2.2047 |  |  | -8.994
[13 empty] | C Non choked w/ reducers | 7 |  | 0.71457 |  |  | 11.2883 |  |  | 27.4967 |  |  | 55.0683 |  |  | 102.9071 |  |  | 221.5991 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.59348 |  |  | 9.3641 |  |  | 22.9205 |  |  | 45.9137 |  |  | 83.0691 |  |  | 149.2123 |  |  | 269.4281 |  |  | 600.2115 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.71457 |  |  | 11.2883 |  |  | 27.4967 |  |  | 55.0683 |  |  | 102.9071 |  |  | 221.5991 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2854 | 4.0579 |  | 0.71172 | 63.896 |  | 4.4967 | 153.375 |  | 16.0683 | 292.849 |  | 41.9071 | 481.6288 |  | 133.5991 | 717.0796 |  | 5500 | 956.9455 |  | 5500 | 1167.6554 |  | 5500 | 1355.6117 |  | 5500 | 1542.8126
[13 empty] | Next iteration flow rate |  |  | 4.1391 | Abs Value of | Flow this | 64.5349 | Abs Value of | Flow this | 154.9087 | Abs Value of | Flow this | 295.7775 | Abs Value of | Flow this | 486.4451 | Abs Value of | Flow this | 724.2504 | Abs Value of | Flow this | 966.515 | Abs Value of | Flow this | 1179.332 | Abs Value of | Flow this | 1369.1678 | Abs Value of | Flow this | 1558.2407 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9156 |  |  | 56.7755 |  |  | 56.1057 |  |  | 53.9616 |  |  | 48.9246 |  |  | 39.2012 |  |  | 25.3676 |  |  | 9.9447 |  |  | -6.3942 |  |  | -25.087
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6849 |  |  | 24.8189 |  |  | 25.2477 |  |  | 26.2551 |  |  | 28.1998 |  |  | 30.9665 |  |  | 34.0511 |  |  | 37.3188 |  |  | 41.0574
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2587 |  |  | 32.0906 |  |  | 31.2869 |  |  | 28.7139 |  |  | 22.6696 |  |  | 11.0015 |  |  | -5.5988 |  |  | -24.1063 |  |  | -43.7131 |  |  | -66.1444
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7647 |  |  | 46.636 |  |  | 45.0421 |  |  | 41.3613 |  |  | 34.9665 |  |  | 24.9639 |  |  | 14.4172 |  |  | 4.5477 |  |  | -2.697 |  |  | -9.6018
[13 empty] | C Non choked w/ reducers | 7 |  | 0.72886 |  |  | 11.4018 |  |  | 27.7802 |  |  | 55.6866 |  |  | 104.3684 |  |  | 228.036 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.60535 |  |  | 9.458 |  |  | 23.153 |  |  | 46.398 |  |  | 84.0359 |  |  | 151.3814 |  |  | 275.4945 |  |  | 635.0433 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.72886 |  |  | 11.4018 |  |  | 27.7802 |  |  | 55.6866 |  |  | 104.3684 |  |  | 228.036 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2711 | 4.1391 |  | 0.59824 | 64.5349 |  | 4.7802 | 154.9087 |  | 16.6866 | 295.7775 |  | 43.3684 | 486.4451 |  | 140.036 | 724.2504 |  | 5500 | 966.515 |  | 5500 | 1179.332 |  | 5500 | 1369.1678 |  | 5500 | 1558.2407
[13 empty] | Next iteration flow rate |  |  | 4.2219 | Abs Value of | Flow this | 65.1803 | Abs Value of | Flow this | 156.4578 | Abs Value of | Flow this | 298.7353 | Abs Value of | Flow this | 491.3095 | Abs Value of | Flow this | 731.4929 | Abs Value of | Flow this | 976.1801 | Abs Value of | Flow this | 1191.1253 | Abs Value of | Flow this | 1382.8595 | Abs Value of | Flow this | 1573.8231 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9155 |  |  | 56.7727 |  |  | 56.0894 |  |  | 53.9022 |  |  | 48.764 |  |  | 38.8452 |  |  | 24.7335 |  |  | 9.0006 |  |  | -7.6668 |  |  | -26.7353
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6855 |  |  | 24.8221 |  |  | 25.2596 |  |  | 26.2872 |  |  | 28.271 |  |  | 31.0933 |  |  | 34.2399 |  |  | 37.5734 |  |  | 41.3871
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2586 |  |  | 32.0872 |  |  | 31.2673 |  |  | 28.6426 |  |  | 22.4768 |  |  | 10.5742 |  |  | -6.3598 |  |  | -25.2393 |  |  | -45.2401 |  |  | -68.1224
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7647 |  |  | 46.6336 |  |  | 45.0289 |  |  | 41.3154 |  |  | 34.8506 |  |  | 24.7346 |  |  | 14.0505 |  |  | 4.096 |  |  | -3.1992 |  |  | -10.2218
[13 empty] | C Non choked w/ reducers | 7 |  | 0.74344 |  |  | 11.5164 |  |  | 28.0668 |  |  | 56.3134 |  |  | 105.8632 |  |  | 234.9236 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.61746 |  |  | 9.5528 |  |  | 23.3879 |  |  | 46.888 |  |  | 85.0172 |  |  | 153.6024 |  |  | 281.8576 |  |  | 675.8379 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.74344 |  |  | 11.5164 |  |  | 28.0668 |  |  | 56.3134 |  |  | 105.8632 |  |  | 234.9236 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2566 | 4.2219 |  | 0.48362 | 65.1803 |  | 5.0668 | 156.4578 |  | 17.3134 | 298.7353 |  | 44.8632 | 491.3095 |  | 146.9236 | 731.4929 |  | 5500 | 976.1801 |  | 5500 | 1191.1253 |  | 5500 | 1382.8595 |  | 5500 | 1573.8231
[13 empty] | Next iteration flow rate |  |  | 4.3063 | Abs Value of | Flow this | 65.8321 | Abs Value of | Flow this | 158.0224 | Abs Value of | Flow this | 301.7226 | Abs Value of | Flow this | 496.2226 | Abs Value of | Flow this | 738.8079 | Abs Value of | Flow this | 985.9419 | Abs Value of | Flow this | 1203.0365 | Abs Value of | Flow this | 1396.6881 | Abs Value of | Flow this | 1589.5613 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9155 |  |  | 56.7698 |  |  | 56.0728 |  |  | 53.8416 |  |  | 48.6001 |  |  | 38.4819 |  |  | 24.0866 |  |  | 8.0375 |  |  | -8.9649 |  |  | -28.4167
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.686 |  |  | 24.8254 |  |  | 25.2717 |  |  | 26.32 |  |  | 28.3436 |  |  | 31.2227 |  |  | 34.4325 |  |  | 37.833 |  |  | 41.7233
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2586 |  |  | 32.0837 |  |  | 31.2474 |  |  | 28.5699 |  |  | 22.2802 |  |  | 10.1383 |  |  | -7.136 |  |  | -26.395 |  |  | -46.7979 |  |  | -70.14
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7646 |  |  | 46.6313 |  |  | 45.0154 |  |  | 41.2686 |  |  | 34.7324 |  |  | 24.5006 |  |  | 13.6763 |  |  | 3.6352 |  |  | -3.7114 |  |  | -10.8542
[13 empty] | C Non choked w/ reducers | 7 |  | 0.75831 |  |  | 11.6322 |  |  | 28.3565 |  |  | 56.9488 |  |  | 107.3926 |  |  | 242.3197 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.62981 |  |  | 9.6486 |  |  | 23.6253 |  |  | 47.3838 |  |  | 86.0133 |  |  | 155.8773 |  |  | 288.5437 |  |  | 724.571 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.75831 |  |  | 11.6322 |  |  | 28.3565 |  |  | 56.9488 |  |  | 107.3926 |  |  | 242.3197 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2417 | 4.3063 |  | 0.36783 | 65.8321 |  | 5.3565 | 158.0224 |  | 17.9488 | 301.7226 |  | 46.3926 | 496.2226 |  | 154.3197 | 738.8079 |  | 5500 | 985.9419 |  | 5500 | 1203.0365 |  | 5500 | 1396.6881 |  | 5500 | 1589.5613
[13 empty] | Next iteration flow rate |  |  | 4.3924 | Abs Value of | Flow this | 66.4904 | Abs Value of | Flow this | 159.6026 | Abs Value of | Flow this | 304.7398 | Abs Value of | Flow this | 501.1848 | Abs Value of | Flow this | 746.1959 | Abs Value of | Flow this | 995.8014 | Abs Value of | Flow this | 1215.0669 | Abs Value of | Flow this | 1410.655 | Abs Value of | Flow this | 1605.4569 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9155 |  |  | 56.7668 |  |  | 56.0559 |  |  | 53.7798 |  |  | 48.433 |  |  | 38.1114 |  |  | 23.4268 |  |  | 7.055 |  |  | -10.2891 |  |  | -30.1319
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6866 |  |  | 24.8288 |  |  | 25.284 |  |  | 26.3534 |  |  | 28.4177 |  |  | 31.3546 |  |  | 34.629 |  |  | 38.0978 |  |  | 42.0664
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2586 |  |  | 32.0802 |  |  | 31.227 |  |  | 28.4958 |  |  | 22.0796 |  |  | 9.6937 |  |  | -7.9279 |  |  | -27.574 |  |  | -48.3869 |  |  | -72.1983
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7646 |  |  | 46.6288 |  |  | 45.0017 |  |  | 41.2208 |  |  | 34.6119 |  |  | 24.262 |  |  | 13.2947 |  |  | 3.1651 |  |  | -4.234 |  |  | -11.4994
[13 empty] | C Non choked w/ reducers | 7 |  | 0.77347 |  |  | 11.7491 |  |  | 28.6494 |  |  | 57.5931 |  |  | 108.958 |  |  | 250.2929 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.64241 |  |  | 9.7454 |  |  | 23.8652 |  |  | 47.8853 |  |  | 87.0246 |  |  | 158.2084 |  |  | 295.5825 |  |  | 784.2811 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.77347 |  |  | 11.7491 |  |  | 28.6494 |  |  | 57.5931 |  |  | 108.958 |  |  | 250.2929 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2265 | 4.3924 |  | 0.25086 | 66.4904 |  | 5.6494 | 159.6026 |  | 18.5931 | 304.7398 |  | 47.958 | 501.1848 |  | 162.2929 | 746.1959 |  | 5500 | 995.8014 |  | 5500 | 1215.0669 |  | 5500 | 1410.655 |  | 5500 | 1605.4569
[13 empty] | Next iteration flow rate |  |  | 4.4803 | Abs Value of | Flow this | 67.1553 | Abs Value of | Flow this | 161.1986 | Abs Value of | Flow this | 307.7872 | Abs Value of | Flow this | 506.1967 | Abs Value of | Flow this | 753.6579 | Abs Value of | Flow this | 1005.7594 | Abs Value of | Flow this | 1227.2176 | Abs Value of | Flow this | 1424.7615 | Abs Value of | Flow this | 1621.5115 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9155 |  |  | 56.7638 |  |  | 56.0386 |  |  | 53.7168 |  |  | 48.2625 |  |  | 37.7334 |  |  | 22.7536 |  |  | 6.0528 |  |  | -11.6399 |  |  | -31.8815
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6872 |  |  | 24.8323 |  |  | 25.2966 |  |  | 26.3875 |  |  | 28.4933 |  |  | 31.4893 |  |  | 34.8294 |  |  | 38.368 |  |  | 42.4163
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2586 |  |  | 32.0766 |  |  | 31.2063 |  |  | 28.4201 |  |  | 21.875 |  |  | 9.2401 |  |  | -8.7356 |  |  | -28.7766 |  |  | -50.0079 |  |  | -74.2979
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7646 |  |  | 46.6263 |  |  | 44.9877 |  |  | 41.1721 |  |  | 34.4889 |  |  | 24.0186 |  |  | 12.9054 |  |  | 2.6856 |  |  | -4.7671 |  |  | -12.1575
[13 empty] | C Non choked w/ reducers | 7 |  | 0.78894 |  |  | 11.8673 |  |  | 28.9455 |  |  | 58.2464 |  |  | 110.5611 |  |  | 258.926 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.65525 |  |  | 9.8431 |  |  | 24.1076 |  |  | 48.3928 |  |  | 88.0514 |  |  | 160.5982 |  |  | 303.0079 |  |  | 859.9413 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.78894 |  |  | 11.8673 |  |  | 28.9455 |  |  | 58.2464 |  |  | 110.5611 |  |  | 258.926 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2111 | 4.4803 |  | 0.1327 | 67.1553 |  | 5.9455 | 161.1986 |  | 19.2464 | 307.7872 |  | 49.5611 | 506.1967 |  | 170.926 | 753.6579 |  | 5500 | 1005.7594 |  | 5500 | 1227.2176 |  | 5500 | 1424.7615 |  | 5500 | 1621.5115
[13 empty] | Next iteration flow rate |  |  | 4.5699 | Abs Value of | Flow this | 67.8269 | Abs Value of | Flow this | 162.8106 | Abs Value of | Flow this | 310.8651 | Abs Value of | Flow this | 511.2587 | Abs Value of | Flow this | 761.1945 | Abs Value of | Flow this | 1015.817 | Abs Value of | Flow this | 1239.4898 | Abs Value of | Flow this | 1439.0091 | Abs Value of | Flow this | 1637.7266 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9154 |  |  | 56.7608 |  |  | 56.0209 |  |  | 53.6525 |  |  | 48.0885 |  |  | 37.3479 |  |  | 22.067 |  |  | 5.0305 |  |  | -13.0179 |  |  | -33.6664
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6878 |  |  | 24.8358 |  |  | 25.3095 |  |  | 26.4223 |  |  | 28.5704 |  |  | 31.6266 |  |  | 35.0339 |  |  | 38.6436 |  |  | 42.7733
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2585 |  |  | 32.0729 |  |  | 31.1851 |  |  | 28.343 |  |  | 21.6662 |  |  | 8.7774 |  |  | -9.5596 |  |  | -30.0034 |  |  | -51.6615 |  |  | -76.4397
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7646 |  |  | 46.6238 |  |  | 44.9735 |  |  | 41.1224 |  |  | 34.3635 |  |  | 23.7702 |  |  | 12.5082 |  |  | 2.1964 |  |  | -5.3109 |  |  | -12.8288
[13 empty] | C Non choked w/ reducers | 7 |  | 0.80472 |  |  | 11.9867 |  |  | 29.2448 |  |  | 58.9089 |  |  | 112.2033 |  |  | 268.3194 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.66836 |  |  | 9.9418 |  |  | 24.3526 |  |  | 48.9062 |  |  | 89.0941 |  |  | 163.0493 |  |  | 310.8585 |  |  | 960.4014 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.80472 |  |  | 11.9867 |  |  | 29.2448 |  |  | 58.9089 |  |  | 112.2033 |  |  | 268.3194 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1953 | 4.5699 |  | 0.013341 | 67.8269 |  | 6.2448 | 162.8106 |  | 19.9089 | 310.8651 |  | 51.2033 | 511.2587 |  | 180.3194 | 761.1945 |  | 5500 | 1015.817 |  | 5500 | 1239.4898 |  | 5500 | 1439.0091 |  | 5500 | 1637.7266
[13 empty] | Next iteration flow rate |  |  | 4.6613 | Abs Value of | Flow this | 68.5051 | Abs Value of | Flow this | 164.4387 | Abs Value of | Flow this | 313.9738 | Abs Value of | Flow this | 516.3712 | Abs Value of | Flow this | 768.8064 | Abs Value of | Flow this | 1025.9751 | Abs Value of | Flow this | 1251.8847 | Abs Value of | Flow this | 1453.3992 | Abs Value of | Flow this | 1654.1039 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9154 |  |  | 56.7577 |  |  | 56.0029 |  |  | 53.5869 |  |  | 47.9111 |  |  | 36.9545 |  |  | 21.3665 |  |  | 3.9876 |  |  | -14.4236 |  |  | -35.4871
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6885 |  |  | 24.8394 |  |  | 25.3226 |  |  | 26.4578 |  |  | 28.6491 |  |  | 31.7667 |  |  | 35.2425 |  |  | 38.9247 |  |  | 43.1374
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2585 |  |  | 32.0692 |  |  | 31.1635 |  |  | 28.2643 |  |  | 21.4533 |  |  | 8.3054 |  |  | -10.4002 |  |  | -31.2549 |  |  | -53.3483 |  |  | -78.6245
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7646 |  |  | 46.6212 |  |  | 44.9589 |  |  | 41.0717 |  |  | 34.2355 |  |  | 23.5169 |  |  | 12.1031 |  |  | 1.6974 |  |  | -5.8656 |  |  | -13.5137
[13 empty] | C Non choked w/ reducers | 7 |  | 0.82082 |  |  | 12.1072 |  |  | 29.5475 |  |  | 59.5808 |  |  | 113.8863 |  |  | 278.5966 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.68173 |  |  | 10.0415 |  |  | 24.6001 |  |  | 49.4258 |  |  | 90.1531 |  |  | 165.5643 |  |  | 319.1785 |  |  | 1103.4132 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.82082 |  |  | 12.1072 |  |  | 29.5475 |  |  | 59.5808 |  |  | 113.8863 |  |  | 278.5966 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1792 | 4.6613 |  | 0.10723 | 68.5051 |  | 6.5475 | 164.4387 |  | 20.5808 | 313.9738 |  | 52.8863 | 516.3712 |  | 190.5966 | 768.8064 |  | 5500 | 1025.9751 |  | 5500 | 1251.8847 |  | 5500 | 1453.3992 |  | 5500 | 1654.1039
[13 empty] | Next iteration flow rate |  |  | 4.7545 | Abs Value of | Flow this | 69.1902 | Abs Value of | Flow this | 166.0831 | Abs Value of | Flow this | 317.1135 | Abs Value of | Flow this | 521.535 | Abs Value of | Flow this | 776.4945 | Abs Value of | Flow this | 1036.2349 | Abs Value of | Flow this | 1264.4035 | Abs Value of | Flow this | 1467.9332 | Abs Value of | Flow this | 1670.6449 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9154 |  |  | 56.7545 |  |  | 55.9846 |  |  | 53.52 |  |  | 47.7301 |  |  | 36.5533 |  |  | 20.652 |  |  | 2.9237 |  |  | -15.8575 |  |  | -37.3444
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6891 |  |  | 24.8431 |  |  | 25.336 |  |  | 26.494 |  |  | 28.7293 |  |  | 31.9096 |  |  | 35.4553 |  |  | 39.2115 |  |  | 43.5089
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2585 |  |  | 32.0654 |  |  | 31.1415 |  |  | 28.184 |  |  | 21.2361 |  |  | 7.824 |  |  | -11.2577 |  |  | -32.5316 |  |  | -55.069 |  |  | -80.8533
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7645 |  |  | 46.6186 |  |  | 44.944 |  |  | 41.02 |  |  | 34.105 |  |  | 23.2585 |  |  | 11.6898 |  |  | 1.1884 |  |  | -6.4315 |  |  | -14.2123
[13 empty] | C Non choked w/ reducers | 7 |  | 0.83723 |  |  | 12.229 |  |  | 29.8536 |  |  | 60.2623 |  |  | 115.6119 |  |  | 289.9112 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.69536 |  |  | 10.1422 |  |  | 24.8502 |  |  | 49.9515 |  |  | 91.2287 |  |  | 168.1463 |  |  | 328.0191 |  |  | 1331.9153 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.83723 |  |  | 12.229 |  |  | 29.8536 |  |  | 60.2623 |  |  | 115.6119 |  |  | 289.9112 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1628 | 4.7545 |  | 0.22903 | 69.1902 |  | 6.8536 | 166.0831 |  | 21.2623 | 317.1135 |  | 54.6119 | 521.535 |  | 201.9112 | 776.4945 |  | 5500 | 1036.2349 |  | 5500 | 1264.4035 |  | 5500 | 1467.9332 |  | 5500 | 1670.6449
[13 empty] | Next iteration flow rate |  |  | 4.8496 | Abs Value of | Flow this | 69.8821 | Abs Value of | Flow this | 167.7439 | Abs Value of | Flow this | 320.2846 | Abs Value of | Flow this | 526.7503 | Abs Value of | Flow this | 784.2594 | Abs Value of | Flow this | 1046.5972 | Abs Value of | Flow this | 1277.0475 | Abs Value of | Flow this | 1482.6125 | Abs Value of | Flow this | 1687.3514 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9153 |  |  | 56.7512 |  |  | 55.9659 |  |  | 53.4517 |  |  | 47.5455 |  |  | 36.144 |  |  | 19.923 |  |  | 1.8385 |  |  | -17.3203 |  |  | -39.239
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6898 |  |  | 24.8468 |  |  | 25.3497 |  |  | 26.5309 |  |  | 28.8112 |  |  | 32.0554 |  |  | 35.6723 |  |  | 39.5041 |  |  | 43.8878
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2584 |  |  | 32.0615 |  |  | 31.119 |  |  | 28.102 |  |  | 21.0146 |  |  | 7.3328 |  |  | -12.1324 |  |  | -33.8339 |  |  | -56.8243 |  |  | -83.1268
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7645 |  |  | 46.6159 |  |  | 44.9289 |  |  | 40.9672 |  |  | 33.9718 |  |  | 22.9949 |  |  | 11.2683 |  |  | 0.66909 |  |  | -7.0087 |  |  | -14.9249
[13 empty] | C Non choked w/ reducers | 7 |  | 0.85398 |  |  | 12.3521 |  |  | 30.163 |  |  | 60.9535 |  |  | 117.382 |  |  | 302.4576 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.70927 |  |  | 10.2439 |  |  | 25.1029 |  |  | 50.4835 |  |  | 92.3214 |  |  | 170.7984 |  |  | 337.4398 |  |  | 1792.7826 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.85398 |  |  | 12.3521 |  |  | 30.163 |  |  | 60.9535 |  |  | 117.382 |  |  | 302.4576 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.146 | 4.8496 |  | 0.35208 | 69.8821 |  | 7.163 | 167.7439 |  | 21.9535 | 320.2846 |  | 56.382 | 526.7503 |  | 214.4576 | 784.2594 |  | 5500 | 1046.5972 |  | 5500 | 1277.0475 |  | 5500 | 1482.6125 |  | 5500 | 1687.3514
[13 empty] | Next iteration flow rate |  |  | 4.9466 | Abs Value of | Flow this | 70.5809 | Abs Value of | Flow this | 169.4214 | Abs Value of | Flow this | 323.4875 | Abs Value of | Flow this | 532.0178 | Abs Value of | Flow this | 792.102 | Abs Value of | Flow this | 1057.0632 | Abs Value of | Flow this | 1289.818 | Abs Value of | Flow this | 1497.4387 | Abs Value of | Flow this | 1704.2249 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9153 |  |  | 56.7479 |  |  | 55.9468 |  |  | 53.3821 |  |  | 47.3571 |  |  | 35.7265 |  |  | 19.1795 |  |  | 0.73139 |  |  | -18.8124 |  |  | -41.1717
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6904 |  |  | 24.8506 |  |  | 25.3636 |  |  | 26.5686 |  |  | 28.8947 |  |  | 32.2041 |  |  | 35.8937 |  |  | 39.8025 |  |  | 44.2743
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2584 |  |  | 32.0575 |  |  | 31.0961 |  |  | 28.0185 |  |  | 20.7885 |  |  | 6.8318 |  |  | -13.0246 |  |  | -35.1623 |  |  | -58.6149 |  |  | -85.4461
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7645 |  |  | 46.6131 |  |  | 44.9134 |  |  | 40.9134 |  |  | 33.836 |  |  | 22.726 |  |  | 10.8382 |  |  | 0.1394 |  |  | -7.5975 |  |  | -15.6519
[13 empty] | C Non choked w/ reducers | 7 |  | 0.87106 |  |  | 12.4764 |  |  | 30.4758 |  |  | 61.6548 |  |  | 119.1986 |  |  | 316.4856 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.72345 |  |  | 10.3466 |  |  | 25.3583 |  |  | 51.0218 |  |  | 93.4316 |  |  | 173.524 |  |  | 347.51 |  |  | 3967.0579 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.87106 |  |  | 12.4764 |  |  | 30.4758 |  |  | 61.6548 |  |  | 119.1986 |  |  | 316.4856 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1289 | 4.9466 |  | 0.47637 | 70.5809 |  | 7.4758 | 169.4214 |  | 22.6548 | 323.4875 |  | 58.1986 | 532.0178 |  | 228.4856 | 792.102 |  | 5500 | 1057.0632 |  | 5500 | 1289.818 |  | 5500 | 1497.4387 |  | 5500 | 1704.2249
[13 empty] | Next iteration flow rate |  |  | 5.0455 | Abs Value of | Flow this | 71.2867 | Abs Value of | Flow this | 171.1156 | Abs Value of | Flow this | 326.7224 | Abs Value of | Flow this | 537.338 | Abs Value of | Flow this | 800.023 | Abs Value of | Flow this | 1067.6338 | Abs Value of | Flow this | 1302.7162 | Abs Value of | Flow this | 1512.4131 | Abs Value of | Flow this | 1721.2671 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9153 |  |  | 56.7445 |  |  | 55.9273 |  |  | 53.311 |  |  | 47.165 |  |  | 35.3006 |  |  | 18.421 |  |  | -0.39792 |  |  | -20.3346 |  |  | -43.1433
[13 empty] | P2 at this iteration flow rate |  |  | 24.6569 |  |  | 24.6911 |  |  | 24.8545 |  |  | 25.3778 |  |  | 26.607 |  |  | 28.9799 |  |  | 32.3558 |  |  | 36.1196 |  |  | 40.1069 |  |  | 44.6687
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2583 |  |  | 32.0534 |  |  | 31.0727 |  |  | 27.9332 |  |  | 20.558 |  |  | 6.3207 |  |  | -13.9348 |  |  | -36.5175 |  |  | -60.4415 |  |  | -87.812
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7645 |  |  | 46.6103 |  |  | 44.8977 |  |  | 40.8585 |  |  | 33.6974 |  |  | 22.4517 |  |  | 10.3995 |  |  | -0.40095 |  |  | -8.1982 |  |  | -16.3935
[13 empty] | C Non choked w/ reducers | 7 |  | 0.88848 |  |  | 12.6019 |  |  | 30.7922 |  |  | 62.3663 |  |  | 121.0638 |  |  | 332.3228 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.73792 |  |  | 10.4504 |  |  | 25.6164 |  |  | 51.5667 |  |  | 94.5597 |  |  | 176.3266 |  |  | 358.3116 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.88848 |  |  | 12.6019 |  |  | 30.7922 |  |  | 62.3663 |  |  | 121.0638 |  |  | 332.3228 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.1115 | 5.0455 |  | 0.60193 | 71.2867 |  | 7.7922 | 171.1156 |  | 23.3663 | 326.7224 |  | 60.0638 | 537.338 |  | 244.3228 | 800.023 |  | 5500 | 1067.6338 |  | 5500 | 1302.7162 |  | 5500 | 1512.4131 |  | 5500 | 1721.2671
[13 empty] | Next iteration flow rate |  |  | 5.1464 | Abs Value of | Flow this | 71.9996 | Abs Value of | Flow this | 172.8267 | Abs Value of | Flow this | 329.9896 | Abs Value of | Flow this | 542.7114 | Abs Value of | Flow this | 808.0233 | Abs Value of | Flow this | 1078.3102 | Abs Value of | Flow this | 1315.7434 | Abs Value of | Flow this | 1527.5372 | Abs Value of | Flow this | 1738.4798 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9152 |  |  | 56.7411 |  |  | 55.9074 |  |  | 53.2386 |  |  | 46.969 |  |  | 34.8661 |  |  | 17.6472 |  |  | -1.5499 |  |  | -21.8873 |  |  | -45.1545
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6918 |  |  | 24.8585 |  |  | 25.3923 |  |  | 26.6462 |  |  | 29.0668 |  |  | 32.5106 |  |  | 36.35 |  |  | 40.4175 |  |  | 45.0709
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2583 |  |  | 32.0493 |  |  | 31.0489 |  |  | 27.8463 |  |  | 20.3228 |  |  | 5.7993 |  |  | -14.8633 |  |  | -37.8999 |  |  | -62.3048 |  |  | -90.2254
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7644 |  |  | 46.6075 |  |  | 44.8816 |  |  | 40.8025 |  |  | 33.5561 |  |  | 22.1719 |  |  | 9.952 |  |  | -0.95216 |  |  | -8.811 |  |  | -17.15
[13 empty] | C Non choked w/ reducers | 7 |  | 0.90625 |  |  | 12.7288 |  |  | 31.112 |  |  | 63.0882 |  |  | 122.9799 |  |  | 350.4089 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.75268 |  |  | 10.5552 |  |  | 25.8772 |  |  | 52.1181 |  |  | 95.7062 |  |  | 179.2101 |  |  | 369.9419 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.90625 |  |  | 12.7288 |  |  | 31.112 |  |  | 63.0882 |  |  | 122.9799 |  |  | 350.4089 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.0937 | 5.1464 |  | 0.72877 | 71.9996 |  | 8.112 | 172.8267 |  | 24.0882 | 329.9896 |  | 61.9799 | 542.7114 |  | 262.4089 | 808.0233 |  | 5500 | 1078.3102 |  | 5500 | 1315.7434 |  | 5500 | 1527.5372 |  | 5500 | 1738.4798
[13 empty] | Next iteration flow rate |  |  | 5.2494 | Abs Value of | Flow this | 72.7196 | Abs Value of | Flow this | 174.555 | Abs Value of | Flow this | 333.2895 | Abs Value of | Flow this | 548.1385 | Abs Value of | Flow this | 816.1035 | Abs Value of | Flow this | 1089.0933 | Abs Value of | Flow this | 1328.9008 | Abs Value of | Flow this | 1542.8126 | Abs Value of | Flow this | 1755.8646 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9152 |  |  | 56.7376 |  |  | 55.8871 |  |  | 53.1646 |  |  | 46.769 |  |  | 34.4229 |  |  | 16.8579 |  |  | -2.7251 |  |  | -23.4712 |  |  | -47.2061
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6925 |  |  | 24.8626 |  |  | 25.4071 |  |  | 26.6862 |  |  | 29.1554 |  |  | 32.6684 |  |  | 36.585 |  |  | 40.7342 |  |  | 45.4812
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2583 |  |  | 32.0451 |  |  | 31.0245 |  |  | 27.7576 |  |  | 20.0828 |  |  | 5.2675 |  |  | -15.8105 |  |  | -39.3101 |  |  | -64.2055 |  |  | -92.6874
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7644 |  |  | 46.6046 |  |  | 44.8652 |  |  | 40.7454 |  |  | 33.4119 |  |  | 21.8864 |  |  | 9.4955 |  |  | -1.5144 |  |  | -9.436 |  |  | -17.9217
[13 empty] | C Non choked w/ reducers | 7 |  | 0.92438 |  |  | 12.8569 |  |  | 31.4355 |  |  | 63.8208 |  |  | 124.9495 |  |  | 371.3504 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.76774 |  |  | 10.6611 |  |  | 26.1407 |  |  | 52.6761 |  |  | 96.8717 |  |  | 182.1787 |  |  | 382.5175 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.92438 |  |  | 12.8569 |  |  | 31.4355 |  |  | 63.8208 |  |  | 124.9495 |  |  | 371.3504 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.0756 | 5.2494 |  | 0.85691 | 72.7196 |  | 8.4355 | 174.555 |  | 24.8208 | 333.2895 |  | 63.9495 | 548.1385 |  | 283.3504 | 816.1035 |  | 5500 | 1089.0933 |  | 5500 | 1328.9008 |  | 5500 | 1542.8126 |  | 5500 | 1755.8646
[13 empty] | Next iteration flow rate |  |  | 5.3543 | Abs Value of | Flow this | 73.4468 | Abs Value of | Flow this | 176.3006 | Abs Value of | Flow this | 336.6224 | Abs Value of | Flow this | 553.6199 | Abs Value of | Flow this | 824.2645 | Abs Value of | Flow this | 1099.9842 | Abs Value of | Flow this | 1342.1898 | Abs Value of | Flow this | 1558.2407 | Abs Value of | Flow this | 1773.4232 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9152 |  |  | 56.734 |  |  | 55.8664 |  |  | 53.0892 |  |  | 46.5651 |  |  | 33.9708 |  |  | 16.0527 |  |  | -3.9239 |  |  | -25.087 |  |  | -49.299
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6932 |  |  | 24.8667 |  |  | 25.4222 |  |  | 26.727 |  |  | 29.2458 |  |  | 32.8295 |  |  | 36.8248 |  |  | 41.0574 |  |  | 45.8998
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2582 |  |  | 32.0408 |  |  | 30.9997 |  |  | 27.6671 |  |  | 19.8381 |  |  | 4.7249 |  |  | -16.7767 |  |  | -40.7487 |  |  | -66.1444 |  |  | -95.1988
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7644 |  |  | 46.6016 |  |  | 44.8485 |  |  | 40.6871 |  |  | 33.2648 |  |  | 21.5953 |  |  | 9.0298 |  |  | -2.088 |  |  | -10.0737 |  |  | -18.7089
[13 empty] | C Non choked w/ reducers | 7 |  | 0.94287 |  |  | 12.9864 |  |  | 31.7625 |  |  | 64.5644 |  |  | 126.9751 |  |  | 396.012 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.78309 |  |  | 10.7681 |  |  | 26.4071 |  |  | 53.241 |  |  | 98.0564 |  |  | 185.2369 |  |  | 396.1796 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.94287 |  |  | 12.9864 |  |  | 31.7625 |  |  | 64.5644 |  |  | 126.9751 |  |  | 396.012 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.0571 | 5.3543 |  | 0.98635 | 73.4468 |  | 8.7625 | 176.3006 |  | 25.5644 | 336.6224 |  | 65.9751 | 553.6199 |  | 308.012 | 824.2645 |  | 5500 | 1099.9842 |  | 5500 | 1342.1898 |  | 5500 | 1558.2407 |  | 5500 | 1773.4232
[13 empty] | Next iteration flow rate |  |  | 5.4614 | Abs Value of | Flow this | 74.1813 | Abs Value of | Flow this | 178.0636 | Abs Value of | Flow this | 339.9886 | Abs Value of | Flow this | 559.1561 | Abs Value of | Flow this | 832.5072 | Abs Value of | Flow this | 1110.9841 | Abs Value of | Flow this | 1355.6117 | Abs Value of | Flow this | 1573.8231 | Abs Value of | Flow this | 1791.1575 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9151 |  |  | 56.7303 |  |  | 55.8453 |  |  | 53.0123 |  |  | 46.357 |  |  | 33.5096 |  |  | 15.2314 |  |  | -5.1468 |  |  | -26.7353 |  |  | -51.4339
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6939 |  |  | 24.8709 |  |  | 25.4375 |  |  | 26.7686 |  |  | 29.3381 |  |  | 32.9937 |  |  | 37.0694 |  |  | 41.3871 |  |  | 46.3268
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2582 |  |  | 32.0364 |  |  | 30.9744 |  |  | 27.5748 |  |  | 19.5884 |  |  | 4.1715 |  |  | -17.7623 |  |  | -42.2161 |  |  | -68.1224 |  |  | -97.7607
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7643 |  |  | 46.5986 |  |  | 44.8314 |  |  | 40.6277 |  |  | 33.1147 |  |  | 21.2982 |  |  | 8.5548 |  |  | -2.6731 |  |  | -10.7241 |  |  | -19.5119
[13 empty] | C Non choked w/ reducers | 7 |  | 0.96172 |  |  | 13.1171 |  |  | 32.0933 |  |  | 65.3191 |  |  | 129.0595 |  |  | 425.6786 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.79875 |  |  | 10.8761 |  |  | 26.6762 |  |  | 53.8127 |  |  | 99.2611 |  |  | 188.3893 |  |  | 411.1011 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.96172 |  |  | 13.1171 |  |  | 32.0933 |  |  | 65.3191 |  |  | 129.0595 |  |  | 425.6786 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.0383 | 5.4614 |  | 1.1171 | 74.1813 |  | 9.0933 | 178.0636 |  | 26.3191 | 339.9886 |  | 68.0595 | 559.1561 |  | 337.6786 | 832.5072 |  | 5500 | 1110.9841 |  | 5500 | 1355.6117 |  | 5500 | 1573.8231 |  | 5500 | 1791.1575
[13 empty] | Next iteration flow rate |  |  | 5.5707 | Abs Value of | Flow this | 74.9231 | Abs Value of | Flow this | 179.8442 | Abs Value of | Flow this | 343.3885 | Abs Value of | Flow this | 564.7476 | Abs Value of | Flow this | 840.8323 | Abs Value of | Flow this | 1122.0939 | Abs Value of | Flow this | 1369.1678 | Abs Value of | Flow this | 1589.5613 | Abs Value of | Flow this | 1809.0691 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9151 |  |  | 56.7266 |  |  | 55.8238 |  |  | 52.9339 |  |  | 46.1448 |  |  | 33.0391 |  |  | 14.3935 |  |  | -6.3942 |  |  | -28.4167 |  |  | -53.6117
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6947 |  |  | 24.8752 |  |  | 25.4532 |  |  | 26.811 |  |  | 29.4322 |  |  | 33.1613 |  |  | 37.3188 |  |  | 41.7233 |  |  | 46.7623
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2581 |  |  | 32.0319 |  |  | 30.9486 |  |  | 27.4806 |  |  | 19.3337 |  |  | 3.6069 |  |  | -18.7678 |  |  | -43.7131 |  |  | -70.14 |  |  | -100.3741
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7643 |  |  | 46.5955 |  |  | 44.814 |  |  | 40.5671 |  |  | 32.9617 |  |  | 20.9952 |  |  | 8.0702 |  |  | -3.27 |  |  | -11.3876 |  |  | -20.3311
[13 empty] | C Non choked w/ reducers | 7 |  | 0.98096 |  |  | 13.2492 |  |  | 32.4277 |  |  | 66.0852 |  |  | 131.2059 |  |  | 462.36 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.81473 |  |  | 10.9852 |  |  | 26.9482 |  |  | 54.3914 |  |  | 100.4862 |  |  | 191.6413 |  |  | 427.4965 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 0.98096 |  |  | 13.2492 |  |  | 32.4277 |  |  | 66.0852 |  |  | 131.2059 |  |  | 462.36 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.019 | 5.5707 |  | 1.2492 | 74.9231 |  | 9.4277 | 179.8442 |  | 27.0852 | 343.3885 |  | 70.2059 | 564.7476 |  | 374.36 | 840.8323 |  | 5500 | 1122.0939 |  | 5500 | 1369.1678 |  | 5500 | 1589.5613 |  | 5500 | 1809.0691
[13 empty] | Next iteration flow rate |  |  | 5.6821 | Abs Value of | Flow this | 75.6723 | Abs Value of | Flow this | 181.6426 | Abs Value of | Flow this | 346.8224 | Abs Value of | Flow this | 570.3951 | Abs Value of | Flow this | 849.2406 | Abs Value of | Flow this | 1133.3148 | Abs Value of | Flow this | 1382.8595 | Abs Value of | Flow this | 1605.4569 | Abs Value of | Flow this | 1827.1597 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9151 |  |  | 56.7228 |  |  | 55.8019 |  |  | 52.8538 |  |  | 45.9283 |  |  | 32.5592 |  |  | 13.5388 |  |  | -7.6668 |  |  | -30.1319 |  |  | -55.8334
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6954 |  |  | 24.8796 |  |  | 25.4692 |  |  | 26.8543 |  |  | 29.5282 |  |  | 33.3322 |  |  | 37.5734 |  |  | 42.0664 |  |  | 47.2067
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2581 |  |  | 32.0273 |  |  | 30.9222 |  |  | 27.3846 |  |  | 19.0739 |  |  | 3.031 |  |  | -19.7934 |  |  | -45.2401 |  |  | -72.1983 |  |  | -103.04
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7643 |  |  | 46.5923 |  |  | 44.7962 |  |  | 40.5052 |  |  | 32.8055 |  |  | 20.6861 |  |  | 7.5759 |  |  | -3.8789 |  |  | -12.0645 |  |  | -21.1667
[13 empty] | C Non choked w/ reducers | 7 |  | 1.0006 |  |  | 13.3827 |  |  | 32.7659 |  |  | 66.863 |  |  | 133.4174 |  |  | 509.4204 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.83102 |  |  | 11.0955 |  |  | 27.2231 |  |  | 54.9773 |  |  | 101.7323 |  |  | 194.9985 |  |  | 445.6356 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.0006 |  |  | 13.3827 |  |  | 32.7659 |  |  | 66.863 |  |  | 133.4174 |  |  | 509.4204 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.9994 | 5.6821 |  | 1.3827 | 75.6723 |  | 9.7659 | 181.6426 |  | 27.863 | 346.8224 |  | 72.4174 | 570.3951 |  | 421.4204 | 849.2406 |  | 5500 | 1133.3148 |  | 5500 | 1382.8595 |  | 5500 | 1605.4569 |  | 5500 | 1827.1597
[13 empty] | Next iteration flow rate |  |  | 5.7957 | Abs Value of | Flow this | 76.429 | Abs Value of | Flow this | 183.4591 | Abs Value of | Flow this | 350.2906 | Abs Value of | Flow this | 576.0991 | Abs Value of | Flow this | 857.733 | Abs Value of | Flow this | 1144.648 | Abs Value of | Flow this | 1396.6881 | Abs Value of | Flow this | 1621.5115 | Abs Value of | Flow this | 1845.4313 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.915 |  |  | 56.7189 |  |  | 55.7795 |  |  | 52.7722 |  |  | 45.7074 |  |  | 32.0696 |  |  | 12.6669 |  |  | -8.9649 |  |  | -31.8815 |  |  | -58.0996
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6962 |  |  | 24.8841 |  |  | 25.4856 |  |  | 26.8985 |  |  | 29.6261 |  |  | 33.5066 |  |  | 37.833 |  |  | 42.4163 |  |  | 47.6599
[13 empty] | Delta P at this iteration flow rate |  |  | 32.258 |  |  | 32.0226 |  |  | 30.8954 |  |  | 27.2866 |  |  | 18.8089 |  |  | 2.4435 |  |  | -20.8397 |  |  | -46.7979 |  |  | -74.2979 |  |  | -105.7595
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7642 |  |  | 46.5891 |  |  | 44.7781 |  |  | 40.4421 |  |  | 32.6463 |  |  | 20.3708 |  |  | 7.0716 |  |  | -4.5 |  |  | -12.755 |  |  | -22.0192
[13 empty] | C Non choked w/ reducers | 7 |  | 1.0206 |  |  | 13.5175 |  |  | 33.108 |  |  | 67.6528 |  |  | 135.6976 |  |  | 573.0378 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.84764 |  |  | 11.2068 |  |  | 27.5009 |  |  | 55.5704 |  |  | 103 |  |  | 198.4668 |  |  | 465.8634 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.0206 |  |  | 13.5175 |  |  | 33.108 |  |  | 67.6528 |  |  | 135.6976 |  |  | 573.0378 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.9794 | 5.7957 |  | 1.5175 | 76.429 |  | 10.108 | 183.4591 |  | 28.6528 | 350.2906 |  | 74.6976 | 576.0991 |  | 485.0378 | 857.733 |  | 5500 | 1144.648 |  | 5500 | 1396.6881 |  | 5500 | 1621.5115 |  | 5500 | 1845.4313
[13 empty] | Next iteration flow rate |  |  | 5.9116 | Abs Value of | Flow this | 77.1933 | Abs Value of | Flow this | 185.2937 | Abs Value of | Flow this | 353.7935 | Abs Value of | Flow this | 581.86 | Abs Value of | Flow this | 866.3103 | Abs Value of | Flow this | 1156.0945 | Abs Value of | Flow this | 1410.655 | Abs Value of | Flow this | 1637.7266 | Abs Value of | Flow this | 1863.8857 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.915 |  |  | 56.7149 |  |  | 55.7566 |  |  | 52.6889 |  |  | 45.4821 |  |  | 31.5702 |  |  | 11.7775 |  |  | -10.2891 |  |  | -33.6664 |  |  | -60.4114
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.697 |  |  | 24.8887 |  |  | 25.5022 |  |  | 26.9436 |  |  | 29.726 |  |  | 33.6845 |  |  | 38.0978 |  |  | 42.7733 |  |  | 48.1223
[13 empty] | Delta P at this iteration flow rate |  |  | 32.258 |  |  | 32.0179 |  |  | 30.8679 |  |  | 27.1866 |  |  | 18.5386 |  |  | 1.8442 |  |  | -21.907 |  |  | -48.3869 |  |  | -76.4397 |  |  | -108.5337
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7642 |  |  | 46.5858 |  |  | 44.7596 |  |  | 40.3777 |  |  | 32.4838 |  |  | 20.0492 |  |  | 6.5572 |  |  | -5.1336 |  |  | -13.4593 |  |  | -22.8887
[13 empty] | C Non choked w/ reducers | 7 |  | 1.041 |  |  | 13.6537 |  |  | 33.4539 |  |  | 68.4548 |  |  | 138.0503 |  |  | 666.2016 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.8646 |  |  | 11.3193 |  |  | 27.7816 |  |  | 56.1708 |  |  | 104.2899 |  |  | 202.053 |  |  | 488.6295 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.041 |  |  | 13.6537 |  |  | 33.4539 |  |  | 68.4548 |  |  | 138.0503 |  |  | 666.2016 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.959 | 5.9116 |  | 1.6537 | 77.1933 |  | 10.4539 | 185.2937 |  | 29.4548 | 353.7935 |  | 77.0503 | 581.86 |  | 578.2016 | 866.3103 |  | 5500 | 1156.0945 |  | 5500 | 1410.655 |  | 5500 | 1637.7266 |  | 5500 | 1863.8857
[13 empty] | Next iteration flow rate |  |  | 6.0299 | Abs Value of | Flow this | 77.9652 | Abs Value of | Flow this | 187.1466 | Abs Value of | Flow this | 357.3314 | Abs Value of | Flow this | 587.6786 | Abs Value of | Flow this | 874.9734 | Abs Value of | Flow this | 1167.6554 | Abs Value of | Flow this | 1424.7615 | Abs Value of | Flow this | 1654.1039 | Abs Value of | Flow this | 1882.5245 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9149 |  |  | 56.7109 |  |  | 55.7333 |  |  | 52.6039 |  |  | 45.2523 |  |  | 31.0607 |  |  | 10.8702 |  |  | -11.6399 |  |  | -35.4871 |  |  | -62.7697
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6978 |  |  | 24.8933 |  |  | 25.5192 |  |  | 26.9895 |  |  | 29.8279 |  |  | 33.866 |  |  | 38.368 |  |  | 43.1374 |  |  | 48.5939
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2579 |  |  | 32.013 |  |  | 30.84 |  |  | 27.0847 |  |  | 18.2628 |  |  | 1.2329 |  |  | -22.9957 |  |  | -50.0079 |  |  | -78.6245 |  |  | -111.3637
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7641 |  |  | 46.5825 |  |  | 44.7407 |  |  | 40.3121 |  |  | 32.318 |  |  | 19.7211 |  |  | 6.0324 |  |  | -5.7799 |  |  | -14.1778 |  |  | -23.7758
[13 empty] | C Non choked w/ reducers | 7 |  | 1.0618 |  |  | 13.7912 |  |  | 33.8038 |  |  | 69.2693 |  |  | 140.4797 |  |  | 822.9493 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.88189 |  |  | 11.4329 |  |  | 28.0654 |  |  | 56.7787 |  |  | 105.6025 |  |  | 205.7642 |  |  | 514.5329 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.0618 |  |  | 13.7912 |  |  | 33.8038 |  |  | 69.2693 |  |  | 140.4797 |  |  | 822.9493 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.9382 | 6.0299 |  | 1.7912 | 77.9652 |  | 10.8038 | 187.1466 |  | 30.2693 | 357.3314 |  | 79.4797 | 587.6786 |  | 734.9493 | 874.9734 |  | 5500 | 1167.6554 |  | 5500 | 1424.7615 |  | 5500 | 1654.1039 |  | 5500 | 1882.5245
[13 empty] | Next iteration flow rate |  |  | 6.1505 | Abs Value of | Flow this | 78.7449 | Abs Value of | Flow this | 189.0181 | Abs Value of | Flow this | 360.9047 | Abs Value of | Flow this | 593.5554 | Abs Value of | Flow this | 883.7232 | Abs Value of | Flow this | 1179.332 | Abs Value of | Flow this | 1439.0091 | Abs Value of | Flow this | 1670.6449 | Abs Value of | Flow this | 1901.3498 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9149 |  |  | 56.7067 |  |  | 55.7095 |  |  | 52.5172 |  |  | 45.0179 |  |  | 30.541 |  |  | 9.9447 |  |  | -13.0179 |  |  | -37.3444 |  |  | -65.1754
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6987 |  |  | 24.8981 |  |  | 25.5366 |  |  | 27.0364 |  |  | 29.9318 |  |  | 34.0511 |  |  | 38.6436 |  |  | 43.5089 |  |  | 49.0751
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2578 |  |  | 32.0081 |  |  | 30.8114 |  |  | 26.9807 |  |  | 17.9814 |  |  | 0.60926 |  |  | -24.1063 |  |  | -51.6615 |  |  | -80.8533 |  |  | -114.2505
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7641 |  |  | 46.5791 |  |  | 44.7215 |  |  | 40.2451 |  |  | 32.149 |  |  | 19.3864 |  |  | 5.4972 |  |  | -6.4393 |  |  | -14.9108 |  |  | -24.6807
[13 empty] | C Non choked w/ reducers | 7 |  | 1.0831 |  |  | 13.9302 |  |  | 34.1576 |  |  | 70.0968 |  |  | 142.9901 |  |  | 1182.3782 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.89953 |  |  | 11.5476 |  |  | 28.3521 |  |  | 57.3942 |  |  | 106.9387 |  |  | 209.6081 |  |  | 544.3926 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.0831 |  |  | 13.9302 |  |  | 34.1576 |  |  | 70.0968 |  |  | 142.9901 |  |  | 1182.3782 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.9169 | 6.1505 |  | 1.9302 | 78.7449 |  | 11.1576 | 189.0181 |  | 31.0968 | 360.9047 |  | 81.9901 | 593.5554 |  | 1094.3782 | 883.7232 |  | 5500 | 1179.332 |  | 5500 | 1439.0091 |  | 5500 | 1670.6449 |  | 5500 | 1901.3498
[13 empty] | Next iteration flow rate |  |  | 6.2735 | Abs Value of | Flow this | 79.5323 | Abs Value of | Flow this | 190.9082 | Abs Value of | Flow this | 364.5138 | Abs Value of | Flow this | 599.491 | Abs Value of | Flow this | 892.5604 | Abs Value of | Flow this | 1191.1253 | Abs Value of | Flow this | 1453.3992 | Abs Value of | Flow this | 1687.3514 | Abs Value of | Flow this | 1920.3633 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9148 |  |  | 56.7025 |  |  | 55.6853 |  |  | 52.4288 |  |  | 44.7787 |  |  | 30.0109 |  |  | 9.0006 |  |  | -14.4236 |  |  | -39.239 |  |  | -67.6295
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.6995 |  |  | 24.9029 |  |  | 25.5542 |  |  | 27.0843 |  |  | 30.0378 |  |  | 34.2399 |  |  | 38.9247 |  |  | 43.8878 |  |  | 49.5659
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2578 |  |  | 32.003 |  |  | 30.7823 |  |  | 26.8746 |  |  | 17.6945 |  |  | -0.026911 |  |  | -25.2393 |  |  | -53.3483 |  |  | -83.1268 |  |  | -117.1953
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7641 |  |  | 46.5756 |  |  | 44.7019 |  |  | 40.1768 |  |  | 31.9765 |  |  | 19.0449 |  |  | 4.9511 |  |  | -7.1118 |  |  | -15.6584 |  |  | -25.6037
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1047 |  |  | 14.0706 |  |  | 34.5155 |  |  | 70.9373 |  |  | 145.5865 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.91752 |  |  | 11.6635 |  |  | 28.6419 |  |  | 58.0174 |  |  | 108.2989 |  |  | 213.5935 |  |  | 579.3639 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.1047 |  |  | 14.0706 |  |  | 34.5155 |  |  | 70.9373 |  |  | 145.5865 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.8953 | 6.2735 |  | 2.0706 | 79.5323 |  | 11.5155 | 190.9082 |  | 31.9373 | 364.5138 |  | 84.5865 | 599.491 |  | 5500 | 892.5604 |  | 5500 | 1191.1253 |  | 5500 | 1453.3992 |  | 5500 | 1687.3514 |  | 5500 | 1920.3633
[13 empty] | Next iteration flow rate |  |  | 6.3989 | Abs Value of | Flow this | 80.3277 | Abs Value of | Flow this | 192.8173 | Abs Value of | Flow this | 368.1589 | Abs Value of | Flow this | 605.4859 | Abs Value of | Flow this | 901.486 | Abs Value of | Flow this | 1203.0365 | Abs Value of | Flow this | 1467.9332 | Abs Value of | Flow this | 1704.2249 | Abs Value of | Flow this | 1939.5669 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9148 |  |  | 56.6982 |  |  | 55.6605 |  |  | 52.3386 |  |  | 44.5347 |  |  | 29.4701 |  |  | 8.0375 |  |  | -15.8575 |  |  | -41.1717 |  |  | -70.1328
[13 empty] | P2 at this iteration flow rate |  |  | 24.657 |  |  | 24.7004 |  |  | 24.9079 |  |  | 25.5723 |  |  | 27.1331 |  |  | 30.146 |  |  | 34.4325 |  |  | 39.2115 |  |  | 44.2743 |  |  | 50.0666
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2577 |  |  | 31.9979 |  |  | 30.7526 |  |  | 26.7663 |  |  | 17.4017 |  |  | -0.67587 |  |  | -26.395 |  |  | -55.069 |  |  | -85.4461 |  |  | -120.1994
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.764 |  |  | 46.572 |  |  | 44.6818 |  |  | 40.1071 |  |  | 31.8005 |  |  | 18.6966 |  |  | 4.3941 |  |  | -7.7979 |  |  | -16.4211 |  |  | -26.5453
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1268 |  |  | 14.2125 |  |  | 34.8775 |  |  | 71.7914 |  |  | 148.274 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.93587 |  |  | 11.7806 |  |  | 28.9348 |  |  | 58.6485 |  |  | 109.6841 |  |  | 217.7295 |  |  | 621.1405 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.1268 |  |  | 14.2125 |  |  | 34.8775 |  |  | 71.7914 |  |  | 148.274 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.8732 | 6.3989 |  | 2.2125 | 80.3277 |  | 11.8775 | 192.8173 |  | 32.7914 | 368.1589 |  | 87.274 | 605.4859 |  | 5500 | 901.486 |  | 5500 | 1203.0365 |  | 5500 | 1467.9332 |  | 5500 | 1704.2249 |  | 5500 | 1939.5669
[13 empty] | Next iteration flow rate |  |  | 6.5269 | Abs Value of | Flow this | 81.1309 | Abs Value of | Flow this | 194.7455 | Abs Value of | Flow this | 371.8405 | Abs Value of | Flow this | 611.5408 | Abs Value of | Flow this | 910.5008 | Abs Value of | Flow this | 1215.0669 | Abs Value of | Flow this | 1482.6125 | Abs Value of | Flow this | 1721.2671 | Abs Value of | Flow this | 1958.9626 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9147 |  |  | 56.6938 |  |  | 55.6353 |  |  | 52.2466 |  |  | 44.2859 |  |  | 28.9184 |  |  | 7.055 |  |  | -17.3203 |  |  | -43.1433 |  |  | -72.6865
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.7012 |  |  | 24.9129 |  |  | 25.5907 |  |  | 27.1828 |  |  | 30.2563 |  |  | 34.629 |  |  | 39.5041 |  |  | 44.6687 |  |  | 50.5773
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2576 |  |  | 31.9926 |  |  | 30.7224 |  |  | 26.6559 |  |  | 17.1031 |  |  | -1.3379 |  |  | -27.574 |  |  | -56.8243 |  |  | -87.812 |  |  | -123.2638
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.764 |  |  | 46.5684 |  |  | 44.6614 |  |  | 40.0359 |  |  | 31.6211 |  |  | 18.3413 |  |  | 3.8259 |  |  | -8.4978 |  |  | -17.1992 |  |  | -27.5059
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1494 |  |  | 14.3558 |  |  | 35.2436 |  |  | 72.6594 |  |  | 151.0586 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.95459 |  |  | 11.8989 |  |  | 29.2308 |  |  | 59.2875 |  |  | 111.0949 |  |  | 222.0266 |  |  | 672.3272 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.1494 |  |  | 14.3558 |  |  | 35.2436 |  |  | 72.6594 |  |  | 151.0586 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.8506 | 6.5269 |  | 2.3558 | 81.1309 |  | 12.2436 | 194.7455 |  | 33.6594 | 371.8405 |  | 90.0586 | 611.5408 |  | 5500 | 910.5008 |  | 5500 | 1215.0669 |  | 5500 | 1482.6125 |  | 5500 | 1721.2671 |  | 5500 | 1958.9626
[13 empty] | Next iteration flow rate |  |  | 6.6575 | Abs Value of | Flow this | 81.9423 | Abs Value of | Flow this | 196.6929 | Abs Value of | Flow this | 375.5589 | Abs Value of | Flow this | 617.6562 | Abs Value of | Flow this | 919.6059 | Abs Value of | Flow this | 1227.2176 | Abs Value of | Flow this | 1497.4387 | Abs Value of | Flow this | 1738.4798 | Abs Value of | Flow this | 1978.5522 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9146 |  |  | 56.6894 |  |  | 55.6096 |  |  | 52.1527 |  |  | 44.032 |  |  | 28.3557 |  |  | 6.0528 |  |  | -18.8124 |  |  | -45.1545 |  |  | -75.2915
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.7021 |  |  | 24.9181 |  |  | 25.6095 |  |  | 27.2336 |  |  | 30.3689 |  |  | 34.8294 |  |  | 39.8025 |  |  | 45.0709 |  |  | 51.0983
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2576 |  |  | 31.9873 |  |  | 30.6915 |  |  | 26.5433 |  |  | 16.7984 |  |  | -2.0132 |  |  | -28.7766 |  |  | -58.6149 |  |  | -90.2254 |  |  | -126.3898
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7639 |  |  | 46.5647 |  |  | 44.6406 |  |  | 39.9634 |  |  | 31.438 |  |  | 17.9789 |  |  | 3.2462 |  |  | -9.2118 |  |  | -17.9928 |  |  | -28.4857
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1723 |  |  | 14.5006 |  |  | 35.614 |  |  | 73.5415 |  |  | 153.9464 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.97368 |  |  | 12.0184 |  |  | 29.53 |  |  | 59.9347 |  |  | 112.5321 |  |  | 226.4959 |  |  | 737.187 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.1723 |  |  | 14.5006 |  |  | 35.614 |  |  | 73.5415 |  |  | 153.9464 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.8277 | 6.6575 |  | 2.5006 | 81.9423 |  | 12.614 | 196.6929 |  | 34.5415 | 375.5589 |  | 92.9464 | 617.6562 |  | 5500 | 919.6059 |  | 5500 | 1227.2176 |  | 5500 | 1497.4387 |  | 5500 | 1738.4798 |  | 5500 | 1978.5522
[13 empty] | Next iteration flow rate |  |  | 6.7906 | Abs Value of | Flow this | 82.7617 | Abs Value of | Flow this | 198.6599 | Abs Value of | Flow this | 379.3145 | Abs Value of | Flow this | 623.8327 | Abs Value of | Flow this | 928.8019 | Abs Value of | Flow this | 1239.4898 | Abs Value of | Flow this | 1512.4131 | Abs Value of | Flow this | 1755.8646 | Abs Value of | Flow this | 1998.3377 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9146 |  |  | 56.6848 |  |  | 55.5833 |  |  | 52.057 |  |  | 43.773 |  |  | 27.7816 |  |  | 5.0305 |  |  | -20.3346 |  |  | -47.2061 |  |  | -77.9489
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.703 |  |  | 24.9233 |  |  | 25.6286 |  |  | 27.2854 |  |  | 30.4837 |  |  | 35.0339 |  |  | 40.1069 |  |  | 45.4812 |  |  | 51.6298
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2575 |  |  | 31.9818 |  |  | 30.6599 |  |  | 26.4284 |  |  | 16.4876 |  |  | -2.702 |  |  | -30.0034 |  |  | -60.4415 |  |  | -92.6874 |  |  | -129.5787
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7639 |  |  | 46.5609 |  |  | 44.6193 |  |  | 39.8894 |  |  | 31.2512 |  |  | 17.6092 |  |  | 2.6549 |  |  | -9.9401 |  |  | -18.8025 |  |  | -29.4853
[13 empty] | C Non choked w/ reducers | 7 |  | 1.1958 |  |  | 14.6468 |  |  | 35.9886 |  |  | 74.4382 |  |  | 156.9443 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 0.99315 |  |  | 12.139 |  |  | 29.8324 |  |  | 60.5902 |  |  | 113.9965 |  |  | 231.1499 |  |  | 823.3067 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.1958 |  |  | 14.6468 |  |  | 35.9886 |  |  | 74.4382 |  |  | 156.9443 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.8042 | 6.7906 |  | 2.6468 | 82.7617 |  | 12.9886 | 198.6599 |  | 35.4382 | 379.3145 |  | 95.9443 | 623.8327 |  | 5500 | 928.8019 |  | 5500 | 1239.4898 |  | 5500 | 1512.4131 |  | 5500 | 1755.8646 |  | 5500 | 1998.3377
[13 empty] | Next iteration flow rate |  |  | 6.9264 | Abs Value of | Flow this | 83.5893 | Abs Value of | Flow this | 200.6465 | Abs Value of | Flow this | 383.1077 | Abs Value of | Flow this | 630.071 | Abs Value of | Flow this | 938.0899 | Abs Value of | Flow this | 1251.8847 | Abs Value of | Flow this | 1527.5372 | Abs Value of | Flow this | 1773.4232 | Abs Value of | Flow this | 2018.3211 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9145 |  |  | 56.6802 |  |  | 55.5565 |  |  | 51.9593 |  |  | 43.5089 |  |  | 27.196 |  |  | 3.9876 |  |  | -21.8873 |  |  | -49.299 |  |  | -80.6597
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.704 |  |  | 24.9287 |  |  | 25.6481 |  |  | 27.3382 |  |  | 30.6008 |  |  | 35.2425 |  |  | 40.4175 |  |  | 45.8998 |  |  | 52.1719
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2574 |  |  | 31.9762 |  |  | 30.6278 |  |  | 26.3112 |  |  | 16.1706 |  |  | -3.4048 |  |  | -31.2549 |  |  | -62.3048 |  |  | -95.1988 |  |  | -132.8316
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7638 |  |  | 46.5571 |  |  | 44.5977 |  |  | 39.8139 |  |  | 31.0607 |  |  | 17.232 |  |  | 2.0518 |  |  | -10.683 |  |  | -19.6284 |  |  | -30.5049
[13 empty] | C Non choked w/ reducers | 7 |  | 1.2197 |  |  | 14.7946 |  |  | 36.3675 |  |  | 75.3498 |  |  | 160.06 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.013 |  |  | 12.2609 |  |  | 30.1381 |  |  | 61.2541 |  |  | 115.4891 |  |  | 236.0024 |  |  | 945.904 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.2197 |  |  | 14.7946 |  |  | 36.3675 |  |  | 75.3498 |  |  | 160.06 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.7803 | 6.9264 |  | 2.7946 | 83.5893 |  | 13.3675 | 200.6465 |  | 36.3498 | 383.1077 |  | 99.06 | 630.071 |  | 5500 | 938.0899 |  | 5500 | 1251.8847 |  | 5500 | 1527.5372 |  | 5500 | 1773.4232 |  | 5500 | 2018.3211
[13 empty] | Next iteration flow rate |  |  | 7.0649 | Abs Value of | Flow this | 84.4252 | Abs Value of | Flow this | 202.6529 | Abs Value of | Flow this | 386.9387 | Abs Value of | Flow this | 636.3718 | Abs Value of | Flow this | 947.4708 | Abs Value of | Flow this | 1264.4035 | Abs Value of | Flow this | 1542.8126 | Abs Value of | Flow this | 1791.1575 | Abs Value of | Flow this | 2038.5043 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9145 |  |  | 56.6754 |  |  | 55.5292 |  |  | 51.8597 |  |  | 43.2394 |  |  | 26.5986 |  |  | 2.9237 |  |  | -23.4712 |  |  | -51.4339 |  |  | -83.4249
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.7049 |  |  | 24.9342 |  |  | 25.6681 |  |  | 27.3921 |  |  | 30.7203 |  |  | 35.4553 |  |  | 40.7342 |  |  | 46.3268 |  |  | 52.725
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2573 |  |  | 31.9705 |  |  | 30.595 |  |  | 26.1916 |  |  | 15.8473 |  |  | -4.1216 |  |  | -32.5316 |  |  | -64.2055 |  |  | -97.7607 |  |  | -136.1499
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7638 |  |  | 46.5531 |  |  | 44.5756 |  |  | 39.7369 |  |  | 30.8663 |  |  | 16.8473 |  |  | 1.4365 |  |  | -11.4409 |  |  | -20.4709 |  |  | -31.5451
[13 empty] | C Non choked w/ reducers | 7 |  | 1.2441 |  |  | 14.9439 |  |  | 36.7509 |  |  | 76.2768 |  |  | 163.3017 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.0333 |  |  | 12.3841 |  |  | 30.447 |  |  | 61.9265 |  |  | 117.0106 |  |  | 241.0688 |  |  | 1141.7881 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.2441 |  |  | 14.9439 |  |  | 36.7509 |  |  | 76.2768 |  |  | 163.3017 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.7559 | 7.0649 |  | 2.9439 | 84.4252 |  | 13.7509 | 202.6529 |  | 37.2768 | 386.9387 |  | 102.3017 | 636.3718 |  | 5500 | 947.4708 |  | 5500 | 1264.4035 |  | 5500 | 1542.8126 |  | 5500 | 1791.1575 |  | 5500 | 2038.5043
[13 empty] | Next iteration flow rate |  |  | 7.2062 | Abs Value of | Flow this | 85.2694 | Abs Value of | Flow this | 204.6795 | Abs Value of | Flow this | 390.8081 | Abs Value of | Flow this | 642.7355 | Abs Value of | Flow this | 956.9455 | Abs Value of | Flow this | 1277.0475 | Abs Value of | Flow this | 1558.2407 | Abs Value of | Flow this | 1809.0691 | Abs Value of | Flow this | 2058.8893 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9144 |  |  | 56.6706 |  |  | 55.5013 |  |  | 51.7581 |  |  | 42.9645 |  |  | 25.9893 |  |  | 1.8385 |  |  | -25.087 |  |  | -53.6117 |  |  | -86.2458
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.7059 |  |  | 24.9397 |  |  | 25.6884 |  |  | 27.4471 |  |  | 30.8421 |  |  | 35.6723 |  |  | 41.0574 |  |  | 46.7623 |  |  | 53.2892
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2573 |  |  | 31.9647 |  |  | 30.5616 |  |  | 26.0697 |  |  | 15.5174 |  |  | -4.8529 |  |  | -33.8339 |  |  | -66.1444 |  |  | -100.3741 |  |  | -139.535
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7637 |  |  | 46.5491 |  |  | 44.553 |  |  | 39.6584 |  |  | 30.6681 |  |  | 16.4548 |  |  | 0.80878 |  |  | -12.214 |  |  | -21.3303 |  |  | -32.6061
[13 empty] | C Non choked w/ reducers | 7 |  | 1.269 |  |  | 15.0947 |  |  | 37.1387 |  |  | 77.2196 |  |  | 166.6787 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.0539 |  |  | 12.5084 |  |  | 30.7593 |  |  | 62.6077 |  |  | 118.5621 |  |  | 246.366 |  |  | 1536.8678 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.269 |  |  | 15.0947 |  |  | 37.1387 |  |  | 77.2196 |  |  | 166.6787 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.731 | 7.2062 |  | 3.0947 | 85.2694 |  | 14.1387 | 204.6795 |  | 38.2196 | 390.8081 |  | 105.6787 | 642.7355 |  | 5500 | 956.9455 |  | 5500 | 1277.0475 |  | 5500 | 1558.2407 |  | 5500 | 1809.0691 |  | 5500 | 2058.8893
[13 empty] | Next iteration flow rate |  |  | 7.3504 | Abs Value of | Flow this | 86.1221 | Abs Value of | Flow this | 206.7263 | Abs Value of | Flow this | 394.7162 | Abs Value of | Flow this | 649.1628 | Abs Value of | Flow this | 966.515 | Abs Value of | Flow this | 1289.818 | Abs Value of | Flow this | 1573.8231 | Abs Value of | Flow this | 1827.1597 | Abs Value of | Flow this | 2079.4782 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9143 |  |  | 56.6657 |  |  | 55.4729 |  |  | 51.6544 |  |  | 42.684 |  |  | 25.3676 |  |  | 0.73139 |  |  | -26.7353 |  |  | -55.8334 |  |  | -89.1234
[13 empty] | P2 at this iteration flow rate |  |  | 24.6571 |  |  | 24.7069 |  |  | 24.9454 |  |  | 25.7091 |  |  | 27.5032 |  |  | 30.9665 |  |  | 35.8937 |  |  | 41.3871 |  |  | 47.2067 |  |  | 53.8647
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2572 |  |  | 31.9588 |  |  | 30.5274 |  |  | 25.9453 |  |  | 15.1809 |  |  | -5.5988 |  |  | -35.1623 |  |  | -68.1224 |  |  | -103.04 |  |  | -142.988
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7637 |  |  | 46.5451 |  |  | 44.53 |  |  | 39.5783 |  |  | 30.4658 |  |  | 16.0545 |  |  | 0.1685 |  |  | -13.0026 |  |  | -22.207 |  |  | -33.6885
[13 empty] | C Non choked w/ reducers | 7 |  | 1.2944 |  |  | 15.247 |  |  | 37.5311 |  |  | 78.1786 |  |  | 170.2011 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.075 |  |  | 12.6341 |  |  | 31.0749 |  |  | 63.2977 |  |  | 120.1445 |  |  | 251.9131 |  |  | 3400.7713 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.2944 |  |  | 15.247 |  |  | 37.5311 |  |  | 78.1786 |  |  | 170.2011 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.7056 | 7.3504 |  | 3.247 | 86.1221 |  | 14.5311 | 206.7263 |  | 39.1786 | 394.7162 |  | 109.2011 | 649.1628 |  | 5500 | 966.515 |  | 5500 | 1289.818 |  | 5500 | 1573.8231 |  | 5500 | 1827.1597 |  | 5500 | 2079.4782
[13 empty] | Next iteration flow rate |  |  | 7.4974 | Abs Value of | Flow this | 86.9834 | Abs Value of | Flow this | 208.7935 | Abs Value of | Flow this | 398.6634 | Abs Value of | Flow this | 655.6545 | Abs Value of | Flow this | 976.1801 | Abs Value of | Flow this | 1302.7162 | Abs Value of | Flow this | 1589.5613 | Abs Value of | Flow this | 1845.4313 | Abs Value of | Flow this | 2100.273 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9142 |  |  | 56.6606 |  |  | 55.4438 |  |  | 51.5486 |  |  | 42.398 |  |  | 24.7335 |  |  | -0.39792 |  |  | -28.4167 |  |  | -58.0996 |  |  | -92.0588
[13 empty] | P2 at this iteration flow rate |  |  | 24.6572 |  |  | 24.7079 |  |  | 24.9512 |  |  | 25.7303 |  |  | 27.5604 |  |  | 31.0933 |  |  | 36.1196 |  |  | 41.7233 |  |  | 47.6599 |  |  | 54.4518
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2571 |  |  | 31.9527 |  |  | 30.4926 |  |  | 25.8183 |  |  | 14.8376 |  |  | -6.3598 |  |  | -36.5175 |  |  | -70.14 |  |  | -105.7595 |  |  | -146.5105
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7636 |  |  | 46.5409 |  |  | 44.5065 |  |  | 39.4966 |  |  | 30.2595 |  |  | 15.6461 |  |  | -0.48466 |  |  | -13.8072 |  |  | -23.1013 |  |  | -34.7926
[13 empty] | C Non choked w/ reducers | 7 |  | 1.3203 |  |  | 15.401 |  |  | 37.928 |  |  | 79.1542 |  |  | 173.8803 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.0965 |  |  | 12.761 |  |  | 31.3939 |  |  | 63.9968 |  |  | 121.7589 |  |  | 257.7316 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.3203 |  |  | 15.401 |  |  | 37.928 |  |  | 79.1542 |  |  | 173.8803 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.6797 | 7.4974 |  | 3.401 | 86.9834 |  | 14.928 | 208.7935 |  | 40.1542 | 398.6634 |  | 112.8803 | 655.6545 |  | 5500 | 976.1801 |  | 5500 | 1302.7162 |  | 5500 | 1589.5613 |  | 5500 | 1845.4313 |  | 5500 | 2100.273
[13 empty] | Next iteration flow rate |  |  | 7.6473 | Abs Value of | Flow this | 87.8532 | Abs Value of | Flow this | 210.8815 | Abs Value of | Flow this | 402.65 | Abs Value of | Flow this | 662.211 | Abs Value of | Flow this | 985.9419 | Abs Value of | Flow this | 1315.7434 | Abs Value of | Flow this | 1605.4569 | Abs Value of | Flow this | 1863.8857 | Abs Value of | Flow this | 2121.2757 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9142 |  |  | 56.6555 |  |  | 55.4143 |  |  | 51.4407 |  |  | 42.1062 |  |  | 24.0866 |  |  | -1.5499 |  |  | -30.1319 |  |  | -60.4114 |  |  | -95.0532
[13 empty] | P2 at this iteration flow rate |  |  | 24.6572 |  |  | 24.7089 |  |  | 24.9571 |  |  | 25.7519 |  |  | 27.6188 |  |  | 31.2227 |  |  | 36.35 |  |  | 42.0664 |  |  | 48.1223 |  |  | 55.0506
[13 empty] | Delta P at this iteration flow rate |  |  | 32.257 |  |  | 31.9466 |  |  | 30.4571 |  |  | 25.6889 |  |  | 14.4874 |  |  | -7.136 |  |  | -37.8999 |  |  | -72.1983 |  |  | -108.5337 |  |  | -150.1038
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7635 |  |  | 46.5366 |  |  | 44.4826 |  |  | 39.4132 |  |  | 30.0491 |  |  | 15.2294 |  |  | -1.1509 |  |  | -14.6278 |  |  | -24.0136 |  |  | -35.9189
[13 empty] | C Non choked w/ reducers | 7 |  | 1.3467 |  |  | 15.5565 |  |  | 38.3296 |  |  | 80.1469 |  |  | 177.7289 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.1185 |  |  | 12.8892 |  |  | 31.7164 |  |  | 64.7051 |  |  | 123.4064 |  |  | 263.8453 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.3467 |  |  | 15.5565 |  |  | 38.3296 |  |  | 80.1469 |  |  | 177.7289 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.6533 | 7.6473 |  | 3.5565 | 87.8532 |  | 15.3296 | 210.8815 |  | 41.1469 | 402.65 |  | 116.7289 | 662.211 |  | 5500 | 985.9419 |  | 5500 | 1315.7434 |  | 5500 | 1605.4569 |  | 5500 | 1863.8857 |  | 5500 | 2121.2757
[13 empty] | Next iteration flow rate |  |  | 7.8003 | Abs Value of | Flow this | 88.7317 | Abs Value of | Flow this | 212.9903 | Abs Value of | Flow this | 406.6765 | Abs Value of | Flow this | 668.8331 | Abs Value of | Flow this | 995.8014 | Abs Value of | Flow this | 1328.9008 | Abs Value of | Flow this | 1621.5115 | Abs Value of | Flow this | 1882.5245 | Abs Value of | Flow this | 2142.4885 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9141 |  |  | 56.6502 |  |  | 55.3841 |  |  | 51.3307 |  |  | 41.8085 |  |  | 23.4268 |  |  | -2.7251 |  |  | -31.8815 |  |  | -62.7697 |  |  | -98.1077
[13 empty] | P2 at this iteration flow rate |  |  | 24.6572 |  |  | 24.71 |  |  | 24.9632 |  |  | 25.7739 |  |  | 27.6783 |  |  | 31.3546 |  |  | 36.585 |  |  | 42.4163 |  |  | 48.5939 |  |  | 55.6615
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2569 |  |  | 31.9403 |  |  | 30.4209 |  |  | 25.5568 |  |  | 14.1302 |  |  | -7.9279 |  |  | -39.3101 |  |  | -74.2979 |  |  | -111.3637 |  |  | -153.7693
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7635 |  |  | 46.5323 |  |  | 44.4581 |  |  | 39.3281 |  |  | 29.8344 |  |  | 14.8045 |  |  | -1.8306 |  |  | -15.465 |  |  | -24.9443 |  |  | -37.0678
[13 empty] | C Non choked w/ reducers | 7 |  | 1.3736 |  |  | 15.7136 |  |  | 38.736 |  |  | 81.1573 |  |  | 181.761 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.1408 |  |  | 13.0187 |  |  | 32.0424 |  |  | 65.4228 |  |  | 125.0881 |  |  | 270.2817 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.3736 |  |  | 15.7136 |  |  | 38.736 |  |  | 81.1573 |  |  | 181.761 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.6264 | 7.8003 |  | 3.7136 | 88.7317 |  | 15.736 | 212.9903 |  | 42.1573 | 406.6765 |  | 120.761 | 668.8331 |  | 5500 | 995.8014 |  | 5500 | 1328.9008 |  | 5500 | 1621.5115 |  | 5500 | 1882.5245 |  | 5500 | 2142.4885
[13 empty] | Next iteration flow rate |  |  | 7.9563 | Abs Value of | Flow this | 89.619 | Abs Value of | Flow this | 215.1202 | Abs Value of | Flow this | 410.7433 | Abs Value of | Flow this | 675.5214 | Abs Value of | Flow this | 1005.7594 | Abs Value of | Flow this | 1342.1898 | Abs Value of | Flow this | 1637.7266 | Abs Value of | Flow this | 1901.3498 | Abs Value of | Flow this | 2163.9134 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.914 |  |  | 56.6449 |  |  | 55.3533 |  |  | 51.2184 |  |  | 41.5048 |  |  | 22.7536 |  |  | -3.9239 |  |  | -33.6664 |  |  | -65.1754 |  |  | -101.2237
[13 empty] | P2 at this iteration flow rate |  |  | 24.6572 |  |  | 24.711 |  |  | 24.9693 |  |  | 25.7963 |  |  | 27.739 |  |  | 31.4893 |  |  | 36.8248 |  |  | 42.7733 |  |  | 49.0751 |  |  | 56.2847
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2568 |  |  | 31.9339 |  |  | 30.3839 |  |  | 25.4221 |  |  | 13.7658 |  |  | -8.7356 |  |  | -40.7487 |  |  | -76.4397 |  |  | -114.2505 |  |  | -157.5085
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7634 |  |  | 46.5279 |  |  | 44.4332 |  |  | 39.2414 |  |  | 29.6154 |  |  | 14.3709 |  |  | -2.524 |  |  | -16.319 |  |  | -25.8936 |  |  | -38.2399
[13 empty] | C Non choked w/ reducers | 7 |  | 1.4011 |  |  | 15.8723 |  |  | 39.1471 |  |  | 82.1857 |  |  | 185.9925 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.1636 |  |  | 13.1495 |  |  | 32.3719 |  |  | 66.15 |  |  | 126.8053 |  |  | 277.0715 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.4011 |  |  | 15.8723 |  |  | 39.1471 |  |  | 82.1857 |  |  | 185.9925 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.5989 | 7.9563 |  | 3.8723 | 89.619 |  | 16.1471 | 215.1202 |  | 43.1857 | 410.7433 |  | 124.9925 | 675.5214 |  | 5500 | 1005.7594 |  | 5500 | 1342.1898 |  | 5500 | 1637.7266 |  | 5500 | 1901.3498 |  | 5500 | 2163.9134
[13 empty] | Next iteration flow rate |  |  | 8.1154 | Abs Value of | Flow this | 90.5152 | Abs Value of | Flow this | 217.2714 | Abs Value of | Flow this | 414.8507 | Abs Value of | Flow this | 682.2767 | Abs Value of | Flow this | 1015.817 | Abs Value of | Flow this | 1355.6117 | Abs Value of | Flow this | 1654.1039 | Abs Value of | Flow this | 1920.3633 | Abs Value of | Flow this | 2185.5525 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9139 |  |  | 56.6394 |  |  | 55.3219 |  |  | 51.1039 |  |  | 41.1951 |  |  | 22.067 |  |  | -5.1468 |  |  | -35.4871 |  |  | -67.6295 |  |  | -104.4023
[13 empty] | P2 at this iteration flow rate |  |  | 24.6572 |  |  | 24.7121 |  |  | 24.9756 |  |  | 25.8192 |  |  | 27.801 |  |  | 31.6266 |  |  | 37.0694 |  |  | 43.1374 |  |  | 49.5659 |  |  | 56.9205
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2567 |  |  | 31.9273 |  |  | 30.3462 |  |  | 25.2847 |  |  | 13.3941 |  |  | -9.5596 |  |  | -42.2161 |  |  | -78.6245 |  |  | -117.1953 |  |  | -161.3228
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7633 |  |  | 46.5234 |  |  | 44.4078 |  |  | 39.1529 |  |  | 29.392 |  |  | 13.9287 |  |  | -3.2312 |  |  | -17.1901 |  |  | -26.8621 |  |  | -39.4355
[13 empty] | C Non choked w/ reducers | 7 |  | 1.4291 |  |  | 16.0327 |  |  | 39.5631 |  |  | 83.2329 |  |  | 190.4413 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.1869 |  |  | 13.2816 |  |  | 32.7049 |  |  | 66.887 |  |  | 128.5591 |  |  | 284.25 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.4291 |  |  | 16.0327 |  |  | 39.5631 |  |  | 83.2329 |  |  | 190.4413 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.5709 | 8.1154 |  | 4.0327 | 90.5152 |  | 16.5631 | 217.2714 |  | 44.2329 | 414.8507 |  | 129.4413 | 682.2767 |  | 5500 | 1015.817 |  | 5500 | 1355.6117 |  | 5500 | 1654.1039 |  | 5500 | 1920.3633 |  | 5500 | 2185.5525
[13 empty] | Next iteration flow rate |  |  | 8.2777 | Abs Value of | Flow this | 91.4204 | Abs Value of | Flow this | 219.4441 | Abs Value of | Flow this | 418.9992 | Abs Value of | Flow this | 689.0994 | Abs Value of | Flow this | 1025.9751 | Abs Value of | Flow this | 1369.1678 | Abs Value of | Flow this | 1670.6449 | Abs Value of | Flow this | 1939.5669 | Abs Value of | Flow this | 2207.408 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9138 |  |  | 56.6339 |  |  | 55.2898 |  |  | 50.9871 |  |  | 40.8791 |  |  | 21.3665 |  |  | -6.3942 |  |  | -37.3444 |  |  | -70.1328 |  |  | -107.6448
[13 empty] | P2 at this iteration flow rate |  |  | 24.6572 |  |  | 24.7132 |  |  | 24.982 |  |  | 25.8426 |  |  | 27.8642 |  |  | 31.7667 |  |  | 37.3188 |  |  | 43.5089 |  |  | 50.0666 |  |  | 57.569
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2566 |  |  | 31.9207 |  |  | 30.3078 |  |  | 25.1445 |  |  | 13.0149 |  |  | -10.4002 |  |  | -43.7131 |  |  | -80.8533 |  |  | -120.1994 |  |  | -165.2138
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7632 |  |  | 46.5188 |  |  | 44.3819 |  |  | 39.0626 |  |  | 29.1641 |  |  | 13.4775 |  |  | -3.9527 |  |  | -18.0788 |  |  | -27.8499 |  |  | -40.6551
[13 empty] | C Non choked w/ reducers | 7 |  | 1.4577 |  |  | 16.1947 |  |  | 39.9841 |  |  | 84.2992 |  |  | 195.1276 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.2107 |  |  | 13.4151 |  |  | 33.0416 |  |  | 67.6339 |  |  | 130.351 |  |  | 291.8579 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.4577 |  |  | 16.1947 |  |  | 39.9841 |  |  | 84.2992 |  |  | 195.1276 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.5423 | 8.2777 |  | 4.1947 | 91.4204 |  | 16.9841 | 219.4441 |  | 45.2992 | 418.9992 |  | 134.1276 | 689.0994 |  | 5500 | 1025.9751 |  | 5500 | 1369.1678 |  | 5500 | 1670.6449 |  | 5500 | 1939.5669 |  | 5500 | 2207.408
[13 empty] | Next iteration flow rate |  |  | 8.4433 | Abs Value of | Flow this | 92.3346 | Abs Value of | Flow this | 221.6385 | Abs Value of | Flow this | 423.1892 | Abs Value of | Flow this | 695.9904 | Abs Value of | Flow this | 1036.2349 | Abs Value of | Flow this | 1382.8595 | Abs Value of | Flow this | 1687.3514 | Abs Value of | Flow this | 1958.9626 | Abs Value of | Flow this | 2229.4821 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9137 |  |  | 56.6282 |  |  | 55.2571 |  |  | 50.8679 |  |  | 40.5567 |  |  | 20.652 |  |  | -7.6668 |  |  | -39.239 |  |  | -72.6865 |  |  | -110.9525
[13 empty] | P2 at this iteration flow rate |  |  | 24.6573 |  |  | 24.7144 |  |  | 24.9886 |  |  | 25.8664 |  |  | 27.9287 |  |  | 31.9096 |  |  | 37.5734 |  |  | 43.8878 |  |  | 50.5773 |  |  | 58.2305
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2565 |  |  | 31.9139 |  |  | 30.2685 |  |  | 25.0015 |  |  | 12.6281 |  |  | -11.2577 |  |  | -45.2401 |  |  | -83.1268 |  |  | -123.2638 |  |  | -169.183
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7632 |  |  | 46.5141 |  |  | 44.3554 |  |  | 38.9705 |  |  | 28.9316 |  |  | 13.0173 |  |  | -4.6887 |  |  | -18.9853 |  |  | -28.8577 |  |  | -41.8993
[13 empty] | C Non choked w/ reducers | 7 |  | 1.4868 |  |  | 16.3584 |  |  | 40.4101 |  |  | 85.3854 |  |  | 200.0745 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.2349 |  |  | 13.55 |  |  | 33.382 |  |  | 68.3909 |  |  | 132.1824 |  |  | 299.9418 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.4868 |  |  | 16.3584 |  |  | 40.4101 |  |  | 85.3854 |  |  | 200.0745 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.5132 | 8.4433 |  | 4.3584 | 92.3346 |  | 17.4101 | 221.6385 |  | 46.3854 | 423.1892 |  | 139.0745 | 695.9904 |  | 5500 | 1036.2349 |  | 5500 | 1382.8595 |  | 5500 | 1687.3514 |  | 5500 | 1958.9626 |  | 5500 | 2229.4821
[13 empty] | Next iteration flow rate |  |  | 8.6121 | Abs Value of | Flow this | 93.2579 | Abs Value of | Flow this | 223.8549 | Abs Value of | Flow this | 427.4211 | Abs Value of | Flow this | 702.9503 | Abs Value of | Flow this | 1046.5972 | Abs Value of | Flow this | 1396.6881 | Abs Value of | Flow this | 1704.2249 | Abs Value of | Flow this | 1978.5522 | Abs Value of | Flow this | 2251.7769 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9136 |  |  | 56.6224 |  |  | 55.2238 |  |  | 50.7463 |  |  | 40.2279 |  |  | 19.923 |  |  | -8.9649 |  |  | -41.1717 |  |  | -75.2915 |  |  | -114.3267
[13 empty] | P2 at this iteration flow rate |  |  | 24.6573 |  |  | 24.7155 |  |  | 24.9952 |  |  | 25.8907 |  |  | 27.9944 |  |  | 32.0554 |  |  | 37.833 |  |  | 44.2743 |  |  | 51.0983 |  |  | 58.9053
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2564 |  |  | 31.9069 |  |  | 30.2285 |  |  | 24.8556 |  |  | 12.2335 |  |  | -12.1324 |  |  | -46.7979 |  |  | -85.4461 |  |  | -126.3898 |  |  | -173.232
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7631 |  |  | 46.5093 |  |  | 44.3284 |  |  | 38.8765 |  |  | 28.6945 |  |  | 12.5479 |  |  | -5.4395 |  |  | -19.9101 |  |  | -29.8857 |  |  | -43.1684
[13 empty] | C Non choked w/ reducers | 7 |  | 1.5166 |  |  | 16.5238 |  |  | 40.8412 |  |  | 86.492 |  |  | 205.3084 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.2596 |  |  | 13.6862 |  |  | 33.7261 |  |  | 69.1582 |  |  | 134.0548 |  |  | 308.5561 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.5166 |  |  | 16.5238 |  |  | 40.8412 |  |  | 86.492 |  |  | 205.3084 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.4834 | 8.6121 |  | 4.5238 | 93.2579 |  | 17.8412 | 223.8549 |  | 47.492 | 427.4211 |  | 144.3084 | 702.9503 |  | 5500 | 1046.5972 |  | 5500 | 1396.6881 |  | 5500 | 1704.2249 |  | 5500 | 1978.5522 |  | 5500 | 2251.7769
[13 empty] | Next iteration flow rate |  |  | 8.7844 | Abs Value of | Flow this | 94.1905 | Abs Value of | Flow this | 226.0935 | Abs Value of | Flow this | 431.6953 | Abs Value of | Flow this | 709.9798 | Abs Value of | Flow this | 1057.0632 | Abs Value of | Flow this | 1410.655 | Abs Value of | Flow this | 1721.2671 | Abs Value of | Flow this | 1998.3377 | Abs Value of | Flow this | 2274.2947 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9135 |  |  | 56.6165 |  |  | 55.1898 |  |  | 50.6223 |  |  | 39.8925 |  |  | 19.1795 |  |  | -10.2891 |  |  | -43.1433 |  |  | -77.9489 |  |  | -117.7686
[13 empty] | P2 at this iteration flow rate |  |  | 24.6573 |  |  | 24.7167 |  |  | 25.002 |  |  | 25.9155 |  |  | 28.0615 |  |  | 32.2041 |  |  | 38.0978 |  |  | 44.6687 |  |  | 51.6298 |  |  | 59.5937
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2562 |  |  | 31.8998 |  |  | 30.1877 |  |  | 24.7068 |  |  | 11.8309 |  |  | -13.0246 |  |  | -48.3869 |  |  | -87.812 |  |  | -129.5787 |  |  | -177.3624
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.763 |  |  | 46.5044 |  |  | 44.3009 |  |  | 38.7807 |  |  | 28.4526 |  |  | 12.069 |  |  | -6.2054 |  |  | -20.8534 |  |  | -30.9344 |  |  | -44.4631
[13 empty] | C Non choked w/ reducers | 7 |  | 1.5469 |  |  | 16.6909 |  |  | 41.2775 |  |  | 87.6196 |  |  | 210.8595 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.2848 |  |  | 13.8237 |  |  | 34.0739 |  |  | 69.9361 |  |  | 135.9697 |  |  | 317.7644 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.5469 |  |  | 16.6909 |  |  | 41.2775 |  |  | 87.6196 |  |  | 210.8595 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.4531 | 8.7844 |  | 4.6909 | 94.1905 |  | 18.2775 | 226.0935 |  | 48.6196 | 431.6953 |  | 149.8595 | 709.9798 |  | 5500 | 1057.0632 |  | 5500 | 1410.655 |  | 5500 | 1721.2671 |  | 5500 | 1998.3377 |  | 5500 | 2274.2947
[13 empty] | Next iteration flow rate |  |  | 8.9601 | Abs Value of | Flow this | 95.1324 | Abs Value of | Flow this | 228.3544 | Abs Value of | Flow this | 436.0123 | Abs Value of | Flow this | 717.0796 | Abs Value of | Flow this | 1067.6338 | Abs Value of | Flow this | 1424.7615 | Abs Value of | Flow this | 1738.4798 | Abs Value of | Flow this | 2018.3211 | Abs Value of | Flow this | 2297.0377 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9134 |  |  | 56.6105 |  |  | 55.1551 |  |  | 50.4958 |  |  | 39.5503 |  |  | 18.421 |  |  | -11.6399 |  |  | -45.1545 |  |  | -80.6597 |  |  | -121.2798
[13 empty] | P2 at this iteration flow rate |  |  | 24.6573 |  |  | 24.7179 |  |  | 25.009 |  |  | 25.9408 |  |  | 28.1299 |  |  | 32.3558 |  |  | 38.368 |  |  | 45.0709 |  |  | 52.1719 |  |  | 60.296
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2561 |  |  | 31.8926 |  |  | 30.1461 |  |  | 24.5549 |  |  | 11.4203 |  |  | -13.9348 |  |  | -50.0079 |  |  | -90.2254 |  |  | -132.8316 |  |  | -181.5758
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7629 |  |  | 46.4994 |  |  | 44.2728 |  |  | 38.6829 |  |  | 28.2058 |  |  | 11.5805 |  |  | -6.9866 |  |  | -21.8157 |  |  | -32.0041 |  |  | -45.7838
[13 empty] | C Non choked w/ reducers | 7 |  | 1.5779 |  |  | 16.8597 |  |  | 41.719 |  |  | 88.7689 |  |  | 216.7628 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.3105 |  |  | 13.9627 |  |  | 34.4256 |  |  | 70.7246 |  |  | 137.9288 |  |  | 327.6414 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.5779 |  |  | 16.8597 |  |  | 41.719 |  |  | 88.7689 |  |  | 216.7628 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.4221 | 8.9601 |  | 4.8597 | 95.1324 |  | 18.719 | 228.3544 |  | 49.7689 | 436.0123 |  | 155.7628 | 717.0796 |  | 5500 | 1067.6338 |  | 5500 | 1424.7615 |  | 5500 | 1738.4798 |  | 5500 | 2018.3211 |  | 5500 | 2297.0377
[13 empty] | Next iteration flow rate |  |  | 9.1393 | Abs Value of | Flow this | 96.0837 | Abs Value of | Flow this | 230.638 | Abs Value of | Flow this | 440.3724 | Abs Value of | Flow this | 724.2504 | Abs Value of | Flow this | 1078.3102 | Abs Value of | Flow this | 1439.0091 | Abs Value of | Flow this | 1755.8646 | Abs Value of | Flow this | 2038.5043 | Abs Value of | Flow this | 2320.008 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9133 |  |  | 56.6044 |  |  | 55.1197 |  |  | 50.3667 |  |  | 39.2012 |  |  | 17.6472 |  |  | -13.0179 |  |  | -47.2061 |  |  | -83.4249 |  |  | -124.8615
[13 empty] | P2 at this iteration flow rate |  |  | 24.6573 |  |  | 24.7191 |  |  | 25.0161 |  |  | 25.9667 |  |  | 28.1998 |  |  | 32.5106 |  |  | 38.6436 |  |  | 45.4812 |  |  | 52.725 |  |  | 61.0123
[13 empty] | Delta P at this iteration flow rate |  |  | 32.256 |  |  | 31.8852 |  |  | 30.1036 |  |  | 24.4001 |  |  | 11.0015 |  |  | -14.8633 |  |  | -51.6615 |  |  | -92.6874 |  |  | -136.1499 |  |  | -185.8739
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7628 |  |  | 46.4943 |  |  | 44.2442 |  |  | 38.5832 |  |  | 27.9541 |  |  | 11.0822 |  |  | -7.7836 |  |  | -22.7974 |  |  | -33.0954 |  |  | -47.131
[13 empty] | C Non choked w/ reducers | 7 |  | 1.6094 |  |  | 17.0302 |  |  | 42.166 |  |  | 89.9406 |  |  | 223.0592 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.3367 |  |  | 14.1031 |  |  | 34.7811 |  |  | 71.5241 |  |  | 139.934 |  |  | 338.2762 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.6094 |  |  | 17.0302 |  |  | 42.166 |  |  | 89.9406 |  |  | 223.0592 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.3906 | 9.1393 |  | 5.0302 | 96.0837 |  | 19.166 | 230.638 |  | 50.9406 | 440.3724 |  | 162.0592 | 724.2504 |  | 5500 | 1078.3102 |  | 5500 | 1439.0091 |  | 5500 | 1755.8646 |  | 5500 | 2038.5043 |  | 5500 | 2320.008
[13 empty] | Next iteration flow rate |  |  | 9.322 | Abs Value of | Flow this | 97.0446 | Abs Value of | Flow this | 232.9443 | Abs Value of | Flow this | 444.7761 | Abs Value of | Flow this | 731.4929 | Abs Value of | Flow this | 1089.0933 | Abs Value of | Flow this | 1453.3992 | Abs Value of | Flow this | 1773.4232 | Abs Value of | Flow this | 2058.8893 | Abs Value of | Flow this | 2343.2081 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9132 |  |  | 56.5981 |  |  | 55.0836 |  |  | 50.2351 |  |  | 38.8452 |  |  | 16.8579 |  |  | -14.4236 |  |  | -49.299 |  |  | -86.2458 |  |  | -128.5153
[13 empty] | P2 at this iteration flow rate |  |  | 24.6574 |  |  | 24.7204 |  |  | 25.0233 |  |  | 25.993 |  |  | 28.271 |  |  | 32.6684 |  |  | 38.9247 |  |  | 45.8998 |  |  | 53.2892 |  |  | 61.7431
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2559 |  |  | 31.8777 |  |  | 30.0603 |  |  | 24.2421 |  |  | 10.5742 |  |  | -15.8105 |  |  | -53.3483 |  |  | -95.1988 |  |  | -139.535 |  |  | -190.2583
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7627 |  |  | 46.4891 |  |  | 44.215 |  |  | 38.4815 |  |  | 27.6973 |  |  | 10.5738 |  |  | -8.5966 |  |  | -23.7987 |  |  | -34.2086 |  |  | -48.5054
[13 empty] | C Non choked w/ reducers | 7 |  | 1.6416 |  |  | 17.2026 |  |  | 42.6183 |  |  | 91.1356 |  |  | 229.7965 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.3634 |  |  | 14.245 |  |  | 35.1405 |  |  | 72.3348 |  |  | 141.987 |  |  | 349.7753 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.6416 |  |  | 17.2026 |  |  | 42.6183 |  |  | 91.1356 |  |  | 229.7965 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.3584 | 9.322 |  | 5.2026 | 97.0446 |  | 19.6183 | 232.9443 |  | 52.1356 | 444.7761 |  | 168.7965 | 731.4929 |  | 5500 | 1089.0933 |  | 5500 | 1453.3992 |  | 5500 | 1773.4232 |  | 5500 | 2058.8893 |  | 5500 | 2343.2081
[13 empty] | Next iteration flow rate |  |  | 9.5085 | Abs Value of | Flow this | 98.015 | Abs Value of | Flow this | 235.2738 | Abs Value of | Flow this | 449.2239 | Abs Value of | Flow this | 738.8079 | Abs Value of | Flow this | 1099.9842 | Abs Value of | Flow this | 1467.9332 | Abs Value of | Flow this | 1791.1575 | Abs Value of | Flow this | 2079.4782 | Abs Value of | Flow this | 2366.6402 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9131 |  |  | 56.5917 |  |  | 55.0467 |  |  | 50.1008 |  |  | 38.4819 |  |  | 16.0527 |  |  | -15.8575 |  |  | -51.4339 |  |  | -89.1234 |  |  | -132.2424
[13 empty] | P2 at this iteration flow rate |  |  | 24.6574 |  |  | 24.7217 |  |  | 25.0307 |  |  | 26.0198 |  |  | 28.3436 |  |  | 32.8295 |  |  | 39.2115 |  |  | 46.3268 |  |  | 53.8647 |  |  | 62.4885
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2557 |  |  | 31.87 |  |  | 30.0161 |  |  | 24.081 |  |  | 10.1383 |  |  | -16.7767 |  |  | -55.069 |  |  | -97.7607 |  |  | -142.988 |  |  | -194.7309
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7626 |  |  | 46.4838 |  |  | 44.1852 |  |  | 38.3777 |  |  | 27.4353 |  |  | 10.0553 |  |  | -9.4259 |  |  | -24.8202 |  |  | -35.3441 |  |  | -49.9073
[13 empty] | C Non choked w/ reducers | 7 |  | 1.6744 |  |  | 17.3767 |  |  | 43.0762 |  |  | 92.3544 |  |  | 237.0312 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.3907 |  |  | 14.3882 |  |  | 35.5039 |  |  | 73.1569 |  |  | 144.0898 |  |  | 362.268 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.6744 |  |  | 17.3767 |  |  | 43.0762 |  |  | 92.3544 |  |  | 237.0312 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.3256 | 9.5085 |  | 5.3767 | 98.015 |  | 20.0762 | 235.2738 |  | 53.3544 | 449.2239 |  | 176.0312 | 738.8079 |  | 5500 | 1099.9842 |  | 5500 | 1467.9332 |  | 5500 | 1791.1575 |  | 5500 | 2079.4782 |  | 5500 | 2366.6402
[13 empty] | Next iteration flow rate |  |  | 9.6987 | Abs Value of | Flow this | 98.9952 | Abs Value of | Flow this | 237.6265 | Abs Value of | Flow this | 453.7161 | Abs Value of | Flow this | 746.1959 | Abs Value of | Flow this | 1110.9841 | Abs Value of | Flow this | 1482.6125 | Abs Value of | Flow this | 1809.0691 | Abs Value of | Flow this | 2100.273 | Abs Value of | Flow this | 2390.3066 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.913 |  |  | 56.5852 |  |  | 55.0091 |  |  | 49.9638 |  |  | 38.1114 |  |  | 15.2314 |  |  | -17.3203 |  |  | -53.6117 |  |  | -92.0588 |  |  | -136.0445
[13 empty] | P2 at this iteration flow rate |  |  | 24.6574 |  |  | 24.723 |  |  | 25.0382 |  |  | 26.0472 |  |  | 28.4177 |  |  | 32.9937 |  |  | 39.5041 |  |  | 46.7623 |  |  | 54.4518 |  |  | 63.2489
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2556 |  |  | 31.8622 |  |  | 29.971 |  |  | 23.9166 |  |  | 9.6937 |  |  | -17.7623 |  |  | -56.8243 |  |  | -100.3741 |  |  | -146.5105 |  |  | -199.2934
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7625 |  |  | 46.4784 |  |  | 44.1548 |  |  | 38.2718 |  |  | 27.1681 |  |  | 9.5263 |  |  | -10.2719 |  |  | -25.8623 |  |  | -36.5025 |  |  | -51.3374
[13 empty] | C Non choked w/ reducers | 7 |  | 1.7079 |  |  | 17.5526 |  |  | 43.5396 |  |  | 93.5979 |  |  | 244.8304 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.4185 |  |  | 14.533 |  |  | 35.8712 |  |  | 73.9905 |  |  | 146.2447 |  |  | 375.9123 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.7079 |  |  | 17.5526 |  |  | 43.5396 |  |  | 93.5979 |  |  | 244.8304 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.2921 | 9.6987 |  | 5.5526 | 98.9952 |  | 20.5396 | 237.6265 |  | 54.5979 | 453.7161 |  | 183.8304 | 746.1959 |  | 5500 | 1110.9841 |  | 5500 | 1482.6125 |  | 5500 | 1809.0691 |  | 5500 | 2100.273 |  | 5500 | 2390.3066
[13 empty] | Next iteration flow rate |  |  | 9.8926 | Abs Value of | Flow this | 99.9851 | Abs Value of | Flow this | 240.0028 | Abs Value of | Flow this | 458.2533 | Abs Value of | Flow this | 753.6579 | Abs Value of | Flow this | 1122.0939 | Abs Value of | Flow this | 1497.4387 | Abs Value of | Flow this | 1827.1597 | Abs Value of | Flow this | 2121.2757 | Abs Value of | Flow this | 2414.2097 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9128 |  |  | 56.5785 |  |  | 54.9708 |  |  | 49.8241 |  |  | 37.7334 |  |  | 14.3935 |  |  | -18.8124 |  |  | -55.8334 |  |  | -95.0532 |  |  | -139.923
[13 empty] | P2 at this iteration flow rate |  |  | 24.6574 |  |  | 24.7243 |  |  | 25.0458 |  |  | 26.0752 |  |  | 28.4933 |  |  | 33.1613 |  |  | 39.8025 |  |  | 47.2067 |  |  | 55.0506 |  |  | 64.0246
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2554 |  |  | 31.8542 |  |  | 29.925 |  |  | 23.7489 |  |  | 9.2401 |  |  | -18.7678 |  |  | -58.6149 |  |  | -103.04 |  |  | -150.1038 |  |  | -203.9477
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7624 |  |  | 46.4729 |  |  | 44.1238 |  |  | 38.1638 |  |  | 26.8955 |  |  | 8.9866 |  |  | -11.1349 |  |  | -26.9253 |  |  | -37.6842 |  |  | -52.7963
[13 empty] | C Non choked w/ reducers | 7 |  | 1.7421 |  |  | 17.7304 |  |  | 44.0088 |  |  | 94.8671 |  |  | 253.2751 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.4469 |  |  | 14.6792 |  |  | 36.2427 |  |  | 74.8361 |  |  | 148.4538 |  |  | 390.9043 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.7421 |  |  | 17.7304 |  |  | 44.0088 |  |  | 94.8671 |  |  | 253.2751 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.2579 | 9.8926 |  | 5.7304 | 99.9851 |  | 21.0088 | 240.0028 |  | 55.8671 | 458.2533 |  | 192.2751 | 753.6579 |  | 5500 | 1122.0939 |  | 5500 | 1497.4387 |  | 5500 | 1827.1597 |  | 5500 | 2121.2757 |  | 5500 | 2414.2097
[13 empty] | Next iteration flow rate |  |  | 10.0905 | Abs Value of | Flow this | 100.985 | Abs Value of | Flow this | 242.4028 | Abs Value of | Flow this | 462.8358 | Abs Value of | Flow this | 761.1945 | Abs Value of | Flow this | 1133.3148 | Abs Value of | Flow this | 1512.4131 | Abs Value of | Flow this | 1845.4313 | Abs Value of | Flow this | 2142.4885 | Abs Value of | Flow this | 2438.3518 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9127 |  |  | 56.5717 |  |  | 54.9317 |  |  | 49.6815 |  |  | 37.3479 |  |  | 13.5388 |  |  | -20.3346 |  |  | -58.0996 |  |  | -98.1077 |  |  | -143.8795
[13 empty] | P2 at this iteration flow rate |  |  | 24.6575 |  |  | 24.7257 |  |  | 25.0537 |  |  | 26.1037 |  |  | 28.5704 |  |  | 33.3322 |  |  | 40.1069 |  |  | 47.6599 |  |  | 55.6615 |  |  | 64.8159
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2552 |  |  | 31.8461 |  |  | 29.878 |  |  | 23.5778 |  |  | 8.7774 |  |  | -19.7934 |  |  | -60.4415 |  |  | -105.7595 |  |  | -153.7693 |  |  | -208.6954
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7623 |  |  | 46.4673 |  |  | 44.0921 |  |  | 38.0537 |  |  | 26.6174 |  |  | 8.4362 |  |  | -12.0153 |  |  | -28.0096 |  |  | -38.8896 |  |  | -54.2845
[13 empty] | C Non choked w/ reducers | 7 |  | 1.777 |  |  | 17.91 |  |  | 44.4838 |  |  | 96.1627 |  |  | 262.4635 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.4758 |  |  | 14.8268 |  |  | 36.6182 |  |  | 75.6938 |  |  | 150.7195 |  |  | 407.4907 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.777 |  |  | 17.91 |  |  | 44.4838 |  |  | 96.1627 |  |  | 262.4635 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.223 | 10.0905 |  | 5.91 | 100.985 |  | 21.4838 | 242.4028 |  | 57.1627 | 462.8358 |  | 201.4635 | 761.1945 |  | 5500 | 1133.3148 |  | 5500 | 1512.4131 |  | 5500 | 1845.4313 |  | 5500 | 2142.4885 |  | 5500 | 2438.3518
[13 empty] | Next iteration flow rate |  |  | 10.2923 | Abs Value of | Flow this | 101.9948 | Abs Value of | Flow this | 244.8268 | Abs Value of | Flow this | 467.4642 | Abs Value of | Flow this | 768.8064 | Abs Value of | Flow this | 1144.648 | Abs Value of | Flow this | 1527.5372 | Abs Value of | Flow this | 1863.8857 | Abs Value of | Flow this | 2163.9134 | Abs Value of | Flow this | 2462.7353 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9126 |  |  | 56.5648 |  |  | 54.8918 |  |  | 49.5361 |  |  | 36.9545 |  |  | 12.6669 |  |  | -21.8873 |  |  | -60.4114 |  |  | -101.2237 |  |  | -147.9155
[13 empty] | P2 at this iteration flow rate |  |  | 24.6575 |  |  | 24.727 |  |  | 25.0616 |  |  | 26.1328 |  |  | 28.6491 |  |  | 33.5066 |  |  | 40.4175 |  |  | 48.1223 |  |  | 56.2847 |  |  | 65.6231
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2551 |  |  | 31.8378 |  |  | 29.8302 |  |  | 23.4033 |  |  | 8.3054 |  |  | -20.8397 |  |  | -62.3048 |  |  | -108.5337 |  |  | -157.5085 |  |  | -213.5386
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7622 |  |  | 46.4616 |  |  | 44.0598 |  |  | 37.9413 |  |  | 26.3338 |  |  | 7.8746 |  |  | -12.9133 |  |  | -29.1157 |  |  | -40.1193 |  |  | -55.8026
[13 empty] | C Non choked w/ reducers | 7 |  | 1.8125 |  |  | 18.0914 |  |  | 44.9647 |  |  | 97.4857 |  |  | 272.5164 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.5053 |  |  | 14.976 |  |  | 36.998 |  |  | 76.5639 |  |  | 153.0443 |  |  | 425.9871 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.8125 |  |  | 18.0914 |  |  | 44.9647 |  |  | 97.4857 |  |  | 272.5164 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.1875 | 10.2923 |  | 6.0914 | 101.9948 |  | 21.9647 | 244.8268 |  | 58.4857 | 467.4642 |  | 211.5164 | 768.8064 |  | 5500 | 1144.648 |  | 5500 | 1527.5372 |  | 5500 | 1863.8857 |  | 5500 | 2163.9134 |  | 5500 | 2462.7353
[13 empty] | Next iteration flow rate |  |  | 10.4981 | Abs Value of | Flow this | 103.0148 | Abs Value of | Flow this | 247.2751 | Abs Value of | Flow this | 472.1388 | Abs Value of | Flow this | 776.4945 | Abs Value of | Flow this | 1156.0945 | Abs Value of | Flow this | 1542.8126 | Abs Value of | Flow this | 1882.5245 | Abs Value of | Flow this | 2185.5525 | Abs Value of | Flow this | 2487.3626 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9124 |  |  | 56.5577 |  |  | 54.8511 |  |  | 49.3878 |  |  | 36.5533 |  |  | 11.7775 |  |  | -23.4712 |  |  | -62.7697 |  |  | -104.4023 |  |  | -152.0326
[13 empty] | P2 at this iteration flow rate |  |  | 24.6575 |  |  | 24.7285 |  |  | 25.0698 |  |  | 26.1624 |  |  | 28.7293 |  |  | 33.6845 |  |  | 40.7342 |  |  | 48.5939 |  |  | 56.9205 |  |  | 66.4465
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2549 |  |  | 31.8293 |  |  | 29.7814 |  |  | 23.2253 |  |  | 7.824 |  |  | -21.907 |  |  | -64.2055 |  |  | -111.3637 |  |  | -161.3228 |  |  | -218.4791
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7621 |  |  | 46.4557 |  |  | 44.0269 |  |  | 37.8267 |  |  | 26.0444 |  |  | 7.3018 |  |  | -13.8294 |  |  | -30.2441 |  |  | -41.3736 |  |  | -57.3512
[13 empty] | C Non choked w/ reducers | 7 |  | 1.8487 |  |  | 18.2748 |  |  | 45.4515 |  |  | 98.8372 |  |  | 283.584 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.5354 |  |  | 15.1267 |  |  | 37.3819 |  |  | 77.4466 |  |  | 155.4311 |  |  | 446.8045 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.8487 |  |  | 18.2748 |  |  | 45.4515 |  |  | 98.8372 |  |  | 283.584 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.1513 | 10.4981 |  | 6.2748 | 103.0148 |  | 22.4515 | 247.2751 |  | 59.8372 | 472.1388 |  | 222.584 | 776.4945 |  | 5500 | 1156.0945 |  | 5500 | 1542.8126 |  | 5500 | 1882.5245 |  | 5500 | 2185.5525 |  | 5500 | 2487.3626
[13 empty] | Next iteration flow rate |  |  | 10.7081 | Abs Value of | Flow this | 104.0449 | Abs Value of | Flow this | 249.7479 | Abs Value of | Flow this | 476.8602 | Abs Value of | Flow this | 784.2594 | Abs Value of | Flow this | 1167.6554 | Abs Value of | Flow this | 1558.2407 | Abs Value of | Flow this | 1901.3498 | Abs Value of | Flow this | 2207.408 | Abs Value of | Flow this | 2512.2363 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9123 |  |  | 56.5505 |  |  | 54.8096 |  |  | 49.2365 |  |  | 36.144 |  |  | 10.8702 |  |  | -25.087 |  |  | -65.1754 |  |  | -107.6448 |  |  | -156.2325
[13 empty] | P2 at this iteration flow rate |  |  | 24.6575 |  |  | 24.7299 |  |  | 25.0781 |  |  | 26.1927 |  |  | 28.8112 |  |  | 33.866 |  |  | 41.0574 |  |  | 49.0751 |  |  | 57.569 |  |  | 67.2865
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2547 |  |  | 31.8207 |  |  | 29.7316 |  |  | 23.0437 |  |  | 7.3328 |  |  | -22.9957 |  |  | -66.1444 |  |  | -114.2505 |  |  | -165.2138 |  |  | -223.519
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.762 |  |  | 46.4498 |  |  | 43.9933 |  |  | 37.7097 |  |  | 25.7492 |  |  | 6.7175 |  |  | -14.764 |  |  | -31.3952 |  |  | -42.6532 |  |  | -58.9309
[13 empty] | C Non choked w/ reducers | 7 |  | 1.8857 |  |  | 18.46 |  |  | 45.9445 |  |  | 100.2181 |  |  | 295.8566 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.5661 |  |  | 15.279 |  |  | 37.7701 |  |  | 78.3423 |  |  | 157.8826 |  |  | 470.4907 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.8857 |  |  | 18.46 |  |  | 45.9445 |  |  | 100.2181 |  |  | 295.8566 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.1143 | 10.7081 |  | 6.46 | 104.0449 |  | 22.9445 | 249.7479 |  | 61.2181 | 476.8602 |  | 234.8566 | 784.2594 |  | 5500 | 1167.6554 |  | 5500 | 1558.2407 |  | 5500 | 1901.3498 |  | 5500 | 2207.408 |  | 5500 | 2512.2363
[13 empty] | Next iteration flow rate |  |  | 10.9223 | Abs Value of | Flow this | 105.0854 | Abs Value of | Flow this | 252.2453 | Abs Value of | Flow this | 481.6288 | Abs Value of | Flow this | 792.102 | Abs Value of | Flow this | 1179.332 | Abs Value of | Flow this | 1573.8231 | Abs Value of | Flow this | 1920.3633 | Abs Value of | Flow this | 2229.4821 | Abs Value of | Flow this | 2537.3586 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9121 |  |  | 56.5432 |  |  | 54.7673 |  |  | 49.0821 |  |  | 35.7265 |  |  | 9.9447 |  |  | -26.7353 |  |  | -67.6295 |  |  | -110.9525 |  |  | -160.5168
[13 empty] | P2 at this iteration flow rate |  |  | 24.6576 |  |  | 24.7314 |  |  | 25.0865 |  |  | 26.2236 |  |  | 28.8947 |  |  | 34.0511 |  |  | 41.3871 |  |  | 49.5659 |  |  | 58.2305 |  |  | 68.1434
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2545 |  |  | 31.8118 |  |  | 29.6807 |  |  | 22.8585 |  |  | 6.8318 |  |  | -24.1063 |  |  | -68.1224 |  |  | -117.1953 |  |  | -169.183 |  |  | -228.6601
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7618 |  |  | 46.4437 |  |  | 43.9591 |  |  | 37.5904 |  |  | 25.4481 |  |  | 6.1214 |  |  | -15.7173 |  |  | -32.5694 |  |  | -43.9585 |  |  | -60.5424
[13 empty] | C Non choked w/ reducers | 7 |  | 1.9234 |  |  | 18.6472 |  |  | 46.4436 |  |  | 101.6296 |  |  | 309.5785 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.5975 |  |  | 15.4328 |  |  | 38.1627 |  |  | 79.2511 |  |  | 160.4021 |  |  | 497.7945 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.9234 |  |  | 18.6472 |  |  | 46.4436 |  |  | 101.6296 |  |  | 309.5785 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.0766 | 10.9223 |  | 6.6472 | 105.0854 |  | 23.4436 | 252.2453 |  | 62.6296 | 481.6288 |  | 248.5785 | 792.102 |  | 5500 | 1179.332 |  | 5500 | 1573.8231 |  | 5500 | 1920.3633 |  | 5500 | 2229.4821 |  | 5500 | 2537.3586
[13 empty] | Next iteration flow rate |  |  | 11.1407 | Abs Value of | Flow this | 106.1362 | Abs Value of | Flow this | 254.7678 | Abs Value of | Flow this | 486.4451 | Abs Value of | Flow this | 800.023 | Abs Value of | Flow this | 1191.1253 | Abs Value of | Flow this | 1589.5613 | Abs Value of | Flow this | 1939.5669 | Abs Value of | Flow this | 2251.7769 | Abs Value of | Flow this | 2562.7322 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.912 |  |  | 56.5357 |  |  | 54.7241 |  |  | 48.9246 |  |  | 35.3006 |  |  | 9.0006 |  |  | -28.4167 |  |  | -70.1328 |  |  | -114.3267 |  |  | -164.8872
[13 empty] | P2 at this iteration flow rate |  |  | 24.6576 |  |  | 24.7329 |  |  | 25.0952 |  |  | 26.2551 |  |  | 28.9799 |  |  | 34.2399 |  |  | 41.7233 |  |  | 50.0666 |  |  | 58.9053 |  |  | 69.0174
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2543 |  |  | 31.8028 |  |  | 29.6289 |  |  | 22.6696 |  |  | 6.3207 |  |  | -25.2393 |  |  | -70.14 |  |  | -120.1994 |  |  | -173.232 |  |  | -233.9046
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7617 |  |  | 46.4375 |  |  | 43.9241 |  |  | 37.4687 |  |  | 25.141 |  |  | 5.5134 |  |  | -16.6897 |  |  | -33.7672 |  |  | -45.29 |  |  | -62.1863
[13 empty] | C Non choked w/ reducers | 7 |  | 1.9619 |  |  | 18.8363 |  |  | 46.9491 |  |  | 103.0728 |  |  | 325.07 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.6294 |  |  | 15.5882 |  |  | 38.5597 |  |  | 80.1735 |  |  | 162.9928 |  |  | 529.7724 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1.9619 |  |  | 18.8363 |  |  | 46.9491 |  |  | 103.0728 |  |  | 325.07 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.0381 | 11.1407 |  | 6.8363 | 106.1362 |  | 23.9491 | 254.7678 |  | 64.0728 | 486.4451 |  | 264.07 | 800.023 |  | 5500 | 1191.1253 |  | 5500 | 1589.5613 |  | 5500 | 1939.5669 |  | 5500 | 2251.7769 |  | 5500 | 2562.7322
[13 empty] | Next iteration flow rate |  |  | 11.3635 | Abs Value of | Flow this | 107.1976 | Abs Value of | Flow this | 257.3155 | Abs Value of | Flow this | 491.3095 | Abs Value of | Flow this | 808.0233 | Abs Value of | Flow this | 1203.0365 | Abs Value of | Flow this | 1605.4569 | Abs Value of | Flow this | 1958.9626 | Abs Value of | Flow this | 2274.2947 | Abs Value of | Flow this | 2588.3595 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9118 |  |  | 56.5281 |  |  | 54.68 |  |  | 48.764 |  |  | 34.8661 |  |  | 8.0375 |  |  | -30.1319 |  |  | -72.6865 |  |  | -117.7686 |  |  | -169.3454
[13 empty] | P2 at this iteration flow rate |  |  | 24.6576 |  |  | 24.7344 |  |  | 25.104 |  |  | 26.2872 |  |  | 29.0668 |  |  | 34.4325 |  |  | 42.0664 |  |  | 50.5773 |  |  | 59.5937 |  |  | 69.9091
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2541 |  |  | 31.7937 |  |  | 29.576 |  |  | 22.4768 |  |  | 5.7993 |  |  | -26.395 |  |  | -72.1983 |  |  | -123.2638 |  |  | -177.3624 |  |  | -239.2545
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7616 |  |  | 46.4311 |  |  | 43.8885 |  |  | 37.3446 |  |  | 24.8276 |  |  | 4.8931 |  |  | -17.6817 |  |  | -34.989 |  |  | -46.6483 |  |  | -63.8632
[13 empty] | C Non choked w/ reducers | 7 |  | 2.0012 |  |  | 19.0274 |  |  | 47.4609 |  |  | 104.5489 |  |  | 342.7614 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.662 |  |  | 15.7451 |  |  | 38.9611 |  |  | 81.1097 |  |  | 165.6582 |  |  | 567.973 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.0012 |  |  | 19.0274 |  |  | 47.4609 |  |  | 104.5489 |  |  | 342.7614 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.9988 | 11.3635 |  | 7.0274 | 107.1976 |  | 24.4609 | 257.3155 |  | 65.5489 | 491.3095 |  | 281.7614 | 808.0233 |  | 5500 | 1203.0365 |  | 5500 | 1605.4569 |  | 5500 | 1958.9626 |  | 5500 | 2274.2947 |  | 5500 | 2588.3595
[13 empty] | Next iteration flow rate |  |  | 11.5908 | Abs Value of | Flow this | 108.2696 | Abs Value of | Flow this | 259.8886 | Abs Value of | Flow this | 496.2226 | Abs Value of | Flow this | 816.1035 | Abs Value of | Flow this | 1215.0669 | Abs Value of | Flow this | 1621.5115 | Abs Value of | Flow this | 1978.5522 | Abs Value of | Flow this | 2297.0377 | Abs Value of | Flow this | 2614.2431 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9116 |  |  | 56.5203 |  |  | 54.6351 |  |  | 48.6001 |  |  | 34.4229 |  |  | 7.055 |  |  | -31.8815 |  |  | -75.2915 |  |  | -121.2798 |  |  | -173.8933
[13 empty] | P2 at this iteration flow rate |  |  | 24.6577 |  |  | 24.7359 |  |  | 25.113 |  |  | 26.32 |  |  | 29.1554 |  |  | 34.629 |  |  | 42.4163 |  |  | 51.0983 |  |  | 60.296 |  |  | 70.8187
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2539 |  |  | 31.7843 |  |  | 29.5221 |  |  | 22.2802 |  |  | 5.2675 |  |  | -27.574 |  |  | -74.2979 |  |  | -126.3898 |  |  | -181.5758 |  |  | -244.7119
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7614 |  |  | 46.4247 |  |  | 43.8521 |  |  | 37.218 |  |  | 24.508 |  |  | 4.2603 |  |  | -18.6937 |  |  | -36.2354 |  |  | -48.0339 |  |  | -65.5739
[13 empty] | C Non choked w/ reducers | 7 |  | 2.0412 |  |  | 19.2205 |  |  | 47.9793 |  |  | 106.0594 |  |  | 363.2458 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.6952 |  |  | 15.9037 |  |  | 39.367 |  |  | 82.0601 |  |  | 168.4024 |  |  | 614.7783 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.0412 |  |  | 19.2205 |  |  | 47.9793 |  |  | 106.0594 |  |  | 363.2458 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.9588 | 11.5908 |  | 7.2205 | 108.2696 |  | 24.9793 | 259.8886 |  | 67.0594 | 496.2226 |  | 302.2458 | 816.1035 |  | 5500 | 1215.0669 |  | 5500 | 1621.5115 |  | 5500 | 1978.5522 |  | 5500 | 2297.0377 |  | 5500 | 2614.2431
[13 empty] | Next iteration flow rate |  |  | 11.8226 | Abs Value of | Flow this | 109.3523 | Abs Value of | Flow this | 262.4875 | Abs Value of | Flow this | 501.1848 | Abs Value of | Flow this | 824.2645 | Abs Value of | Flow this | 1227.2176 | Abs Value of | Flow this | 1637.7266 | Abs Value of | Flow this | 1998.3377 | Abs Value of | Flow this | 2320.008 | Abs Value of | Flow this | 2640.3856 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9114 |  |  | 56.5123 |  |  | 54.5892 |  |  | 48.433 |  |  | 33.9708 |  |  | 6.0528 |  |  | -33.6664 |  |  | -77.9489 |  |  | -124.8615 |  |  | -178.5326
[13 empty] | P2 at this iteration flow rate |  |  | 24.6577 |  |  | 24.7375 |  |  | 25.1222 |  |  | 26.3534 |  |  | 29.2458 |  |  | 34.8294 |  |  | 42.7733 |  |  | 51.6298 |  |  | 61.0123 |  |  | 71.7465
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2537 |  |  | 31.7748 |  |  | 29.4671 |  |  | 22.0796 |  |  | 4.7249 |  |  | -28.7766 |  |  | -76.4397 |  |  | -129.5787 |  |  | -185.8739 |  |  | -250.2791
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7613 |  |  | 46.4181 |  |  | 43.815 |  |  | 37.0888 |  |  | 24.1819 |  |  | 3.6149 |  |  | -19.7259 |  |  | -37.5069 |  |  | -49.4474 |  |  | -67.3189
[13 empty] | C Non choked w/ reducers | 7 |  | 2.082 |  |  | 19.4157 |  |  | 48.5043 |  |  | 107.6054 |  |  | 387.3693 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.7292 |  |  | 16.0639 |  |  | 39.7775 |  |  | 83.0249 |  |  | 171.2292 |  |  | 674.0863 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.082 |  |  | 19.4157 |  |  | 48.5043 |  |  | 107.6054 |  |  | 387.3693 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.918 | 11.8226 |  | 7.4157 | 109.3523 |  | 25.5043 | 262.4875 |  | 68.6054 | 501.1848 |  | 326.3693 | 824.2645 |  | 5500 | 1227.2176 |  | 5500 | 1637.7266 |  | 5500 | 1998.3377 |  | 5500 | 2320.008 |  | 5500 | 2640.3856
[13 empty] | Next iteration flow rate |  |  | 12.0591 | Abs Value of | Flow this | 110.4458 | Abs Value of | Flow this | 265.1124 | Abs Value of | Flow this | 506.1967 | Abs Value of | Flow this | 832.5072 | Abs Value of | Flow this | 1239.4898 | Abs Value of | Flow this | 1654.1039 | Abs Value of | Flow this | 2018.3211 | Abs Value of | Flow this | 2343.2081 | Abs Value of | Flow this | 2666.7894 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9112 |  |  | 56.5042 |  |  | 54.5425 |  |  | 48.2625 |  |  | 33.5096 |  |  | 5.0305 |  |  | -35.4871 |  |  | -80.6597 |  |  | -128.5153 |  |  | -183.2651
[13 empty] | P2 at this iteration flow rate |  |  | 24.6578 |  |  | 24.7392 |  |  | 25.1315 |  |  | 26.3875 |  |  | 29.3381 |  |  | 35.0339 |  |  | 43.1374 |  |  | 52.1719 |  |  | 61.7431 |  |  | 72.693
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2535 |  |  | 31.765 |  |  | 29.411 |  |  | 21.875 |  |  | 4.1715 |  |  | -30.0034 |  |  | -78.6245 |  |  | -132.8316 |  |  | -190.2583 |  |  | -255.9581
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7611 |  |  | 46.4114 |  |  | 43.7772 |  |  | 36.957 |  |  | 23.8493 |  |  | 2.9564 |  |  | -20.779 |  |  | -38.804 |  |  | -50.8892 |  |  | -69.099
[13 empty] | C Non choked w/ reducers | 7 |  | 2.1237 |  |  | 19.6128 |  |  | 49.0361 |  |  | 109.1886 |  |  | 416.3884 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.7637 |  |  | 16.2257 |  |  | 40.1926 |  |  | 84.0045 |  |  | 174.1433 |  |  | 752.8345 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.1237 |  |  | 19.6128 |  |  | 49.0361 |  |  | 109.1886 |  |  | 416.3884 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.8763 | 12.0591 |  | 7.6128 | 110.4458 |  | 26.0361 | 265.1124 |  | 70.1886 | 506.1967 |  | 355.3884 | 832.5072 |  | 5500 | 1239.4898 |  | 5500 | 1654.1039 |  | 5500 | 2018.3211 |  | 5500 | 2343.2081 |  | 5500 | 2666.7894
[13 empty] | Next iteration flow rate |  |  | 12.3002 | Abs Value of | Flow this | 111.5502 | Abs Value of | Flow this | 267.7635 | Abs Value of | Flow this | 511.2587 | Abs Value of | Flow this | 840.8323 | Abs Value of | Flow this | 1251.8847 | Abs Value of | Flow this | 1670.6449 | Abs Value of | Flow this | 2038.5043 | Abs Value of | Flow this | 2366.6402 | Abs Value of | Flow this | 2693.4573 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.911 |  |  | 56.4959 |  |  | 54.4948 |  |  | 48.0885 |  |  | 33.0391 |  |  | 3.9876 |  |  | -37.3444 |  |  | -83.4249 |  |  | -132.2424 |  |  | -188.0927
[13 empty] | P2 at this iteration flow rate |  |  | 24.6578 |  |  | 24.7408 |  |  | 25.141 |  |  | 26.4223 |  |  | 29.4322 |  |  | 35.2425 |  |  | 43.5089 |  |  | 52.725 |  |  | 62.4885 |  |  | 73.6585
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2532 |  |  | 31.7551 |  |  | 29.3537 |  |  | 21.6662 |  |  | 3.6069 |  |  | -31.2549 |  |  | -80.8533 |  |  | -136.1499 |  |  | -194.7309 |  |  | -261.7513
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7609 |  |  | 46.4045 |  |  | 43.7386 |  |  | 36.8226 |  |  | 23.51 |  |  | 2.2848 |  |  | -21.8532 |  |  | -40.1271 |  |  | -52.3601 |  |  | -70.9149
[13 empty] | C Non choked w/ reducers | 7 |  | 2.1662 |  |  | 19.8121 |  |  | 49.5747 |  |  | 110.8104 |  |  | 452.2693 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.799 |  |  | 16.3891 |  |  | 40.6125 |  |  | 84.9992 |  |  | 177.1494 |  |  | 864.9379 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.1662 |  |  | 19.8121 |  |  | 49.5747 |  |  | 110.8104 |  |  | 452.2693 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.8338 | 12.3002 |  | 7.8121 | 111.5502 |  | 26.5747 | 267.7635 |  | 71.8104 | 511.2587 |  | 391.2693 | 840.8323 |  | 5500 | 1251.8847 |  | 5500 | 1670.6449 |  | 5500 | 2038.5043 |  | 5500 | 2366.6402 |  | 5500 | 2693.4573
[13 empty] | Next iteration flow rate |  |  | 12.5462 | Abs Value of | Flow this | 112.6657 | Abs Value of | Flow this | 270.4411 | Abs Value of | Flow this | 516.3712 | Abs Value of | Flow this | 849.2406 | Abs Value of | Flow this | 1264.4035 | Abs Value of | Flow this | 1687.3514 | Abs Value of | Flow this | 2058.8893 | Abs Value of | Flow this | 2390.3066 | Abs Value of | Flow this | 2720.3919 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9108 |  |  | 56.4875 |  |  | 54.4461 |  |  | 47.9111 |  |  | 32.5592 |  |  | 2.9237 |  |  | -39.239 |  |  | -86.2458 |  |  | -136.0445 |  |  | -193.0174
[13 empty] | P2 at this iteration flow rate |  |  | 24.6578 |  |  | 24.7425 |  |  | 25.1508 |  |  | 26.4578 |  |  | 29.5282 |  |  | 35.4553 |  |  | 43.8878 |  |  | 53.2892 |  |  | 63.2489 |  |  | 74.6435
[13 empty] | Delta P at this iteration flow rate |  |  | 32.253 |  |  | 31.7449 |  |  | 29.2953 |  |  | 21.4533 |  |  | 3.031 |  |  | -32.5316 |  |  | -83.1268 |  |  | -139.535 |  |  | -199.2934 |  |  | -267.6609
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7608 |  |  | 46.3975 |  |  | 43.6992 |  |  | 36.6855 |  |  | 23.1639 |  |  | 1.5996 |  |  | -22.949 |  |  | -41.4768 |  |  | -53.8605 |  |  | -72.7672
[13 empty] | C Non choked w/ reducers | 7 |  | 2.2095 |  |  | 20.0134 |  |  | 50.1203 |  |  | 112.4725 |  |  | 498.3026 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.835 |  |  | 16.5543 |  |  | 41.0371 |  |  | 86.0095 |  |  | 180.2526 |  |  | 1044.055 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.2095 |  |  | 20.0134 |  |  | 50.1203 |  |  | 112.4725 |  |  | 498.3026 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.7905 | 12.5462 |  | 8.0134 | 112.6657 |  | 27.1203 | 270.4411 |  | 73.4725 | 516.3712 |  | 437.3026 | 849.2406 |  | 5500 | 1264.4035 |  | 5500 | 1687.3514 |  | 5500 | 2058.8893 |  | 5500 | 2390.3066 |  | 5500 | 2720.3919
[13 empty] | Next iteration flow rate |  |  | 12.7972 | Abs Value of | Flow this | 113.7924 | Abs Value of | Flow this | 273.1455 | Abs Value of | Flow this | 521.535 | Abs Value of | Flow this | 857.733 | Abs Value of | Flow this | 1277.0475 | Abs Value of | Flow this | 1704.2249 | Abs Value of | Flow this | 2079.4782 | Abs Value of | Flow this | 2414.2097 | Abs Value of | Flow this | 2747.5958 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9106 |  |  | 56.4788 |  |  | 54.3964 |  |  | 47.7301 |  |  | 32.0696 |  |  | 1.8385 |  |  | -41.1717 |  |  | -89.1234 |  |  | -139.923 |  |  | -198.0411
[13 empty] | P2 at this iteration flow rate |  |  | 24.6579 |  |  | 24.7442 |  |  | 25.1607 |  |  | 26.494 |  |  | 29.6261 |  |  | 35.6723 |  |  | 44.2743 |  |  | 53.8647 |  |  | 64.0246 |  |  | 75.6482
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2527 |  |  | 31.7346 |  |  | 29.2357 |  |  | 21.2361 |  |  | 2.4435 |  |  | -33.8339 |  |  | -85.4461 |  |  | -142.988 |  |  | -203.9477 |  |  | -273.6893
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7606 |  |  | 46.3904 |  |  | 43.659 |  |  | 36.5456 |  |  | 22.8108 |  |  | 0.90063 |  |  | -24.0668 |  |  | -42.8536 |  |  | -55.391 |  |  | -74.6568
[13 empty] | C Non choked w/ reducers | 7 |  | 2.2537 |  |  | 20.2168 |  |  | 50.6731 |  |  | 114.1767 |  |  | 560.5315 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.8717 |  |  | 16.7211 |  |  | 41.4665 |  |  | 87.0357 |  |  | 183.4587 |  |  | 1405.3172 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.2537 |  |  | 20.2168 |  |  | 50.6731 |  |  | 114.1767 |  |  | 560.5315 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.7463 | 12.7972 |  | 8.2168 | 113.7924 |  | 27.6731 | 273.1455 |  | 75.1767 | 521.535 |  | 499.5315 | 857.733 |  | 5500 | 1277.0475 |  | 5500 | 1704.2249 |  | 5500 | 2079.4782 |  | 5500 | 2414.2097 |  | 5500 | 2747.5958
[13 empty] | Next iteration flow rate |  |  | 13.0531 | Abs Value of | Flow this | 114.9303 | Abs Value of | Flow this | 275.877 | Abs Value of | Flow this | 526.7503 | Abs Value of | Flow this | 866.3103 | Abs Value of | Flow this | 1289.818 | Abs Value of | Flow this | 1721.2671 | Abs Value of | Flow this | 2100.273 | Abs Value of | Flow this | 2438.3518 | Abs Value of | Flow this | 2775.0718 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9104 |  |  | 56.47 |  |  | 54.3458 |  |  | 47.5455 |  |  | 31.5702 |  |  | 0.73139 |  |  | -43.1433 |  |  | -92.0588 |  |  | -143.8795 |  |  | -203.1657
[13 empty] | P2 at this iteration flow rate |  |  | 24.6579 |  |  | 24.746 |  |  | 25.1708 |  |  | 26.5309 |  |  | 29.726 |  |  | 35.8937 |  |  | 44.6687 |  |  | 54.4518 |  |  | 64.8159 |  |  | 76.6731
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2525 |  |  | 31.7241 |  |  | 29.1749 |  |  | 21.0146 |  |  | 1.8442 |  |  | -35.1623 |  |  | -87.812 |  |  | -146.5105 |  |  | -208.6954 |  |  | -279.8388
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7604 |  |  | 46.3831 |  |  | 43.618 |  |  | 36.4029 |  |  | 22.4507 |  |  | 0.18763 |  |  | -25.2071 |  |  | -44.2581 |  |  | -56.9524 |  |  | -76.5844
[13 empty] | C Non choked w/ reducers | 7 |  | 2.2988 |  |  | 20.4224 |  |  | 51.2331 |  |  | 115.9248 |  |  | 651.6621 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.9091 |  |  | 16.8896 |  |  | 41.9009 |  |  | 88.0782 |  |  | 186.7737 |  |  | 3109.677 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.2988 |  |  | 20.4224 |  |  | 51.2331 |  |  | 115.9248 |  |  | 651.6621 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.7012 | 13.0531 |  | 8.4224 | 114.9303 |  | 28.2331 | 275.877 |  | 76.9248 | 526.7503 |  | 590.6621 | 866.3103 |  | 5500 | 1289.818 |  | 5500 | 1721.2671 |  | 5500 | 2100.273 |  | 5500 | 2438.3518 |  | 5500 | 2775.0718
[13 empty] | Next iteration flow rate |  |  | 13.3142 | Abs Value of | Flow this | 116.0796 | Abs Value of | Flow this | 278.6358 | Abs Value of | Flow this | 532.0178 | Abs Value of | Flow this | 874.9734 | Abs Value of | Flow this | 1302.7162 | Abs Value of | Flow this | 1738.4798 | Abs Value of | Flow this | 2121.2757 | Abs Value of | Flow this | 2462.7353 | Abs Value of | Flow this | 2802.8225 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9102 |  |  | 56.4611 |  |  | 54.2941 |  |  | 47.3571 |  |  | 31.0607 |  |  | -0.39792 |  |  | -45.1545 |  |  | -95.0532 |  |  | -147.9155 |  |  | -208.3933
[13 empty] | P2 at this iteration flow rate |  |  | 24.658 |  |  | 24.7478 |  |  | 25.1812 |  |  | 26.5686 |  |  | 29.8279 |  |  | 36.1196 |  |  | 45.0709 |  |  | 55.0506 |  |  | 65.6231 |  |  | 77.7187
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2522 |  |  | 31.7133 |  |  | 29.113 |  |  | 20.7885 |  |  | 1.2329 |  |  | -36.5175 |  |  | -90.2254 |  |  | -150.1038 |  |  | -213.5386 |  |  | -286.112
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7602 |  |  | 46.3757 |  |  | 43.5762 |  |  | 36.2574 |  |  | 22.0833 |  |  | -0.5397 |  |  | -26.3703 |  |  | -45.6908 |  |  | -58.5451 |  |  | -78.5508
[13 empty] | C Non choked w/ reducers | 7 |  | 2.3448 |  |  | 20.6301 |  |  | 51.8005 |  |  | 117.7188 |  |  | 804.9888 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.9473 |  |  | 17.0599 |  |  | 42.3402 |  |  | 89.1373 |  |  | 190.2042 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.3448 |  |  | 20.6301 |  |  | 51.8005 |  |  | 117.7188 |  |  | 804.9888 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.6552 | 13.3142 |  | 8.6301 | 116.0796 |  | 28.8005 | 278.6358 |  | 78.7188 | 532.0178 |  | 743.9888 | 874.9734 |  | 5500 | 1302.7162 |  | 5500 | 1738.4798 |  | 5500 | 2121.2757 |  | 5500 | 2462.7353 |  | 5500 | 2802.8225
[13 empty] | Next iteration flow rate |  |  | 13.5805 | Abs Value of | Flow this | 117.2404 | Abs Value of | Flow this | 281.4221 | Abs Value of | Flow this | 537.338 | Abs Value of | Flow this | 883.7232 | Abs Value of | Flow this | 1315.7434 | Abs Value of | Flow this | 1755.8646 | Abs Value of | Flow this | 2142.4885 | Abs Value of | Flow this | 2487.3626 | Abs Value of | Flow this | 2830.8507 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9099 |  |  | 56.4519 |  |  | 54.2414 |  |  | 47.165 |  |  | 30.541 |  |  | -1.5499 |  |  | -47.2061 |  |  | -98.1077 |  |  | -152.0326 |  |  | -213.7261
[13 empty] | P2 at this iteration flow rate |  |  | 24.658 |  |  | 24.7496 |  |  | 25.1917 |  |  | 26.607 |  |  | 29.9318 |  |  | 36.35 |  |  | 45.4812 |  |  | 55.6615 |  |  | 66.4465 |  |  | 78.7852
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2519 |  |  | 31.7023 |  |  | 29.0497 |  |  | 20.558 |  |  | 0.60926 |  |  | -37.8999 |  |  | -92.6874 |  |  | -153.7693 |  |  | -218.4791 |  |  | -292.5113
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.76 |  |  | 46.3681 |  |  | 43.5336 |  |  | 36.1089 |  |  | 21.7085 |  |  | -1.2816 |  |  | -27.5569 |  |  | -47.1524 |  |  | -60.1698 |  |  | -80.5566
[13 empty] | C Non choked w/ reducers | 7 |  | 2.3917 |  |  | 20.84 |  |  | 52.3754 |  |  | 119.5609 |  |  | 1156.5734 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 1.9863 |  |  | 17.2319 |  |  | 42.7845 |  |  | 90.2136 |  |  | 193.7575 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.3917 |  |  | 20.84 |  |  | 52.3754 |  |  | 119.5609 |  |  | 1156.5734 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.6083 | 13.5805 |  | 8.84 | 117.2404 |  | 29.3754 | 281.4221 |  | 80.5609 | 537.338 |  | 1095.5734 | 883.7232 |  | 5500 | 1315.7434 |  | 5500 | 1755.8646 |  | 5500 | 2142.4885 |  | 5500 | 2487.3626 |  | 5500 | 2830.8507
[13 empty] | Next iteration flow rate |  |  | 13.8521 | Abs Value of | Flow this | 118.4128 | Abs Value of | Flow this | 284.2364 | Abs Value of | Flow this | 542.7114 | Abs Value of | Flow this | 892.5604 | Abs Value of | Flow this | 1328.9008 | Abs Value of | Flow this | 1773.4232 | Abs Value of | Flow this | 2163.9134 | Abs Value of | Flow this | 2512.2363 | Abs Value of | Flow this | 2859.1592 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9097 |  |  | 56.4426 |  |  | 54.1877 |  |  | 46.969 |  |  | 30.0109 |  |  | -2.7251 |  |  | -49.299 |  |  | -101.2237 |  |  | -156.2325 |  |  | -219.166
[13 empty] | P2 at this iteration flow rate |  |  | 24.6581 |  |  | 24.7515 |  |  | 25.2025 |  |  | 26.6462 |  |  | 30.0378 |  |  | 36.585 |  |  | 45.8998 |  |  | 56.2847 |  |  | 67.2865 |  |  | 79.8732
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2516 |  |  | 31.6911 |  |  | 28.9852 |  |  | 20.3228 |  |  | -0.026911 |  |  | -39.3101 |  |  | -95.1988 |  |  | -157.5085 |  |  | -223.519 |  |  | -299.0392
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7598 |  |  | 46.3604 |  |  | 43.4901 |  |  | 35.9574 |  |  | 21.3261 |  |  | -2.0385 |  |  | -28.7673 |  |  | -48.6433 |  |  | -61.8272 |  |  | -82.6028
[13 empty] | C Non choked w/ reducers | 7 |  | 2.4395 |  |  | 21.0521 |  |  | 52.958 |  |  | 121.4532 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.026 |  |  | 17.4057 |  |  | 43.2339 |  |  | 91.3075 |  |  | 197.4415 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.4395 |  |  | 21.0521 |  |  | 52.958 |  |  | 121.4532 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.5605 | 13.8521 |  | 9.0521 | 118.4128 |  | 29.958 | 284.2364 |  | 82.4532 | 542.7114 |  | 5500 | 892.5604 |  | 5500 | 1328.9008 |  | 5500 | 1773.4232 |  | 5500 | 2163.9134 |  | 5500 | 2512.2363 |  | 5500 | 2859.1592
[13 empty] | Next iteration flow rate |  |  | 14.1291 | Abs Value of | Flow this | 119.5969 | Abs Value of | Flow this | 287.0787 | Abs Value of | Flow this | 548.1385 | Abs Value of | Flow this | 901.486 | Abs Value of | Flow this | 1342.1898 | Abs Value of | Flow this | 1791.1575 | Abs Value of | Flow this | 2185.5525 | Abs Value of | Flow this | 2537.3586 | Abs Value of | Flow this | 2887.7508 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9094 |  |  | 56.4331 |  |  | 54.1328 |  |  | 46.769 |  |  | 29.4701 |  |  | -3.9239 |  |  | -51.4339 |  |  | -104.4023 |  |  | -160.5168 |  |  | -224.7152
[13 empty] | P2 at this iteration flow rate |  |  | 24.6581 |  |  | 24.7534 |  |  | 25.2134 |  |  | 26.6862 |  |  | 30.146 |  |  | 36.8248 |  |  | 46.3268 |  |  | 56.9205 |  |  | 68.1434 |  |  | 80.983
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2513 |  |  | 31.6797 |  |  | 28.9194 |  |  | 20.0828 |  |  | -0.67587 |  |  | -40.7487 |  |  | -97.7607 |  |  | -161.3228 |  |  | -228.6601 |  |  | -305.6983
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7596 |  |  | 46.3525 |  |  | 43.4457 |  |  | 35.8029 |  |  | 20.9361 |  |  | -2.8106 |  |  | -30.0021 |  |  | -50.1642 |  |  | -63.5179 |  |  | -84.6901
[13 empty] | C Non choked w/ reducers | 7 |  | 2.4883 |  |  | 21.2665 |  |  | 53.5484 |  |  | 123.3983 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.0665 |  |  | 17.5812 |  |  | 43.6886 |  |  | 92.4193 |  |  | 201.2648 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.4883 |  |  | 21.2665 |  |  | 53.5484 |  |  | 123.3983 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.5117 | 14.1291 |  | 9.2665 | 119.5969 |  | 30.5484 | 287.0787 |  | 84.3983 | 548.1385 |  | 5500 | 901.486 |  | 5500 | 1342.1898 |  | 5500 | 1791.1575 |  | 5500 | 2185.5525 |  | 5500 | 2537.3586 |  | 5500 | 2887.7508
[13 empty] | Next iteration flow rate |  |  | 14.4117 | Abs Value of | Flow this | 120.7929 | Abs Value of | Flow this | 289.9495 | Abs Value of | Flow this | 553.6199 | Abs Value of | Flow this | 910.5008 | Abs Value of | Flow this | 1355.6117 | Abs Value of | Flow this | 1809.0691 | Abs Value of | Flow this | 2207.408 | Abs Value of | Flow this | 2562.7322 | Abs Value of | Flow this | 2916.6283 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9091 |  |  | 56.4234 |  |  | 54.0769 |  |  | 46.5651 |  |  | 28.9184 |  |  | -5.1468 |  |  | -53.6117 |  |  | -107.6448 |  |  | -164.8872 |  |  | -230.376
[13 empty] | P2 at this iteration flow rate |  |  | 24.6582 |  |  | 24.7553 |  |  | 25.2246 |  |  | 26.727 |  |  | 30.2563 |  |  | 37.0694 |  |  | 46.7623 |  |  | 57.569 |  |  | 69.0174 |  |  | 82.1152
[13 empty] | Delta P at this iteration flow rate |  |  | 32.251 |  |  | 31.668 |  |  | 28.8523 |  |  | 19.8381 |  |  | -1.3379 |  |  | -42.2161 |  |  | -100.3741 |  |  | -165.2138 |  |  | -233.9046 |  |  | -312.4912
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7594 |  |  | 46.3445 |  |  | 43.4004 |  |  | 35.6453 |  |  | 20.5383 |  |  | -3.5982 |  |  | -31.2616 |  |  | -51.7156 |  |  | -65.2426 |  |  | -86.8193
[13 empty] | C Non choked w/ reducers | 7 |  | 2.5381 |  |  | 21.4831 |  |  | 54.1468 |  |  | 125.3988 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.1079 |  |  | 17.7586 |  |  | 44.1485 |  |  | 93.5497 |  |  | 205.2369 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.5381 |  |  | 21.4831 |  |  | 54.1468 |  |  | 125.3988 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.4619 | 14.4117 |  | 9.4831 | 120.7929 |  | 31.1468 | 289.9495 |  | 86.3988 | 553.6199 |  | 5500 | 910.5008 |  | 5500 | 1355.6117 |  | 5500 | 1809.0691 |  | 5500 | 2207.408 |  | 5500 | 2562.7322 |  | 5500 | 2916.6283
[13 empty] | Next iteration flow rate |  |  | 14.6999 | Abs Value of | Flow this | 122.0008 | Abs Value of | Flow this | 292.849 | Abs Value of | Flow this | 559.1561 | Abs Value of | Flow this | 919.6059 | Abs Value of | Flow this | 1369.1678 | Abs Value of | Flow this | 1827.1597 | Abs Value of | Flow this | 2229.4821 | Abs Value of | Flow this | 2588.3595 | Abs Value of | Flow this | 2945.7946 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9088 |  |  | 56.4135 |  |  | 54.0198 |  |  | 46.357 |  |  | 28.3557 |  |  | -6.3942 |  |  | -55.8334 |  |  | -110.9525 |  |  | -169.3454 |  |  | -236.1506
[13 empty] | P2 at this iteration flow rate |  |  | 24.6582 |  |  | 24.7573 |  |  | 25.236 |  |  | 26.7686 |  |  | 30.3689 |  |  | 37.3188 |  |  | 47.2067 |  |  | 58.2305 |  |  | 69.9091 |  |  | 83.2701
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2506 |  |  | 31.6562 |  |  | 28.7838 |  |  | 19.5884 |  |  | -2.0132 |  |  | -43.7131 |  |  | -103.04 |  |  | -169.183 |  |  | -239.2545 |  |  | -319.4207
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7591 |  |  | 46.3363 |  |  | 43.3542 |  |  | 35.4845 |  |  | 20.1324 |  |  | -4.4016 |  |  | -32.5465 |  |  | -53.2982 |  |  | -67.0019 |  |  | -88.9914
[13 empty] | C Non choked w/ reducers | 7 |  | 2.5889 |  |  | 21.702 |  |  | 54.7533 |  |  | 127.4573 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.15 |  |  | 17.9377 |  |  | 44.6137 |  |  | 94.699 |  |  | 209.3682 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.5889 |  |  | 21.702 |  |  | 54.7533 |  |  | 127.4573 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.4111 | 14.6999 |  | 9.702 | 122.0008 |  | 31.7533 | 292.849 |  | 88.4573 | 559.1561 |  | 5500 | 919.6059 |  | 5500 | 1369.1678 |  | 5500 | 1827.1597 |  | 5500 | 2229.4821 |  | 5500 | 2588.3595 |  | 5500 | 2945.7946
[13 empty] | Next iteration flow rate |  |  | 14.9939 | Abs Value of | Flow this | 123.2209 | Abs Value of | Flow this | 295.7775 | Abs Value of | Flow this | 564.7476 | Abs Value of | Flow this | 928.8019 | Abs Value of | Flow this | 1382.8595 | Abs Value of | Flow this | 1845.4313 | Abs Value of | Flow this | 2251.7769 | Abs Value of | Flow this | 2614.2431 | Abs Value of | Flow this | 2975.2525 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9086 |  |  | 56.4034 |  |  | 53.9616 |  |  | 46.1448 |  |  | 27.7816 |  |  | -7.6668 |  |  | -58.0996 |  |  | -114.3267 |  |  | -173.8933 |  |  | -242.0412
[13 empty] | P2 at this iteration flow rate |  |  | 24.6583 |  |  | 24.7593 |  |  | 25.2477 |  |  | 26.811 |  |  | 30.4837 |  |  | 37.5734 |  |  | 47.6599 |  |  | 58.9053 |  |  | 70.8187 |  |  | 84.4482
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2503 |  |  | 31.644 |  |  | 28.7139 |  |  | 19.3337 |  |  | -2.702 |  |  | -45.2401 |  |  | -105.7595 |  |  | -173.232 |  |  | -244.7119 |  |  | -326.4895
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7589 |  |  | 46.3279 |  |  | 43.3071 |  |  | 35.3205 |  |  | 19.7184 |  |  | -5.2212 |  |  | -33.8573 |  |  | -54.9127 |  |  | -68.7966 |  |  | -91.2071
[13 empty] | C Non choked w/ reducers | 7 |  | 2.6407 |  |  | 21.9232 |  |  | 55.3681 |  |  | 129.577 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.193 |  |  | 18.1188 |  |  | 45.0843 |  |  | 95.8678 |  |  | 213.6703 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.6407 |  |  | 21.9232 |  |  | 55.3681 |  |  | 129.577 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.3593 | 14.9939 |  | 9.9232 | 123.2209 |  | 32.3681 | 295.7775 |  | 90.577 | 564.7476 |  | 5500 | 928.8019 |  | 5500 | 1382.8595 |  | 5500 | 1845.4313 |  | 5500 | 2251.7769 |  | 5500 | 2614.2431 |  | 5500 | 2975.2525
[13 empty] | Next iteration flow rate |  |  | 15.2938 | Abs Value of | Flow this | 124.4531 | Abs Value of | Flow this | 298.7353 | Abs Value of | Flow this | 570.3951 | Abs Value of | Flow this | 938.0899 | Abs Value of | Flow this | 1396.6881 | Abs Value of | Flow this | 1863.8857 | Abs Value of | Flow this | 2274.2947 | Abs Value of | Flow this | 2640.3856 | Abs Value of | Flow this | 3005.0051 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9082 |  |  | 56.3931 |  |  | 53.9022 |  |  | 45.9283 |  |  | 27.196 |  |  | -8.9649 |  |  | -60.4114 |  |  | -117.7686 |  |  | -178.5326 |  |  | -248.0503
[13 empty] | P2 at this iteration flow rate |  |  | 24.6584 |  |  | 24.7614 |  |  | 25.2596 |  |  | 26.8543 |  |  | 30.6008 |  |  | 37.833 |  |  | 48.1223 |  |  | 59.5937 |  |  | 71.7465 |  |  | 85.6501
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2499 |  |  | 31.6317 |  |  | 28.6426 |  |  | 19.0739 |  |  | -3.4048 |  |  | -46.7979 |  |  | -108.5337 |  |  | -177.3624 |  |  | -250.2791 |  |  | -333.7003
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7586 |  |  | 46.3194 |  |  | 43.2591 |  |  | 35.1532 |  |  | 19.2961 |  |  | -6.0572 |  |  | -35.1943 |  |  | -56.5596 |  |  | -70.6274 |  |  | -93.4673
[13 empty] | C Non choked w/ reducers | 7 |  | 2.6935 |  |  | 22.1468 |  |  | 55.9913 |  |  | 131.7611 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.2369 |  |  | 18.3016 |  |  | 45.5605 |  |  | 97.0566 |  |  | 218.1559 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.6935 |  |  | 22.1468 |  |  | 55.9913 |  |  | 131.7611 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.3065 | 15.2938 |  | 10.1468 | 124.4531 |  | 32.9913 | 298.7353 |  | 92.7611 | 570.3951 |  | 5500 | 938.0899 |  | 5500 | 1396.6881 |  | 5500 | 1863.8857 |  | 5500 | 2274.2947 |  | 5500 | 2640.3856 |  | 5500 | 3005.0051
[13 empty] | Next iteration flow rate |  |  | 15.5997 | Abs Value of | Flow this | 125.6976 | Abs Value of | Flow this | 301.7226 | Abs Value of | Flow this | 576.0991 | Abs Value of | Flow this | 947.4708 | Abs Value of | Flow this | 1410.655 | Abs Value of | Flow this | 1882.5245 | Abs Value of | Flow this | 2297.0377 | Abs Value of | Flow this | 2666.7894 | Abs Value of | Flow this | 3035.0551 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9079 |  |  | 56.3825 |  |  | 53.8416 |  |  | 45.7074 |  |  | 26.5986 |  |  | -10.2891 |  |  | -62.7697 |  |  | -121.2798 |  |  | -183.2651 |  |  | -254.1801
[13 empty] | P2 at this iteration flow rate |  |  | 24.6584 |  |  | 24.7635 |  |  | 25.2717 |  |  | 26.8985 |  |  | 30.7203 |  |  | 38.0978 |  |  | 48.5939 |  |  | 60.296 |  |  | 72.693 |  |  | 86.876
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2495 |  |  | 31.6191 |  |  | 28.5699 |  |  | 18.8089 |  |  | -4.1216 |  |  | -48.3869 |  |  | -111.3637 |  |  | -181.5758 |  |  | -255.9581 |  |  | -341.0561
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7584 |  |  | 46.3107 |  |  | 43.2101 |  |  | 34.9825 |  |  | 18.8652 |  |  | -6.9101 |  |  | -36.5583 |  |  | -58.2396 |  |  | -72.495 |  |  | -95.773
[13 empty] | C Non choked w/ reducers | 7 |  | 2.7474 |  |  | 22.3727 |  |  | 56.6231 |  |  | 134.013 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.2817 |  |  | 18.4864 |  |  | 46.0422 |  |  | 98.266 |  |  | 222.8391 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.7474 |  |  | 22.3727 |  |  | 56.6231 |  |  | 134.013 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.2526 | 15.5997 |  | 10.3727 | 125.6976 |  | 33.6231 | 301.7226 |  | 95.013 | 576.0991 |  | 5500 | 947.4708 |  | 5500 | 1410.655 |  | 5500 | 1882.5245 |  | 5500 | 2297.0377 |  | 5500 | 2666.7894 |  | 5500 | 3035.0551
[13 empty] | Next iteration flow rate |  |  | 15.9117 | Abs Value of | Flow this | 126.9546 | Abs Value of | Flow this | 304.7398 | Abs Value of | Flow this | 581.86 | Abs Value of | Flow this | 956.9455 | Abs Value of | Flow this | 1424.7615 | Abs Value of | Flow this | 1901.3498 | Abs Value of | Flow this | 2320.008 | Abs Value of | Flow this | 2693.4573 | Abs Value of | Flow this | 3065.4057 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9076 |  |  | 56.3718 |  |  | 53.7798 |  |  | 45.4821 |  |  | 25.9893 |  |  | -11.6399 |  |  | -65.1754 |  |  | -124.8615 |  |  | -188.0927 |  |  | -260.4331
[13 empty] | P2 at this iteration flow rate |  |  | 24.6585 |  |  | 24.7656 |  |  | 25.284 |  |  | 26.9436 |  |  | 30.8421 |  |  | 38.368 |  |  | 49.0751 |  |  | 61.0123 |  |  | 73.6585 |  |  | 88.1266
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2491 |  |  | 31.6062 |  |  | 28.4958 |  |  | 18.5386 |  |  | -4.8529 |  |  | -50.0079 |  |  | -114.2505 |  |  | -185.8739 |  |  | -261.7513 |  |  | -348.5598
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7581 |  |  | 46.3018 |  |  | 43.1601 |  |  | 34.8084 |  |  | 18.4258 |  |  | -7.78 |  |  | -37.9496 |  |  | -59.9533 |  |  | -74.4001 |  |  | -98.125
[13 empty] | C Non choked w/ reducers | 7 |  | 2.8023 |  |  | 22.601 |  |  | 57.2637 |  |  | 136.3365 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.3273 |  |  | 18.673 |  |  | 46.5295 |  |  | 99.4966 |  |  | 227.7358 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.8023 |  |  | 22.601 |  |  | 57.2637 |  |  | 136.3365 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.1977 | 15.9117 |  | 10.601 | 126.9546 |  | 34.2637 | 304.7398 |  | 97.3365 | 581.86 |  | 5500 | 956.9455 |  | 5500 | 1424.7615 |  | 5500 | 1901.3498 |  | 5500 | 2320.008 |  | 5500 | 2693.4573 |  | 5500 | 3065.4057
[13 empty] | Next iteration flow rate |  |  | 16.2299 | Abs Value of | Flow this | 128.2241 | Abs Value of | Flow this | 307.7872 | Abs Value of | Flow this | 587.6786 | Abs Value of | Flow this | 966.515 | Abs Value of | Flow this | 1439.0091 | Abs Value of | Flow this | 1920.3633 | Abs Value of | Flow this | 2343.2081 | Abs Value of | Flow this | 2720.3919 | Abs Value of | Flow this | 3096.0597 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9072 |  |  | 56.3609 |  |  | 53.7168 |  |  | 45.2523 |  |  | 25.3676 |  |  | -13.0179 |  |  | -67.6295 |  |  | -128.5153 |  |  | -193.0174 |  |  | -266.8118
[13 empty] | P2 at this iteration flow rate |  |  | 24.6586 |  |  | 24.7678 |  |  | 25.2966 |  |  | 26.9895 |  |  | 30.9665 |  |  | 38.6436 |  |  | 49.5659 |  |  | 61.7431 |  |  | 74.6435 |  |  | 89.4024
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2487 |  |  | 31.5931 |  |  | 28.4201 |  |  | 18.2628 |  |  | -5.5988 |  |  | -51.6615 |  |  | -117.1953 |  |  | -190.2583 |  |  | -267.6609 |  |  | -356.2142
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7578 |  |  | 46.2928 |  |  | 43.1091 |  |  | 34.6308 |  |  | 17.9775 |  |  | -8.6675 |  |  | -39.369 |  |  | -61.7015 |  |  | -76.3435 |  |  | -100.5243
[13 empty] | C Non choked w/ reducers | 7 |  | 2.8584 |  |  | 22.8318 |  |  | 57.9132 |  |  | 138.7357 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.3738 |  |  | 18.8616 |  |  | 47.0226 |  |  | 100.7489 |  |  | 232.8634 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.8584 |  |  | 22.8318 |  |  | 57.9132 |  |  | 138.7357 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.1416 | 16.2299 |  | 10.8318 | 128.2241 |  | 34.9132 | 307.7872 |  | 99.7357 | 587.6786 |  | 5500 | 966.515 |  | 5500 | 1439.0091 |  | 5500 | 1920.3633 |  | 5500 | 2343.2081 |  | 5500 | 2720.3919 |  | 5500 | 3096.0597
[13 empty] | Next iteration flow rate |  |  | 16.5545 | Abs Value of | Flow this | 129.5064 | Abs Value of | Flow this | 310.8651 | Abs Value of | Flow this | 593.5554 | Abs Value of | Flow this | 976.1801 | Abs Value of | Flow this | 1453.3992 | Abs Value of | Flow this | 1939.5669 | Abs Value of | Flow this | 2366.6402 | Abs Value of | Flow this | 2747.5958 | Abs Value of | Flow this | 3127.0203 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9069 |  |  | 56.3497 |  |  | 53.6525 |  |  | 45.0179 |  |  | 24.7335 |  |  | -14.4236 |  |  | -70.1328 |  |  | -132.2424 |  |  | -198.0411 |  |  | -273.3188
[13 empty] | P2 at this iteration flow rate |  |  | 24.6586 |  |  | 24.7701 |  |  | 25.3095 |  |  | 27.0364 |  |  | 31.0933 |  |  | 38.9247 |  |  | 50.0666 |  |  | 62.4885 |  |  | 75.6482 |  |  | 90.7038
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2483 |  |  | 31.5797 |  |  | 28.343 |  |  | 17.9814 |  |  | -6.3598 |  |  | -53.3483 |  |  | -120.1994 |  |  | -194.7309 |  |  | -273.6893 |  |  | -364.0225
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7575 |  |  | 46.2835 |  |  | 43.057 |  |  | 34.4496 |  |  | 17.5201 |  |  | -9.5728 |  |  | -40.8168 |  |  | -63.4849 |  |  | -78.326 |  |  | -102.9719
[13 empty] | C Non choked w/ reducers | 7 |  | 2.9156 |  |  | 23.065 |  |  | 58.5719 |  |  | 141.215 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.4213 |  |  | 19.0521 |  |  | 47.5215 |  |  | 102.0236 |  |  | 238.2419 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.9156 |  |  | 23.065 |  |  | 58.5719 |  |  | 141.215 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.0844 | 16.5545 |  | 11.065 | 129.5064 |  | 35.5719 | 310.8651 |  | 102.215 | 593.5554 |  | 5500 | 976.1801 |  | 5500 | 1453.3992 |  | 5500 | 1939.5669 |  | 5500 | 2366.6402 |  | 5500 | 2747.5958 |  | 5500 | 3127.0203
[13 empty] | Next iteration flow rate |  |  | 16.8856 | Abs Value of | Flow this | 130.8014 | Abs Value of | Flow this | 313.9738 | Abs Value of | Flow this | 599.491 | Abs Value of | Flow this | 985.9419 | Abs Value of | Flow this | 1467.9332 | Abs Value of | Flow this | 1958.9626 | Abs Value of | Flow this | 2390.3066 | Abs Value of | Flow this | 2775.0718 | Abs Value of | Flow this | 3158.2905 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9065 |  |  | 56.3383 |  |  | 53.5869 |  |  | 44.7787 |  |  | 24.0866 |  |  | -15.8575 |  |  | -72.6865 |  |  | -136.0445 |  |  | -203.1657 |  |  | -279.9565
[13 empty] | P2 at this iteration flow rate |  |  | 24.6587 |  |  | 24.7723 |  |  | 25.3226 |  |  | 27.0843 |  |  | 31.2227 |  |  | 39.2115 |  |  | 50.5773 |  |  | 63.2489 |  |  | 76.6731 |  |  | 92.0313
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2478 |  |  | 31.566 |  |  | 28.2643 |  |  | 17.6945 |  |  | -7.136 |  |  | -55.069 |  |  | -123.2638 |  |  | -199.2934 |  |  | -279.8388 |  |  | -371.9878
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7572 |  |  | 46.2741 |  |  | 43.0039 |  |  | 34.2648 |  |  | 17.0536 |  |  | -10.4964 |  |  | -42.2938 |  |  | -65.3041 |  |  | -80.3483 |  |  | -105.4686
[13 empty] | C Non choked w/ reducers | 7 |  | 2.9739 |  |  | 23.3007 |  |  | 59.24 |  |  | 143.7791 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.4698 |  |  | 19.2446 |  |  | 48.0263 |  |  | 103.3214 |  |  | 243.8933 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 2.9739 |  |  | 23.3007 |  |  | 59.24 |  |  | 143.7791 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.0261 | 16.8856 |  | 11.3007 | 130.8014 |  | 36.24 | 313.9738 |  | 104.7791 | 599.491 |  | 5500 | 985.9419 |  | 5500 | 1467.9332 |  | 5500 | 1958.9626 |  | 5500 | 2390.3066 |  | 5500 | 2775.0718 |  | 5500 | 3158.2905
[13 empty] | Next iteration flow rate |  |  | 17.2233 | Abs Value of | Flow this | 132.1094 | Abs Value of | Flow this | 317.1135 | Abs Value of | Flow this | 605.4859 | Abs Value of | Flow this | 995.8014 | Abs Value of | Flow this | 1482.6125 | Abs Value of | Flow this | 1978.5522 | Abs Value of | Flow this | 2414.2097 | Abs Value of | Flow this | 2802.8225 | Abs Value of | Flow this | 3189.8734 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9061 |  |  | 56.3267 |  |  | 53.52 |  |  | 44.5347 |  |  | 23.4268 |  |  | -17.3203 |  |  | -75.2915 |  |  | -139.923 |  |  | -208.3933 |  |  | -286.7276
[13 empty] | P2 at this iteration flow rate |  |  | 24.6588 |  |  | 24.7747 |  |  | 25.336 |  |  | 27.1331 |  |  | 31.3546 |  |  | 39.5041 |  |  | 51.0983 |  |  | 64.0246 |  |  | 77.7187 |  |  | 93.3855
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2473 |  |  | 31.5521 |  |  | 28.184 |  |  | 17.4017 |  |  | -7.9279 |  |  | -56.8243 |  |  | -126.3898 |  |  | -203.9477 |  |  | -286.112 |  |  | -380.1132
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7569 |  |  | 46.2645 |  |  | 42.9498 |  |  | 34.0763 |  |  | 16.5777 |  |  | -11.4384 |  |  | -43.8004 |  |  | -67.1598 |  |  | -82.4113 |  |  | -108.0155
[13 empty] | C Non choked w/ reducers | 7 |  | 3.0334 |  |  | 23.5389 |  |  | 59.9176 |  |  | 146.4333 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.5192 |  |  | 19.4391 |  |  | 48.5372 |  |  | 104.6429 |  |  | 249.8429 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.0334 |  |  | 23.5389 |  |  | 59.9176 |  |  | 146.4333 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.9666 | 17.2233 |  | 11.5389 | 132.1094 |  | 36.9176 | 317.1135 |  | 107.4333 | 605.4859 |  | 5500 | 995.8014 |  | 5500 | 1482.6125 |  | 5500 | 1978.5522 |  | 5500 | 2414.2097 |  | 5500 | 2802.8225 |  | 5500 | 3189.8734
[13 empty] | Next iteration flow rate |  |  | 17.5678 | Abs Value of | Flow this | 133.4305 | Abs Value of | Flow this | 320.2846 | Abs Value of | Flow this | 611.5408 | Abs Value of | Flow this | 1005.7594 | Abs Value of | Flow this | 1497.4387 | Abs Value of | Flow this | 1998.3377 | Abs Value of | Flow this | 2438.3518 | Abs Value of | Flow this | 2830.8507 | Abs Value of | Flow this | 3221.7722 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9057 |  |  | 56.3149 |  |  | 53.4517 |  |  | 44.2859 |  |  | 22.7536 |  |  | -18.8124 |  |  | -77.9489 |  |  | -143.8795 |  |  | -213.7261 |  |  | -293.6349
[13 empty] | P2 at this iteration flow rate |  |  | 24.6589 |  |  | 24.777 |  |  | 25.3497 |  |  | 27.1828 |  |  | 31.4893 |  |  | 39.8025 |  |  | 51.6298 |  |  | 64.8159 |  |  | 78.7852 |  |  | 94.767
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2469 |  |  | 31.5378 |  |  | 28.102 |  |  | 17.1031 |  |  | -8.7356 |  |  | -58.6149 |  |  | -129.5787 |  |  | -208.6954 |  |  | -292.5113 |  |  | -388.4019
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7565 |  |  | 46.2547 |  |  | 42.8946 |  |  | 33.8839 |  |  | 16.0923 |  |  | -12.3994 |  |  | -45.3374 |  |  | -69.0529 |  |  | -84.5157 |  |  | -110.6136
[13 empty] | C Non choked w/ reducers | 7 |  | 3.0941 |  |  | 23.7796 |  |  | 60.6049 |  |  | 149.1833 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.5696 |  |  | 19.6356 |  |  | 49.0541 |  |  | 105.9888 |  |  | 256.1193 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.0941 |  |  | 23.7796 |  |  | 60.6049 |  |  | 149.1833 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.9059 | 17.5678 |  | 11.7796 | 133.4305 |  | 37.6049 | 320.2846 |  | 110.1833 | 611.5408 |  | 5500 | 1005.7594 |  | 5500 | 1497.4387 |  | 5500 | 1998.3377 |  | 5500 | 2438.3518 |  | 5500 | 2830.8507 |  | 5500 | 3221.7722
[13 empty] | Next iteration flow rate |  |  | 17.9191 | Abs Value of | Flow this | 134.7648 | Abs Value of | Flow this | 323.4875 | Abs Value of | Flow this | 617.6562 | Abs Value of | Flow this | 1015.817 | Abs Value of | Flow this | 1512.4131 | Abs Value of | Flow this | 2018.3211 | Abs Value of | Flow this | 2462.7353 | Abs Value of | Flow this | 2859.1592 | Abs Value of | Flow this | 3253.9899 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9053 |  |  | 56.3028 |  |  | 53.3821 |  |  | 44.032 |  |  | 22.067 |  |  | -20.3346 |  |  | -80.6597 |  |  | -147.9155 |  |  | -219.166 |  |  | -300.681
[13 empty] | P2 at this iteration flow rate |  |  | 24.6589 |  |  | 24.7794 |  |  | 25.3636 |  |  | 27.2336 |  |  | 31.6266 |  |  | 40.1069 |  |  | 52.1719 |  |  | 65.6231 |  |  | 79.8732 |  |  | 96.1762
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2464 |  |  | 31.5233 |  |  | 28.0185 |  |  | 16.7984 |  |  | -9.5596 |  |  | -60.4415 |  |  | -132.8316 |  |  | -213.5386 |  |  | -299.0392 |  |  | -396.8571
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7562 |  |  | 46.2447 |  |  | 42.8382 |  |  | 33.6877 |  |  | 15.5971 |  |  | -13.3798 |  |  | -46.9052 |  |  | -70.984 |  |  | -86.6624 |  |  | -113.2639
[13 empty] | C Non choked w/ reducers | 7 |  | 3.156 |  |  | 24.0229 |  |  | 61.3021 |  |  | 152.0352 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.621 |  |  | 19.8341 |  |  | 49.5772 |  |  | 107.36 |  |  | 262.755 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.156 |  |  | 24.0229 |  |  | 61.3021 |  |  | 152.0352 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.844 | 17.9191 |  | 12.0229 | 134.7648 |  | 38.3021 | 323.4875 |  | 113.0352 | 617.6562 |  | 5500 | 1015.817 |  | 5500 | 1512.4131 |  | 5500 | 2018.3211 |  | 5500 | 2462.7353 |  | 5500 | 2859.1592 |  | 5500 | 3253.9899
[13 empty] | Next iteration flow rate |  |  | 18.2775 | Abs Value of | Flow this | 136.1125 | Abs Value of | Flow this | 326.7224 | Abs Value of | Flow this | 623.8327 | Abs Value of | Flow this | 1025.9751 | Abs Value of | Flow this | 1527.5372 | Abs Value of | Flow this | 2038.5043 | Abs Value of | Flow this | 2487.3626 | Abs Value of | Flow this | 2887.7508 | Abs Value of | Flow this | 3286.5298 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9049 |  |  | 56.2905 |  |  | 53.311 |  |  | 43.773 |  |  | 21.3665 |  |  | -21.8873 |  |  | -83.4249 |  |  | -152.0326 |  |  | -224.7152 |  |  | -307.8687
[13 empty] | P2 at this iteration flow rate |  |  | 24.659 |  |  | 24.7819 |  |  | 25.3778 |  |  | 27.2854 |  |  | 31.7667 |  |  | 40.4175 |  |  | 52.725 |  |  | 66.4465 |  |  | 80.983 |  |  | 97.6137
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2458 |  |  | 31.5085 |  |  | 27.9332 |  |  | 16.4876 |  |  | -10.4002 |  |  | -62.3048 |  |  | -136.1499 |  |  | -218.4791 |  |  | -305.6983 |  |  | -405.4824
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7558 |  |  | 46.2345 |  |  | 42.7807 |  |  | 33.4876 |  |  | 15.0919 |  |  | -14.3798 |  |  | -48.5045 |  |  | -72.9539 |  |  | -88.8523 |  |  | -115.9675
[13 empty] | C Non choked w/ reducers | 7 |  | 3.2192 |  |  | 24.2689 |  |  | 62.0095 |  |  | 154.996 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.6734 |  |  | 20.0346 |  |  | 50.1066 |  |  | 108.7571 |  |  | 269.7876 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.2192 |  |  | 24.2689 |  |  | 62.0095 |  |  | 154.996 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.7808 | 18.2775 |  | 12.2689 | 136.1125 |  | 39.0095 | 326.7224 |  | 115.996 | 623.8327 |  | 5500 | 1025.9751 |  | 5500 | 1527.5372 |  | 5500 | 2038.5043 |  | 5500 | 2487.3626 |  | 5500 | 2887.7508 |  | 5500 | 3286.5298
[13 empty] | Next iteration flow rate |  |  | 18.6431 | Abs Value of | Flow this | 137.4736 | Abs Value of | Flow this | 329.9896 | Abs Value of | Flow this | 630.071 | Abs Value of | Flow this | 1036.2349 | Abs Value of | Flow this | 1542.8126 | Abs Value of | Flow this | 2058.8893 | Abs Value of | Flow this | 2512.2363 | Abs Value of | Flow this | 2916.6283 | Abs Value of | Flow this | 3319.3951 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9044 |  |  | 56.2779 |  |  | 53.2386 |  |  | 43.5089 |  |  | 20.652 |  |  | -23.4712 |  |  | -86.2458 |  |  | -156.2325 |  |  | -230.376 |  |  | -315.2008
[13 empty] | P2 at this iteration flow rate |  |  | 24.6591 |  |  | 24.7844 |  |  | 25.3923 |  |  | 27.3382 |  |  | 31.9096 |  |  | 40.7342 |  |  | 53.2892 |  |  | 67.2865 |  |  | 82.1152 |  |  | 99.0802
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2453 |  |  | 31.4935 |  |  | 27.8463 |  |  | 16.1706 |  |  | -11.2577 |  |  | -64.2055 |  |  | -139.535 |  |  | -223.519 |  |  | -312.4912 |  |  | -414.281
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7554 |  |  | 46.224 |  |  | 42.7221 |  |  | 33.2835 |  |  | 14.5766 |  |  | -15.3999 |  |  | -50.136 |  |  | -74.9635 |  |  | -91.0862 |  |  | -118.7254
[13 empty] | C Non choked w/ reducers | 7 |  | 3.2836 |  |  | 24.5174 |  |  | 62.7274 |  |  | 158.073 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.7269 |  |  | 20.2372 |  |  | 50.6424 |  |  | 110.1811 |  |  | 277.2602 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.2836 |  |  | 24.5174 |  |  | 62.7274 |  |  | 158.073 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.7164 | 18.6431 |  | 12.5174 | 137.4736 |  | 39.7274 | 329.9896 |  | 119.073 | 630.071 |  | 5500 | 1036.2349 |  | 5500 | 1542.8126 |  | 5500 | 2058.8893 |  | 5500 | 2512.2363 |  | 5500 | 2916.6283 |  | 5500 | 3319.3951
[13 empty] | Next iteration flow rate |  |  | 19.0159 | Abs Value of | Flow this | 138.8483 | Abs Value of | Flow this | 333.2895 | Abs Value of | Flow this | 636.3718 | Abs Value of | Flow this | 1046.5972 | Abs Value of | Flow this | 1558.2407 | Abs Value of | Flow this | 2079.4782 | Abs Value of | Flow this | 2537.3586 | Abs Value of | Flow this | 2945.7946 | Abs Value of | Flow this | 3352.589 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9039 |  |  | 56.2651 |  |  | 53.1646 |  |  | 43.2394 |  |  | 19.923 |  |  | -25.087 |  |  | -89.1234 |  |  | -160.5168 |  |  | -236.1506 |  |  | -322.6804
[13 empty] | P2 at this iteration flow rate |  |  | 24.6592 |  |  | 24.787 |  |  | 25.4071 |  |  | 27.3921 |  |  | 32.0554 |  |  | 41.0574 |  |  | 53.8647 |  |  | 68.1434 |  |  | 83.2701 |  |  | 100.5761
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2447 |  |  | 31.4781 |  |  | 27.7576 |  |  | 15.8473 |  |  | -12.1324 |  |  | -66.1444 |  |  | -142.988 |  |  | -228.6601 |  |  | -319.4207 |  |  | -423.2565
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7551 |  |  | 46.2134 |  |  | 42.6623 |  |  | 33.0752 |  |  | 14.0509 |  |  | -16.4406 |  |  | -51.8003 |  |  | -77.0134 |  |  | -93.365 |  |  | -121.5388
[13 empty] | C Non choked w/ reducers | 7 |  | 3.3493 |  |  | 24.7687 |  |  | 63.4558 |  |  | 161.2744 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.7814 |  |  | 20.4419 |  |  | 51.1847 |  |  | 111.6327 |  |  | 285.2231 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.3493 |  |  | 24.7687 |  |  | 63.4558 |  |  | 161.2744 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.6507 | 19.0159 |  | 12.7687 | 138.8483 |  | 40.4558 | 333.2895 |  | 122.2744 | 636.3718 |  | 5500 | 1046.5972 |  | 5500 | 1558.2407 |  | 5500 | 2079.4782 |  | 5500 | 2537.3586 |  | 5500 | 2945.7946 |  | 5500 | 3352.589
[13 empty] | Next iteration flow rate |  |  | 19.3962 | Abs Value of | Flow this | 140.2368 | Abs Value of | Flow this | 336.6224 | Abs Value of | Flow this | 642.7355 | Abs Value of | Flow this | 1057.0632 | Abs Value of | Flow this | 1573.8231 | Abs Value of | Flow this | 2100.273 | Abs Value of | Flow this | 2562.7322 | Abs Value of | Flow this | 2975.2525 | Abs Value of | Flow this | 3386.1149 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9034 |  |  | 56.252 |  |  | 53.0892 |  |  | 42.9645 |  |  | 19.1795 |  |  | -26.7353 |  |  | -92.0588 |  |  | -164.8872 |  |  | -242.0412 |  |  | -330.3103
[13 empty] | P2 at this iteration flow rate |  |  | 24.6593 |  |  | 24.7896 |  |  | 25.4222 |  |  | 27.4471 |  |  | 32.2041 |  |  | 41.3871 |  |  | 54.4518 |  |  | 69.0174 |  |  | 84.4482 |  |  | 102.1021
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2441 |  |  | 31.4624 |  |  | 27.6671 |  |  | 15.5174 |  |  | -13.0246 |  |  | -68.1224 |  |  | -146.5105 |  |  | -233.9046 |  |  | -326.4895 |  |  | -432.4123
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7546 |  |  | 46.2026 |  |  | 42.6013 |  |  | 32.8628 |  |  | 13.5146 |  |  | -17.5021 |  |  | -53.498 |  |  | -79.1045 |  |  | -95.6896 |  |  | -124.4087
[13 empty] | C Non choked w/ reducers | 7 |  | 3.4163 |  |  | 25.0226 |  |  | 64.1951 |  |  | 164.6095 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.8371 |  |  | 20.6488 |  |  | 51.7335 |  |  | 113.1129 |  |  | 293.735 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.4163 |  |  | 25.0226 |  |  | 64.1951 |  |  | 164.6095 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.5837 | 19.3962 |  | 13.0226 | 140.2368 |  | 41.1951 | 336.6224 |  | 125.6095 | 642.7355 |  | 5500 | 1057.0632 |  | 5500 | 1573.8231 |  | 5500 | 2100.273 |  | 5500 | 2562.7322 |  | 5500 | 2975.2525 |  | 5500 | 3386.1149
[13 empty] | Next iteration flow rate |  |  | 19.7842 | Abs Value of | Flow this | 141.6392 | Abs Value of | Flow this | 339.9886 | Abs Value of | Flow this | 649.1628 | Abs Value of | Flow this | 1067.6338 | Abs Value of | Flow this | 1589.5613 | Abs Value of | Flow this | 2121.2757 | Abs Value of | Flow this | 2588.3595 | Abs Value of | Flow this | 3005.0051 | Abs Value of | Flow this | 3419.9761 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9029 |  |  | 56.2386 |  |  | 53.0123 |  |  | 42.684 |  |  | 18.421 |  |  | -28.4167 |  |  | -95.0532 |  |  | -169.3454 |  |  | -248.0503 |  |  | -338.0935
[13 empty] | P2 at this iteration flow rate |  |  | 24.6594 |  |  | 24.7923 |  |  | 25.4375 |  |  | 27.5032 |  |  | 32.3558 |  |  | 41.7233 |  |  | 55.0506 |  |  | 69.9091 |  |  | 85.6501 |  |  | 103.6587
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2435 |  |  | 31.4463 |  |  | 27.5748 |  |  | 15.1809 |  |  | -13.9348 |  |  | -70.14 |  |  | -150.1038 |  |  | -239.2545 |  |  | -333.7003 |  |  | -441.7522
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7542 |  |  | 46.1915 |  |  | 42.539 |  |  | 32.646 |  |  | 12.9676 |  |  | -18.585 |  |  | -55.2299 |  |  | -81.2376 |  |  | -98.0609 |  |  | -127.3363
[13 empty] | C Non choked w/ reducers | 7 |  | 3.4847 |  |  | 25.2792 |  |  | 64.9454 |  |  | 168.0882 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.8938 |  |  | 20.8578 |  |  | 52.2891 |  |  | 114.6225 |  |  | 302.8651 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.4847 |  |  | 25.2792 |  |  | 64.9454 |  |  | 168.0882 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.5153 | 19.7842 |  | 13.2792 | 141.6392 |  | 41.9454 | 339.9886 |  | 129.0882 | 649.1628 |  | 5500 | 1067.6338 |  | 5500 | 1589.5613 |  | 5500 | 2121.2757 |  | 5500 | 2588.3595 |  | 5500 | 3005.0051 |  | 5500 | 3419.9761
[13 empty] | Next iteration flow rate |  |  | 20.1799 | Abs Value of | Flow this | 143.0556 | Abs Value of | Flow this | 343.3885 | Abs Value of | Flow this | 655.6545 | Abs Value of | Flow this | 1078.3102 | Abs Value of | Flow this | 1605.4569 | Abs Value of | Flow this | 2142.4885 | Abs Value of | Flow this | 2614.2431 | Abs Value of | Flow this | 3035.0551 | Abs Value of | Flow this | 3454.1758 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9024 |  |  | 56.225 |  |  | 52.9339 |  |  | 42.398 |  |  | 17.6472 |  |  | -30.1319 |  |  | -98.1077 |  |  | -173.8933 |  |  | -254.1801 |  |  | -346.0332
[13 empty] | P2 at this iteration flow rate |  |  | 24.6595 |  |  | 24.795 |  |  | 25.4532 |  |  | 27.5604 |  |  | 32.5106 |  |  | 42.0664 |  |  | 55.6615 |  |  | 70.8187 |  |  | 86.876 |  |  | 105.2466
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2429 |  |  | 31.43 |  |  | 27.4806 |  |  | 14.8376 |  |  | -14.8633 |  |  | -72.1983 |  |  | -153.7693 |  |  | -244.7119 |  |  | -341.0561 |  |  | -451.2799
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7538 |  |  | 46.1803 |  |  | 42.4755 |  |  | 32.425 |  |  | 12.4096 |  |  | -19.6897 |  |  | -56.9965 |  |  | -83.4136 |  |  | -100.4799 |  |  | -130.3227
[13 empty] | C Non choked w/ reducers | 7 |  | 3.5544 |  |  | 25.5387 |  |  | 65.7072 |  |  | 171.7217 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 2.9517 |  |  | 21.0689 |  |  | 52.8514 |  |  | 116.1628 |  |  | 312.6957 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.5544 |  |  | 25.5387 |  |  | 65.7072 |  |  | 171.7217 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.4456 | 20.1799 |  | 13.5387 | 143.0556 |  | 42.7072 | 343.3885 |  | 132.7217 | 655.6545 |  | 5500 | 1078.3102 |  | 5500 | 1605.4569 |  | 5500 | 2142.4885 |  | 5500 | 2614.2431 |  | 5500 | 3035.0551 |  | 5500 | 3454.1758
[13 empty] | Next iteration flow rate |  |  | 20.5834 | Abs Value of | Flow this | 144.4861 | Abs Value of | Flow this | 346.8224 | Abs Value of | Flow this | 662.211 | Abs Value of | Flow this | 1089.0933 | Abs Value of | Flow this | 1621.5115 | Abs Value of | Flow this | 2163.9134 | Abs Value of | Flow this | 2640.3856 | Abs Value of | Flow this | 3065.4057 | Abs Value of | Flow this | 3488.7176 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9018 |  |  | 56.2111 |  |  | 52.8538 |  |  | 42.1062 |  |  | 16.8579 |  |  | -31.8815 |  |  | -101.2237 |  |  | -178.5326 |  |  | -260.4331 |  |  | -354.1325
[13 empty] | P2 at this iteration flow rate |  |  | 24.6596 |  |  | 24.7978 |  |  | 25.4692 |  |  | 27.6188 |  |  | 32.6684 |  |  | 42.4163 |  |  | 56.2847 |  |  | 71.7465 |  |  | 88.1266 |  |  | 106.8665
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2422 |  |  | 31.4133 |  |  | 27.3846 |  |  | 14.4874 |  |  | -15.8105 |  |  | -74.2979 |  |  | -157.5085 |  |  | -250.2791 |  |  | -348.5598 |  |  | -460.999
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7533 |  |  | 46.1688 |  |  | 42.4108 |  |  | 32.1995 |  |  | 11.8404 |  |  | -20.8165 |  |  | -58.7987 |  |  | -85.6334 |  |  | -102.9476 |  |  | -133.3692
[13 empty] | C Non choked w/ reducers | 7 |  | 3.6255 |  |  | 25.8009 |  |  | 66.4805 |  |  | 175.5225 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.0108 |  |  | 21.2823 |  |  | 53.4207 |  |  | 117.7345 |  |  | 323.3253 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.6255 |  |  | 25.8009 |  |  | 66.4805 |  |  | 175.5225 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.3745 | 20.5834 |  | 13.8009 | 144.4861 |  | 43.4805 | 346.8224 |  | 136.5225 | 662.211 |  | 5500 | 1089.0933 |  | 5500 | 1621.5115 |  | 5500 | 2163.9134 |  | 5500 | 2640.3856 |  | 5500 | 3065.4057 |  | 5500 | 3488.7176
[13 empty] | Next iteration flow rate |  |  | 20.9951 | Abs Value of | Flow this | 145.931 | Abs Value of | Flow this | 350.2906 | Abs Value of | Flow this | 668.8331 | Abs Value of | Flow this | 1099.9842 | Abs Value of | Flow this | 1637.7266 | Abs Value of | Flow this | 2185.5525 | Abs Value of | Flow this | 2666.7894 | Abs Value of | Flow this | 3096.0597 | Abs Value of | Flow this | 3523.6048 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9013 |  |  | 56.1969 |  |  | 52.7722 |  |  | 41.8085 |  |  | 16.0527 |  |  | -33.6664 |  |  | -104.4023 |  |  | -183.2651 |  |  | -266.8118 |  |  | -362.3946
[13 empty] | P2 at this iteration flow rate |  |  | 24.6597 |  |  | 24.8006 |  |  | 25.4856 |  |  | 27.6783 |  |  | 32.8295 |  |  | 42.7733 |  |  | 56.9205 |  |  | 72.693 |  |  | 89.4024 |  |  | 108.5189
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2415 |  |  | 31.3963 |  |  | 27.2866 |  |  | 14.1302 |  |  | -16.7767 |  |  | -76.4397 |  |  | -161.3228 |  |  | -255.9581 |  |  | -356.2142 |  |  | -470.9135
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7528 |  |  | 46.157 |  |  | 42.3447 |  |  | 31.9694 |  |  | 11.2597 |  |  | -21.966 |  |  | -60.6371 |  |  | -87.8978 |  |  | -105.4648 |  |  | -136.4769
[13 empty] | C Non choked w/ reducers | 7 |  | 3.6981 |  |  | 26.066 |  |  | 67.2658 |  |  | 179.5046 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.071 |  |  | 21.4978 |  |  | 53.997 |  |  | 119.3389 |  |  | 334.8732 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.6981 |  |  | 26.066 |  |  | 67.2658 |  |  | 179.5046 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.3019 | 20.9951 |  | 14.066 | 145.931 |  | 44.2658 | 350.2906 |  | 140.5046 | 668.8331 |  | 5500 | 1099.9842 |  | 5500 | 1637.7266 |  | 5500 | 2185.5525 |  | 5500 | 2666.7894 |  | 5500 | 3096.0597 |  | 5500 | 3523.6048
[13 empty] | Next iteration flow rate |  |  | 21.415 | Abs Value of | Flow this | 147.3903 | Abs Value of | Flow this | 353.7935 | Abs Value of | Flow this | 675.5214 | Abs Value of | Flow this | 1110.9841 | Abs Value of | Flow this | 1654.1039 | Abs Value of | Flow this | 2207.408 | Abs Value of | Flow this | 2693.4573 | Abs Value of | Flow this | 3127.0203 | Abs Value of | Flow this | 3558.8408 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9007 |  |  | 56.1825 |  |  | 52.6889 |  |  | 41.5048 |  |  | 15.2314 |  |  | -35.4871 |  |  | -107.6448 |  |  | -188.0927 |  |  | -273.3188 |  |  | -370.8227
[13 empty] | P2 at this iteration flow rate |  |  | 24.6599 |  |  | 24.8035 |  |  | 25.5022 |  |  | 27.739 |  |  | 32.9937 |  |  | 43.1374 |  |  | 57.569 |  |  | 73.6585 |  |  | 90.7038 |  |  | 110.2045
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2408 |  |  | 31.379 |  |  | 27.1866 |  |  | 13.7658 |  |  | -17.7623 |  |  | -78.6245 |  |  | -165.2138 |  |  | -261.7513 |  |  | -364.0225 |  |  | -481.0273
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7523 |  |  | 46.1451 |  |  | 42.2773 |  |  | 31.7347 |  |  | 10.6673 |  |  | -23.1387 |  |  | -62.5124 |  |  | -90.2077 |  |  | -108.0326 |  |  | -139.6471
[13 empty] | C Non choked w/ reducers | 7 |  | 3.7721 |  |  | 26.3339 |  |  | 68.0632 |  |  | 183.6836 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.1324 |  |  | 21.7156 |  |  | 54.5804 |  |  | 120.9771 |  |  | 347.4857 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.7721 |  |  | 26.3339 |  |  | 68.0632 |  |  | 183.6836 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.2279 | 21.415 |  | 14.3339 | 147.3903 |  | 45.0632 | 353.7935 |  | 144.6836 | 675.5214 |  | 5500 | 1110.9841 |  | 5500 | 1654.1039 |  | 5500 | 2207.408 |  | 5500 | 2693.4573 |  | 5500 | 3127.0203 |  | 5500 | 3558.8408
[13 empty] | Next iteration flow rate |  |  | 21.8433 | Abs Value of | Flow this | 148.8642 | Abs Value of | Flow this | 357.3314 | Abs Value of | Flow this | 682.2767 | Abs Value of | Flow this | 1122.0939 | Abs Value of | Flow this | 1670.6449 | Abs Value of | Flow this | 2229.4821 | Abs Value of | Flow this | 2720.3919 | Abs Value of | Flow this | 3158.2905 | Abs Value of | Flow this | 3594.4292 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.9 |  |  | 56.1677 |  |  | 52.6039 |  |  | 41.1951 |  |  | 14.3935 |  |  | -37.3444 |  |  | -110.9525 |  |  | -193.0174 |  |  | -279.9565 |  |  | -379.4203
[13 empty] | P2 at this iteration flow rate |  |  | 24.66 |  |  | 24.8065 |  |  | 25.5192 |  |  | 27.801 |  |  | 33.1613 |  |  | 43.5089 |  |  | 58.2305 |  |  | 74.6435 |  |  | 92.0313 |  |  | 111.9241
[13 empty] | Delta P at this iteration flow rate |  |  | 32.24 |  |  | 31.3613 |  |  | 27.0847 |  |  | 13.3941 |  |  | -18.7678 |  |  | -80.8533 |  |  | -169.183 |  |  | -267.6609 |  |  | -371.9878 |  |  | -491.3443
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7518 |  |  | 46.1329 |  |  | 42.2086 |  |  | 31.4953 |  |  | 10.0631 |  |  | -24.3348 |  |  | -64.4255 |  |  | -92.564 |  |  | -110.652 |  |  | -142.881
[13 empty] | C Non choked w/ reducers | 7 |  | 3.8476 |  |  | 26.6047 |  |  | 68.8731 |  |  | 188.0771 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.1951 |  |  | 21.9357 |  |  | 55.1711 |  |  | 122.6504 |  |  | 361.3441 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.8476 |  |  | 26.6047 |  |  | 68.8731 |  |  | 188.0771 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.1524 | 21.8433 |  | 14.6047 | 148.8642 |  | 45.8731 | 357.3314 |  | 149.0771 | 682.2767 |  | 5500 | 1122.0939 |  | 5500 | 1670.6449 |  | 5500 | 2229.4821 |  | 5500 | 2720.3919 |  | 5500 | 3158.2905 |  | 5500 | 3594.4292
[13 empty] | Next iteration flow rate |  |  | 22.2802 | Abs Value of | Flow this | 150.3529 | Abs Value of | Flow this | 360.9047 | Abs Value of | Flow this | 689.0994 | Abs Value of | Flow this | 1133.3148 | Abs Value of | Flow this | 1687.3514 | Abs Value of | Flow this | 2251.7769 | Abs Value of | Flow this | 2747.5958 | Abs Value of | Flow this | 3189.8734 | Abs Value of | Flow this | 3630.3735 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8994 |  |  | 56.1527 |  |  | 52.5172 |  |  | 40.8791 |  |  | 13.5388 |  |  | -39.239 |  |  | -114.3267 |  |  | -198.0411 |  |  | -286.7276 |  |  | -388.1906
[13 empty] | P2 at this iteration flow rate |  |  | 24.6601 |  |  | 24.8095 |  |  | 25.5366 |  |  | 27.8642 |  |  | 33.3322 |  |  | 43.8878 |  |  | 58.9053 |  |  | 75.6482 |  |  | 93.3855 |  |  | 113.6781
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2393 |  |  | 31.3432 |  |  | 26.9807 |  |  | 13.0149 |  |  | -19.7934 |  |  | -83.1268 |  |  | -173.232 |  |  | -273.6893 |  |  | -380.1132 |  |  | -501.8688
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7513 |  |  | 46.1204 |  |  | 42.1384 |  |  | 31.2511 |  |  | 9.4467 |  |  | -25.5551 |  |  | -66.377 |  |  | -94.9677 |  |  | -113.3241 |  |  | -146.1799
[13 empty] | C Non choked w/ reducers | 7 |  | 3.9246 |  |  | 26.8785 |  |  | 69.6958 |  |  | 192.7053 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.259 |  |  | 22.158 |  |  | 55.7691 |  |  | 124.3599 |  |  | 376.6762 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 3.9246 |  |  | 26.8785 |  |  | 69.6958 |  |  | 192.7053 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.0754 | 22.2802 |  | 14.8785 | 150.3529 |  | 46.6958 | 360.9047 |  | 153.7053 | 689.0994 |  | 5500 | 1133.3148 |  | 5500 | 1687.3514 |  | 5500 | 2251.7769 |  | 5500 | 2747.5958 |  | 5500 | 3189.8734 |  | 5500 | 3630.3735
[13 empty] | Next iteration flow rate |  |  | 22.7258 | Abs Value of | Flow this | 151.8564 | Abs Value of | Flow this | 364.5138 | Abs Value of | Flow this | 695.9904 | Abs Value of | Flow this | 1144.648 | Abs Value of | Flow this | 1704.2249 | Abs Value of | Flow this | 2274.2947 | Abs Value of | Flow this | 2775.0718 | Abs Value of | Flow this | 3221.7722 | Abs Value of | Flow this | 3666.6772 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8987 |  |  | 56.1373 |  |  | 52.4288 |  |  | 40.5567 |  |  | 12.6669 |  |  | -41.1717 |  |  | -117.7686 |  |  | -203.1657 |  |  | -293.6349 |  |  | -397.1373
[13 empty] | P2 at this iteration flow rate |  |  | 24.6603 |  |  | 24.8125 |  |  | 25.5542 |  |  | 27.9287 |  |  | 33.5066 |  |  | 44.2743 |  |  | 59.5937 |  |  | 76.6731 |  |  | 94.767 |  |  | 115.4675
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2384 |  |  | 31.3248 |  |  | 26.8746 |  |  | 12.6281 |  |  | -20.8397 |  |  | -85.4461 |  |  | -177.3624 |  |  | -279.8388 |  |  | -388.4019 |  |  | -512.6047
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7507 |  |  | 46.1077 |  |  | 42.0669 |  |  | 31.002 |  |  | 8.8179 |  |  | -26.7998 |  |  | -68.3677 |  |  | -97.4197 |  |  | -116.0499 |  |  | -149.5451
[13 empty] | C Non choked w/ reducers | 7 |  | 4.0031 |  |  | 27.1553 |  |  | 70.5316 |  |  | 197.5908 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.3242 |  |  | 22.3827 |  |  | 56.3747 |  |  | 126.1072 |  |  | 393.7739 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.0031 |  |  | 27.1553 |  |  | 70.5316 |  |  | 197.5908 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.99691 | 22.7258 |  | 15.1553 | 151.8564 |  | 47.5316 | 364.5138 |  | 158.5908 | 695.9904 |  | 5500 | 1144.648 |  | 5500 | 1704.2249 |  | 5500 | 2274.2947 |  | 5500 | 2775.0718 |  | 5500 | 3221.7722 |  | 5500 | 3666.6772
[13 empty] | Next iteration flow rate |  |  | 23.1803 | Abs Value of | Flow this | 153.375 | Abs Value of | Flow this | 368.1589 | Abs Value of | Flow this | 702.9503 | Abs Value of | Flow this | 1156.0945 | Abs Value of | Flow this | 1721.2671 | Abs Value of | Flow this | 2297.0377 | Abs Value of | Flow this | 2802.8225 | Abs Value of | Flow this | 3253.9899 | Abs Value of | Flow this | 3703.344 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.898 |  |  | 56.1217 |  |  | 52.3386 |  |  | 40.2279 |  |  | 11.7775 |  |  | -43.1433 |  |  | -121.2798 |  |  | -208.3933 |  |  | -300.681 |  |  | -406.2638
[13 empty] | P2 at this iteration flow rate |  |  | 24.6604 |  |  | 24.8157 |  |  | 25.5723 |  |  | 27.9944 |  |  | 33.6845 |  |  | 44.6687 |  |  | 60.296 |  |  | 77.7187 |  |  | 96.1762 |  |  | 117.2928
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2376 |  |  | 31.306 |  |  | 26.7663 |  |  | 12.2335 |  |  | -21.907 |  |  | -87.812 |  |  | -181.5758 |  |  | -286.112 |  |  | -396.8571 |  |  | -523.5565
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7501 |  |  | 46.0947 |  |  | 41.9939 |  |  | 30.7479 |  |  | 8.1764 |  |  | -28.0696 |  |  | -70.3984 |  |  | -99.921 |  |  | -118.8304 |  |  | -152.9779
[13 empty] | C Non choked w/ reducers | 7 |  | 4.0832 |  |  | 27.4351 |  |  | 71.3808 |  |  | 202.7596 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.3907 |  |  | 22.6097 |  |  | 56.9879 |  |  | 127.8935 |  |  | 413.0171 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.0832 |  |  | 27.4351 |  |  | 71.3808 |  |  | 202.7596 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.91679 | 23.1803 |  | 15.4351 | 153.375 |  | 48.3808 | 368.1589 |  | 163.7596 | 702.9503 |  | 5500 | 1156.0945 |  | 5500 | 1721.2671 |  | 5500 | 2297.0377 |  | 5500 | 2802.8225 |  | 5500 | 3253.9899 |  | 5500 | 3703.344
[13 empty] | Next iteration flow rate |  |  | 23.6439 | Abs Value of | Flow this | 154.9087 | Abs Value of | Flow this | 371.8405 | Abs Value of | Flow this | 709.9798 | Abs Value of | Flow this | 1167.6554 | Abs Value of | Flow this | 1738.4798 | Abs Value of | Flow this | 2320.008 | Abs Value of | Flow this | 2830.8507 | Abs Value of | Flow this | 3286.5298 | Abs Value of | Flow this | 3740.3775 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8973 |  |  | 56.1057 |  |  | 52.2466 |  |  | 39.8925 |  |  | 10.8702 |  |  | -45.1545 |  |  | -124.8615 |  |  | -213.7261 |  |  | -307.8687 |  |  | -415.5737
[13 empty] | P2 at this iteration flow rate |  |  | 24.6605 |  |  | 24.8189 |  |  | 25.5907 |  |  | 28.0615 |  |  | 33.866 |  |  | 45.0709 |  |  | 61.0123 |  |  | 78.7852 |  |  | 97.6137 |  |  | 119.1547
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2367 |  |  | 31.2869 |  |  | 26.6559 |  |  | 11.8309 |  |  | -22.9957 |  |  | -90.2254 |  |  | -185.8739 |  |  | -292.5113 |  |  | -405.4824 |  |  | -534.7284
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7495 |  |  | 46.0815 |  |  | 41.9194 |  |  | 30.4887 |  |  | 7.5221 |  |  | -29.3649 |  |  | -72.47 |  |  | -102.4725 |  |  | -121.6669 |  |  | -156.4797
[13 empty] | C Non choked w/ reducers | 7 |  | 4.1649 |  |  | 27.7179 |  |  | 72.2437 |  |  | 208.2418 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.4586 |  |  | 22.8391 |  |  | 57.6089 |  |  | 129.7204 |  |  | 434.9121 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.1649 |  |  | 27.7179 |  |  | 72.2437 |  |  | 208.2418 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.83507 | 23.6439 |  | 15.7179 | 154.9087 |  | 49.2437 | 371.8405 |  | 169.2418 | 709.9798 |  | 5500 | 1167.6554 |  | 5500 | 1738.4798 |  | 5500 | 2320.008 |  | 5500 | 2830.8507 |  | 5500 | 3286.5298 |  | 5500 | 3740.3775
[13 empty] | Next iteration flow rate |  |  | 24.1168 | Abs Value of | Flow this | 156.4578 | Abs Value of | Flow this | 375.5589 | Abs Value of | Flow this | 717.0796 | Abs Value of | Flow this | 1179.332 | Abs Value of | Flow this | 1755.8646 | Abs Value of | Flow this | 2343.2081 | Abs Value of | Flow this | 2859.1592 | Abs Value of | Flow this | 3319.3951 | Abs Value of | Flow this | 3777.7812 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8965 |  |  | 56.0894 |  |  | 52.1527 |  |  | 39.5503 |  |  | 9.9447 |  |  | -47.2061 |  |  | -128.5153 |  |  | -219.166 |  |  | -315.2008 |  |  | -425.0707
[13 empty] | P2 at this iteration flow rate |  |  | 24.6607 |  |  | 24.8221 |  |  | 25.6095 |  |  | 28.1299 |  |  | 34.0511 |  |  | 45.4812 |  |  | 61.7431 |  |  | 79.8732 |  |  | 99.0802 |  |  | 121.0541
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2358 |  |  | 31.2673 |  |  | 26.5433 |  |  | 11.4203 |  |  | -24.1063 |  |  | -92.6874 |  |  | -190.2583 |  |  | -299.0392 |  |  | -414.281 |  |  | -546.1249
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7489 |  |  | 46.068 |  |  | 41.8435 |  |  | 30.2243 |  |  | 6.8546 |  |  | -30.6862 |  |  | -74.5832 |  |  | -105.0754 |  |  | -124.5604 |  |  | -160.052
[13 empty] | C Non choked w/ reducers | 7 |  | 4.2483 |  |  | 28.0038 |  |  | 73.1208 |  |  | 214.0719 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.5277 |  |  | 23.0708 |  |  | 58.2377 |  |  | 131.5895 |  |  | 460.1512 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.2483 |  |  | 28.0038 |  |  | 73.1208 |  |  | 214.0719 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.75171 | 24.1168 |  | 16.0038 | 156.4578 |  | 50.1208 | 375.5589 |  | 175.0719 | 717.0796 |  | 5500 | 1179.332 |  | 5500 | 1755.8646 |  | 5500 | 2343.2081 |  | 5500 | 2859.1592 |  | 5500 | 3319.3951 |  | 5500 | 3777.7812
[13 empty] | Next iteration flow rate |  |  | 24.5991 | Abs Value of | Flow this | 158.0224 | Abs Value of | Flow this | 379.3145 | Abs Value of | Flow this | 724.2504 | Abs Value of | Flow this | 1191.1253 | Abs Value of | Flow this | 1773.4232 | Abs Value of | Flow this | 2366.6402 | Abs Value of | Flow this | 2887.7508 | Abs Value of | Flow this | 3352.589 | Abs Value of | Flow this | 3815.559 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8957 |  |  | 56.0728 |  |  | 52.057 |  |  | 39.2012 |  |  | 9.0006 |  |  | -49.299 |  |  | -132.2424 |  |  | -224.7152 |  |  | -322.6804 |  |  | -434.7587
[13 empty] | P2 at this iteration flow rate |  |  | 24.6609 |  |  | 24.8254 |  |  | 25.6286 |  |  | 28.1998 |  |  | 34.2399 |  |  | 45.8998 |  |  | 62.4885 |  |  | 80.983 |  |  | 100.5761 |  |  | 122.9917
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2348 |  |  | 31.2474 |  |  | 26.4284 |  |  | 11.0015 |  |  | -25.2393 |  |  | -95.1988 |  |  | -194.7309 |  |  | -305.6983 |  |  | -423.2565 |  |  | -557.7504
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7482 |  |  | 46.0543 |  |  | 41.766 |  |  | 29.9545 |  |  | 6.1737 |  |  | -32.0341 |  |  | -76.7388 |  |  | -107.7305 |  |  | -127.512 |  |  | -163.696
[13 empty] | C Non choked w/ reducers | 7 |  | 4.3333 |  |  | 28.2929 |  |  | 74.0124 |  |  | 220.2901 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.5983 |  |  | 23.305 |  |  | 58.8746 |  |  | 133.5024 |  |  | 489.7109 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.3333 |  |  | 28.2929 |  |  | 74.0124 |  |  | 220.2901 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.66668 | 24.5991 |  | 16.2929 | 158.0224 |  | 51.0124 | 379.3145 |  | 181.2901 | 724.2504 |  | 5500 | 1191.1253 |  | 5500 | 1773.4232 |  | 5500 | 2366.6402 |  | 5500 | 2887.7508 |  | 5500 | 3352.589 |  | 5500 | 3815.559
[13 empty] | Next iteration flow rate |  |  | 25.0911 | Abs Value of | Flow this | 159.6026 | Abs Value of | Flow this | 383.1077 | Abs Value of | Flow this | 731.4929 | Abs Value of | Flow this | 1203.0365 | Abs Value of | Flow this | 1791.1575 | Abs Value of | Flow this | 2390.3066 | Abs Value of | Flow this | 2916.6283 | Abs Value of | Flow this | 3386.1149 | Abs Value of | Flow this | 3853.7146 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8949 |  |  | 56.0559 |  |  | 51.9593 |  |  | 38.8452 |  |  | 8.0375 |  |  | -51.4339 |  |  | -136.0445 |  |  | -230.376 |  |  | -330.3103 |  |  | -444.6413
[13 empty] | P2 at this iteration flow rate |  |  | 24.661 |  |  | 24.8288 |  |  | 25.6481 |  |  | 28.271 |  |  | 34.4325 |  |  | 46.3268 |  |  | 63.2489 |  |  | 82.1152 |  |  | 102.1021 |  |  | 124.9683
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2339 |  |  | 31.227 |  |  | 26.3112 |  |  | 10.5742 |  |  | -26.395 |  |  | -97.7607 |  |  | -199.2934 |  |  | -312.4912 |  |  | -432.4123 |  |  | -569.6096
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7476 |  |  | 46.0403 |  |  | 41.687 |  |  | 29.6794 |  |  | 5.4792 |  |  | -33.4091 |  |  | -78.9378 |  |  | -110.4391 |  |  | -130.523 |  |  | -167.4133
[13 empty] | C Non choked w/ reducers | 7 |  | 4.4201 |  |  | 28.5851 |  |  | 74.9188 |  |  | 226.9438 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.6703 |  |  | 23.5416 |  |  | 59.5197 |  |  | 135.4611 |  |  | 525.0228 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.4201 |  |  | 28.5851 |  |  | 74.9188 |  |  | 226.9438 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.57995 | 25.0911 |  | 16.5851 | 159.6026 |  | 51.9188 | 383.1077 |  | 187.9438 | 731.4929 |  | 5500 | 1203.0365 |  | 5500 | 1791.1575 |  | 5500 | 2390.3066 |  | 5500 | 2916.6283 |  | 5500 | 3386.1149 |  | 5500 | 3853.7146
[13 empty] | Next iteration flow rate |  |  | 25.5929 | Abs Value of | Flow this | 161.1986 | Abs Value of | Flow this | 386.9387 | Abs Value of | Flow this | 738.8079 | Abs Value of | Flow this | 1215.0669 | Abs Value of | Flow this | 1809.0691 | Abs Value of | Flow this | 2414.2097 | Abs Value of | Flow this | 2945.7946 | Abs Value of | Flow this | 3419.9761 | Abs Value of | Flow this | 3892.2518 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.894 |  |  | 56.0386 |  |  | 51.8597 |  |  | 38.4819 |  |  | 7.055 |  |  | -53.6117 |  |  | -139.923 |  |  | -236.1506 |  |  | -338.0935 |  |  | -454.7226
[13 empty] | P2 at this iteration flow rate |  |  | 24.6612 |  |  | 24.8323 |  |  | 25.6681 |  |  | 28.3436 |  |  | 34.629 |  |  | 46.7623 |  |  | 64.0246 |  |  | 83.2701 |  |  | 103.6587 |  |  | 126.9845
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2328 |  |  | 31.2063 |  |  | 26.1916 |  |  | 10.1383 |  |  | -27.574 |  |  | -100.3741 |  |  | -203.9477 |  |  | -319.4207 |  |  | -441.7522 |  |  | -581.7072
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7468 |  |  | 46.0259 |  |  | 41.6064 |  |  | 29.3987 |  |  | 4.7706 |  |  | -34.8117 |  |  | -81.181 |  |  | -113.202 |  |  | -133.5944 |  |  | -171.2053
[13 empty] | C Non choked w/ reducers | 7 |  | 4.5085 |  |  | 28.8806 |  |  | 75.8405 |  |  | 234.0886 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.7438 |  |  | 23.7808 |  |  | 60.1731 |  |  | 137.4673 |  |  | 568.2887 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.5085 |  |  | 28.8806 |  |  | 75.8405 |  |  | 234.0886 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.49148 | 25.5929 |  | 16.8806 | 161.1986 |  | 52.8405 | 386.9387 |  | 195.0886 | 738.8079 |  | 5500 | 1215.0669 |  | 5500 | 1809.0691 |  | 5500 | 2414.2097 |  | 5500 | 2945.7946 |  | 5500 | 3419.9761 |  | 5500 | 3892.2518
[13 empty] | Next iteration flow rate |  |  | 26.1048 | Abs Value of | Flow this | 162.8106 | Abs Value of | Flow this | 390.8081 | Abs Value of | Flow this | 746.1959 | Abs Value of | Flow this | 1227.2176 | Abs Value of | Flow this | 1827.1597 | Abs Value of | Flow this | 2438.3518 | Abs Value of | Flow this | 2975.2525 | Abs Value of | Flow this | 3454.1758 | Abs Value of | Flow this | 3931.1743 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8931 |  |  | 56.0209 |  |  | 51.7581 |  |  | 38.1114 |  |  | 6.0528 |  |  | -55.8334 |  |  | -143.8795 |  |  | -242.0412 |  |  | -346.0332 |  |  | -465.0066
[13 empty] | P2 at this iteration flow rate |  |  | 24.6614 |  |  | 24.8358 |  |  | 25.6884 |  |  | 28.4177 |  |  | 34.8294 |  |  | 47.2067 |  |  | 64.8159 |  |  | 84.4482 |  |  | 105.2466 |  |  | 129.0413
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2318 |  |  | 31.1851 |  |  | 26.0697 |  |  | 9.6937 |  |  | -28.7766 |  |  | -103.04 |  |  | -208.6954 |  |  | -326.4895 |  |  | -451.2799 |  |  | -594.0479
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7461 |  |  | 46.0113 |  |  | 41.5241 |  |  | 29.1123 |  |  | 4.0479 |  |  | -36.2426 |  |  | -83.4693 |  |  | -116.0205 |  |  | -136.7277 |  |  | -175.0735
[13 empty] | C Non choked w/ reducers | 7 |  | 4.5988 |  |  | 29.1793 |  |  | 76.7779 |  |  | 241.791 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.8187 |  |  | 24.0224 |  |  | 60.835 |  |  | 139.5231 |  |  | 623.1118 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.5988 |  |  | 29.1793 |  |  | 76.7779 |  |  | 241.791 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.40123 | 26.1048 |  | 17.1793 | 162.8106 |  | 53.7779 | 390.8081 |  | 202.791 | 746.1959 |  | 5500 | 1227.2176 |  | 5500 | 1827.1597 |  | 5500 | 2438.3518 |  | 5500 | 2975.2525 |  | 5500 | 3454.1758 |  | 5500 | 3931.1743
[13 empty] | Next iteration flow rate |  |  | 26.6269 | Abs Value of | Flow this | 164.4387 | Abs Value of | Flow this | 394.7162 | Abs Value of | Flow this | 753.6579 | Abs Value of | Flow this | 1239.4898 | Abs Value of | Flow this | 1845.4313 | Abs Value of | Flow this | 2462.7353 | Abs Value of | Flow this | 3005.0051 | Abs Value of | Flow this | 3488.7176 | Abs Value of | Flow this | 3970.486 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8922 |  |  | 56.0029 |  |  | 51.6544 |  |  | 37.7334 |  |  | 5.0305 |  |  | -58.0996 |  |  | -147.9155 |  |  | -248.0503 |  |  | -354.1325 |  |  | -475.4972
[13 empty] | P2 at this iteration flow rate |  |  | 24.6616 |  |  | 24.8394 |  |  | 25.7091 |  |  | 28.4933 |  |  | 35.0339 |  |  | 47.6599 |  |  | 65.6231 |  |  | 85.6501 |  |  | 106.8665 |  |  | 131.1394
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2306 |  |  | 31.1635 |  |  | 25.9453 |  |  | 9.2401 |  |  | -30.0034 |  |  | -105.7595 |  |  | -213.5386 |  |  | -333.7003 |  |  | -460.999 |  |  | -606.6367
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7453 |  |  | 45.9964 |  |  | 41.4402 |  |  | 28.8202 |  |  | 3.3105 |  |  | -37.7021 |  |  | -85.8036 |  |  | -118.8957 |  |  | -139.9238 |  |  | -179.0194
[13 empty] | C Non choked w/ reducers | 7 |  | 4.6908 |  |  | 29.4813 |  |  | 77.7314 |  |  | 250.1309 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.8951 |  |  | 24.2665 |  |  | 61.5055 |  |  | 141.6307 |  |  | 695.905 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.6908 |  |  | 29.4813 |  |  | 77.7314 |  |  | 250.1309 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.30917 | 26.6269 |  | 17.4813 | 164.4387 |  | 54.7314 | 394.7162 |  | 211.1309 | 753.6579 |  | 5500 | 1239.4898 |  | 5500 | 1845.4313 |  | 5500 | 2462.7353 |  | 5500 | 3005.0051 |  | 5500 | 3488.7176 |  | 5500 | 3970.486
[13 empty] | Next iteration flow rate |  |  | 27.1594 | Abs Value of | Flow this | 166.0831 | Abs Value of | Flow this | 398.6634 | Abs Value of | Flow this | 761.1945 | Abs Value of | Flow this | 1251.8847 | Abs Value of | Flow this | 1863.8857 | Abs Value of | Flow this | 2487.3626 | Abs Value of | Flow this | 3035.0551 | Abs Value of | Flow this | 3523.6048 | Abs Value of | Flow this | 4010.1909 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8912 |  |  | 55.9846 |  |  | 51.5486 |  |  | 37.3479 |  |  | 3.9876 |  |  | -60.4114 |  |  | -152.0326 |  |  | -254.1801 |  |  | -362.3946 |  |  | -486.1987
[13 empty] | P2 at this iteration flow rate |  |  | 24.6618 |  |  | 24.8431 |  |  | 25.7303 |  |  | 28.5704 |  |  | 35.2425 |  |  | 48.1223 |  |  | 66.4465 |  |  | 86.876 |  |  | 108.5189 |  |  | 133.2797
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2295 |  |  | 31.1415 |  |  | 25.8183 |  |  | 8.7774 |  |  | -31.2549 |  |  | -108.5337 |  |  | -218.4791 |  |  | -341.0561 |  |  | -470.9135 |  |  | -619.4785
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7445 |  |  | 45.9812 |  |  | 41.3547 |  |  | 28.5222 |  |  | 2.5584 |  |  | -39.191 |  |  | -88.1848 |  |  | -121.8287 |  |  | -143.1843 |  |  | -183.0447
[13 empty] | C Non choked w/ reducers | 7 |  | 4.7847 |  |  | 29.7866 |  |  | 78.7014 |  |  | 259.2052 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3.973 |  |  | 24.5132 |  |  | 62.1848 |  |  | 143.7922 |  |  | 799.5312 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.7847 |  |  | 29.7866 |  |  | 78.7014 |  |  | 259.2052 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.21527 | 27.1594 |  | 17.7866 | 166.0831 |  | 55.7014 | 398.6634 |  | 220.2052 | 761.1945 |  | 5500 | 1251.8847 |  | 5500 | 1863.8857 |  | 5500 | 2487.3626 |  | 5500 | 3035.0551 |  | 5500 | 3523.6048 |  | 5500 | 4010.1909
[13 empty] | Next iteration flow rate |  |  | 27.7026 | Abs Value of | Flow this | 167.7439 | Abs Value of | Flow this | 402.65 | Abs Value of | Flow this | 768.8064 | Abs Value of | Flow this | 1264.4035 | Abs Value of | Flow this | 1882.5245 | Abs Value of | Flow this | 2512.2363 | Abs Value of | Flow this | 3065.4057 | Abs Value of | Flow this | 3558.8408 | Abs Value of | Flow this | 4050.2928 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8902 |  |  | 55.9659 |  |  | 51.4407 |  |  | 36.9545 |  |  | 2.9237 |  |  | -62.7697 |  |  | -156.2325 |  |  | -260.4331 |  |  | -370.8227 |  |  | -497.1153
[13 empty] | P2 at this iteration flow rate |  |  | 24.662 |  |  | 24.8468 |  |  | 25.7519 |  |  | 28.6491 |  |  | 35.4553 |  |  | 48.5939 |  |  | 67.2865 |  |  | 88.1266 |  |  | 110.2045 |  |  | 135.4631
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2283 |  |  | 31.119 |  |  | 25.6889 |  |  | 8.3054 |  |  | -32.5316 |  |  | -111.3637 |  |  | -223.519 |  |  | -348.5598 |  |  | -481.0273 |  |  | -632.5784
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7437 |  |  | 45.9657 |  |  | 41.2674 |  |  | 28.2183 |  |  | 1.7912 |  |  | -40.7099 |  |  | -90.6138 |  |  | -124.8206 |  |  | -146.5103 |  |  | -187.1509
[13 empty] | C Non choked w/ reducers | 7 |  | 4.8805 |  |  | 30.0954 |  |  | 79.6885 |  |  | 269.1333 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.0525 |  |  | 24.7625 |  |  | 62.8731 |  |  | 146.0102 |  |  | 965.1034 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.8805 |  |  | 30.0954 |  |  | 79.6885 |  |  | 269.1333 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.11948 | 27.7026 |  | 18.0954 | 167.7439 |  | 56.6885 | 402.65 |  | 230.1333 | 768.8064 |  | 5500 | 1264.4035 |  | 5500 | 1882.5245 |  | 5500 | 2512.2363 |  | 5500 | 3065.4057 |  | 5500 | 3558.8408 |  | 5500 | 4050.2928
[13 empty] | Next iteration flow rate |  |  | 28.2567 | Abs Value of | Flow this | 169.4214 | Abs Value of | Flow this | 406.6765 | Abs Value of | Flow this | 776.4945 | Abs Value of | Flow this | 1277.0475 | Abs Value of | Flow this | 1901.3498 | Abs Value of | Flow this | 2537.3586 | Abs Value of | Flow this | 3096.0597 | Abs Value of | Flow this | 3594.4292 | Abs Value of | Flow this | 4090.7957 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8892 |  |  | 55.9468 |  |  | 51.3307 |  |  | 36.5533 |  |  | 1.8385 |  |  | -65.1754 |  |  | -160.5168 |  |  | -266.8118 |  |  | -379.4203 |  |  | -508.2514
[13 empty] | P2 at this iteration flow rate |  |  | 24.6622 |  |  | 24.8506 |  |  | 25.7739 |  |  | 28.7293 |  |  | 35.6723 |  |  | 49.0751 |  |  | 68.1434 |  |  | 89.4024 |  |  | 111.9241 |  |  | 137.6903
[13 empty] | Delta P at this iteration flow rate |  |  | 32.227 |  |  | 31.0961 |  |  | 25.5568 |  |  | 7.824 |  |  | -33.8339 |  |  | -114.2505 |  |  | -228.6601 |  |  | -356.2142 |  |  | -491.3443 |  |  | -645.9416
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7428 |  |  | 45.9499 |  |  | 41.1783 |  |  | 27.9082 |  |  | 1.0085 |  |  | -42.2592 |  |  | -93.0917 |  |  | -127.8726 |  |  | -149.9031 |  |  | -191.3396
[13 empty] | C Non choked w/ reducers | 7 |  | 4.9782 |  |  | 30.4075 |  |  | 80.693 |  |  | 280.0635 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.1336 |  |  | 25.0145 |  |  | 63.5704 |  |  | 148.2873 |  |  | 1299.047 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 4.9782 |  |  | 30.4075 |  |  | 80.693 |  |  | 280.0635 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.021776 | 28.2567 |  | 18.4075 | 169.4214 |  | 57.693 | 406.6765 |  | 241.0635 | 776.4945 |  | 5500 | 1277.0475 |  | 5500 | 1901.3498 |  | 5500 | 2537.3586 |  | 5500 | 3096.0597 |  | 5500 | 3594.4292 |  | 5500 | 4090.7957
[13 empty] | Next iteration flow rate |  |  | 28.8218 | Abs Value of | Flow this | 171.1156 | Abs Value of | Flow this | 410.7433 | Abs Value of | Flow this | 784.2594 | Abs Value of | Flow this | 1289.818 | Abs Value of | Flow this | 1920.3633 | Abs Value of | Flow this | 2562.7322 | Abs Value of | Flow this | 3127.0203 | Abs Value of | Flow this | 3630.3735 | Abs Value of | Flow this | 4131.7037 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8881 |  |  | 55.9273 |  |  | 51.2184 |  |  | 36.144 |  |  | 0.73139 |  |  | -67.6295 |  |  | -164.8872 |  |  | -273.3188 |  |  | -388.1906 |  |  | -519.6112
[13 empty] | P2 at this iteration flow rate |  |  | 24.6624 |  |  | 24.8545 |  |  | 25.7963 |  |  | 28.8112 |  |  | 35.8937 |  |  | 49.5659 |  |  | 69.0174 |  |  | 90.7038 |  |  | 113.6781 |  |  | 139.9622
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2257 |  |  | 31.0727 |  |  | 25.4221 |  |  | 7.3328 |  |  | -35.1623 |  |  | -117.1953 |  |  | -233.9046 |  |  | -364.0225 |  |  | -501.8688 |  |  | -659.5735
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7419 |  |  | 45.9338 |  |  | 41.0875 |  |  | 27.5919 |  |  | 0.21011 |  |  | -43.8398 |  |  | -95.6194 |  |  | -130.986 |  |  | -153.3641 |  |  | -195.6125
[13 empty] | C Non choked w/ reducers | 7 |  | 5.0779 |  |  | 30.7231 |  |  | 81.7156 |  |  | 292.1838 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.2163 |  |  | 25.2691 |  |  | 64.2771 |  |  | 150.6262 |  |  | 2874.5228 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.0779 |  |  | 30.7231 |  |  | 81.7156 |  |  | 292.1838 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.077891 | 28.8218 |  | 18.7231 | 171.1156 |  | 58.7156 | 410.7433 |  | 253.1838 | 784.2594 |  | 5500 | 1289.818 |  | 5500 | 1920.3633 |  | 5500 | 2562.7322 |  | 5500 | 3127.0203 |  | 5500 | 3630.3735 |  | 5500 | 4131.7037
[13 empty] | Next iteration flow rate |  |  | 29.3982 | Abs Value of | Flow this | 172.8267 | Abs Value of | Flow this | 414.8507 | Abs Value of | Flow this | 792.102 | Abs Value of | Flow this | 1302.7162 | Abs Value of | Flow this | 1939.5669 | Abs Value of | Flow this | 2588.3595 | Abs Value of | Flow this | 3158.2905 | Abs Value of | Flow this | 3666.6772 | Abs Value of | Flow this | 4173.0207 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.887 |  |  | 55.9074 |  |  | 51.1039 |  |  | 35.7265 |  |  | -0.39792 |  |  | -70.1328 |  |  | -169.3454 |  |  | -279.9565 |  |  | -397.1373 |  |  | -531.1994
[13 empty] | P2 at this iteration flow rate |  |  | 24.6626 |  |  | 24.8585 |  |  | 25.8192 |  |  | 28.8947 |  |  | 36.1196 |  |  | 50.0666 |  |  | 69.9091 |  |  | 92.0313 |  |  | 115.4675 |  |  | 142.2799
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2243 |  |  | 31.0489 |  |  | 25.2847 |  |  | 6.8318 |  |  | -36.5175 |  |  | -120.1994 |  |  | -239.2545 |  |  | -371.9878 |  |  | -512.6047 |  |  | -673.4793
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.741 |  |  | 45.9173 |  |  | 40.9948 |  |  | 27.2693 |  |  | -0.60434 |  |  | -45.452 |  |  | -98.1979 |  |  | -134.1619 |  |  | -156.8947 |  |  | -199.9713
[13 empty] | C Non choked w/ reducers | 7 |  | 5.1796 |  |  | 31.0423 |  |  | 82.7568 |  |  | 305.7353 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.3007 |  |  | 25.5263 |  |  | 64.9932 |  |  | 153.0298 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.1796 |  |  | 31.0423 |  |  | 82.7568 |  |  | 305.7353 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.17956 | 29.3982 |  | 19.0423 | 172.8267 |  | 59.7568 | 414.8507 |  | 266.7353 | 792.102 |  | 5500 | 1302.7162 |  | 5500 | 1939.5669 |  | 5500 | 2588.3595 |  | 5500 | 3158.2905 |  | 5500 | 3666.6772 |  | 5500 | 4173.0207
[13 empty] | Next iteration flow rate |  |  | 29.9862 | Abs Value of | Flow this | 174.555 | Abs Value of | Flow this | 418.9992 | Abs Value of | Flow this | 800.023 | Abs Value of | Flow this | 1315.7434 | Abs Value of | Flow this | 1958.9626 | Abs Value of | Flow this | 2614.2431 | Abs Value of | Flow this | 3189.8734 | Abs Value of | Flow this | 3703.344 | Abs Value of | Flow this | 4214.7509 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8858 |  |  | 55.8871 |  |  | 50.9871 |  |  | 35.3006 |  |  | -1.5499 |  |  | -72.6865 |  |  | -173.8933 |  |  | -286.7276 |  |  | -406.2638 |  |  | -543.0206
[13 empty] | P2 at this iteration flow rate |  |  | 24.6628 |  |  | 24.8626 |  |  | 25.8426 |  |  | 28.9799 |  |  | 36.35 |  |  | 50.5773 |  |  | 70.8187 |  |  | 93.3855 |  |  | 117.2928 |  |  | 144.6441
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2229 |  |  | 31.0245 |  |  | 25.1445 |  |  | 6.3207 |  |  | -37.8999 |  |  | -123.2638 |  |  | -244.7119 |  |  | -380.1132 |  |  | -523.5565 |  |  | -687.6647
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.74 |  |  | 45.9006 |  |  | 40.9003 |  |  | 26.9401 |  |  | -1.4352 |  |  | -47.0967 |  |  | -100.8282 |  |  | -137.4017 |  |  | -160.4962 |  |  | -204.4177
[13 empty] | C Non choked w/ reducers | 7 |  | 5.2833 |  |  | 31.365 |  |  | 83.817 |  |  | 321.0345 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.3867 |  |  | 25.7863 |  |  | 65.7189 |  |  | 155.5014 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.2833 |  |  | 31.365 |  |  | 83.817 |  |  | 321.0345 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.28327 | 29.9862 |  | 19.365 | 174.555 |  | 60.817 | 418.9992 |  | 282.0345 | 800.023 |  | 5500 | 1315.7434 |  | 5500 | 1958.9626 |  | 5500 | 2614.2431 |  | 5500 | 3189.8734 |  | 5500 | 3703.344 |  | 5500 | 4214.7509
[13 empty] | Next iteration flow rate |  |  | 30.5859 | Abs Value of | Flow this | 176.3006 | Abs Value of | Flow this | 423.1892 | Abs Value of | Flow this | 808.0233 | Abs Value of | Flow this | 1328.9008 | Abs Value of | Flow this | 1978.5522 | Abs Value of | Flow this | 2640.3856 | Abs Value of | Flow this | 3221.7722 | Abs Value of | Flow this | 3740.3775 | Abs Value of | Flow this | 4256.8985 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8845 |  |  | 55.8664 |  |  | 50.8679 |  |  | 34.8661 |  |  | -2.7251 |  |  | -75.2915 |  |  | -178.5326 |  |  | -293.6349 |  |  | -415.5737 |  |  | -555.0793
[13 empty] | P2 at this iteration flow rate |  |  | 24.6631 |  |  | 24.8667 |  |  | 25.8664 |  |  | 29.0668 |  |  | 36.585 |  |  | 51.0983 |  |  | 71.7465 |  |  | 94.767 |  |  | 119.1547 |  |  | 147.0559
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2215 |  |  | 30.9997 |  |  | 25.0015 |  |  | 5.7993 |  |  | -39.3101 |  |  | -126.3898 |  |  | -250.2791 |  |  | -388.4019 |  |  | -534.7284 |  |  | -702.1351
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.739 |  |  | 45.8834 |  |  | 40.8039 |  |  | 26.6044 |  |  | -2.2827 |  |  | -48.7745 |  |  | -103.5114 |  |  | -140.7067 |  |  | -164.1702 |  |  | -208.9535
[13 empty] | C Non choked w/ reducers | 7 |  | 5.3891 |  |  | 31.6913 |  |  | 84.897 |  |  | 338.5063 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.4745 |  |  | 26.049 |  |  | 66.4545 |  |  | 158.0444 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.3891 |  |  | 31.6913 |  |  | 84.897 |  |  | 338.5063 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.38905 | 30.5859 |  | 19.6913 | 176.3006 |  | 61.897 | 423.1892 |  | 299.5063 | 808.0233 |  | 5500 | 1328.9008 |  | 5500 | 1978.5522 |  | 5500 | 2640.3856 |  | 5500 | 3221.7722 |  | 5500 | 3740.3775 |  | 5500 | 4256.8985
[13 empty] | Next iteration flow rate |  |  | 31.1976 | Abs Value of | Flow this | 178.0636 | Abs Value of | Flow this | 427.4211 | Abs Value of | Flow this | 816.1035 | Abs Value of | Flow this | 1342.1898 | Abs Value of | Flow this | 1998.3377 | Abs Value of | Flow this | 2666.7894 | Abs Value of | Flow this | 3253.9899 | Abs Value of | Flow this | 3777.7812 | Abs Value of | Flow this | 4299.4674 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8833 |  |  | 55.8453 |  |  | 50.7463 |  |  | 34.4229 |  |  | -3.9239 |  |  | -77.9489 |  |  | -183.2651 |  |  | -300.681 |  |  | -425.0707 |  |  | -567.3804
[13 empty] | P2 at this iteration flow rate |  |  | 24.6633 |  |  | 24.8709 |  |  | 25.8907 |  |  | 29.1554 |  |  | 36.8248 |  |  | 51.6298 |  |  | 72.693 |  |  | 96.1762 |  |  | 121.0541 |  |  | 149.5161
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2199 |  |  | 30.9744 |  |  | 24.8556 |  |  | 5.2675 |  |  | -40.7487 |  |  | -129.5787 |  |  | -255.9581 |  |  | -396.8571 |  |  | -546.1249 |  |  | -716.8965
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7379 |  |  | 45.866 |  |  | 40.7055 |  |  | 26.2618 |  |  | -3.1472 |  |  | -50.4859 |  |  | -106.2485 |  |  | -144.078 |  |  | -167.918 |  |  | -213.5804
[13 empty] | C Non choked w/ reducers | 7 |  | 5.497 |  |  | 32.0213 |  |  | 85.9972 |  |  | 358.7364 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.5641 |  |  | 26.3145 |  |  | 67.2001 |  |  | 160.6624 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.497 |  |  | 32.0213 |  |  | 85.9972 |  |  | 358.7364 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.49697 | 31.1976 |  | 20.0213 | 178.0636 |  | 62.9972 | 427.4211 |  | 319.7364 | 816.1035 |  | 5500 | 1342.1898 |  | 5500 | 1998.3377 |  | 5500 | 2666.7894 |  | 5500 | 3253.9899 |  | 5500 | 3777.7812 |  | 5500 | 4299.4674
[13 empty] | Next iteration flow rate |  |  | 31.8216 | Abs Value of | Flow this | 179.8442 | Abs Value of | Flow this | 431.6953 | Abs Value of | Flow this | 824.2645 | Abs Value of | Flow this | 1355.6117 | Abs Value of | Flow this | 2018.3211 | Abs Value of | Flow this | 2693.4573 | Abs Value of | Flow this | 3286.5298 | Abs Value of | Flow this | 3815.559 | Abs Value of | Flow this | 4342.4621 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8819 |  |  | 55.8238 |  |  | 50.6223 |  |  | 33.9708 |  |  | -5.1468 |  |  | -80.6597 |  |  | -188.0927 |  |  | -307.8687 |  |  | -434.7587 |  |  | -579.9287
[13 empty] | P2 at this iteration flow rate |  |  | 24.6636 |  |  | 24.8752 |  |  | 25.9155 |  |  | 29.2458 |  |  | 37.0694 |  |  | 52.1719 |  |  | 73.6585 |  |  | 97.6137 |  |  | 122.9917 |  |  | 152.0257
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2183 |  |  | 30.9486 |  |  | 24.7068 |  |  | 4.7249 |  |  | -42.2161 |  |  | -132.8316 |  |  | -261.7513 |  |  | -405.4824 |  |  | -557.7504 |  |  | -731.9545
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7368 |  |  | 45.8482 |  |  | 40.6051 |  |  | 25.9125 |  |  | -4.0292 |  |  | -52.2318 |  |  | -109.0406 |  |  | -147.5171 |  |  | -171.7411 |  |  | -218.3004
[13 empty] | C Non choked w/ reducers | 7 |  | 5.607 |  |  | 32.355 |  |  | 87.1184 |  |  | 382.5604 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.6554 |  |  | 26.5828 |  |  | 67.9559 |  |  | 163.3593 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.607 |  |  | 32.355 |  |  | 87.1184 |  |  | 382.5604 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.60704 | 31.8216 |  | 20.355 | 179.8442 |  | 64.1184 | 431.6953 |  | 343.5604 | 824.2645 |  | 5500 | 1355.6117 |  | 5500 | 2018.3211 |  | 5500 | 2693.4573 |  | 5500 | 3286.5298 |  | 5500 | 3815.559 |  | 5500 | 4342.4621
[13 empty] | Next iteration flow rate |  |  | 32.458 | Abs Value of | Flow this | 181.6426 | Abs Value of | Flow this | 436.0123 | Abs Value of | Flow this | 832.5072 | Abs Value of | Flow this | 1369.1678 | Abs Value of | Flow this | 2038.5043 | Abs Value of | Flow this | 2720.3919 | Abs Value of | Flow this | 3319.3951 | Abs Value of | Flow this | 3853.7146 | Abs Value of | Flow this | 4385.8867 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8806 |  |  | 55.8019 |  |  | 50.4958 |  |  | 33.5096 |  |  | -6.3942 |  |  | -83.4249 |  |  | -193.0174 |  |  | -315.2008 |  |  | -444.6413 |  |  | -592.7293
[13 empty] | P2 at this iteration flow rate |  |  | 24.6639 |  |  | 24.8796 |  |  | 25.9408 |  |  | 29.3381 |  |  | 37.3188 |  |  | 52.725 |  |  | 74.6435 |  |  | 99.0802 |  |  | 124.9683 |  |  | 154.5859
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2167 |  |  | 30.9222 |  |  | 24.5549 |  |  | 4.1715 |  |  | -43.7131 |  |  | -136.1499 |  |  | -267.6609 |  |  | -414.281 |  |  | -569.6096 |  |  | -747.3152
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7357 |  |  | 45.83 |  |  | 40.5028 |  |  | 25.556 |  |  | -4.9288 |  |  | -54.0128 |  |  | -111.8889 |  |  | -151.0254 |  |  | -175.6411 |  |  | -223.1152
[13 empty] | C Non choked w/ reducers | 7 |  | 5.7193 |  |  | 32.6925 |  |  | 88.2611 |  |  | 411.2193 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.7486 |  |  | 26.854 |  |  | 68.7221 |  |  | 166.1395 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.7193 |  |  | 32.6925 |  |  | 88.2611 |  |  | 411.2193 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.71933 | 32.458 |  | 20.6925 | 181.6426 |  | 65.2611 | 436.0123 |  | 372.2193 | 832.5072 |  | 5500 | 1369.1678 |  | 5500 | 2038.5043 |  | 5500 | 2720.3919 |  | 5500 | 3319.3951 |  | 5500 | 3853.7146 |  | 5500 | 4385.8867
[13 empty] | Next iteration flow rate |  |  | 33.1072 | Abs Value of | Flow this | 183.4591 | Abs Value of | Flow this | 440.3724 | Abs Value of | Flow this | 840.8323 | Abs Value of | Flow this | 1382.8595 | Abs Value of | Flow this | 2058.8893 | Abs Value of | Flow this | 2747.5958 | Abs Value of | Flow this | 3352.589 | Abs Value of | Flow this | 3892.2518 | Abs Value of | Flow this | 4429.7456 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8791 |  |  | 55.7795 |  |  | 50.3667 |  |  | 33.0391 |  |  | -7.6668 |  |  | -86.2458 |  |  | -198.0411 |  |  | -322.6804 |  |  | -454.7226 |  |  | -605.7872
[13 empty] | P2 at this iteration flow rate |  |  | 24.6642 |  |  | 24.8841 |  |  | 25.9667 |  |  | 29.4322 |  |  | 37.5734 |  |  | 53.2892 |  |  | 75.6482 |  |  | 100.5761 |  |  | 126.9845 |  |  | 157.1974
[13 empty] | Delta P at this iteration flow rate |  |  | 32.215 |  |  | 30.8954 |  |  | 24.4001 |  |  | 3.6069 |  |  | -45.2401 |  |  | -139.535 |  |  | -273.6893 |  |  | -423.2565 |  |  | -581.7072 |  |  | -762.9846
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7345 |  |  | 45.8114 |  |  | 40.3984 |  |  | 25.1925 |  |  | -5.8465 |  |  | -55.8295 |  |  | -114.7944 |  |  | -154.6041 |  |  | -179.6194 |  |  | -228.0268
[13 empty] | C Non choked w/ reducers | 7 |  | 5.8339 |  |  | 33.0338 |  |  | 89.4262 |  |  | 446.6547 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.8436 |  |  | 27.128 |  |  | 69.499 |  |  | 169.0074 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.8339 |  |  | 33.0338 |  |  | 89.4262 |  |  | 446.6547 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.83387 | 33.1072 |  | 21.0338 | 183.4591 |  | 66.4262 | 440.3724 |  | 407.6547 | 840.8323 |  | 5500 | 1382.8595 |  | 5500 | 2058.8893 |  | 5500 | 2747.5958 |  | 5500 | 3352.589 |  | 5500 | 3892.2518 |  | 5500 | 4429.7456
[13 empty] | Next iteration flow rate |  |  | 33.7693 | Abs Value of | Flow this | 185.2937 | Abs Value of | Flow this | 444.7761 | Abs Value of | Flow this | 849.2406 | Abs Value of | Flow this | 1396.6881 | Abs Value of | Flow this | 2079.4782 | Abs Value of | Flow this | 2775.0718 | Abs Value of | Flow this | 3386.1149 | Abs Value of | Flow this | 3931.1743 | Abs Value of | Flow this | 4474.0431 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8776 |  |  | 55.7566 |  |  | 50.2351 |  |  | 32.5592 |  |  | -8.9649 |  |  | -89.1234 |  |  | -203.1657 |  |  | -330.3103 |  |  | -465.0066 |  |  | -619.1075
[13 empty] | P2 at this iteration flow rate |  |  | 24.6645 |  |  | 24.8887 |  |  | 25.993 |  |  | 29.5282 |  |  | 37.833 |  |  | 53.8647 |  |  | 76.6731 |  |  | 102.1021 |  |  | 129.0413 |  |  | 159.8615
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2132 |  |  | 30.8679 |  |  | 24.2421 |  |  | 3.031 |  |  | -46.7979 |  |  | -142.988 |  |  | -279.8388 |  |  | -432.4123 |  |  | -594.0479 |  |  | -778.969
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7333 |  |  | 45.7925 |  |  | 40.2918 |  |  | 24.8216 |  |  | -6.7827 |  |  | -57.6828 |  |  | -117.7583 |  |  | -158.2548 |  |  | -183.6777 |  |  | -233.0371
[13 empty] | C Non choked w/ reducers | 7 |  | 5.9507 |  |  | 33.3789 |  |  | 90.6142 |  |  | 492.1165 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 4.9405 |  |  | 27.4049 |  |  | 70.2867 |  |  | 171.968 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 5.9507 |  |  | 33.3789 |  |  | 90.6142 |  |  | 492.1165 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 0.95072 | 33.7693 |  | 21.3789 | 185.2937 |  | 67.6142 | 444.7761 |  | 453.1165 | 849.2406 |  | 5500 | 1396.6881 |  | 5500 | 2079.4782 |  | 5500 | 2775.0718 |  | 5500 | 3386.1149 |  | 5500 | 3931.1743 |  | 5500 | 4474.0431
[13 empty] | Next iteration flow rate |  |  | 34.4447 | Abs Value of | Flow this | 187.1466 | Abs Value of | Flow this | 449.2239 | Abs Value of | Flow this | 857.733 | Abs Value of | Flow this | 1410.655 | Abs Value of | Flow this | 2100.273 | Abs Value of | Flow this | 2802.8225 | Abs Value of | Flow this | 3419.9761 | Abs Value of | Flow this | 3970.486 | Abs Value of | Flow this | 4518.7835 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8761 |  |  | 55.7333 |  |  | 50.1008 |  |  | 32.0696 |  |  | -10.2891 |  |  | -92.0588 |  |  | -208.3933 |  |  | -338.0935 |  |  | -475.4972 |  |  | -632.6956
[13 empty] | P2 at this iteration flow rate |  |  | 24.6648 |  |  | 24.8933 |  |  | 26.0198 |  |  | 29.6261 |  |  | 38.0978 |  |  | 54.4518 |  |  | 77.7187 |  |  | 103.6587 |  |  | 131.1394 |  |  | 162.5791
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2113 |  |  | 30.84 |  |  | 24.081 |  |  | 2.4435 |  |  | -48.3869 |  |  | -146.5105 |  |  | -286.112 |  |  | -441.7522 |  |  | -606.6367 |  |  | -795.2747
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.732 |  |  | 45.7732 |  |  | 40.1832 |  |  | 24.4432 |  |  | -7.7377 |  |  | -59.5733 |  |  | -120.7818 |  |  | -161.9789 |  |  | -187.8176 |  |  | -238.1482
[13 empty] | C Non choked w/ reducers | 7 |  | 6.0699 |  |  | 33.728 |  |  | 91.8261 |  |  | 553.5729 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.0394 |  |  | 27.6848 |  |  | 71.0855 |  |  | 175.0268 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.0699 |  |  | 33.728 |  |  | 91.8261 |  |  | 553.5729 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.0699 | 34.4447 |  | 21.728 | 187.1466 |  | 68.8261 | 449.2239 |  | 514.5729 | 857.733 |  | 5500 | 1410.655 |  | 5500 | 2100.273 |  | 5500 | 2802.8225 |  | 5500 | 3419.9761 |  | 5500 | 3970.486 |  | 5500 | 4518.7835
[13 empty] | Next iteration flow rate |  |  | 35.1336 | Abs Value of | Flow this | 189.0181 | Abs Value of | Flow this | 453.7161 | Abs Value of | Flow this | 866.3103 | Abs Value of | Flow this | 1424.7615 | Abs Value of | Flow this | 2121.2757 | Abs Value of | Flow this | 2830.8507 | Abs Value of | Flow this | 3454.1758 | Abs Value of | Flow this | 4010.1909 | Abs Value of | Flow this | 4563.9713 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8745 |  |  | 55.7095 |  |  | 49.9638 |  |  | 31.5702 |  |  | -11.6399 |  |  | -95.0532 |  |  | -213.7261 |  |  | -346.0332 |  |  | -486.1987 |  |  | -646.5568
[13 empty] | P2 at this iteration flow rate |  |  | 24.6651 |  |  | 24.8981 |  |  | 26.0472 |  |  | 29.726 |  |  | 38.368 |  |  | 55.0506 |  |  | 78.7852 |  |  | 105.2466 |  |  | 133.2797 |  |  | 165.3514
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2093 |  |  | 30.8114 |  |  | 23.9166 |  |  | 1.8442 |  |  | -50.0079 |  |  | -150.1038 |  |  | -292.5113 |  |  | -451.2799 |  |  | -619.4785 |  |  | -811.9082
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7306 |  |  | 45.7535 |  |  | 40.0723 |  |  | 24.0573 |  |  | -8.7119 |  |  | -61.5018 |  |  | -123.866 |  |  | -165.7778 |  |  | -192.0407 |  |  | -243.3619
[13 empty] | C Non choked w/ reducers | 7 |  | 6.1915 |  |  | 34.0811 |  |  | 93.0625 |  |  | 643.5722 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.1403 |  |  | 27.9677 |  |  | 71.8956 |  |  | 178.1894 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.1915 |  |  | 34.0811 |  |  | 93.0625 |  |  | 643.5722 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.1915 | 35.1336 |  | 22.0811 | 189.0181 |  | 70.0625 | 453.7161 |  | 604.5722 | 866.3103 |  | 5500 | 1424.7615 |  | 5500 | 2121.2757 |  | 5500 | 2830.8507 |  | 5500 | 3454.1758 |  | 5500 | 4010.1909 |  | 5500 | 4563.9713
[13 empty] | Next iteration flow rate |  |  | 35.8363 | Abs Value of | Flow this | 190.9082 | Abs Value of | Flow this | 458.2533 | Abs Value of | Flow this | 874.9734 | Abs Value of | Flow this | 1439.0091 | Abs Value of | Flow this | 2142.4885 | Abs Value of | Flow this | 2859.1592 | Abs Value of | Flow this | 3488.7176 | Abs Value of | Flow this | 4050.2928 | Abs Value of | Flow this | 4609.611 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8728 |  |  | 55.6853 |  |  | 49.8241 |  |  | 31.0607 |  |  | -13.0179 |  |  | -98.1077 |  |  | -219.166 |  |  | -354.1325 |  |  | -497.1153 |  |  | -660.6966
[13 empty] | P2 at this iteration flow rate |  |  | 24.6654 |  |  | 24.9029 |  |  | 26.0752 |  |  | 29.8279 |  |  | 38.6436 |  |  | 55.6615 |  |  | 79.8732 |  |  | 106.8665 |  |  | 135.4631 |  |  | 168.1793
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2073 |  |  | 30.7823 |  |  | 23.7489 |  |  | 1.2329 |  |  | -51.6615 |  |  | -153.7693 |  |  | -299.0392 |  |  | -460.999 |  |  | -632.5784 |  |  | -828.8759
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7292 |  |  | 45.7335 |  |  | 39.9593 |  |  | 23.6636 |  |  | -9.7057 |  |  | -63.4691 |  |  | -127.0123 |  |  | -169.6531 |  |  | -196.3487 |  |  | -248.6805
[13 empty] | C Non choked w/ reducers | 7 |  | 6.3155 |  |  | 34.4381 |  |  | 94.3244 |  |  | 794.9954 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.2431 |  |  | 28.2536 |  |  | 72.7172 |  |  | 181.4623 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.3155 |  |  | 34.4381 |  |  | 94.3244 |  |  | 794.9954 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.3155 | 35.8363 |  | 22.4381 | 190.9082 |  | 71.3244 | 458.2533 |  | 755.9954 | 874.9734 |  | 5500 | 1439.0091 |  | 5500 | 2142.4885 |  | 5500 | 2859.1592 |  | 5500 | 3488.7176 |  | 5500 | 4050.2928 |  | 5500 | 4609.611
[13 empty] | Next iteration flow rate |  |  | 36.553 | Abs Value of | Flow this | 192.8173 | Abs Value of | Flow this | 462.8358 | Abs Value of | Flow this | 883.7232 | Abs Value of | Flow this | 1453.3992 | Abs Value of | Flow this | 2163.9134 | Abs Value of | Flow this | 2887.7508 | Abs Value of | Flow this | 3523.6048 | Abs Value of | Flow this | 4090.7957 | Abs Value of | Flow this | 4655.7071 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.871 |  |  | 55.6605 |  |  | 49.6815 |  |  | 30.541 |  |  | -14.4236 |  |  | -101.2237 |  |  | -224.7152 |  |  | -362.3946 |  |  | -508.2514 |  |  | -675.1206
[13 empty] | P2 at this iteration flow rate |  |  | 24.6658 |  |  | 24.9079 |  |  | 26.1037 |  |  | 29.9318 |  |  | 38.9247 |  |  | 56.2847 |  |  | 80.983 |  |  | 108.5189 |  |  | 137.6903 |  |  | 171.0641
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2052 |  |  | 30.7526 |  |  | 23.5778 |  |  | 0.60926 |  |  | -53.3483 |  |  | -157.5085 |  |  | -305.6983 |  |  | -470.9135 |  |  | -645.9416 |  |  | -846.1848
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7278 |  |  | 45.713 |  |  | 39.8439 |  |  | 23.262 |  |  | -10.7195 |  |  | -65.4759 |  |  | -130.2218 |  |  | -173.6063 |  |  | -200.7433 |  |  | -254.1059
[13 empty] | C Non choked w/ reducers | 7 |  | 6.442 |  |  | 34.7993 |  |  | 95.6126 |  |  | 1142.2153 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.3481 |  |  | 28.5425 |  |  | 73.5506 |  |  | 184.8522 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.442 |  |  | 34.7993 |  |  | 95.6126 |  |  | 1142.2153 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.442 | 36.553 |  | 22.7993 | 192.8173 |  | 72.6126 | 462.8358 |  | 1103.2153 | 883.7232 |  | 5500 | 1453.3992 |  | 5500 | 2163.9134 |  | 5500 | 2887.7508 |  | 5500 | 3523.6048 |  | 5500 | 4090.7957 |  | 5500 | 4655.7071
[13 empty] | Next iteration flow rate |  |  | 37.2841 | Abs Value of | Flow this | 194.7455 | Abs Value of | Flow this | 467.4642 | Abs Value of | Flow this | 892.5604 | Abs Value of | Flow this | 1467.9332 | Abs Value of | Flow this | 2185.5525 | Abs Value of | Flow this | 2916.6283 | Abs Value of | Flow this | 3558.8408 | Abs Value of | Flow this | 4131.7037 | Abs Value of | Flow this | 4702.2642 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8692 |  |  | 55.6353 |  |  | 49.5361 |  |  | 30.0109 |  |  | -15.8575 |  |  | -104.4023 |  |  | -230.376 |  |  | -370.8227 |  |  | -519.6112 |  |  | -689.8346
[13 empty] | P2 at this iteration flow rate |  |  | 24.6662 |  |  | 24.9129 |  |  | 26.1328 |  |  | 30.0378 |  |  | 39.2115 |  |  | 56.9205 |  |  | 82.1152 |  |  | 110.2045 |  |  | 139.9622 |  |  | 174.0069
[13 empty] | Delta P at this iteration flow rate |  |  | 32.203 |  |  | 30.7224 |  |  | 23.4033 |  |  | -0.026911 |  |  | -55.069 |  |  | -161.3228 |  |  | -312.4912 |  |  | -481.0273 |  |  | -659.5735 |  |  | -863.8415
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7263 |  |  | 45.6921 |  |  | 39.7262 |  |  | 22.8523 |  |  | -11.7536 |  |  | -67.5231 |  |  | -133.4958 |  |  | -177.6389 |  |  | -205.2262 |  |  | -259.6404
[13 empty] | C Non choked w/ reducers | 7 |  | 6.5711 |  |  | 35.1646 |  |  | 96.9281 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.4551 |  |  | 28.8345 |  |  | 74.396 |  |  | 188.3669 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.5711 |  |  | 35.1646 |  |  | 96.9281 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.5711 | 37.2841 |  | 23.1646 | 194.7455 |  | 73.9281 | 467.4642 |  | 5500 | 892.5604 |  | 5500 | 1467.9332 |  | 5500 | 2185.5525 |  | 5500 | 2916.6283 |  | 5500 | 3558.8408 |  | 5500 | 4131.7037 |  | 5500 | 4702.2642
[13 empty] | Next iteration flow rate |  |  | 38.0298 | Abs Value of | Flow this | 196.6929 | Abs Value of | Flow this | 472.1388 | Abs Value of | Flow this | 901.486 | Abs Value of | Flow this | 1482.6125 | Abs Value of | Flow this | 2207.408 | Abs Value of | Flow this | 2945.7946 | Abs Value of | Flow this | 3594.4292 | Abs Value of | Flow this | 4173.0207 | Abs Value of | Flow this | 4749.2869 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8673 |  |  | 55.6096 |  |  | 49.3878 |  |  | 29.4701 |  |  | -17.3203 |  |  | -107.6448 |  |  | -236.1506 |  |  | -379.4203 |  |  | -531.1994 |  |  | -704.8443
[13 empty] | P2 at this iteration flow rate |  |  | 24.6665 |  |  | 24.9181 |  |  | 26.1624 |  |  | 30.146 |  |  | 39.5041 |  |  | 57.569 |  |  | 83.2701 |  |  | 111.9241 |  |  | 142.2799 |  |  | 177.0089
[13 empty] | Delta P at this iteration flow rate |  |  | 32.2008 |  |  | 30.6915 |  |  | 23.2253 |  |  | -0.67587 |  |  | -56.8243 |  |  | -165.2138 |  |  | -319.4207 |  |  | -491.3443 |  |  | -673.4793 |  |  | -881.8531
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7247 |  |  | 45.6708 |  |  | 39.6062 |  |  | 22.4343 |  |  | -12.8085 |  |  | -69.6114 |  |  | -136.8356 |  |  | -181.7526 |  |  | -209.7992 |  |  | -265.2862
[13 empty] | C Non choked w/ reducers | 7 |  | 6.7028 |  |  | 35.5341 |  |  | 98.2718 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.5643 |  |  | 29.1296 |  |  | 75.2538 |  |  | 192.0145 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.7028 |  |  | 35.5341 |  |  | 98.2718 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.7028 | 38.0298 |  | 23.5341 | 196.6929 |  | 75.2718 | 472.1388 |  | 5500 | 901.486 |  | 5500 | 1482.6125 |  | 5500 | 2207.408 |  | 5500 | 2945.7946 |  | 5500 | 3594.4292 |  | 5500 | 4173.0207 |  | 5500 | 4749.2869
[13 empty] | Next iteration flow rate |  |  | 38.7903 | Abs Value of | Flow this | 198.6599 | Abs Value of | Flow this | 476.8602 | Abs Value of | Flow this | 910.5008 | Abs Value of | Flow this | 1497.4387 | Abs Value of | Flow this | 2229.4821 | Abs Value of | Flow this | 2975.2525 | Abs Value of | Flow this | 3630.3735 | Abs Value of | Flow this | 4214.7509 | Abs Value of | Flow this | 4796.7797 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8653 |  |  | 55.5833 |  |  | 49.2365 |  |  | 28.9184 |  |  | -18.8124 |  |  | -110.9525 |  |  | -242.0412 |  |  | -388.1906 |  |  | -543.0206 |  |  | -720.1556
[13 empty] | P2 at this iteration flow rate |  |  | 24.6669 |  |  | 24.9233 |  |  | 26.1927 |  |  | 30.2563 |  |  | 39.8025 |  |  | 58.2305 |  |  | 84.4482 |  |  | 113.6781 |  |  | 144.6441 |  |  | 180.0711
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1984 |  |  | 30.6599 |  |  | 23.0437 |  |  | -1.3379 |  |  | -58.6149 |  |  | -169.183 |  |  | -326.4895 |  |  | -501.8688 |  |  | -687.6647 |  |  | -900.2268
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7231 |  |  | 45.649 |  |  | 39.4838 |  |  | 22.008 |  |  | -13.8846 |  |  | -71.7417 |  |  | -140.2425 |  |  | -185.949 |  |  | -214.4641 |  |  | -271.0454
[13 empty] | C Non choked w/ reducers | 7 |  | 6.8371 |  |  | 35.9079 |  |  | 99.6449 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.6757 |  |  | 29.4279 |  |  | 76.1241 |  |  | 195.804 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.8371 |  |  | 35.9079 |  |  | 99.6449 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.8371 | 38.7903 |  | 23.9079 | 198.6599 |  | 76.6449 | 476.8602 |  | 5500 | 910.5008 |  | 5500 | 1497.4387 |  | 5500 | 2229.4821 |  | 5500 | 2975.2525 |  | 5500 | 3630.3735 |  | 5500 | 4214.7509 |  | 5500 | 4796.7797
[13 empty] | Next iteration flow rate |  |  | 39.5662 | Abs Value of | Flow this | 200.6465 | Abs Value of | Flow this | 481.6288 | Abs Value of | Flow this | 919.6059 | Abs Value of | Flow this | 1512.4131 | Abs Value of | Flow this | 2251.7769 | Abs Value of | Flow this | 3005.0051 | Abs Value of | Flow this | 3666.6772 | Abs Value of | Flow this | 4256.8985 | Abs Value of | Flow this | 4844.7475 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8633 |  |  | 55.5565 |  |  | 49.0821 |  |  | 28.3557 |  |  | -20.3346 |  |  | -114.3267 |  |  | -248.0503 |  |  | -397.1373 |  |  | -555.0793 |  |  | -735.7748
[13 empty] | P2 at this iteration flow rate |  |  | 24.6673 |  |  | 24.9287 |  |  | 26.2236 |  |  | 30.3689 |  |  | 40.1069 |  |  | 58.9053 |  |  | 85.6501 |  |  | 115.4675 |  |  | 147.0559 |  |  | 183.195
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1959 |  |  | 30.6278 |  |  | 22.8585 |  |  | -2.0132 |  |  | -60.4415 |  |  | -173.232 |  |  | -333.7003 |  |  | -512.6047 |  |  | -702.1351 |  |  | -918.9698
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7214 |  |  | 45.6269 |  |  | 39.3589 |  |  | 21.5731 |  |  | -14.9824 |  |  | -73.9148 |  |  | -143.7179 |  |  | -190.2297 |  |  | -219.2228 |  |  | -276.9204
[13 empty] | C Non choked w/ reducers | 7 |  | 6.9741 |  |  | 36.286 |  |  | 101.0483 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.7893 |  |  | 29.7295 |  |  | 77.0072 |  |  | 199.7454 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 6.9741 |  |  | 36.286 |  |  | 101.0483 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1.9741 | 39.5662 |  | 24.286 | 200.6465 |  | 78.0483 | 481.6288 |  | 5500 | 919.6059 |  | 5500 | 1512.4131 |  | 5500 | 2251.7769 |  | 5500 | 3005.0051 |  | 5500 | 3666.6772 |  | 5500 | 4256.8985 |  | 5500 | 4844.7475
[13 empty] | Next iteration flow rate |  |  | 40.3575 | Abs Value of | Flow this | 202.6529 | Abs Value of | Flow this | 486.4451 | Abs Value of | Flow this | 928.8019 | Abs Value of | Flow this | 1527.5372 | Abs Value of | Flow this | 2274.2947 | Abs Value of | Flow this | 3035.0551 | Abs Value of | Flow this | 3703.344 | Abs Value of | Flow this | 4299.4674 | Abs Value of | Flow this | 4893.195 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8611 |  |  | 55.5292 |  |  | 48.9246 |  |  | 27.7816 |  |  | -21.8873 |  |  | -117.7686 |  |  | -254.1801 |  |  | -406.2638 |  |  | -567.3804 |  |  | -751.7079
[13 empty] | P2 at this iteration flow rate |  |  | 24.6678 |  |  | 24.9342 |  |  | 26.2551 |  |  | 30.4837 |  |  | 40.4175 |  |  | 59.5937 |  |  | 86.876 |  |  | 117.2928 |  |  | 149.5161 |  |  | 186.3816
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1934 |  |  | 30.595 |  |  | 22.6696 |  |  | -2.702 |  |  | -62.3048 |  |  | -177.3624 |  |  | -341.0561 |  |  | -523.5565 |  |  | -716.8965 |  |  | -938.0895
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7196 |  |  | 45.6042 |  |  | 39.2315 |  |  | 21.1295 |  |  | -16.1022 |  |  | -76.1316 |  |  | -147.2632 |  |  | -194.5964 |  |  | -224.0772 |  |  | -282.9135
[13 empty] | C Non choked w/ reducers | 7 |  | 7.1138 |  |  | 36.6685 |  |  | 102.4832 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 5.9052 |  |  | 30.0342 |  |  | 77.9035 |  |  | 203.8498 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 7.1138 |  |  | 36.6685 |  |  | 102.4832 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.1138 | 40.3575 |  | 24.6685 | 202.6529 |  | 79.4832 | 486.4451 |  | 5500 | 928.8019 |  | 5500 | 1527.5372 |  | 5500 | 2274.2947 |  | 5500 | 3035.0551 |  | 5500 | 3703.344 |  | 5500 | 4299.4674 |  | 5500 | 4893.195
[13 empty] | Next iteration flow rate |  |  | 41.1646 | Abs Value of | Flow this | 204.6795 | Abs Value of | Flow this | 491.3095 | Abs Value of | Flow this | 938.0899 | Abs Value of | Flow this | 1542.8126 | Abs Value of | Flow this | 2297.0377 | Abs Value of | Flow this | 3065.4057 | Abs Value of | Flow this | 3740.3775 | Abs Value of | Flow this | 4342.4621 | Abs Value of | Flow this | 4942.127 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8589 |  |  | 55.5013 |  |  | 48.764 |  |  | 27.196 |  |  | -23.4712 |  |  | -121.2798 |  |  | -260.4331 |  |  | -415.5737 |  |  | -579.9287 |  |  | -767.9612
[13 empty] | P2 at this iteration flow rate |  |  | 24.6682 |  |  | 24.9397 |  |  | 26.2872 |  |  | 30.6008 |  |  | 40.7342 |  |  | 60.296 |  |  | 88.1266 |  |  | 119.1547 |  |  | 152.0257 |  |  | 189.6322
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1907 |  |  | 30.5616 |  |  | 22.4768 |  |  | -3.4048 |  |  | -64.2055 |  |  | -181.5758 |  |  | -348.5598 |  |  | -534.7284 |  |  | -731.9545 |  |  | -957.5935
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7178 |  |  | 45.5812 |  |  | 39.1015 |  |  | 20.6769 |  |  | -17.2445 |  |  | -78.3929 |  |  | -150.8797 |  |  | -199.051 |  |  | -229.0291 |  |  | -289.0271
[13 empty] | C Non choked w/ reducers | 7 |  | 7.2564 |  |  | 37.0555 |  |  | 103.9509 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.0235 |  |  | 30.3422 |  |  | 78.8132 |  |  | 208.1292 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 7.2564 |  |  | 37.0555 |  |  | 103.9509 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.2564 | 41.1646 |  | 25.0555 | 204.6795 |  | 80.9509 | 491.3095 |  | 5500 | 938.0899 |  | 5500 | 1542.8126 |  | 5500 | 2297.0377 |  | 5500 | 3065.4057 |  | 5500 | 3740.3775 |  | 5500 | 4342.4621 |  | 5500 | 4942.127
[13 empty] | Next iteration flow rate |  |  | 41.9879 | Abs Value of | Flow this | 206.7263 | Abs Value of | Flow this | 496.2226 | Abs Value of | Flow this | 947.4708 | Abs Value of | Flow this | 1558.2407 | Abs Value of | Flow this | 2320.008 | Abs Value of | Flow this | 3096.0597 | Abs Value of | Flow this | 3777.7812 | Abs Value of | Flow this | 4385.8867 | Abs Value of | Flow this | 4991.5482 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8566 |  |  | 55.4729 |  |  | 48.6001 |  |  | 26.5986 |  |  | -25.087 |  |  | -124.8615 |  |  | -266.8118 |  |  | -425.0707 |  |  | -592.7293 |  |  | -784.5413
[13 empty] | P2 at this iteration flow rate |  |  | 24.6687 |  |  | 24.9454 |  |  | 26.32 |  |  | 30.7203 |  |  | 41.0574 |  |  | 61.0123 |  |  | 89.4024 |  |  | 121.0541 |  |  | 154.5859 |  |  | 192.9483
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1879 |  |  | 30.5274 |  |  | 22.2802 |  |  | -4.1216 |  |  | -66.1444 |  |  | -185.8739 |  |  | -356.2142 |  |  | -546.1249 |  |  | -747.3152 |  |  | -977.4895
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7159 |  |  | 45.5576 |  |  | 38.9689 |  |  | 20.2153 |  |  | -18.4098 |  |  | -80.6997 |  |  | -154.569 |  |  | -203.5951 |  |  | -234.0806 |  |  | -295.2635
[13 empty] | C Non choked w/ reducers | 7 |  | 7.4019 |  |  | 37.4469 |  |  | 105.4527 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.1441 |  |  | 30.6536 |  |  | 79.7366 |  |  | 212.5972 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 7.4019 |  |  | 37.4469 |  |  | 105.4527 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.4019 | 41.9879 |  | 25.4469 | 206.7263 |  | 82.4527 | 496.2226 |  | 5500 | 947.4708 |  | 5500 | 1558.2407 |  | 5500 | 2320.008 |  | 5500 | 3096.0597 |  | 5500 | 3777.7812 |  | 5500 | 4385.8867 |  | 5500 | 4991.5482
[13 empty] | Next iteration flow rate |  |  | 42.8277 | Abs Value of | Flow this | 208.7935 | Abs Value of | Flow this | 501.1848 | Abs Value of | Flow this | 956.9455 | Abs Value of | Flow this | 1573.8231 | Abs Value of | Flow this | 2343.2081 | Abs Value of | Flow this | 3127.0203 | Abs Value of | Flow this | 3815.559 | Abs Value of | Flow this | 4429.7456 | Abs Value of | Flow this | 5041.4637 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8542 |  |  | 55.4438 |  |  | 48.433 |  |  | 25.9893 |  |  | -26.7353 |  |  | -128.5153 |  |  | -273.3188 |  |  | -434.7587 |  |  | -605.7872 |  |  | -801.4546
[13 empty] | P2 at this iteration flow rate |  |  | 24.6692 |  |  | 24.9512 |  |  | 26.3534 |  |  | 30.8421 |  |  | 41.3871 |  |  | 61.7431 |  |  | 90.7038 |  |  | 122.9917 |  |  | 157.1974 |  |  | 196.3309
[13 empty] | Delta P at this iteration flow rate |  |  | 32.185 |  |  | 30.4926 |  |  | 22.0796 |  |  | -4.8529 |  |  | -68.1224 |  |  | -190.2583 |  |  | -364.0225 |  |  | -557.7504 |  |  | -762.9846 |  |  | -997.7855
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7139 |  |  | 45.5336 |  |  | 38.8337 |  |  | 19.7444 |  |  | -19.5985 |  |  | -83.0529 |  |  | -158.3323 |  |  | -208.2305 |  |  | -239.2335 |  |  | -301.6253
[13 empty] | C Non choked w/ reducers | 7 |  | 7.5502 |  |  | 37.843 |  |  | 106.9899 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.2671 |  |  | 30.9683 |  |  | 80.6741 |  |  | 217.2688 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 7.5502 |  |  | 37.843 |  |  | 106.9899 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.5502 | 42.8277 |  | 25.843 | 208.7935 |  | 83.9899 | 501.1848 |  | 5500 | 956.9455 |  | 5500 | 1573.8231 |  | 5500 | 2343.2081 |  | 5500 | 3127.0203 |  | 5500 | 3815.559 |  | 5500 | 4429.7456 |  | 5500 | 5041.4637
[13 empty] | Next iteration flow rate |  |  | 43.6842 | Abs Value of | Flow this | 210.8815 | Abs Value of | Flow this | 506.1967 | Abs Value of | Flow this | 966.515 | Abs Value of | Flow this | 1589.5613 | Abs Value of | Flow this | 2366.6402 | Abs Value of | Flow this | 3158.2905 | Abs Value of | Flow this | 3853.7146 | Abs Value of | Flow this | 4474.0431 | Abs Value of | Flow this | 5091.8783 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8517 |  |  | 55.4143 |  |  | 48.2625 |  |  | 25.3676 |  |  | -28.4167 |  |  | -132.2424 |  |  | -279.9565 |  |  | -444.6413 |  |  | -619.1075 |  |  | -818.7078
[13 empty] | P2 at this iteration flow rate |  |  | 24.6697 |  |  | 24.9571 |  |  | 26.3875 |  |  | 30.9665 |  |  | 41.7233 |  |  | 62.4885 |  |  | 92.0313 |  |  | 124.9683 |  |  | 159.8615 |  |  | 199.7816
[13 empty] | Delta P at this iteration flow rate |  |  | 32.182 |  |  | 30.4571 |  |  | 21.875 |  |  | -5.5988 |  |  | -70.14 |  |  | -194.7309 |  |  | -371.9878 |  |  | -569.6096 |  |  | -778.969 |  |  | -1018.4894
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7118 |  |  | 45.5091 |  |  | 38.6957 |  |  | 19.264 |  |  | -20.8111 |  |  | -85.4534 |  |  | -162.1714 |  |  | -212.959 |  |  | -244.4901 |  |  | -308.1149
[13 empty] | C Non choked w/ reducers | 7 |  | 7.7016 |  |  | 38.2437 |  |  | 108.564 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.3926 |  |  | 31.2864 |  |  | 81.626 |  |  | 222.1608 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 7.7016 |  |  | 38.2437 |  |  | 108.564 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.7016 | 43.6842 |  | 26.2437 | 210.8815 |  | 85.564 | 506.1967 |  | 5500 | 966.515 |  | 5500 | 1589.5613 |  | 5500 | 2366.6402 |  | 5500 | 3158.2905 |  | 5500 | 3853.7146 |  | 5500 | 4474.0431 |  | 5500 | 5091.8783
[13 empty] | Next iteration flow rate |  |  | 44.5579 | Abs Value of | Flow this | 212.9903 | Abs Value of | Flow this | 511.2587 | Abs Value of | Flow this | 976.1801 | Abs Value of | Flow this | 1605.4569 | Abs Value of | Flow this | 2390.3066 | Abs Value of | Flow this | 3189.8734 | Abs Value of | Flow this | 3892.2518 | Abs Value of | Flow this | 4518.7835 | Abs Value of | Flow this | 5142.7971 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8491 |  |  | 55.3841 |  |  | 48.0885 |  |  | 24.7335 |  |  | -30.1319 |  |  | -136.0445 |  |  | -286.7276 |  |  | -454.7226 |  |  | -632.6956 |  |  | -836.3078
[13 empty] | P2 at this iteration flow rate |  |  | 24.6702 |  |  | 24.9632 |  |  | 26.4223 |  |  | 31.0933 |  |  | 42.0664 |  |  | 63.2489 |  |  | 93.3855 |  |  | 126.9845 |  |  | 162.5791 |  |  | 203.3016
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1789 |  |  | 30.4209 |  |  | 21.6662 |  |  | -6.3598 |  |  | -72.1983 |  |  | -199.2934 |  |  | -380.1132 |  |  | -581.7072 |  |  | -795.2747 |  |  | -1039.6094
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7096 |  |  | 45.4841 |  |  | 38.5549 |  |  | 18.7739 |  |  | -22.0481 |  |  | -87.9021 |  |  | -166.0876 |  |  | -217.7827 |  |  | -249.8523 |  |  | -314.735
[13 empty] | C Non choked w/ reducers | 7 |  | 7.856 |  |  | 38.6491 |  |  | 110.1766 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.5206 |  |  | 31.6079 |  |  | 82.5926 |  |  | 227.292 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 7.856 |  |  | 38.6491 |  |  | 110.1766 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 2.856 | 44.5579 |  | 26.6491 | 212.9903 |  | 87.1766 | 511.2587 |  | 5500 | 976.1801 |  | 5500 | 1605.4569 |  | 5500 | 2390.3066 |  | 5500 | 3189.8734 |  | 5500 | 3892.2518 |  | 5500 | 4518.7835 |  | 5500 | 5142.7971
[13 empty] | Next iteration flow rate |  |  | 45.4491 | Abs Value of | Flow this | 215.1202 | Abs Value of | Flow this | 516.3712 | Abs Value of | Flow this | 985.9419 | Abs Value of | Flow this | 1621.5115 | Abs Value of | Flow this | 2414.2097 | Abs Value of | Flow this | 3221.7722 | Abs Value of | Flow this | 3931.1743 | Abs Value of | Flow this | 4563.9713 | Abs Value of | Flow this | 5194.2251 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8464 |  |  | 55.3533 |  |  | 47.9111 |  |  | 24.0866 |  |  | -31.8815 |  |  | -139.923 |  |  | -293.6349 |  |  | -465.0066 |  |  | -646.5568 |  |  | -854.2616
[13 empty] | P2 at this iteration flow rate |  |  | 24.6707 |  |  | 24.9693 |  |  | 26.4578 |  |  | 31.2227 |  |  | 42.4163 |  |  | 64.0246 |  |  | 94.767 |  |  | 129.0413 |  |  | 165.3514 |  |  | 206.8923
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1757 |  |  | 30.3839 |  |  | 21.4533 |  |  | -7.136 |  |  | -74.2979 |  |  | -203.9477 |  |  | -388.4019 |  |  | -594.0479 |  |  | -811.9082 |  |  | -1061.154
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7074 |  |  | 45.4586 |  |  | 38.4114 |  |  | 18.274 |  |  | -23.3099 |  |  | -90.4 |  |  | -170.0825 |  |  | -222.7032 |  |  | -255.3223 |  |  | -321.4882
[13 empty] | C Non choked w/ reducers | 7 |  | 8.0135 |  |  | 39.0593 |  |  | 111.8292 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.6511 |  |  | 31.9329 |  |  | 83.5743 |  |  | 232.6837 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 8.0135 |  |  | 39.0593 |  |  | 111.8292 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.0135 | 45.4491 |  | 27.0593 | 215.1202 |  | 88.8292 | 516.3712 |  | 5500 | 985.9419 |  | 5500 | 1621.5115 |  | 5500 | 2414.2097 |  | 5500 | 3221.7722 |  | 5500 | 3931.1743 |  | 5500 | 4563.9713 |  | 5500 | 5194.2251
[13 empty] | Next iteration flow rate |  |  | 46.3581 | Abs Value of | Flow this | 217.2714 | Abs Value of | Flow this | 521.535 | Abs Value of | Flow this | 995.8014 | Abs Value of | Flow this | 1637.7266 | Abs Value of | Flow this | 2438.3518 | Abs Value of | Flow this | 3253.9899 | Abs Value of | Flow this | 3970.486 | Abs Value of | Flow this | 4609.611 | Abs Value of | Flow this | 5246.1673 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8436 |  |  | 55.3219 |  |  | 47.7301 |  |  | 23.4268 |  |  | -33.6664 |  |  | -143.8795 |  |  | -300.681 |  |  | -475.4972 |  |  | -660.6966 |  |  | -872.5763
[13 empty] | P2 at this iteration flow rate |  |  | 24.6713 |  |  | 24.9756 |  |  | 26.494 |  |  | 31.3546 |  |  | 42.7733 |  |  | 64.8159 |  |  | 96.1762 |  |  | 131.1394 |  |  | 168.1793 |  |  | 210.5553
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1723 |  |  | 30.3462 |  |  | 21.2361 |  |  | -7.9279 |  |  | -76.4397 |  |  | -208.6954 |  |  | -396.8571 |  |  | -606.6367 |  |  | -828.8759 |  |  | -1083.1316
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7051 |  |  | 45.4326 |  |  | 38.2649 |  |  | 17.7641 |  |  | -24.5971 |  |  | -92.9481 |  |  | -174.1577 |  |  | -227.7227 |  |  | -260.9023 |  |  | -328.3771
[13 empty] | C Non choked w/ reducers | 7 |  | 8.1742 |  |  | 39.4744 |  |  | 113.5236 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.7843 |  |  | 32.2615 |  |  | 84.5714 |  |  | 238.3599 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 8.1742 |  |  | 39.4744 |  |  | 113.5236 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.1742 | 46.3581 |  | 27.4744 | 217.2714 |  | 90.5236 | 521.535 |  | 5500 | 995.8014 |  | 5500 | 1637.7266 |  | 5500 | 2438.3518 |  | 5500 | 3253.9899 |  | 5500 | 3970.486 |  | 5500 | 4609.611 |  | 5500 | 5246.1673
[13 empty] | Next iteration flow rate |  |  | 47.2852 | Abs Value of | Flow this | 219.4441 | Abs Value of | Flow this | 526.7503 | Abs Value of | Flow this | 1005.7594 | Abs Value of | Flow this | 1654.1039 | Abs Value of | Flow this | 2462.7353 | Abs Value of | Flow this | 3286.5298 | Abs Value of | Flow this | 4010.1909 | Abs Value of | Flow this | 4655.7071 | Abs Value of | Flow this | 5298.629 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8406 |  |  | 55.2898 |  |  | 47.5455 |  |  | 22.7536 |  |  | -35.4871 |  |  | -147.9155 |  |  | -307.8687 |  |  | -486.1987 |  |  | -675.1206 |  |  | -891.2591
[13 empty] | P2 at this iteration flow rate |  |  | 24.6719 |  |  | 24.982 |  |  | 26.5309 |  |  | 31.4893 |  |  | 43.1374 |  |  | 65.6231 |  |  | 97.6137 |  |  | 133.2797 |  |  | 171.0641 |  |  | 214.2918
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1688 |  |  | 30.3078 |  |  | 21.0146 |  |  | -8.7356 |  |  | -78.6245 |  |  | -213.5386 |  |  | -405.4824 |  |  | -619.4785 |  |  | -846.1848 |  |  | -1105.5509
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7026 |  |  | 45.4061 |  |  | 38.1155 |  |  | 17.2439 |  |  | -25.9102 |  |  | -95.5475 |  |  | -178.3148 |  |  | -232.8431 |  |  | -266.5944 |  |  | -335.4044
[13 empty] | C Non choked w/ reducers | 7 |  | 8.3382 |  |  | 39.8945 |  |  | 115.2617 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 6.9202 |  |  | 32.5936 |  |  | 85.5843 |  |  | 244.3478 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 8.3382 |  |  | 39.8945 |  |  | 115.2617 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.3382 | 47.2852 |  | 27.8945 | 219.4441 |  | 92.2617 | 526.7503 |  | 5500 | 1005.7594 |  | 5500 | 1654.1039 |  | 5500 | 2462.7353 |  | 5500 | 3286.5298 |  | 5500 | 4010.1909 |  | 5500 | 4655.7071 |  | 5500 | 5298.629
[13 empty] | Next iteration flow rate |  |  | 48.2309 | Abs Value of | Flow this | 221.6385 | Abs Value of | Flow this | 532.0178 | Abs Value of | Flow this | 1015.817 | Abs Value of | Flow this | 1670.6449 | Abs Value of | Flow this | 2487.3626 | Abs Value of | Flow this | 3319.3951 | Abs Value of | Flow this | 4050.2928 | Abs Value of | Flow this | 4702.2642 | Abs Value of | Flow this | 5351.6153 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8376 |  |  | 55.2571 |  |  | 47.3571 |  |  | 22.067 |  |  | -37.3444 |  |  | -152.0326 |  |  | -315.2008 |  |  | -497.1153 |  |  | -689.8346 |  |  | -910.3174
[13 empty] | P2 at this iteration flow rate |  |  | 24.6725 |  |  | 24.9886 |  |  | 26.5686 |  |  | 31.6266 |  |  | 43.5089 |  |  | 66.4465 |  |  | 99.0802 |  |  | 135.4631 |  |  | 174.0069 |  |  | 218.1035
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1651 |  |  | 30.2685 |  |  | 20.7885 |  |  | -9.5596 |  |  | -80.8533 |  |  | -218.4791 |  |  | -414.281 |  |  | -632.5784 |  |  | -863.8415 |  |  | -1128.4209
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.7001 |  |  | 45.379 |  |  | 37.9631 |  |  | 16.7132 |  |  | -27.2497 |  |  | -98.1991 |  |  | -182.5554 |  |  | -238.0664 |  |  | -272.4009 |  |  | -342.573
[13 empty] | C Non choked w/ reducers | 7 |  | 8.5054 |  |  | 40.3195 |  |  | 117.0455 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 7.0588 |  |  | 32.9294 |  |  | 86.6135 |  |  | 250.6785 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 8.5054 |  |  | 40.3195 |  |  | 117.0455 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.5054 | 48.2309 |  | 28.3195 | 221.6385 |  | 94.0455 | 532.0178 |  | 5500 | 1015.817 |  | 5500 | 1670.6449 |  | 5500 | 2487.3626 |  | 5500 | 3319.3951 |  | 5500 | 4050.2928 |  | 5500 | 4702.2642 |  | 5500 | 5351.6153
[13 empty] | Next iteration flow rate |  |  | 49.1955 | Abs Value of | Flow this | 223.8549 | Abs Value of | Flow this | 537.338 | Abs Value of | Flow this | 1025.9751 | Abs Value of | Flow this | 1687.3514 | Abs Value of | Flow this | 2512.2363 | Abs Value of | Flow this | 3352.589 | Abs Value of | Flow this | 4090.7957 | Abs Value of | Flow this | 4749.2869 | Abs Value of | Flow this | 5405.1315 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8344 |  |  | 55.2238 |  |  | 47.165 |  |  | 21.3665 |  |  | -39.239 |  |  | -156.2325 |  |  | -322.6804 |  |  | -508.2514 |  |  | -704.8443 |  |  | -929.7588
[13 empty] | P2 at this iteration flow rate |  |  | 24.6731 |  |  | 24.9952 |  |  | 26.607 |  |  | 31.7667 |  |  | 43.8878 |  |  | 67.2865 |  |  | 100.5761 |  |  | 137.6903 |  |  | 177.0089 |  |  | 221.9918
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1613 |  |  | 30.2285 |  |  | 20.558 |  |  | -10.4002 |  |  | -83.1268 |  |  | -223.519 |  |  | -423.2565 |  |  | -645.9416 |  |  | -881.8531 |  |  | -1151.7506
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6975 |  |  | 45.3514 |  |  | 37.8076 |  |  | 16.1719 |  |  | -28.6161 |  |  | -100.904 |  |  | -186.8813 |  |  | -243.3947 |  |  | -278.3241 |  |  | -349.8858
[13 empty] | C Non choked w/ reducers | 7 |  | 8.6761 |  |  | 40.7496 |  |  | 118.877 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 7.2002 |  |  | 33.2688 |  |  | 87.6593 |  |  | 257.3878 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 8.6761 |  |  | 40.7496 |  |  | 118.877 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.6761 | 49.1955 |  | 28.7496 | 223.8549 |  | 95.877 | 537.338 |  | 5500 | 1025.9751 |  | 5500 | 1687.3514 |  | 5500 | 2512.2363 |  | 5500 | 3352.589 |  | 5500 | 4090.7957 |  | 5500 | 4749.2869 |  | 5500 | 5405.1315
[13 empty] | Next iteration flow rate |  |  | 50.1794 | Abs Value of | Flow this | 226.0935 | Abs Value of | Flow this | 542.7114 | Abs Value of | Flow this | 1036.2349 | Abs Value of | Flow this | 1704.2249 | Abs Value of | Flow this | 2537.3586 | Abs Value of | Flow this | 3386.1149 | Abs Value of | Flow this | 4131.7037 | Abs Value of | Flow this | 4796.7797 | Abs Value of | Flow this | 5459.1828 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8311 |  |  | 55.1898 |  |  | 46.969 |  |  | 20.652 |  |  | -41.1717 |  |  | -160.5168 |  |  | -330.3103 |  |  | -519.6112 |  |  | -720.1556 |  |  | -949.591
[13 empty] | P2 at this iteration flow rate |  |  | 24.6738 |  |  | 25.002 |  |  | 26.6462 |  |  | 31.9096 |  |  | 44.2743 |  |  | 68.1434 |  |  | 102.1021 |  |  | 139.9622 |  |  | 180.0711 |  |  | 225.9582
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1573 |  |  | 30.1877 |  |  | 20.3228 |  |  | -11.2577 |  |  | -85.4461 |  |  | -228.6601 |  |  | -432.4123 |  |  | -659.5735 |  |  | -900.2268 |  |  | -1175.5492
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6947 |  |  | 45.3233 |  |  | 37.649 |  |  | 15.6197 |  |  | -30.0099 |  |  | -103.6633 |  |  | -191.2942 |  |  | -248.8301 |  |  | -284.3664 |  |  | -357.3454
[13 empty] | C Non choked w/ reducers | 7 |  | 8.8501 |  |  | 41.185 |  |  | 120.7585 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 7.3444 |  |  | 33.6119 |  |  | 88.7222 |  |  | 264.517 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 8.8501 |  |  | 41.185 |  |  | 120.7585 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 3.8501 | 50.1794 |  | 29.185 | 226.0935 |  | 97.7585 | 542.7114 |  | 5500 | 1036.2349 |  | 5500 | 1704.2249 |  | 5500 | 2537.3586 |  | 5500 | 3386.1149 |  | 5500 | 4131.7037 |  | 5500 | 4796.7797 |  | 5500 | 5459.1828
[13 empty] | Next iteration flow rate |  |  | 51.183 | Abs Value of | Flow this | 228.3544 | Abs Value of | Flow this | 548.1385 | Abs Value of | Flow this | 1046.5972 | Abs Value of | Flow this | 1721.2671 | Abs Value of | Flow this | 2562.7322 | Abs Value of | Flow this | 3419.9761 | Abs Value of | Flow this | 4173.0207 | Abs Value of | Flow this | 4844.7475 | Abs Value of | Flow this | 5513.7746 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8277 |  |  | 55.1551 |  |  | 46.769 |  |  | 19.923 |  |  | -43.1433 |  |  | -164.8872 |  |  | -338.0935 |  |  | -531.1994 |  |  | -735.7748 |  |  | -969.8218
[13 empty] | P2 at this iteration flow rate |  |  | 24.6745 |  |  | 25.009 |  |  | 26.6862 |  |  | 32.0554 |  |  | 44.6687 |  |  | 69.0174 |  |  | 103.6587 |  |  | 142.2799 |  |  | 183.195 |  |  | 230.0044
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1532 |  |  | 30.1461 |  |  | 20.0828 |  |  | -12.1324 |  |  | -87.812 |  |  | -233.9046 |  |  | -441.7522 |  |  | -673.4793 |  |  | -918.9698 |  |  | -1199.8262
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6919 |  |  | 45.2945 |  |  | 37.4873 |  |  | 15.0564 |  |  | -31.4318 |  |  | -106.478 |  |  | -195.7958 |  |  | -254.3747 |  |  | -290.5301 |  |  | -364.9551
[13 empty] | C Non choked w/ reducers | 7 |  | 9.0277 |  |  | 41.6255 |  |  | 122.6925 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 7.4915 |  |  | 33.9588 |  |  | 89.8026 |  |  | 272.1139 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 9.0277 |  |  | 41.6255 |  |  | 122.6925 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.0277 | 51.183 |  | 29.6255 | 228.3544 |  | 99.6925 | 548.1385 |  | 5500 | 1046.5972 |  | 5500 | 1721.2671 |  | 5500 | 2562.7322 |  | 5500 | 3419.9761 |  | 5500 | 4173.0207 |  | 5500 | 4844.7475 |  | 5500 | 5513.7746
[13 empty] | Next iteration flow rate |  |  | 52.2067 | Abs Value of | Flow this | 230.638 | Abs Value of | Flow this | 553.6199 | Abs Value of | Flow this | 1057.0632 | Abs Value of | Flow this | 1738.4798 | Abs Value of | Flow this | 2588.3595 | Abs Value of | Flow this | 3454.1758 | Abs Value of | Flow this | 4214.7509 | Abs Value of | Flow this | 4893.195 | Abs Value of | Flow this | 5568.9124 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8241 |  |  | 55.1197 |  |  | 46.5651 |  |  | 19.1795 |  |  | -45.1545 |  |  | -169.3454 |  |  | -346.0332 |  |  | -543.0206 |  |  | -751.7079 |  |  | -990.4592
[13 empty] | P2 at this iteration flow rate |  |  | 24.6752 |  |  | 25.0161 |  |  | 26.727 |  |  | 32.2041 |  |  | 45.0709 |  |  | 69.9091 |  |  | 105.2466 |  |  | 144.6441 |  |  | 186.3816 |  |  | 234.1318
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1489 |  |  | 30.1036 |  |  | 19.8381 |  |  | -13.0246 |  |  | -90.2254 |  |  | -239.2545 |  |  | -451.2799 |  |  | -687.6647 |  |  | -938.0895 |  |  | -1224.5911
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6889 |  |  | 45.2652 |  |  | 37.3222 |  |  | 14.4818 |  |  | -32.8822 |  |  | -109.3493 |  |  | -200.3878 |  |  | -260.0308 |  |  | -296.8178 |  |  | -372.7176
[13 empty] | C Non choked w/ reducers | 7 |  | 9.2089 |  |  | 42.0714 |  |  | 124.6815 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 7.6416 |  |  | 34.3095 |  |  | 90.9009 |  |  | 280.2346 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 9.2089 |  |  | 42.0714 |  |  | 124.6815 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.2089 | 52.2067 |  | 30.0714 | 230.638 |  | 101.6815 | 553.6199 |  | 5500 | 1057.0632 |  | 5500 | 1738.4798 |  | 5500 | 2588.3595 |  | 5500 | 3454.1758 |  | 5500 | 4214.7509 |  | 5500 | 4893.195 |  | 5500 | 5568.9124
[13 empty] | Next iteration flow rate |  |  | 53.2508 | Abs Value of | Flow this | 232.9443 | Abs Value of | Flow this | 559.1561 | Abs Value of | Flow this | 1067.6338 | Abs Value of | Flow this | 1755.8646 | Abs Value of | Flow this | 2614.2431 | Abs Value of | Flow this | 3488.7176 | Abs Value of | Flow this | 4256.8985 | Abs Value of | Flow this | 4942.127 | Abs Value of | Flow this | 5624.6015 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8204 |  |  | 55.0836 |  |  | 46.357 |  |  | 18.421 |  |  | -47.2061 |  |  | -173.8933 |  |  | -354.1325 |  |  | -555.0793 |  |  | -767.9612 |  |  | -1011.5115
[13 empty] | P2 at this iteration flow rate |  |  | 24.6759 |  |  | 25.0233 |  |  | 26.7686 |  |  | 32.3558 |  |  | 45.4812 |  |  | 70.8187 |  |  | 106.8665 |  |  | 147.0559 |  |  | 189.6322 |  |  | 238.3423
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1445 |  |  | 30.0603 |  |  | 19.5884 |  |  | -13.9348 |  |  | -92.6874 |  |  | -244.7119 |  |  | -460.999 |  |  | -702.1351 |  |  | -957.5935 |  |  | -1249.8538
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6859 |  |  | 45.2353 |  |  | 37.1539 |  |  | 13.8956 |  |  | -34.3618 |  |  | -112.2783 |  |  | -205.0721 |  |  | -265.8005 |  |  | -303.2318 |  |  | -380.6363
[13 empty] | C Non choked w/ reducers | 7 |  | 9.3937 |  |  | 42.5228 |  |  | 126.7283 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 7.7947 |  |  | 34.664 |  |  | 92.0177 |  |  | 288.9451 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 9.3937 |  |  | 42.5228 |  |  | 126.7283 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.3937 | 53.2508 |  | 30.5228 | 232.9443 |  | 103.7283 | 559.1561 |  | 5500 | 1067.6338 |  | 5500 | 1755.8646 |  | 5500 | 2614.2431 |  | 5500 | 3488.7176 |  | 5500 | 4256.8985 |  | 5500 | 4942.127 |  | 5500 | 5624.6015
[13 empty] | Next iteration flow rate |  |  | 54.3158 | Abs Value of | Flow this | 235.2738 | Abs Value of | Flow this | 564.7476 | Abs Value of | Flow this | 1078.3102 | Abs Value of | Flow this | 1773.4232 | Abs Value of | Flow this | 2640.3856 | Abs Value of | Flow this | 3523.6048 | Abs Value of | Flow this | 4299.4674 | Abs Value of | Flow this | 4991.5482 | Abs Value of | Flow this | 5680.8475 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8165 |  |  | 55.0467 |  |  | 46.1448 |  |  | 17.6472 |  |  | -49.299 |  |  | -178.5326 |  |  | -362.3946 |  |  | -567.3804 |  |  | -784.5413 |  |  | -1032.9869
[13 empty] | P2 at this iteration flow rate |  |  | 24.6767 |  |  | 25.0307 |  |  | 26.811 |  |  | 32.5106 |  |  | 45.8998 |  |  | 71.7465 |  |  | 108.5189 |  |  | 149.5161 |  |  | 192.9483 |  |  | 242.6374
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1398 |  |  | 30.0161 |  |  | 19.3337 |  |  | -14.8633 |  |  | -95.1988 |  |  | -250.2791 |  |  | -470.9135 |  |  | -716.8965 |  |  | -977.4895 |  |  | -1275.6242
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6827 |  |  | 45.2049 |  |  | 36.9821 |  |  | 13.2976 |  |  | -35.8712 |  |  | -115.2662 |  |  | -209.8506 |  |  | -271.6863 |  |  | -309.7747 |  |  | -388.714
[13 empty] | C Non choked w/ reducers | 7 |  | 9.5823 |  |  | 42.9796 |  |  | 128.8359 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 7.9508 |  |  | 35.0225 |  |  | 93.1534 |  |  | 298.3238 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 9.5823 |  |  | 42.9796 |  |  | 128.8359 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.5823 | 54.3158 |  | 30.9796 | 235.2738 |  | 105.8359 | 564.7476 |  | 5500 | 1078.3102 |  | 5500 | 1773.4232 |  | 5500 | 2640.3856 |  | 5500 | 3523.6048 |  | 5500 | 4299.4674 |  | 5500 | 4991.5482 |  | 5500 | 5680.8475
[13 empty] | Next iteration flow rate |  |  | 55.4022 | Abs Value of | Flow this | 237.6265 | Abs Value of | Flow this | 570.3951 | Abs Value of | Flow this | 1089.0933 | Abs Value of | Flow this | 1791.1575 | Abs Value of | Flow this | 2666.7894 | Abs Value of | Flow this | 3558.8408 | Abs Value of | Flow this | 4342.4621 | Abs Value of | Flow this | 5041.4637 | Abs Value of | Flow this | 5737.656 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8125 |  |  | 55.0091 |  |  | 45.9283 |  |  | 16.8579 |  |  | -51.4339 |  |  | -183.2651 |  |  | -370.8227 |  |  | -579.9287 |  |  | -801.4546 |  |  | -1054.8939
[13 empty] | P2 at this iteration flow rate |  |  | 24.6775 |  |  | 25.0382 |  |  | 26.8543 |  |  | 32.6684 |  |  | 46.3268 |  |  | 72.693 |  |  | 110.2045 |  |  | 152.0257 |  |  | 196.3309 |  |  | 247.0188
[13 empty] | Delta P at this iteration flow rate |  |  | 32.135 |  |  | 29.971 |  |  | 19.0739 |  |  | -15.8105 |  |  | -97.7607 |  |  | -255.9581 |  |  | -481.0273 |  |  | -731.9545 |  |  | -997.7855 |  |  | -1301.9127
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6793 |  |  | 45.1737 |  |  | 36.807 |  |  | 12.6877 |  |  | -37.4109 |  |  | -118.3142 |  |  | -214.7252 |  |  | -277.6903 |  |  | -316.4491 |  |  | -396.9542
[13 empty] | C Non choked w/ reducers | 7 |  | 9.7747 |  |  | 43.442 |  |  | 131.0074 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 8.1101 |  |  | 35.3849 |  |  | 94.3086 |  |  | 308.4649 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 9.7747 |  |  | 43.442 |  |  | 131.0074 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.7747 | 55.4022 |  | 31.442 | 237.6265 |  | 108.0074 | 570.3951 |  | 5500 | 1089.0933 |  | 5500 | 1791.1575 |  | 5500 | 2666.7894 |  | 5500 | 3558.8408 |  | 5500 | 4342.4621 |  | 5500 | 5041.4637 |  | 5500 | 5737.656
[13 empty] | Next iteration flow rate |  |  | 56.5102 | Abs Value of | Flow this | 240.0028 | Abs Value of | Flow this | 576.0991 | Abs Value of | Flow this | 1099.9842 | Abs Value of | Flow this | 1809.0691 | Abs Value of | Flow this | 2693.4573 | Abs Value of | Flow this | 3594.4292 | Abs Value of | Flow this | 4385.8867 | Abs Value of | Flow this | 5091.8783 | Abs Value of | Flow this | 5795.0325 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8083 |  |  | 54.9708 |  |  | 45.7074 |  |  | 16.0527 |  |  | -53.6117 |  |  | -188.0927 |  |  | -379.4203 |  |  | -592.7293 |  |  | -818.7078 |  |  | -1077.2413
[13 empty] | P2 at this iteration flow rate |  |  | 24.6783 |  |  | 25.0458 |  |  | 26.8985 |  |  | 32.8295 |  |  | 46.7623 |  |  | 73.6585 |  |  | 111.9241 |  |  | 154.5859 |  |  | 199.7816 |  |  | 251.4883
[13 empty] | Delta P at this iteration flow rate |  |  | 32.13 |  |  | 29.925 |  |  | 18.8089 |  |  | -16.7767 |  |  | -100.3741 |  |  | -261.7513 |  |  | -491.3443 |  |  | -747.3152 |  |  | -1018.4894 |  |  | -1328.7296
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6759 |  |  | 45.142 |  |  | 36.6283 |  |  | 12.0654 |  |  | -38.9815 |  |  | -121.4234 |  |  | -219.6977 |  |  | -283.815 |  |  | -323.2577 |  |  | -405.3599
[13 empty] | C Non choked w/ reducers | 7 |  | 9.9709 |  |  | 43.9102 |  |  | 133.2465 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 8.2726 |  |  | 35.7513 |  |  | 95.4837 |  |  | 319.4821 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 9.9709 |  |  | 43.9102 |  |  | 133.2465 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 4.9709 | 56.5102 |  | 31.9102 | 240.0028 |  | 110.2465 | 576.0991 |  | 5500 | 1099.9842 |  | 5500 | 1809.0691 |  | 5500 | 2693.4573 |  | 5500 | 3594.4292 |  | 5500 | 4385.8867 |  | 5500 | 5091.8783 |  | 5500 | 5795.0325
[13 empty] | Next iteration flow rate |  |  | 57.6404 | Abs Value of | Flow this | 242.4028 | Abs Value of | Flow this | 581.86 | Abs Value of | Flow this | 1110.9841 | Abs Value of | Flow this | 1827.1597 | Abs Value of | Flow this | 2720.3919 | Abs Value of | Flow this | 3630.3735 | Abs Value of | Flow this | 4429.7456 | Abs Value of | Flow this | 5142.7971 | Abs Value of | Flow this | 5852.9829 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.8039 |  |  | 54.9317 |  |  | 45.4821 |  |  | 15.2314 |  |  | -55.8334 |  |  | -193.0174 |  |  | -388.1906 |  |  | -605.7872 |  |  | -836.3078 |  |  | -1100.0379
[13 empty] | P2 at this iteration flow rate |  |  | 24.6792 |  |  | 25.0537 |  |  | 26.9436 |  |  | 32.9937 |  |  | 47.2067 |  |  | 74.6435 |  |  | 113.6781 |  |  | 157.1974 |  |  | 203.3016 |  |  | 256.0476
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1247 |  |  | 29.878 |  |  | 18.5386 |  |  | -17.7623 |  |  | -103.04 |  |  | -267.6609 |  |  | -501.8688 |  |  | -762.9846 |  |  | -1039.6094 |  |  | -1356.0854
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6723 |  |  | 45.1096 |  |  | 36.446 |  |  | 11.4307 |  |  | -40.5837 |  |  | -124.5951 |  |  | -224.7701 |  |  | -290.0629 |  |  | -330.2032 |  |  | -413.9346
[13 empty] | C Non choked w/ reducers | 7 |  | 10.1712 |  |  | 44.3841 |  |  | 135.5567 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 8.4384 |  |  | 36.1217 |  |  | 96.6795 |  |  | 331.5149 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 10.1712 |  |  | 44.3841 |  |  | 135.5567 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5.1712 | 57.6404 |  | 32.3841 | 242.4028 |  | 112.5567 | 581.86 |  | 5500 | 1110.9841 |  | 5500 | 1827.1597 |  | 5500 | 2720.3919 |  | 5500 | 3630.3735 |  | 5500 | 4429.7456 |  | 5500 | 5142.7971 |  | 5500 | 5852.9829
[13 empty] | Next iteration flow rate |  |  | 58.7932 | Abs Value of | Flow this | 244.8268 | Abs Value of | Flow this | 587.6786 | Abs Value of | Flow this | 1122.0939 | Abs Value of | Flow this | 1845.4313 | Abs Value of | Flow this | 2747.5958 | Abs Value of | Flow this | 3666.6772 | Abs Value of | Flow this | 4474.0431 | Abs Value of | Flow this | 5194.2251 | Abs Value of | Flow this | 5911.5127 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7994 |  |  | 54.8918 |  |  | 45.2523 |  |  | 14.3935 |  |  | -58.0996 |  |  | -198.0411 |  |  | -397.1373 |  |  | -619.1075 |  |  | -854.2616 |  |  | -1123.2926
[13 empty] | P2 at this iteration flow rate |  |  | 24.6801 |  |  | 25.0616 |  |  | 26.9895 |  |  | 33.1613 |  |  | 47.6599 |  |  | 75.6482 |  |  | 115.4675 |  |  | 159.8615 |  |  | 206.8923 |  |  | 260.6985
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1193 |  |  | 29.8302 |  |  | 18.2628 |  |  | -18.7678 |  |  | -105.7595 |  |  | -273.6893 |  |  | -512.6047 |  |  | -778.969 |  |  | -1061.154 |  |  | -1383.9912
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6685 |  |  | 45.0766 |  |  | 36.26 |  |  | 10.7832 |  |  | -42.2181 |  |  | -127.8306 |  |  | -229.9446 |  |  | -296.4363 |  |  | -337.2882 |  |  | -422.6817
[13 empty] | C Non choked w/ reducers | 7 |  | 10.3755 |  |  | 44.8639 |  |  | 137.9421 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 8.6075 |  |  | 36.4963 |  |  | 97.8963 |  |  | 344.7363 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 10.3755 |  |  | 44.8639 |  |  | 137.9421 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5.3755 | 58.7932 |  | 32.8639 | 244.8268 |  | 114.9421 | 587.6786 |  | 5500 | 1122.0939 |  | 5500 | 1845.4313 |  | 5500 | 2747.5958 |  | 5500 | 3666.6772 |  | 5500 | 4474.0431 |  | 5500 | 5194.2251 |  | 5500 | 5911.5127
[13 empty] | Next iteration flow rate |  |  | 59.9691 | Abs Value of | Flow this | 247.2751 | Abs Value of | Flow this | 593.5554 | Abs Value of | Flow this | 1133.3148 | Abs Value of | Flow this | 1863.8857 | Abs Value of | Flow this | 2775.0718 | Abs Value of | Flow this | 3703.344 | Abs Value of | Flow this | 4518.7835 | Abs Value of | Flow this | 5246.1673 | Abs Value of | Flow this | 5970.6278 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7947 |  |  | 54.8511 |  |  | 45.0179 |  |  | 13.5388 |  |  | -60.4114 |  |  | -203.1657 |  |  | -406.2638 |  |  | -632.6956 |  |  | -872.5763 |  |  | -1147.0148
[13 empty] | P2 at this iteration flow rate |  |  | 24.6811 |  |  | 25.0698 |  |  | 27.0364 |  |  | 33.3322 |  |  | 48.1223 |  |  | 76.6731 |  |  | 117.2928 |  |  | 162.5791 |  |  | 210.5553 |  |  | 265.443
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1136 |  |  | 29.7814 |  |  | 17.9814 |  |  | -19.7934 |  |  | -108.5337 |  |  | -279.8388 |  |  | -523.5565 |  |  | -795.2747 |  |  | -1083.1316 |  |  | -1412.4578
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6646 |  |  | 45.0429 |  |  | 36.0703 |  |  | 10.1227 |  |  | -43.8853 |  |  | -131.1311 |  |  | -235.223 |  |  | -302.9378 |  |  | -344.5157 |  |  | -431.6046
[13 empty] | C Non choked w/ reducers | 7 |  | 10.5839 |  |  | 45.3496 |  |  | 140.4072 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 8.7801 |  |  | 36.8751 |  |  | 99.1349 |  |  | 359.3638 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 10.5839 |  |  | 45.3496 |  |  | 140.4072 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5.5839 | 59.9691 |  | 33.3496 | 247.2751 |  | 117.4072 | 593.5554 |  | 5500 | 1133.3148 |  | 5500 | 1863.8857 |  | 5500 | 2775.0718 |  | 5500 | 3703.344 |  | 5500 | 4518.7835 |  | 5500 | 5246.1673 |  | 5500 | 5970.6278
[13 empty] | Next iteration flow rate |  |  | 61.1685 | Abs Value of | Flow this | 249.7479 | Abs Value of | Flow this | 599.491 | Abs Value of | Flow this | 1144.648 | Abs Value of | Flow this | 1882.5245 | Abs Value of | Flow this | 2802.8225 | Abs Value of | Flow this | 3740.3775 | Abs Value of | Flow this | 4563.9713 | Abs Value of | Flow this | 5298.629 | Abs Value of | Flow this | 6030.3341 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7898 |  |  | 54.8096 |  |  | 44.7787 |  |  | 12.6669 |  |  | -62.7697 |  |  | -208.3933 |  |  | -415.5737 |  |  | -646.5568 |  |  | -891.2591 |  |  | -1171.2139
[13 empty] | P2 at this iteration flow rate |  |  | 24.682 |  |  | 25.0781 |  |  | 27.0843 |  |  | 33.5066 |  |  | 48.5939 |  |  | 77.7187 |  |  | 119.1547 |  |  | 165.3514 |  |  | 214.2918 |  |  | 270.2828
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1077 |  |  | 29.7316 |  |  | 17.6945 |  |  | -20.8397 |  |  | -111.3637 |  |  | -286.112 |  |  | -534.7284 |  |  | -811.9082 |  |  | -1105.5509 |  |  | -1441.4966
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6605 |  |  | 45.0086 |  |  | 35.8768 |  |  | 9.4489 |  |  | -45.5861 |  |  | -134.4979 |  |  | -240.6075 |  |  | -309.57 |  |  | -351.8884 |  |  | -440.7068
[13 empty] | C Non choked w/ reducers | 7 |  | 10.7966 |  |  | 45.8415 |  |  | 142.9567 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 8.956 |  |  | 37.258 |  |  | 100.396 |  |  | 375.6756 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 10.7966 |  |  | 45.8415 |  |  | 142.9567 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5.7966 | 61.1685 |  | 33.8415 | 249.7479 |  | 119.9567 | 599.491 |  | 5500 | 1144.648 |  | 5500 | 1882.5245 |  | 5500 | 2802.8225 |  | 5500 | 3740.3775 |  | 5500 | 4563.9713 |  | 5500 | 5298.629 |  | 5500 | 6030.3341
[13 empty] | Next iteration flow rate |  |  | 62.3918 | Abs Value of | Flow this | 252.2453 | Abs Value of | Flow this | 605.4859 | Abs Value of | Flow this | 1156.0945 | Abs Value of | Flow this | 1901.3498 | Abs Value of | Flow this | 2830.8507 | Abs Value of | Flow this | 3777.7812 | Abs Value of | Flow this | 4609.611 | Abs Value of | Flow this | 5351.6153 | Abs Value of | Flow this | 6090.6374 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7847 |  |  | 54.7673 |  |  | 44.5347 |  |  | 11.7775 |  |  | -65.1754 |  |  | -213.7261 |  |  | -425.0707 |  |  | -660.6966 |  |  | -910.3174 |  |  | -1195.8993
[13 empty] | P2 at this iteration flow rate |  |  | 24.6831 |  |  | 25.0865 |  |  | 27.1331 |  |  | 33.6845 |  |  | 49.0751 |  |  | 78.7852 |  |  | 121.0541 |  |  | 168.1793 |  |  | 218.1035 |  |  | 275.2199
[13 empty] | Delta P at this iteration flow rate |  |  | 32.1016 |  |  | 29.6807 |  |  | 17.4017 |  |  | -21.907 |  |  | -114.2505 |  |  | -292.5113 |  |  | -546.1249 |  |  | -828.8759 |  |  | -1128.4209 |  |  | -1471.1191
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6563 |  |  | 44.9735 |  |  | 35.6794 |  |  | 8.7616 |  |  | -47.321 |  |  | -137.9324 |  |  | -246.1003 |  |  | -316.3355 |  |  | -359.4093 |  |  | -449.992
[13 empty] | C Non choked w/ reducers | 7 |  | 11.0136 |  |  | 46.3395 |  |  | 145.5957 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 9.1356 |  |  | 37.6453 |  |  | 101.68 |  |  | 394.0344 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 11.0136 |  |  | 46.3395 |  |  | 145.5957 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 6.0136 | 62.3918 |  | 34.3395 | 252.2453 |  | 122.5957 | 605.4859 |  | 5500 | 1156.0945 |  | 5500 | 1901.3498 |  | 5500 | 2830.8507 |  | 5500 | 3777.7812 |  | 5500 | 4609.611 |  | 5500 | 5351.6153 |  | 5500 | 6090.6374
[13 empty] | Next iteration flow rate |  |  | 63.6397 | Abs Value of | Flow this | 254.7678 | Abs Value of | Flow this | 611.5408 | Abs Value of | Flow this | 1167.6554 | Abs Value of | Flow this | 1920.3633 | Abs Value of | Flow this | 2859.1592 | Abs Value of | Flow this | 3815.559 | Abs Value of | Flow this | 4655.7071 | Abs Value of | Flow this | 5405.1315 | Abs Value of | Flow this | 6151.5438 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7794 |  |  | 54.7241 |  |  | 44.2859 |  |  | 10.8702 |  |  | -67.6295 |  |  | -219.166 |  |  | -434.7587 |  |  | -675.1206 |  |  | -929.7588 |  |  | -1221.0809
[13 empty] | P2 at this iteration flow rate |  |  | 24.6841 |  |  | 25.0952 |  |  | 27.1828 |  |  | 33.866 |  |  | 49.5659 |  |  | 79.8732 |  |  | 122.9917 |  |  | 171.0641 |  |  | 221.9918 |  |  | 280.2562
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0952 |  |  | 29.6289 |  |  | 17.1031 |  |  | -22.9957 |  |  | -117.1953 |  |  | -299.0392 |  |  | -557.7504 |  |  | -846.1848 |  |  | -1151.7506 |  |  | -1501.337
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6519 |  |  | 44.9378 |  |  | 35.478 |  |  | 8.0604 |  |  | -49.0909 |  |  | -141.4359 |  |  | -251.7034 |  |  | -323.237 |  |  | -367.0814 |  |  | -459.4638
[13 empty] | C Non choked w/ reducers | 7 |  | 11.235 |  |  | 46.8438 |  |  | 148.33 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 9.3187 |  |  | 38.0368 |  |  | 102.9879 |  |  | 414.9231 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 11.235 |  |  | 46.8438 |  |  | 148.33 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 6.235 | 63.6397 |  | 34.8438 | 254.7678 |  | 125.33 | 611.5408 |  | 5500 | 1167.6554 |  | 5500 | 1920.3633 |  | 5500 | 2859.1592 |  | 5500 | 3815.559 |  | 5500 | 4655.7071 |  | 5500 | 5405.1315 |  | 5500 | 6151.5438
[13 empty] | Next iteration flow rate |  |  | 64.9125 | Abs Value of | Flow this | 257.3155 | Abs Value of | Flow this | 617.6562 | Abs Value of | Flow this | 1179.332 | Abs Value of | Flow this | 1939.5669 | Abs Value of | Flow this | 2887.7508 | Abs Value of | Flow this | 3853.7146 | Abs Value of | Flow this | 4702.2642 | Abs Value of | Flow this | 5459.1828 | Abs Value of | Flow this | 6213.0592 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7738 |  |  | 54.68 |  |  | 44.032 |  |  | 9.9447 |  |  | -70.1328 |  |  | -224.7152 |  |  | -444.6413 |  |  | -689.8346 |  |  | -949.591 |  |  | -1246.7686
[13 empty] | P2 at this iteration flow rate |  |  | 24.6852 |  |  | 25.104 |  |  | 27.2336 |  |  | 34.0511 |  |  | 50.0666 |  |  | 80.983 |  |  | 124.9683 |  |  | 174.0069 |  |  | 225.9582 |  |  | 285.3937
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0886 |  |  | 29.576 |  |  | 16.7984 |  |  | -24.1063 |  |  | -120.1994 |  |  | -305.6983 |  |  | -569.6096 |  |  | -863.8415 |  |  | -1175.5492 |  |  | -1532.1623
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6473 |  |  | 44.9013 |  |  | 35.2726 |  |  | 7.3452 |  |  | -50.8963 |  |  | -145.0099 |  |  | -257.4192 |  |  | -330.2772 |  |  | -374.9077 |  |  | -469.1261
[13 empty] | C Non choked w/ reducers | 7 |  | 11.4608 |  |  | 47.3545 |  |  | 151.1656 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 9.5056 |  |  | 38.4328 |  |  | 104.3202 |  |  | 439.0021 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 11.4608 |  |  | 47.3545 |  |  | 151.1656 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 6.4608 | 64.9125 |  | 35.3545 | 257.3155 |  | 128.1656 | 617.6562 |  | 5500 | 1179.332 |  | 5500 | 1939.5669 |  | 5500 | 2887.7508 |  | 5500 | 3853.7146 |  | 5500 | 4702.2642 |  | 5500 | 5459.1828 |  | 5500 | 6213.0592
[13 empty] | Next iteration flow rate |  |  | 66.2107 | Abs Value of | Flow this | 259.8886 | Abs Value of | Flow this | 623.8327 | Abs Value of | Flow this | 1191.1253 | Abs Value of | Flow this | 1958.9626 | Abs Value of | Flow this | 2916.6283 | Abs Value of | Flow this | 3892.2518 | Abs Value of | Flow this | 4749.2869 | Abs Value of | Flow this | 5513.7746 | Abs Value of | Flow this | 6275.1898 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7681 |  |  | 54.6351 |  |  | 43.773 |  |  | 9.0006 |  |  | -72.6865 |  |  | -230.376 |  |  | -454.7226 |  |  | -704.8443 |  |  | -969.8218 |  |  | -1272.9727
[13 empty] | P2 at this iteration flow rate |  |  | 24.6864 |  |  | 25.113 |  |  | 27.2854 |  |  | 34.2399 |  |  | 50.5773 |  |  | 82.1152 |  |  | 126.9845 |  |  | 177.0089 |  |  | 230.0044 |  |  | 290.6345
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0817 |  |  | 29.5221 |  |  | 16.4876 |  |  | -25.2393 |  |  | -123.2638 |  |  | -312.4912 |  |  | -581.7072 |  |  | -881.8531 |  |  | -1199.8262 |  |  | -1563.6072
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6426 |  |  | 44.8641 |  |  | 35.063 |  |  | 6.6156 |  |  | -52.738 |  |  | -148.6557 |  |  | -263.2499 |  |  | -337.4589 |  |  | -382.8914 |  |  | -478.9825
[13 empty] | C Non choked w/ reducers | 7 |  | 11.6913 |  |  | 47.8717 |  |  | 154.1094 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 9.6962 |  |  | 38.8332 |  |  | 105.6778 |  |  | 467.2033 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 11.6913 |  |  | 47.8717 |  |  | 154.1094 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 6.6913 | 66.2107 |  | 35.8717 | 259.8886 |  | 131.1094 | 623.8327 |  | 5500 | 1191.1253 |  | 5500 | 1958.9626 |  | 5500 | 2916.6283 |  | 5500 | 3892.2518 |  | 5500 | 4749.2869 |  | 5500 | 5513.7746 |  | 5500 | 6275.1898
[13 empty] | Next iteration flow rate |  |  | 67.5349 | Abs Value of | Flow this | 262.4875 | Abs Value of | Flow this | 630.071 | Abs Value of | Flow this | 1203.0365 | Abs Value of | Flow this | 1978.5522 | Abs Value of | Flow this | 2945.7946 | Abs Value of | Flow this | 3931.1743 | Abs Value of | Flow this | 4796.7797 | Abs Value of | Flow this | 5568.9124 | Abs Value of | Flow this | 6337.9417 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7621 |  |  | 54.5892 |  |  | 43.5089 |  |  | 8.0375 |  |  | -75.2915 |  |  | -236.1506 |  |  | -465.0066 |  |  | -720.1556 |  |  | -990.4592 |  |  | -1299.7034
[13 empty] | P2 at this iteration flow rate |  |  | 24.6876 |  |  | 25.1222 |  |  | 27.3382 |  |  | 34.4325 |  |  | 51.0983 |  |  | 83.2701 |  |  | 129.0413 |  |  | 180.0711 |  |  | 234.1318 |  |  | 295.9807
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0745 |  |  | 29.4671 |  |  | 16.1706 |  |  | -26.395 |  |  | -126.3898 |  |  | -319.4207 |  |  | -594.0479 |  |  | -900.2268 |  |  | -1224.5911 |  |  | -1595.6841
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6376 |  |  | 44.8261 |  |  | 34.8493 |  |  | 5.8713 |  |  | -54.6167 |  |  | -152.3748 |  |  | -269.1977 |  |  | -344.785 |  |  | -391.0354 |  |  | -489.037
[13 empty] | C Non choked w/ reducers | 7 |  | 11.9265 |  |  | 48.3956 |  |  | 157.1688 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 9.8906 |  |  | 39.2382 |  |  | 107.0614 |  |  | 500.8922 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 11.9265 |  |  | 48.3956 |  |  | 157.1688 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 6.9265 | 67.5349 |  | 36.3956 | 262.4875 |  | 134.1688 | 630.071 |  | 5500 | 1203.0365 |  | 5500 | 1978.5522 |  | 5500 | 2945.7946 |  | 5500 | 3931.1743 |  | 5500 | 4796.7797 |  | 5500 | 5568.9124 |  | 5500 | 6337.9417
[13 empty] | Next iteration flow rate |  |  | 68.8856 | Abs Value of | Flow this | 265.1124 | Abs Value of | Flow this | 636.3718 | Abs Value of | Flow this | 1215.0669 | Abs Value of | Flow this | 1998.3377 | Abs Value of | Flow this | 2975.2525 | Abs Value of | Flow this | 3970.486 | Abs Value of | Flow this | 4844.7475 | Abs Value of | Flow this | 5624.6015 | Abs Value of | Flow this | 6401.3211 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7559 |  |  | 54.5425 |  |  | 43.2394 |  |  | 7.055 |  |  | -77.9489 |  |  | -242.0412 |  |  | -475.4972 |  |  | -735.7748 |  |  | -1011.5115 |  |  | -1326.9715
[13 empty] | P2 at this iteration flow rate |  |  | 24.6888 |  |  | 25.1315 |  |  | 27.3921 |  |  | 34.629 |  |  | 51.6298 |  |  | 84.4482 |  |  | 131.1394 |  |  | 183.195 |  |  | 238.3423 |  |  | 301.4343
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0671 |  |  | 29.411 |  |  | 15.8473 |  |  | -27.574 |  |  | -129.5787 |  |  | -326.4895 |  |  | -606.6367 |  |  | -918.9698 |  |  | -1249.8538 |  |  | -1628.4058
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6325 |  |  | 44.7874 |  |  | 34.6312 |  |  | 5.112 |  |  | -56.5331 |  |  | -156.1686 |  |  | -275.2651 |  |  | -352.2583 |  |  | -399.3432 |  |  | -499.2936
[13 empty] | C Non choked w/ reducers | 7 |  | 12.1664 |  |  | 48.9262 |  |  | 160.3519 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 10.089 |  |  | 39.6477 |  |  | 108.4719 |  |  | 542.1695 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 12.1664 |  |  | 48.9262 |  |  | 160.3519 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 7.1664 | 68.8856 |  | 36.9262 | 265.1124 |  | 137.3519 | 636.3718 |  | 5500 | 1215.0669 |  | 5500 | 1998.3377 |  | 5500 | 2975.2525 |  | 5500 | 3970.486 |  | 5500 | 4844.7475 |  | 5500 | 5624.6015 |  | 5500 | 6401.3211
[13 empty] | Next iteration flow rate |  |  | 70.2633 | Abs Value of | Flow this | 267.7635 | Abs Value of | Flow this | 642.7355 | Abs Value of | Flow this | 1227.2176 | Abs Value of | Flow this | 2018.3211 | Abs Value of | Flow this | 3005.0051 | Abs Value of | Flow this | 4010.1909 | Abs Value of | Flow this | 4893.195 | Abs Value of | Flow this | 5680.8475 | Abs Value of | Flow this | 6465.3344 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7494 |  |  | 54.4948 |  |  | 42.9645 |  |  | 6.0528 |  |  | -80.6597 |  |  | -248.0503 |  |  | -486.1987 |  |  | -751.7079 |  |  | -1032.9869 |  |  | -1354.7876
[13 empty] | P2 at this iteration flow rate |  |  | 24.6901 |  |  | 25.141 |  |  | 27.4471 |  |  | 34.8294 |  |  | 52.1719 |  |  | 85.6501 |  |  | 133.2797 |  |  | 186.3816 |  |  | 242.6374 |  |  | 306.9975
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0593 |  |  | 29.3537 |  |  | 15.5174 |  |  | -28.7766 |  |  | -132.8316 |  |  | -333.7003 |  |  | -619.4785 |  |  | -938.0895 |  |  | -1275.6242 |  |  | -1661.7851
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6271 |  |  | 44.7479 |  |  | 34.4088 |  |  | 4.3375 |  |  | -58.4881 |  |  | -160.0387 |  |  | -281.4545 |  |  | -359.8818 |  |  | -407.818 |  |  | -509.7564
[13 empty] | C Non choked w/ reducers | 7 |  | 12.4112 |  |  | 49.4636 |  |  | 163.6679 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 10.2914 |  |  | 40.0618 |  |  | 109.9102 |  |  | 594.4729 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 12.4112 |  |  | 49.4636 |  |  | 163.6679 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 7.4112 | 70.2633 |  | 37.4636 | 267.7635 |  | 140.6679 | 642.7355 |  | 5500 | 1227.2176 |  | 5500 | 2018.3211 |  | 5500 | 3005.0051 |  | 5500 | 4010.1909 |  | 5500 | 4893.195 |  | 5500 | 5680.8475 |  | 5500 | 6465.3344
[13 empty] | Next iteration flow rate |  |  | 71.6686 | Abs Value of | Flow this | 270.4411 | Abs Value of | Flow this | 649.1628 | Abs Value of | Flow this | 1239.4898 | Abs Value of | Flow this | 2038.5043 | Abs Value of | Flow this | 3035.0551 | Abs Value of | Flow this | 4050.2928 | Abs Value of | Flow this | 4942.127 | Abs Value of | Flow this | 5737.656 | Abs Value of | Flow this | 6529.9877 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7427 |  |  | 54.4461 |  |  | 42.684 |  |  | 5.0305 |  |  | -83.4249 |  |  | -254.1801 |  |  | -497.1153 |  |  | -767.9612 |  |  | -1054.8939 |  |  | -1383.1629
[13 empty] | P2 at this iteration flow rate |  |  | 24.6915 |  |  | 25.1508 |  |  | 27.5032 |  |  | 35.0339 |  |  | 52.725 |  |  | 86.876 |  |  | 135.4631 |  |  | 189.6322 |  |  | 247.0188 |  |  | 312.6726
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0512 |  |  | 29.2953 |  |  | 15.1809 |  |  | -30.0034 |  |  | -136.1499 |  |  | -341.0561 |  |  | -632.5784 |  |  | -957.5935 |  |  | -1301.9127 |  |  | -1695.8354
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6215 |  |  | 44.7076 |  |  | 34.1819 |  |  | 3.5475 |  |  | -60.4824 |  |  | -163.9866 |  |  | -287.7683 |  |  | -367.6586 |  |  | -416.4631 |  |  | -520.4295
[13 empty] | C Non choked w/ reducers | 7 |  | 12.6611 |  |  | 50.008 |  |  | 167.1267 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 10.4978 |  |  | 40.4807 |  |  | 111.3771 |  |  | 663.9205 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 12.6611 |  |  | 50.008 |  |  | 167.1267 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 7.6611 | 71.6686 |  | 38.008 | 270.4411 |  | 144.1267 | 649.1628 |  | 5500 | 1239.4898 |  | 5500 | 2038.5043 |  | 5500 | 3035.0551 |  | 5500 | 4050.2928 |  | 5500 | 4942.127 |  | 5500 | 5737.656 |  | 5500 | 6529.9877
[13 empty] | Next iteration flow rate |  |  | 73.102 | Abs Value of | Flow this | 273.1455 | Abs Value of | Flow this | 655.6545 | Abs Value of | Flow this | 1251.8847 | Abs Value of | Flow this | 2058.8893 | Abs Value of | Flow this | 3065.4057 | Abs Value of | Flow this | 4090.7957 | Abs Value of | Flow this | 4991.5482 | Abs Value of | Flow this | 5795.0325 | Abs Value of | Flow this | 6595.2876 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7357 |  |  | 54.3964 |  |  | 42.398 |  |  | 3.9876 |  |  | -86.2458 |  |  | -260.4331 |  |  | -508.2514 |  |  | -784.5413 |  |  | -1077.2413 |  |  | -1412.1085
[13 empty] | P2 at this iteration flow rate |  |  | 24.6929 |  |  | 25.1607 |  |  | 27.5604 |  |  | 35.2425 |  |  | 53.2892 |  |  | 88.1266 |  |  | 137.6903 |  |  | 192.9483 |  |  | 251.4883 |  |  | 318.4617
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0428 |  |  | 29.2357 |  |  | 14.8376 |  |  | -31.2549 |  |  | -139.535 |  |  | -348.5598 |  |  | -645.9416 |  |  | -977.4895 |  |  | -1328.7296 |  |  | -1730.5701
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6157 |  |  | 44.6665 |  |  | 33.9504 |  |  | 2.7415 |  |  | -62.5168 |  |  | -168.0138 |  |  | -294.209 |  |  | -375.5917 |  |  | -425.282 |  |  | -531.3171
[13 empty] | C Non choked w/ reducers | 7 |  | 12.916 |  |  | 50.5595 |  |  | 170.7394 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 10.7084 |  |  | 40.9043 |  |  | 112.8737 |  |  | 762.7839 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 12.916 |  |  | 50.5595 |  |  | 170.7394 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 7.916 | 73.102 |  | 38.5595 | 273.1455 |  | 147.7394 | 655.6545 |  | 5500 | 1251.8847 |  | 5500 | 2058.8893 |  | 5500 | 3065.4057 |  | 5500 | 4090.7957 |  | 5500 | 4991.5482 |  | 5500 | 5795.0325 |  | 5500 | 6595.2876
[13 empty] | Next iteration flow rate |  |  | 74.564 | Abs Value of | Flow this | 275.877 | Abs Value of | Flow this | 662.211 | Abs Value of | Flow this | 1264.4035 | Abs Value of | Flow this | 2079.4782 | Abs Value of | Flow this | 3096.0597 | Abs Value of | Flow this | 4131.7037 | Abs Value of | Flow this | 5041.4637 | Abs Value of | Flow this | 5852.9829 | Abs Value of | Flow this | 6661.2405 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7284 |  |  | 54.3458 |  |  | 42.1062 |  |  | 2.9237 |  |  | -89.1234 |  |  | -266.8118 |  |  | -519.6112 |  |  | -801.4546 |  |  | -1100.0379 |  |  | -1441.6358
[13 empty] | P2 at this iteration flow rate |  |  | 24.6943 |  |  | 25.1708 |  |  | 27.6188 |  |  | 35.4553 |  |  | 53.8647 |  |  | 89.4024 |  |  | 139.9622 |  |  | 196.3309 |  |  | 256.0476 |  |  | 324.3672
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0341 |  |  | 29.1749 |  |  | 14.4874 |  |  | -32.5316 |  |  | -142.988 |  |  | -356.2142 |  |  | -659.5735 |  |  | -997.7855 |  |  | -1356.0854 |  |  | -1766.003
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6097 |  |  | 44.6246 |  |  | 33.7143 |  |  | 1.9194 |  |  | -64.592 |  |  | -172.122 |  |  | -300.7791 |  |  | -383.6842 |  |  | -434.2781 |  |  | -542.4236
[13 empty] | C Non choked w/ reducers | 7 |  | 13.1761 |  |  | 51.1183 |  |  | 174.5185 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 10.9233 |  |  | 41.3327 |  |  | 114.401 |  |  | 920.7462 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 13.1761 |  |  | 51.1183 |  |  | 174.5185 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 8.1761 | 74.564 |  | 39.1183 | 275.877 |  | 151.5185 | 662.211 |  | 5500 | 1264.4035 |  | 5500 | 2079.4782 |  | 5500 | 3096.0597 |  | 5500 | 4131.7037 |  | 5500 | 5041.4637 |  | 5500 | 5852.9829 |  | 5500 | 6661.2405
[13 empty] | Next iteration flow rate |  |  | 76.0553 | Abs Value of | Flow this | 278.6358 | Abs Value of | Flow this | 668.8331 | Abs Value of | Flow this | 1277.0475 | Abs Value of | Flow this | 2100.273 | Abs Value of | Flow this | 3127.0203 | Abs Value of | Flow this | 4173.0207 | Abs Value of | Flow this | 5091.8783 | Abs Value of | Flow this | 5911.5127 | Abs Value of | Flow this | 6727.8529 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7208 |  |  | 54.2941 |  |  | 41.8085 |  |  | 1.8385 |  |  | -92.0588 |  |  | -273.3188 |  |  | -531.1994 |  |  | -818.7078 |  |  | -1123.2926 |  |  | -1471.7567
[13 empty] | P2 at this iteration flow rate |  |  | 24.6958 |  |  | 25.1812 |  |  | 27.6783 |  |  | 35.6723 |  |  | 54.4518 |  |  | 90.7038 |  |  | 142.2799 |  |  | 199.7816 |  |  | 260.6985 |  |  | 330.3913
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0249 |  |  | 29.113 |  |  | 14.1302 |  |  | -33.8339 |  |  | -146.5105 |  |  | -364.0225 |  |  | -673.4793 |  |  | -1018.4894 |  |  | -1383.9912 |  |  | -1802.1481
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.6034 |  |  | 44.5818 |  |  | 33.4734 |  |  | 1.0807 |  |  | -66.709 |  |  | -176.3127 |  |  | -307.4813 |  |  | -391.9394 |  |  | -443.4551 |  |  | -553.7533
[13 empty] | C Non choked w/ reducers | 7 |  | 13.4415 |  |  | 51.6844 |  |  | 178.4778 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 11.1425 |  |  | 41.7661 |  |  | 115.96 |  |  | 1239.3413 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 13.4415 |  |  | 51.6844 |  |  | 178.4778 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 8.4415 | 76.0553 |  | 39.6844 | 278.6358 |  | 155.4778 | 668.8331 |  | 5500 | 1277.0475 |  | 5500 | 2100.273 |  | 5500 | 3127.0203 |  | 5500 | 4173.0207 |  | 5500 | 5091.8783 |  | 5500 | 5911.5127 |  | 5500 | 6727.8529
[13 empty] | Next iteration flow rate |  |  | 77.5764 | Abs Value of | Flow this | 281.4221 | Abs Value of | Flow this | 675.5214 | Abs Value of | Flow this | 1289.818 | Abs Value of | Flow this | 2121.2757 | Abs Value of | Flow this | 3158.2905 | Abs Value of | Flow this | 4214.7509 | Abs Value of | Flow this | 5142.7971 | Abs Value of | Flow this | 5970.6278 | Abs Value of | Flow this | 6795.1314 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7129 |  |  | 54.2414 |  |  | 41.5048 |  |  | 0.73139 |  |  | -95.0532 |  |  | -279.9565 |  |  | -543.0206 |  |  | -836.3078 |  |  | -1147.0148 |  |  | -1502.4831
[13 empty] | P2 at this iteration flow rate |  |  | 24.6974 |  |  | 25.1917 |  |  | 27.739 |  |  | 35.8937 |  |  | 55.0506 |  |  | 92.0313 |  |  | 144.6441 |  |  | 203.3016 |  |  | 265.443 |  |  | 336.5366
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0155 |  |  | 29.0497 |  |  | 13.7658 |  |  | -35.1623 |  |  | -150.1038 |  |  | -371.9878 |  |  | -687.6647 |  |  | -1039.6094 |  |  | -1412.4578 |  |  | -1839.0197
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.5969 |  |  | 44.5382 |  |  | 33.2277 |  |  | 0.22514 |  |  | -68.8685 |  |  | -180.5877 |  |  | -314.3182 |  |  | -400.3606 |  |  | -452.8165 |  |  | -565.3107
[13 empty] | C Non choked w/ reducers | 7 |  | 13.7124 |  |  | 52.258 |  |  | 182.6329 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 11.3662 |  |  | 42.2044 |  |  | 117.5518 |  |  | 2742.4066 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 13.7124 |  |  | 52.258 |  |  | 182.6329 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 8.7124 | 77.5764 |  | 40.258 | 281.4221 |  | 159.6329 | 675.5214 |  | 5500 | 1289.818 |  | 5500 | 2121.2757 |  | 5500 | 3158.2905 |  | 5500 | 4214.7509 |  | 5500 | 5142.7971 |  | 5500 | 5970.6278 |  | 5500 | 6795.1314
[13 empty] | Next iteration flow rate |  |  | 79.1279 | Abs Value of | Flow this | 284.2364 | Abs Value of | Flow this | 682.2767 | Abs Value of | Flow this | 1302.7162 | Abs Value of | Flow this | 2142.4885 | Abs Value of | Flow this | 3189.8734 | Abs Value of | Flow this | 4256.8985 | Abs Value of | Flow this | 5194.2251 | Abs Value of | Flow this | 6030.3341 | Abs Value of | Flow this | 6863.0827 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.7047 |  |  | 54.1877 |  |  | 41.1951 |  |  | -0.39792 |  |  | -98.1077 |  |  | -286.7276 |  |  | -555.0793 |  |  | -854.2616 |  |  | -1171.2139 |  |  | -1533.827
[13 empty] | P2 at this iteration flow rate |  |  | 24.6991 |  |  | 25.2025 |  |  | 27.801 |  |  | 36.1196 |  |  | 55.6615 |  |  | 93.3855 |  |  | 147.0559 |  |  | 206.8923 |  |  | 270.2828 |  |  | 342.8054
[13 empty] | Delta P at this iteration flow rate |  |  | 32.0056 |  |  | 28.9852 |  |  | 13.3941 |  |  | -36.5175 |  |  | -153.7693 |  |  | -380.1132 |  |  | -702.1351 |  |  | -1061.154 |  |  | -1441.4966 |  |  | -1876.6324
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.5901 |  |  | 44.4937 |  |  | 32.9771 |  |  | -0.64759 |  |  | -71.0714 |  |  | -184.9486 |  |  | -321.2926 |  |  | -408.951 |  |  | -462.3661 |  |  | -577.1004
[13 empty] | C Non choked w/ reducers | 7 |  | 13.9888 |  |  | 52.8393 |  |  | 187.0013 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 11.5944 |  |  | 42.6477 |  |  | 119.1777 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 13.9888 |  |  | 52.8393 |  |  | 187.0013 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 8.9888 | 79.1279 |  | 40.8393 | 284.2364 |  | 164.0013 | 682.2767 |  | 5500 | 1302.7162 |  | 5500 | 2142.4885 |  | 5500 | 3189.8734 |  | 5500 | 4256.8985 |  | 5500 | 5194.2251 |  | 5500 | 6030.3341 |  | 5500 | 6863.0827
[13 empty] | Next iteration flow rate |  |  | 80.7105 | Abs Value of | Flow this | 287.0787 | Abs Value of | Flow this | 689.0994 | Abs Value of | Flow this | 1315.7434 | Abs Value of | Flow this | 2163.9134 | Abs Value of | Flow this | 3221.7722 | Abs Value of | Flow this | 4299.4674 | Abs Value of | Flow this | 5246.1673 | Abs Value of | Flow this | 6090.6374 | Abs Value of | Flow this | 6931.7135 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6961 |  |  | 54.1328 |  |  | 40.8791 |  |  | -1.5499 |  |  | -101.2237 |  |  | -293.6349 |  |  | -567.3804 |  |  | -872.5763 |  |  | -1195.8993 |  |  | -1565.8009
[13 empty] | P2 at this iteration flow rate |  |  | 24.7008 |  |  | 25.2134 |  |  | 27.8642 |  |  | 36.35 |  |  | 56.2847 |  |  | 94.767 |  |  | 149.5161 |  |  | 210.5553 |  |  | 275.2199 |  |  | 349.2002
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9954 |  |  | 28.9194 |  |  | 13.0149 |  |  | -37.8999 |  |  | -157.5085 |  |  | -388.4019 |  |  | -716.8965 |  |  | -1083.1316 |  |  | -1471.1191 |  |  | -1915.0011
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.583 |  |  | 44.4483 |  |  | 32.7214 |  |  | -1.5379 |  |  | -73.3186 |  |  | -189.3972 |  |  | -328.4071 |  |  | -417.714 |  |  | -472.1076 |  |  | -589.1271
[13 empty] | C Non choked w/ reducers | 7 |  | 14.2709 |  |  | 53.4284 |  |  | 191.603 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 11.8271 |  |  | 43.0962 |  |  | 120.8388 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 14.2709 |  |  | 53.4284 |  |  | 191.603 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 9.2709 | 80.7105 |  | 41.4284 | 287.0787 |  | 168.603 | 689.0994 |  | 5500 | 1315.7434 |  | 5500 | 2163.9134 |  | 5500 | 3221.7722 |  | 5500 | 4299.4674 |  | 5500 | 5246.1673 |  | 5500 | 6090.6374 |  | 5500 | 6931.7135
[13 empty] | Next iteration flow rate |  |  | 82.3247 | Abs Value of | Flow this | 289.9495 | Abs Value of | Flow this | 695.9904 | Abs Value of | Flow this | 1328.9008 | Abs Value of | Flow this | 2185.5525 | Abs Value of | Flow this | 3253.9899 | Abs Value of | Flow this | 4342.4621 | Abs Value of | Flow this | 5298.629 | Abs Value of | Flow this | 6151.5438 | Abs Value of | Flow this | 7001.0307 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6873 |  |  | 54.0769 |  |  | 40.5567 |  |  | -2.7251 |  |  | -104.4023 |  |  | -300.681 |  |  | -579.9287 |  |  | -891.2591 |  |  | -1221.0809 |  |  | -1598.4175
[13 empty] | P2 at this iteration flow rate |  |  | 24.7025 |  |  | 25.2246 |  |  | 27.9287 |  |  | 36.585 |  |  | 56.9205 |  |  | 96.1762 |  |  | 152.0257 |  |  | 214.2918 |  |  | 280.2562 |  |  | 355.7235
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9847 |  |  | 28.8523 |  |  | 12.6281 |  |  | -39.3101 |  |  | -161.3228 |  |  | -396.8571 |  |  | -731.9545 |  |  | -1105.5509 |  |  | -1501.337 |  |  | -1954.141
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.5756 |  |  | 44.402 |  |  | 32.4605 |  |  | -2.446 |  |  | -75.611 |  |  | -193.9352 |  |  | -335.6646 |  |  | -426.6532 |  |  | -482.0449 |  |  | -601.3956
[13 empty] | C Non choked w/ reducers | 7 |  | 14.5587 |  |  | 54.0254 |  |  | 196.4605 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 12.0646 |  |  | 43.5499 |  |  | 122.5366 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 14.5587 |  |  | 54.0254 |  |  | 196.4605 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 9.5587 | 82.3247 |  | 42.0254 | 289.9495 |  | 173.4605 | 695.9904 |  | 5500 | 1328.9008 |  | 5500 | 2185.5525 |  | 5500 | 3253.9899 |  | 5500 | 4342.4621 |  | 5500 | 5298.629 |  | 5500 | 6151.5438 |  | 5500 | 7001.0307
[13 empty] | Next iteration flow rate |  |  | 83.9712 | Abs Value of | Flow this | 292.849 | Abs Value of | Flow this | 702.9503 | Abs Value of | Flow this | 1342.1898 | Abs Value of | Flow this | 2207.408 | Abs Value of | Flow this | 3286.5298 | Abs Value of | Flow this | 4385.8867 | Abs Value of | Flow this | 5351.6153 | Abs Value of | Flow this | 6213.0592 | Abs Value of | Flow this | 7071.041 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.678 |  |  | 54.0198 |  |  | 40.2279 |  |  | -3.9239 |  |  | -107.6448 |  |  | -307.8687 |  |  | -592.7293 |  |  | -910.3174 |  |  | -1246.7686 |  |  | -1631.6897
[13 empty] | P2 at this iteration flow rate |  |  | 24.7044 |  |  | 25.236 |  |  | 27.9944 |  |  | 36.8248 |  |  | 57.569 |  |  | 97.6137 |  |  | 154.5859 |  |  | 218.1035 |  |  | 285.3937 |  |  | 362.3779
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9736 |  |  | 28.7838 |  |  | 12.2335 |  |  | -40.7487 |  |  | -165.2138 |  |  | -405.4824 |  |  | -747.3152 |  |  | -1128.4209 |  |  | -1532.1623 |  |  | -1994.0677
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.568 |  |  | 44.3548 |  |  | 32.1945 |  |  | -3.3724 |  |  | -77.9495 |  |  | -198.5644 |  |  | -343.068 |  |  | -435.7721 |  |  | -492.182 |  |  | -613.9106
[13 empty] | C Non choked w/ reducers | 7 |  | 14.8524 |  |  | 54.6306 |  |  | 201.5998 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 12.3069 |  |  | 44.0088 |  |  | 124.2723 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 14.8524 |  |  | 54.6306 |  |  | 201.5998 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 9.8524 | 83.9712 |  | 42.6306 | 292.849 |  | 178.5998 | 702.9503 |  | 5500 | 1342.1898 |  | 5500 | 2207.408 |  | 5500 | 3286.5298 |  | 5500 | 4385.8867 |  | 5500 | 5351.6153 |  | 5500 | 6213.0592 |  | 5500 | 7071.041
[13 empty] | Next iteration flow rate |  |  | 85.6506 | Abs Value of | Flow this | 295.7775 | Abs Value of | Flow this | 709.9798 | Abs Value of | Flow this | 1355.6117 | Abs Value of | Flow this | 2229.4821 | Abs Value of | Flow this | 3319.3951 | Abs Value of | Flow this | 4429.7456 | Abs Value of | Flow this | 5405.1315 | Abs Value of | Flow this | 6275.1898 | Abs Value of | Flow this | 7141.7514 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6684 |  |  | 53.9616 |  |  | 39.8925 |  |  | -5.1468 |  |  | -110.9525 |  |  | -315.2008 |  |  | -605.7872 |  |  | -929.7588 |  |  | -1272.9727 |  |  | -1665.6307
[13 empty] | P2 at this iteration flow rate |  |  | 24.7063 |  |  | 25.2477 |  |  | 28.0615 |  |  | 37.0694 |  |  | 58.2305 |  |  | 99.0802 |  |  | 157.1974 |  |  | 221.9918 |  |  | 290.6345 |  |  | 369.1661
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9621 |  |  | 28.7139 |  |  | 11.8309 |  |  | -42.2161 |  |  | -169.183 |  |  | -414.281 |  |  | -762.9846 |  |  | -1151.7506 |  |  | -1563.6072 |  |  | -2034.7969
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.56 |  |  | 44.3066 |  |  | 31.923 |  |  | -4.3175 |  |  | -80.3349 |  |  | -203.2866 |  |  | -350.6202 |  |  | -445.0743 |  |  | -502.5228 |  |  | -626.6772
[13 empty] | C Non choked w/ reducers | 7 |  | 15.1522 |  |  | 55.2439 |  |  | 207.0506 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 12.5542 |  |  | 44.473 |  |  | 126.0475 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 15.1522 |  |  | 55.2439 |  |  | 207.0506 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 10.1522 | 85.6506 |  | 43.2439 | 295.7775 |  | 184.0506 | 709.9798 |  | 5500 | 1355.6117 |  | 5500 | 2229.4821 |  | 5500 | 3319.3951 |  | 5500 | 4429.7456 |  | 5500 | 5405.1315 |  | 5500 | 6275.1898 |  | 5500 | 7141.7514
[13 empty] | Next iteration flow rate |  |  | 87.3636 | Abs Value of | Flow this | 298.7353 | Abs Value of | Flow this | 717.0796 | Abs Value of | Flow this | 1369.1678 | Abs Value of | Flow this | 2251.7769 | Abs Value of | Flow this | 3352.589 | Abs Value of | Flow this | 4474.0431 | Abs Value of | Flow this | 5459.1828 | Abs Value of | Flow this | 6337.9417 | Abs Value of | Flow this | 7213.1689 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6584 |  |  | 53.9022 |  |  | 39.5503 |  |  | -6.3942 |  |  | -114.3267 |  |  | -322.6804 |  |  | -619.1075 |  |  | -949.591 |  |  | -1299.7034 |  |  | -1700.2539
[13 empty] | P2 at this iteration flow rate |  |  | 24.7083 |  |  | 25.2596 |  |  | 28.1299 |  |  | 37.3188 |  |  | 58.9053 |  |  | 100.5761 |  |  | 159.8615 |  |  | 225.9582 |  |  | 295.9807 |  |  | 376.0908
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9501 |  |  | 28.6426 |  |  | 11.4203 |  |  | -43.7131 |  |  | -173.232 |  |  | -423.2565 |  |  | -778.969 |  |  | -1175.5492 |  |  | -1595.6841 |  |  | -2076.3447
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.5517 |  |  | 44.2574 |  |  | 31.6462 |  |  | -5.2815 |  |  | -82.7683 |  |  | -208.1038 |  |  | -358.3242 |  |  | -454.5634 |  |  | -513.0715 |  |  | -639.7004
[13 empty] | C Non choked w/ reducers | 7 |  | 15.4582 |  |  | 55.8657 |  |  | 212.8473 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 12.8064 |  |  | 44.9427 |  |  | 127.8636 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 15.4582 |  |  | 55.8657 |  |  | 212.8473 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 10.4582 | 87.3636 |  | 43.8657 | 298.7353 |  | 189.8473 | 717.0796 |  | 5500 | 1369.1678 |  | 5500 | 2251.7769 |  | 5500 | 3352.589 |  | 5500 | 4474.0431 |  | 5500 | 5459.1828 |  | 5500 | 6337.9417 |  | 5500 | 7213.1689
[13 empty] | Next iteration flow rate |  |  | 89.1109 | Abs Value of | Flow this | 301.7226 | Abs Value of | Flow this | 724.2504 | Abs Value of | Flow this | 1382.8595 | Abs Value of | Flow this | 2274.2947 | Abs Value of | Flow this | 3386.1149 | Abs Value of | Flow this | 4518.7835 | Abs Value of | Flow this | 5513.7746 | Abs Value of | Flow this | 6401.3211 | Abs Value of | Flow this | 7285.3006 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.648 |  |  | 53.8416 |  |  | 39.2012 |  |  | -7.6668 |  |  | -117.7686 |  |  | -330.3103 |  |  | -632.6956 |  |  | -969.8218 |  |  | -1326.9715 |  |  | -1735.573
[13 empty] | P2 at this iteration flow rate |  |  | 24.7104 |  |  | 25.2717 |  |  | 28.1998 |  |  | 37.5734 |  |  | 59.5937 |  |  | 102.1021 |  |  | 162.5791 |  |  | 230.0044 |  |  | 301.4343 |  |  | 383.1546
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9376 |  |  | 28.5699 |  |  | 11.0015 |  |  | -45.2401 |  |  | -177.3624 |  |  | -432.4123 |  |  | -795.2747 |  |  | -1199.8262 |  |  | -1628.4058 |  |  | -2118.7276
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.5431 |  |  | 44.2072 |  |  | 31.3637 |  |  | -6.2649 |  |  | -85.2506 |  |  | -213.0178 |  |  | -366.1831 |  |  | -464.2433 |  |  | -523.8322 |  |  | -652.9853
[13 empty] | C Non choked w/ reducers | 7 |  | 15.7704 |  |  | 56.4961 |  |  | 219.03 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 13.0637 |  |  | 45.4179 |  |  | 129.7225 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 15.7704 |  |  | 56.4961 |  |  | 219.03 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 10.7704 | 89.1109 |  | 44.4961 | 301.7226 |  | 196.03 | 724.2504 |  | 5500 | 1382.8595 |  | 5500 | 2274.2947 |  | 5500 | 3386.1149 |  | 5500 | 4518.7835 |  | 5500 | 5513.7746 |  | 5500 | 6401.3211 |  | 5500 | 7285.3006
[13 empty] | Next iteration flow rate |  |  | 90.8931 | Abs Value of | Flow this | 304.7398 | Abs Value of | Flow this | 731.4929 | Abs Value of | Flow this | 1396.6881 | Abs Value of | Flow this | 2297.0377 | Abs Value of | Flow this | 3419.9761 | Abs Value of | Flow this | 4563.9713 | Abs Value of | Flow this | 5568.9124 | Abs Value of | Flow this | 6465.3344 | Abs Value of | Flow this | 7358.1536 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6371 |  |  | 53.7798 |  |  | 38.8452 |  |  | -8.9649 |  |  | -121.2798 |  |  | -338.0935 |  |  | -646.5568 |  |  | -990.4592 |  |  | -1354.7876 |  |  | -1771.6021
[13 empty] | P2 at this iteration flow rate |  |  | 24.7126 |  |  | 25.284 |  |  | 28.271 |  |  | 37.833 |  |  | 60.296 |  |  | 103.6587 |  |  | 165.3514 |  |  | 234.1318 |  |  | 306.9975 |  |  | 390.3604
[13 empty] | Delta P at this iteration flow rate |  |  | 31.9246 |  |  | 28.4958 |  |  | 10.5742 |  |  | -46.7979 |  |  | -181.5758 |  |  | -441.7522 |  |  | -811.9082 |  |  | -1224.5911 |  |  | -1661.7851 |  |  | -2161.9625
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.5341 |  |  | 44.1561 |  |  | 31.0756 |  |  | -7.2681 |  |  | -87.7828 |  |  | -218.0305 |  |  | -374.1999 |  |  | -474.1177 |  |  | -534.8092 |  |  | -666.5373
[13 empty] | C Non choked w/ reducers | 7 |  | 16.0891 |  |  | 57.1353 |  |  | 225.6456 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 13.3263 |  |  | 45.8986 |  |  | 131.6256 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 16.0891 |  |  | 57.1353 |  |  | 225.6456 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 11.0891 | 90.8931 |  | 45.1353 | 304.7398 |  | 202.6456 | 731.4929 |  | 5500 | 1396.6881 |  | 5500 | 2297.0377 |  | 5500 | 3419.9761 |  | 5500 | 4563.9713 |  | 5500 | 5568.9124 |  | 5500 | 6465.3344 |  | 5500 | 7358.1536
[13 empty] | Next iteration flow rate |  |  | 92.711 | Abs Value of | Flow this | 307.7872 | Abs Value of | Flow this | 738.8079 | Abs Value of | Flow this | 1410.655 | Abs Value of | Flow this | 2320.008 | Abs Value of | Flow this | 3454.1758 | Abs Value of | Flow this | 4609.611 | Abs Value of | Flow this | 5624.6015 | Abs Value of | Flow this | 6529.9877 | Abs Value of | Flow this | 7431.7351 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6259 |  |  | 53.7168 |  |  | 38.4819 |  |  | -10.2891 |  |  | -124.8615 |  |  | -346.0332 |  |  | -660.6966 |  |  | -1011.5115 |  |  | -1383.1629 |  |  | -1808.3553
[13 empty] | P2 at this iteration flow rate |  |  | 24.7148 |  |  | 25.2966 |  |  | 28.3436 |  |  | 38.0978 |  |  | 61.0123 |  |  | 105.2466 |  |  | 168.1793 |  |  | 238.3423 |  |  | 312.6726 |  |  | 397.7111
[13 empty] | Delta P at this iteration flow rate |  |  | 31.911 |  |  | 28.4201 |  |  | 10.1383 |  |  | -48.3869 |  |  | -185.8739 |  |  | -451.2799 |  |  | -828.8759 |  |  | -1249.8538 |  |  | -1695.8354 |  |  | -2206.0663
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.5248 |  |  | 44.1039 |  |  | 30.7817 |  |  | -8.2915 |  |  | -90.3659 |  |  | -223.144 |  |  | -382.3779 |  |  | -484.1906 |  |  | -546.0068 |  |  | -680.3617
[13 empty] | C Non choked w/ reducers | 7 |  | 16.4144 |  |  | 57.7834 |  |  | 232.7496 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 13.5942 |  |  | 46.385 |  |  | 133.5751 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 16.4144 |  |  | 57.7834 |  |  | 232.7496 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 11.4144 | 92.711 |  | 45.7834 | 307.7872 |  | 209.7496 | 738.8079 |  | 5500 | 1410.655 |  | 5500 | 2320.008 |  | 5500 | 3454.1758 |  | 5500 | 4609.611 |  | 5500 | 5624.6015 |  | 5500 | 6529.9877 |  | 5500 | 7431.7351
[13 empty] | Next iteration flow rate |  |  | 94.5652 | Abs Value of | Flow this | 310.8651 | Abs Value of | Flow this | 746.1959 | Abs Value of | Flow this | 1424.7615 | Abs Value of | Flow this | 2343.2081 | Abs Value of | Flow this | 3488.7176 | Abs Value of | Flow this | 4655.7071 | Abs Value of | Flow this | 5680.8475 | Abs Value of | Flow this | 6595.2876 | Abs Value of | Flow this | 7506.0525 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6141 |  |  | 53.6525 |  |  | 38.1114 |  |  | -11.6399 |  |  | -128.5153 |  |  | -354.1325 |  |  | -675.1206 |  |  | -1032.9869 |  |  | -1412.1085 |  |  | -1845.8472
[13 empty] | P2 at this iteration flow rate |  |  | 24.7172 |  |  | 25.3095 |  |  | 28.4177 |  |  | 38.368 |  |  | 61.7431 |  |  | 106.8665 |  |  | 171.0641 |  |  | 242.6374 |  |  | 318.4617 |  |  | 405.2094
[13 empty] | Delta P at this iteration flow rate |  |  | 31.897 |  |  | 28.343 |  |  | 9.6937 |  |  | -50.0079 |  |  | -190.2583 |  |  | -460.999 |  |  | -846.1848 |  |  | -1275.6242 |  |  | -1730.5701 |  |  | -2251.0567
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.5151 |  |  | 44.0507 |  |  | 30.4819 |  |  | -9.3354 |  |  | -93.001 |  |  | -228.3603 |  |  | -390.7202 |  |  | -494.466 |  |  | -557.4295 |  |  | -694.464
[13 empty] | C Non choked w/ reducers | 7 |  | 16.7464 |  |  | 58.4406 |  |  | 240.4079 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 13.8675 |  |  | 46.8772 |  |  | 135.5727 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 16.7464 |  |  | 58.4406 |  |  | 240.4079 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 11.7464 | 94.5652 |  | 46.4406 | 310.8651 |  | 217.4079 | 746.1959 |  | 5500 | 1424.7615 |  | 5500 | 2343.2081 |  | 5500 | 3488.7176 |  | 5500 | 4655.7071 |  | 5500 | 5680.8475 |  | 5500 | 6595.2876 |  | 5500 | 7506.0525
[13 empty] | Next iteration flow rate |  |  | 96.4565 | Abs Value of | Flow this | 313.9738 | Abs Value of | Flow this | 753.6579 | Abs Value of | Flow this | 1439.0091 | Abs Value of | Flow this | 2366.6402 | Abs Value of | Flow this | 3523.6048 | Abs Value of | Flow this | 4702.2642 | Abs Value of | Flow this | 5737.656 | Abs Value of | Flow this | 6661.2405 | Abs Value of | Flow this | 7581.113 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.6019 |  |  | 53.5869 |  |  | 37.7334 |  |  | -13.0179 |  |  | -132.2424 |  |  | -362.3946 |  |  | -689.8346 |  |  | -1054.8939 |  |  | -1441.6358 |  |  | -1884.0928
[13 empty] | P2 at this iteration flow rate |  |  | 24.7196 |  |  | 25.3226 |  |  | 28.4933 |  |  | 38.6436 |  |  | 62.4885 |  |  | 108.5189 |  |  | 174.0069 |  |  | 247.0188 |  |  | 324.3672 |  |  | 412.8586
[13 empty] | Delta P at this iteration flow rate |  |  | 31.8823 |  |  | 28.2643 |  |  | 9.2401 |  |  | -51.6615 |  |  | -194.7309 |  |  | -470.9135 |  |  | -863.8415 |  |  | -1301.9127 |  |  | -1766.003 |  |  | -2296.9513
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.505 |  |  | 43.9964 |  |  | 30.1761 |  |  | -10.4003 |  |  | -95.689 |  |  | -233.6815 |  |  | -399.2302 |  |  | -504.9479 |  |  | -569.0818 |  |  | -708.8497
[13 empty] | C Non choked w/ reducers | 7 |  | 17.0852 |  |  | 59.1072 |  |  | 248.7001 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 14.1464 |  |  | 47.3752 |  |  | 137.6205 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 17.0852 |  |  | 59.1072 |  |  | 248.7001 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 12.0852 | 96.4565 |  | 47.1072 | 313.9738 |  | 225.7001 | 753.6579 |  | 5500 | 1439.0091 |  | 5500 | 2366.6402 |  | 5500 | 3523.6048 |  | 5500 | 4702.2642 |  | 5500 | 5737.656 |  | 5500 | 6661.2405 |  | 5500 | 7581.113
[13 empty] | Next iteration flow rate |  |  | 98.3856 | Abs Value of | Flow this | 317.1135 | Abs Value of | Flow this | 761.1945 | Abs Value of | Flow this | 1453.3992 | Abs Value of | Flow this | 2390.3066 | Abs Value of | Flow this | 3558.8408 | Abs Value of | Flow this | 4749.2869 | Abs Value of | Flow this | 5795.0325 | Abs Value of | Flow this | 6727.8529 | Abs Value of | Flow this | 7656.9241 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.5892 |  |  | 53.52 |  |  | 37.3479 |  |  | -14.4236 |  |  | -136.0445 |  |  | -370.8227 |  |  | -704.8443 |  |  | -1077.2413 |  |  | -1471.7567 |  |  | -1923.1071
[13 empty] | P2 at this iteration flow rate |  |  | 24.7222 |  |  | 25.336 |  |  | 28.5704 |  |  | 38.9247 |  |  | 63.2489 |  |  | 110.2045 |  |  | 177.0089 |  |  | 251.4883 |  |  | 330.3913 |  |  | 420.6614
[13 empty] | Delta P at this iteration flow rate |  |  | 31.8671 |  |  | 28.184 |  |  | 8.7774 |  |  | -53.3483 |  |  | -199.2934 |  |  | -481.0273 |  |  | -881.8531 |  |  | -1328.7296 |  |  | -1802.1481 |  |  | -2343.7685
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.4945 |  |  | 43.941 |  |  | 29.8641 |  |  | -11.4866 |  |  | -98.431 |  |  | -239.1096 |  |  | -407.9113 |  |  | -515.6405 |  |  | -580.9684 |  |  | -723.5245
[13 empty] | C Non choked w/ reducers | 7 |  | 17.4311 |  |  | 59.7832 |  |  | 257.7225 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 14.4309 |  |  | 47.8791 |  |  | 139.7209 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 17.4311 |  |  | 59.7832 |  |  | 257.7225 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 12.4311 | 98.3856 |  | 47.7832 | 317.1135 |  | 234.7225 | 761.1945 |  | 5500 | 1453.3992 |  | 5500 | 2390.3066 |  | 5500 | 3558.8408 |  | 5500 | 4749.2869 |  | 5500 | 5795.0325 |  | 5500 | 6727.8529 |  | 5500 | 7656.9241
[13 empty] | Next iteration flow rate |  |  | 100.3534 | Abs Value of | Flow this | 320.2846 | Abs Value of | Flow this | 768.8064 | Abs Value of | Flow this | 1467.9332 | Abs Value of | Flow this | 2414.2097 | Abs Value of | Flow this | 3594.4292 | Abs Value of | Flow this | 4796.7797 | Abs Value of | Flow this | 5852.9829 | Abs Value of | Flow this | 6795.1314 | Abs Value of | Flow this | 7733.4934 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.576 |  |  | 53.4517 |  |  | 36.9545 |  |  | -15.8575 |  |  | -139.923 |  |  | -379.4203 |  |  | -720.1556 |  |  | -1100.0379 |  |  | -1502.4831 |  |  | -1962.9055
[13 empty] | P2 at this iteration flow rate |  |  | 24.7248 |  |  | 25.3497 |  |  | 28.6491 |  |  | 39.2115 |  |  | 64.0246 |  |  | 111.9241 |  |  | 180.0711 |  |  | 256.0476 |  |  | 336.5366 |  |  | 428.6211
[13 empty] | Delta P at this iteration flow rate |  |  | 31.8512 |  |  | 28.102 |  |  | 8.3054 |  |  | -55.069 |  |  | -203.9477 |  |  | -491.3443 |  |  | -900.2268 |  |  | -1356.0854 |  |  | -1839.0197 |  |  | -2391.5266
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.4835 |  |  | 43.8845 |  |  | 29.5458 |  |  | -12.5947 |  |  | -101.2281 |  |  | -244.6468 |  |  | -416.7669 |  |  | -526.548 |  |  | -593.0938 |  |  | -738.4944
[13 empty] | C Non choked w/ reducers | 7 |  | 17.7841 |  |  | 60.469 |  |  | 267.5938 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 14.7213 |  |  | 48.389 |  |  | 141.8761 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 17.7841 |  |  | 60.469 |  |  | 267.5938 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 12.7841 | 100.3534 |  | 48.469 | 320.2846 |  | 244.5938 | 768.8064 |  | 5500 | 1467.9332 |  | 5500 | 2414.2097 |  | 5500 | 3594.4292 |  | 5500 | 4796.7797 |  | 5500 | 5852.9829 |  | 5500 | 6795.1314 |  | 5500 | 7733.4934
[13 empty] | Next iteration flow rate |  |  | 102.3604 | Abs Value of | Flow this | 323.4875 | Abs Value of | Flow this | 776.4945 | Abs Value of | Flow this | 1482.6125 | Abs Value of | Flow this | 2438.3518 | Abs Value of | Flow this | 3630.3735 | Abs Value of | Flow this | 4844.7475 | Abs Value of | Flow this | 5911.5127 | Abs Value of | Flow this | 6863.0827 | Abs Value of | Flow this | 7810.8283 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.5623 |  |  | 53.3821 |  |  | 36.5533 |  |  | -17.3203 |  |  | -143.8795 |  |  | -388.1906 |  |  | -735.7748 |  |  | -1123.2926 |  |  | -1533.827 |  |  | -2003.5039
[13 empty] | P2 at this iteration flow rate |  |  | 24.7275 |  |  | 25.3636 |  |  | 28.7293 |  |  | 39.5041 |  |  | 64.8159 |  |  | 113.6781 |  |  | 183.195 |  |  | 260.6985 |  |  | 342.8054 |  |  | 436.7408
[13 empty] | Delta P at this iteration flow rate |  |  | 31.8347 |  |  | 28.0185 |  |  | 7.824 |  |  | -56.8243 |  |  | -208.6954 |  |  | -501.8688 |  |  | -918.9698 |  |  | -1383.9912 |  |  | -1876.6324 |  |  | -2440.2447
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.4722 |  |  | 43.8268 |  |  | 29.2212 |  |  | -13.7251 |  |  | -104.0815 |  |  | -250.2953 |  |  | -425.8004 |  |  | -537.6748 |  |  | -605.4629 |  |  | -753.7651
[13 empty] | C Non choked w/ reducers | 7 |  | 18.1445 |  |  | 61.1647 |  |  | 278.4616 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 15.0176 |  |  | 48.905 |  |  | 144.0887 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 18.1445 |  |  | 61.1647 |  |  | 278.4616 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 13.1445 | 102.3604 |  | 49.1647 | 323.4875 |  | 255.4616 | 776.4945 |  | 5500 | 1482.6125 |  | 5500 | 2438.3518 |  | 5500 | 3630.3735 |  | 5500 | 4844.7475 |  | 5500 | 5911.5127 |  | 5500 | 6863.0827 |  | 5500 | 7810.8283
[13 empty] | Next iteration flow rate |  |  | 104.4076 | Abs Value of | Flow this | 326.7224 | Abs Value of | Flow this | 784.2594 | Abs Value of | Flow this | 1497.4387 | Abs Value of | Flow this | 2462.7353 | Abs Value of | Flow this | 3666.6772 | Abs Value of | Flow this | 4893.195 | Abs Value of | Flow this | 5970.6278 | Abs Value of | Flow this | 6931.7135 | Abs Value of | Flow this | 7888.9366 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.548 |  |  | 53.311 |  |  | 36.144 |  |  | -18.8124 |  |  | -147.9155 |  |  | -397.1373 |  |  | -751.7079 |  |  | -1147.0148 |  |  | -1565.8009 |  |  | -2044.9184
[13 empty] | P2 at this iteration flow rate |  |  | 24.7304 |  |  | 25.3778 |  |  | 28.8112 |  |  | 39.8025 |  |  | 65.6231 |  |  | 115.4675 |  |  | 186.3816 |  |  | 265.443 |  |  | 349.2002 |  |  | 445.0237
[13 empty] | Delta P at this iteration flow rate |  |  | 31.8176 |  |  | 27.9332 |  |  | 7.3328 |  |  | -58.6149 |  |  | -213.5386 |  |  | -512.6047 |  |  | -938.0895 |  |  | -1412.4578 |  |  | -1915.0011 |  |  | -2489.9421
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.4603 |  |  | 43.768 |  |  | 28.89 |  |  | -14.8783 |  |  | -106.9922 |  |  | -256.0573 |  |  | -435.0155 |  |  | -549.0252 |  |  | -618.0807 |  |  | -769.3428
[13 empty] | C Non choked w/ reducers | 7 |  | 18.5124 |  |  | 61.8705 |  |  | 290.5125 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 15.3199 |  |  | 49.4272 |  |  | 146.3614 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 18.5124 |  |  | 61.8705 |  |  | 290.5125 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 13.5124 | 104.4076 |  | 49.8705 | 326.7224 |  | 267.5125 | 784.2594 |  | 5500 | 1497.4387 |  | 5500 | 2462.7353 |  | 5500 | 3666.6772 |  | 5500 | 4893.195 |  | 5500 | 5970.6278 |  | 5500 | 6931.7135 |  | 5500 | 7888.9366
[13 empty] | Next iteration flow rate |  |  | 106.4958 | Abs Value of | Flow this | 329.9896 | Abs Value of | Flow this | 792.102 | Abs Value of | Flow this | 1512.4131 | Abs Value of | Flow this | 2487.3626 | Abs Value of | Flow this | 3703.344 | Abs Value of | Flow this | 4942.127 | Abs Value of | Flow this | 6030.3341 | Abs Value of | Flow this | 7001.0307 | Abs Value of | Flow this | 7967.826 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.5331 |  |  | 53.2386 |  |  | 35.7265 |  |  | -20.3346 |  |  | -152.0326 |  |  | -406.2638 |  |  | -767.9612 |  |  | -1171.2139 |  |  | -1598.4175 |  |  | -2087.1653
[13 empty] | P2 at this iteration flow rate |  |  | 24.7334 |  |  | 25.3923 |  |  | 28.8947 |  |  | 40.1069 |  |  | 66.4465 |  |  | 117.2928 |  |  | 189.6322 |  |  | 270.2828 |  |  | 355.7235 |  |  | 453.4731
[13 empty] | Delta P at this iteration flow rate |  |  | 31.7997 |  |  | 27.8463 |  |  | 6.8318 |  |  | -60.4415 |  |  | -218.4791 |  |  | -523.5565 |  |  | -957.5935 |  |  | -1441.4966 |  |  | -1954.141 |  |  | -2540.6383
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.448 |  |  | 43.708 |  |  | 28.5521 |  |  | -16.0546 |  |  | -109.9614 |  |  | -261.9351 |  |  | -444.4159 |  |  | -560.6038 |  |  | -630.9521 |  |  | -785.2335
[13 empty] | C Non choked w/ reducers | 7 |  | 18.8879 |  |  | 62.5867 |  |  | 303.9864 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 15.6283 |  |  | 49.9557 |  |  | 148.697 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 18.8879 |  |  | 62.5867 |  |  | 303.9864 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 13.8879 | 106.4958 |  | 50.5867 | 329.9896 |  | 280.9864 | 792.102 |  | 5500 | 1512.4131 |  | 5500 | 2487.3626 |  | 5500 | 3703.344 |  | 5500 | 4942.127 |  | 5500 | 6030.3341 |  | 5500 | 7001.0307 |  | 5500 | 7967.826
[13 empty] | Next iteration flow rate |  |  | 108.6257 | Abs Value of | Flow this | 333.2895 | Abs Value of | Flow this | 800.023 | Abs Value of | Flow this | 1527.5372 | Abs Value of | Flow this | 2512.2363 | Abs Value of | Flow this | 3740.3775 | Abs Value of | Flow this | 4991.5482 | Abs Value of | Flow this | 6090.6374 | Abs Value of | Flow this | 7071.041 | Abs Value of | Flow this | 8047.5042 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.5176 |  |  | 53.1646 |  |  | 35.3006 |  |  | -21.8873 |  |  | -156.2325 |  |  | -415.5737 |  |  | -784.5413 |  |  | -1195.8993 |  |  | -1631.6897 |  |  | -2130.2613
[13 empty] | P2 at this iteration flow rate |  |  | 24.7365 |  |  | 25.4071 |  |  | 28.9799 |  |  | 40.4175 |  |  | 67.2865 |  |  | 119.1547 |  |  | 192.9483 |  |  | 275.2199 |  |  | 362.3779 |  |  | 462.0923
[13 empty] | Delta P at this iteration flow rate |  |  | 31.7812 |  |  | 27.7576 |  |  | 6.3207 |  |  | -62.3048 |  |  | -223.519 |  |  | -534.7284 |  |  | -977.4895 |  |  | -1471.1191 |  |  | -1994.0677 |  |  | -2592.3536
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.4352 |  |  | 43.6468 |  |  | 28.2075 |  |  | -17.2545 |  |  | -112.9903 |  |  | -267.9311 |  |  | -454.0052 |  |  | -572.415 |  |  | -644.0822 |  |  | -801.4437
[13 empty] | C Non choked w/ reducers | 7 |  | 19.2713 |  |  | 63.3135 |  |  | 319.1982 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 15.9431 |  |  | 50.4906 |  |  | 151.0986 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 19.2713 |  |  | 63.3135 |  |  | 319.1982 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 14.2713 | 108.6257 |  | 51.3135 | 333.2895 |  | 296.1982 | 800.023 |  | 5500 | 1527.5372 |  | 5500 | 2512.2363 |  | 5500 | 3740.3775 |  | 5500 | 4991.5482 |  | 5500 | 6090.6374 |  | 5500 | 7071.041 |  | 5500 | 8047.5042
[13 empty] | Next iteration flow rate |  |  | 110.7982 | Abs Value of | Flow this | 336.6224 | Abs Value of | Flow this | 808.0233 | Abs Value of | Flow this | 1542.8126 | Abs Value of | Flow this | 2537.3586 | Abs Value of | Flow this | 3777.7812 | Abs Value of | Flow this | 5041.4637 | Abs Value of | Flow this | 6151.5438 | Abs Value of | Flow this | 7141.7514 | Abs Value of | Flow this | 8127.9793 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.5015 |  |  | 53.0892 |  |  | 34.8661 |  |  | -23.4712 |  |  | -160.5168 |  |  | -425.0707 |  |  | -801.4546 |  |  | -1221.0809 |  |  | -1665.6307 |  |  | -2174.2236
[13 empty] | P2 at this iteration flow rate |  |  | 24.7397 |  |  | 25.4222 |  |  | 29.0668 |  |  | 40.7342 |  |  | 68.1434 |  |  | 121.0541 |  |  | 196.3309 |  |  | 280.2562 |  |  | 369.1661 |  |  | 470.8847
[13 empty] | Delta P at this iteration flow rate |  |  | 31.7619 |  |  | 27.6671 |  |  | 5.7993 |  |  | -64.2055 |  |  | -228.6601 |  |  | -546.1249 |  |  | -997.7855 |  |  | -1501.337 |  |  | -2034.7969 |  |  | -2645.1083
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.4219 |  |  | 43.5844 |  |  | 27.856 |  |  | -18.4786 |  |  | -116.08 |  |  | -274.0476 |  |  | -463.7872 |  |  | -584.4637 |  |  | -657.4762 |  |  | -817.9797
[13 empty] | C Non choked w/ reducers | 7 |  | 19.6627 |  |  | 64.0511 |  |  | 336.57 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 16.2643 |  |  | 51.0321 |  |  | 153.5696 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 19.6627 |  |  | 64.0511 |  |  | 336.57 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 14.6627 | 110.7982 |  | 52.0511 | 336.6224 |  | 313.57 | 808.0233 |  | 5500 | 1542.8126 |  | 5500 | 2537.3586 |  | 5500 | 3777.7812 |  | 5500 | 5041.4637 |  | 5500 | 6151.5438 |  | 5500 | 7141.7514 |  | 5500 | 8127.9793
[13 empty] | Next iteration flow rate |  |  | 113.0142 | Abs Value of | Flow this | 339.9886 | Abs Value of | Flow this | 816.1035 | Abs Value of | Flow this | 1558.2407 | Abs Value of | Flow this | 2562.7322 | Abs Value of | Flow this | 3815.559 | Abs Value of | Flow this | 5091.8783 | Abs Value of | Flow this | 6213.0592 | Abs Value of | Flow this | 7213.1689 | Abs Value of | Flow this | 8209.259 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.4848 |  |  | 53.0123 |  |  | 34.4229 |  |  | -25.087 |  |  | -164.8872 |  |  | -434.7587 |  |  | -818.7078 |  |  | -1246.7686 |  |  | -1700.2539 |  |  | -2219.0695
[13 empty] | P2 at this iteration flow rate |  |  | 24.743 |  |  | 25.4375 |  |  | 29.1554 |  |  | 41.0574 |  |  | 69.0174 |  |  | 122.9917 |  |  | 199.7816 |  |  | 285.3937 |  |  | 376.0908 |  |  | 479.8539
[13 empty] | Delta P at this iteration flow rate |  |  | 31.7418 |  |  | 27.5748 |  |  | 5.2675 |  |  | -66.1444 |  |  | -233.9046 |  |  | -557.7504 |  |  | -1018.4894 |  |  | -1532.1623 |  |  | -2076.3447 |  |  | -2698.9234
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.408 |  |  | 43.5207 |  |  | 27.4973 |  |  | -19.7273 |  |  | -119.2319 |  |  | -280.2871 |  |  | -473.7659 |  |  | -596.7546 |  |  | -671.1395 |  |  | -834.8481
[13 empty] | C Non choked w/ reducers | 7 |  | 20.0623 |  |  | 64.7998 |  |  | 356.6844 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 16.5921 |  |  | 51.5801 |  |  | 156.1134 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 20.0623 |  |  | 64.7998 |  |  | 356.6844 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 15.0623 | 113.0142 |  | 52.7998 | 339.9886 |  | 333.6844 | 816.1035 |  | 5500 | 1558.2407 |  | 5500 | 2562.7322 |  | 5500 | 3815.559 |  | 5500 | 5091.8783 |  | 5500 | 6213.0592 |  | 5500 | 7213.1689 |  | 5500 | 8209.259
[13 empty] | Next iteration flow rate |  |  | 115.2745 | Abs Value of | Flow this | 343.3885 | Abs Value of | Flow this | 824.2645 | Abs Value of | Flow this | 1573.8231 | Abs Value of | Flow this | 2588.3595 | Abs Value of | Flow this | 3853.7146 | Abs Value of | Flow this | 5142.7971 | Abs Value of | Flow this | 6275.1898 | Abs Value of | Flow this | 7285.3006 | Abs Value of | Flow this | 8291.3516 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.4674 |  |  | 52.9339 |  |  | 33.9708 |  |  | -26.7353 |  |  | -169.3454 |  |  | -444.6413 |  |  | -836.3078 |  |  | -1272.9727 |  |  | -1735.573 |  |  | -2264.8168
[13 empty] | P2 at this iteration flow rate |  |  | 24.7465 |  |  | 25.4532 |  |  | 29.2458 |  |  | 41.3871 |  |  | 69.9091 |  |  | 124.9683 |  |  | 203.3016 |  |  | 290.6345 |  |  | 383.1546 |  |  | 489.0034
[13 empty] | Delta P at this iteration flow rate |  |  | 31.7208 |  |  | 27.4806 |  |  | 4.7249 |  |  | -68.1224 |  |  | -239.2545 |  |  | -569.6096 |  |  | -1039.6094 |  |  | -1563.6072 |  |  | -2118.7276 |  |  | -2753.8201
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.3936 |  |  | 43.4558 |  |  | 27.1315 |  |  | -21.001 |  |  | -122.4472 |  |  | -286.652 |  |  | -483.9451 |  |  | -609.2925 |  |  | -685.0773 |  |  | -852.0555
[13 empty] | C Non choked w/ reducers | 7 |  | 20.4703 |  |  | 65.5599 |  |  | 380.3721 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 16.9265 |  |  | 52.1348 |  |  | 158.734 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 20.4703 |  |  | 65.5599 |  |  | 380.3721 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 15.4703 | 115.2745 |  | 53.5599 | 343.3885 |  | 357.3721 | 824.2645 |  | 5500 | 1573.8231 |  | 5500 | 2588.3595 |  | 5500 | 3853.7146 |  | 5500 | 5142.7971 |  | 5500 | 6275.1898 |  | 5500 | 7285.3006 |  | 5500 | 8291.3516
[13 empty] | Next iteration flow rate |  |  | 117.5799 | Abs Value of | Flow this | 346.8224 | Abs Value of | Flow this | 832.5072 | Abs Value of | Flow this | 1589.5613 | Abs Value of | Flow this | 2614.2431 | Abs Value of | Flow this | 3892.2518 | Abs Value of | Flow this | 5194.2251 | Abs Value of | Flow this | 6337.9417 | Abs Value of | Flow this | 7358.1536 | Abs Value of | Flow this | 8374.2652 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.4492 |  |  | 52.8538 |  |  | 33.5096 |  |  | -28.4167 |  |  | -173.8933 |  |  | -454.7226 |  |  | -854.2616 |  |  | -1299.7034 |  |  | -1771.6021 |  |  | -2311.4836
[13 empty] | P2 at this iteration flow rate |  |  | 24.7502 |  |  | 25.4692 |  |  | 29.3381 |  |  | 41.7233 |  |  | 70.8187 |  |  | 126.9845 |  |  | 206.8923 |  |  | 295.9807 |  |  | 390.3604 |  |  | 498.3367
[13 empty] | Delta P at this iteration flow rate |  |  | 31.6991 |  |  | 27.3846 |  |  | 4.1715 |  |  | -70.14 |  |  | -244.7119 |  |  | -581.7072 |  |  | -1061.154 |  |  | -1595.6841 |  |  | -2161.9625 |  |  | -2809.8203
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.3785 |  |  | 43.3895 |  |  | 26.7583 |  |  | -22.3004 |  |  | -125.727 |  |  | -293.1448 |  |  | -494.329 |  |  | -622.0824 |  |  | -699.2954 |  |  | -869.6088
[13 empty] | C Non choked w/ reducers | 7 |  | 20.8869 |  |  | 66.3315 |  |  | 408.8671 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 17.2678 |  |  | 52.6963 |  |  | 161.4354 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 20.8869 |  |  | 66.3315 |  |  | 408.8671 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 15.8869 | 117.5799 |  | 54.3315 | 346.8224 |  | 385.8671 | 832.5072 |  | 5500 | 1589.5613 |  | 5500 | 2614.2431 |  | 5500 | 3892.2518 |  | 5500 | 5194.2251 |  | 5500 | 6337.9417 |  | 5500 | 7358.1536 |  | 5500 | 8374.2652
[13 empty] | Next iteration flow rate |  |  | 119.9315 | Abs Value of | Flow this | 350.2906 | Abs Value of | Flow this | 840.8323 | Abs Value of | Flow this | 1605.4569 | Abs Value of | Flow this | 2640.3856 | Abs Value of | Flow this | 3931.1743 | Abs Value of | Flow this | 5246.1673 | Abs Value of | Flow this | 6401.3211 | Abs Value of | Flow this | 7431.7351 | Abs Value of | Flow this | 8458.0078 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.4304 |  |  | 52.7722 |  |  | 33.0391 |  |  | -30.1319 |  |  | -178.5326 |  |  | -465.0066 |  |  | -872.5763 |  |  | -1326.9715 |  |  | -1808.3553 |  |  | -2359.0885
[13 empty] | P2 at this iteration flow rate |  |  | 24.7539 |  |  | 25.4856 |  |  | 29.4322 |  |  | 42.0664 |  |  | 71.7465 |  |  | 129.0413 |  |  | 210.5553 |  |  | 301.4343 |  |  | 397.7111 |  |  | 507.8577
[13 empty] | Delta P at this iteration flow rate |  |  | 31.6765 |  |  | 27.2866 |  |  | 3.6069 |  |  | -72.1983 |  |  | -250.2791 |  |  | -594.0479 |  |  | -1083.1316 |  |  | -1628.4058 |  |  | -2206.0663 |  |  | -2866.9461
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.3629 |  |  | 43.3219 |  |  | 26.3776 |  |  | -23.6259 |  |  | -129.0728 |  |  | -299.7681 |  |  | -504.9215 |  |  | -635.1294 |  |  | -713.7992 |  |  | -887.5149
[13 empty] | C Non choked w/ reducers | 7 |  | 21.3122 |  |  | 67.115 |  |  | 444.0998 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 17.6162 |  |  | 53.2648 |  |  | 164.2221 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 21.3122 |  |  | 67.115 |  |  | 444.0998 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 16.3122 | 119.9315 |  | 55.115 | 350.2906 |  | 421.0998 | 840.8323 |  | 5500 | 1605.4569 |  | 5500 | 2640.3856 |  | 5500 | 3931.1743 |  | 5500 | 5246.1673 |  | 5500 | 6401.3211 |  | 5500 | 7431.7351 |  | 5500 | 8458.0078
[13 empty] | Next iteration flow rate |  |  | 122.3302 | Abs Value of | Flow this | 353.7935 | Abs Value of | Flow this | 849.2406 | Abs Value of | Flow this | 1621.5115 | Abs Value of | Flow this | 2666.7894 | Abs Value of | Flow this | 3970.486 | Abs Value of | Flow this | 5298.629 | Abs Value of | Flow this | 6465.3344 | Abs Value of | Flow this | 7506.0525 | Abs Value of | Flow this | 8542.5879 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.4108 |  |  | 52.6889 |  |  | 32.5592 |  |  | -31.8815 |  |  | -183.2651 |  |  | -475.4972 |  |  | -891.2591 |  |  | -1354.7876 |  |  | -1845.8472 |  |  | -2407.6501
[13 empty] | P2 at this iteration flow rate |  |  | 24.7578 |  |  | 25.5022 |  |  | 29.5282 |  |  | 42.4163 |  |  | 72.693 |  |  | 131.1394 |  |  | 214.2918 |  |  | 306.9975 |  |  | 405.2094 |  |  | 517.57
[13 empty] | Delta P at this iteration flow rate |  |  | 31.6529 |  |  | 27.1866 |  |  | 3.031 |  |  | -74.2979 |  |  | -255.9581 |  |  | -606.6367 |  |  | -1105.5509 |  |  | -1661.7851 |  |  | -2251.0567 |  |  | -2925.2202
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.3467 |  |  | 43.253 |  |  | 25.9893 |  |  | -24.978 |  |  | -132.4858 |  |  | -306.5245 |  |  | -515.727 |  |  | -648.4387 |  |  | -728.5945 |  |  | -905.781
[13 empty] | C Non choked w/ reducers | 7 |  | 21.7466 |  |  | 67.9106 |  |  | 489.3016 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 17.9716 |  |  | 53.8403 |  |  | 167.0989 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 21.7466 |  |  | 67.9106 |  |  | 489.3016 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 16.7466 | 122.3302 |  | 55.9106 | 353.7935 |  | 466.3016 | 849.2406 |  | 5500 | 1621.5115 |  | 5500 | 2666.7894 |  | 5500 | 3970.486 |  | 5500 | 5298.629 |  | 5500 | 6465.3344 |  | 5500 | 7506.0525 |  | 5500 | 8542.5879
[13 empty] | Next iteration flow rate |  |  | 124.7768 | Abs Value of | Flow this | 357.3314 | Abs Value of | Flow this | 857.733 | Abs Value of | Flow this | 1637.7266 | Abs Value of | Flow this | 2693.4573 | Abs Value of | Flow this | 4010.1909 | Abs Value of | Flow this | 5351.6153 | Abs Value of | Flow this | 6529.9877 | Abs Value of | Flow this | 7581.113 | Abs Value of | Flow this | 8628.0138 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.3903 |  |  | 52.6039 |  |  | 32.0696 |  |  | -33.6664 |  |  | -188.0927 |  |  | -486.1987 |  |  | -910.3174 |  |  | -1383.1629 |  |  | -1884.0928 |  |  | -2457.1879
[13 empty] | P2 at this iteration flow rate |  |  | 24.7619 |  |  | 25.5192 |  |  | 29.6261 |  |  | 42.7733 |  |  | 73.6585 |  |  | 133.2797 |  |  | 218.1035 |  |  | 312.6726 |  |  | 412.8586 |  |  | 527.4776
[13 empty] | Delta P at this iteration flow rate |  |  | 31.6284 |  |  | 27.0847 |  |  | 2.4435 |  |  | -76.4397 |  |  | -261.7513 |  |  | -619.4785 |  |  | -1128.4209 |  |  | -1695.8354 |  |  | -2296.9513 |  |  | -2984.6655
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.3298 |  |  | 43.1826 |  |  | 25.5932 |  |  | -26.3574 |  |  | -135.9675 |  |  | -313.4168 |  |  | -526.7497 |  |  | -662.0155 |  |  | -743.6872 |  |  | -924.4141
[13 empty] | C Non choked w/ reducers | 7 |  | 22.1901 |  |  | 68.7187 |  |  | 550.4064 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 18.3344 |  |  | 54.423 |  |  | 170.0711 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 22.1901 |  |  | 68.7187 |  |  | 550.4064 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 17.1901 | 124.7768 |  | 56.7187 | 357.3314 |  | 527.4064 | 857.733 |  | 5500 | 1637.7266 |  | 5500 | 2693.4573 |  | 5500 | 4010.1909 |  | 5500 | 5351.6153 |  | 5500 | 6529.9877 |  | 5500 | 7581.113 |  | 5500 | 8628.0138
[13 empty] | Next iteration flow rate |  |  | 127.2723 | Abs Value of | Flow this | 360.9047 | Abs Value of | Flow this | 866.3103 | Abs Value of | Flow this | 1654.1039 | Abs Value of | Flow this | 2720.3919 | Abs Value of | Flow this | 4050.2928 | Abs Value of | Flow this | 5405.1315 | Abs Value of | Flow this | 6595.2876 | Abs Value of | Flow this | 7656.9241 | Abs Value of | Flow this | 8714.2939 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.3691 |  |  | 52.5172 |  |  | 31.5702 |  |  | -35.4871 |  |  | -193.0174 |  |  | -497.1153 |  |  | -929.7588 |  |  | -1412.1085 |  |  | -1923.1071 |  |  | -2507.7214
[13 empty] | P2 at this iteration flow rate |  |  | 24.7662 |  |  | 25.5366 |  |  | 29.726 |  |  | 43.1374 |  |  | 74.6435 |  |  | 135.4631 |  |  | 221.9918 |  |  | 318.4617 |  |  | 420.6614 |  |  | 537.5843
[13 empty] | Delta P at this iteration flow rate |  |  | 31.6029 |  |  | 26.9807 |  |  | 1.8442 |  |  | -78.6245 |  |  | -267.6609 |  |  | -632.5784 |  |  | -1151.7506 |  |  | -1730.5701 |  |  | -2343.7685 |  |  | -3045.3057
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.3122 |  |  | 43.1109 |  |  | 25.1891 |  |  | -27.7644 |  |  | -139.5191 |  |  | -320.4475 |  |  | -537.9939 |  |  | -675.8651 |  |  | -759.0833 |  |  | -943.4218
[13 empty] | C Non choked w/ reducers | 7 |  | 22.643 |  |  | 69.5396 |  |  | 639.8909 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 18.7047 |  |  | 55.0129 |  |  | 173.1441 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 22.643 |  |  | 69.5396 |  |  | 639.8909 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 17.643 | 127.2723 |  | 57.5396 | 360.9047 |  | 616.8909 | 866.3103 |  | 5500 | 1654.1039 |  | 5500 | 2720.3919 |  | 5500 | 4050.2928 |  | 5500 | 5405.1315 |  | 5500 | 6595.2876 |  | 5500 | 7656.9241 |  | 5500 | 8714.2939
[13 empty] | Next iteration flow rate |  |  | 129.8178 | Abs Value of | Flow this | 364.5138 | Abs Value of | Flow this | 874.9734 | Abs Value of | Flow this | 1670.6449 | Abs Value of | Flow this | 2747.5958 | Abs Value of | Flow this | 4090.7957 | Abs Value of | Flow this | 5459.1828 | Abs Value of | Flow this | 6661.2405 | Abs Value of | Flow this | 7733.4934 | Abs Value of | Flow this | 8801.4368 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.347 |  |  | 52.4288 |  |  | 31.0607 |  |  | -37.3444 |  |  | -198.0411 |  |  | -508.2514 |  |  | -949.591 |  |  | -1441.6358 |  |  | -1962.9055 |  |  | -2559.2706
[13 empty] | P2 at this iteration flow rate |  |  | 24.7706 |  |  | 25.5542 |  |  | 29.8279 |  |  | 43.5089 |  |  | 75.6482 |  |  | 137.6903 |  |  | 225.9582 |  |  | 324.3672 |  |  | 428.6211 |  |  | 547.8941
[13 empty] | Delta P at this iteration flow rate |  |  | 31.5764 |  |  | 26.8746 |  |  | 1.2329 |  |  | -80.8533 |  |  | -273.6893 |  |  | -645.9416 |  |  | -1175.5492 |  |  | -1766.003 |  |  | -2391.5266 |  |  | -3107.1648
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.2939 |  |  | 43.0377 |  |  | 24.7768 |  |  | -29.1997 |  |  | -143.1421 |  |  | -327.6196 |  |  | -549.4641 |  |  | -689.9932 |  |  | -774.7888 |  |  | -962.8116
[13 empty] | C Non choked w/ reducers | 7 |  | 23.1056 |  |  | 70.3735 |  |  | 790.448 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 19.0825 |  |  | 55.6103 |  |  | 176.3243 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 23.1056 |  |  | 70.3735 |  |  | 790.448 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 18.1056 | 129.8178 |  | 58.3735 | 364.5138 |  | 767.448 | 874.9734 |  | 5500 | 1670.6449 |  | 5500 | 2747.5958 |  | 5500 | 4090.7957 |  | 5500 | 5459.1828 |  | 5500 | 6661.2405 |  | 5500 | 7733.4934 |  | 5500 | 8801.4368
[13 empty] | Next iteration flow rate |  |  | 132.4141 | Abs Value of | Flow this | 368.1589 | Abs Value of | Flow this | 883.7232 | Abs Value of | Flow this | 1687.3514 | Abs Value of | Flow this | 2775.0718 | Abs Value of | Flow this | 4131.7037 | Abs Value of | Flow this | 5513.7746 | Abs Value of | Flow this | 6727.8529 | Abs Value of | Flow this | 7810.8283 | Abs Value of | Flow this | 8889.4512 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.324 |  |  | 52.3386 |  |  | 30.541 |  |  | -39.239 |  |  | -203.1657 |  |  | -519.6112 |  |  | -969.8218 |  |  | -1471.7567 |  |  | -2003.5039 |  |  | -2611.856
[13 empty] | P2 at this iteration flow rate |  |  | 24.7752 |  |  | 25.5723 |  |  | 29.9318 |  |  | 43.8878 |  |  | 76.6731 |  |  | 139.9622 |  |  | 230.0044 |  |  | 330.3913 |  |  | 436.7408 |  |  | 558.4112
[13 empty] | Delta P at this iteration flow rate |  |  | 31.5488 |  |  | 26.7663 |  |  | 0.60926 |  |  | -83.1268 |  |  | -279.8388 |  |  | -659.5735 |  |  | -1199.8262 |  |  | -1802.1481 |  |  | -2440.2447 |  |  | -3170.2672
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.2748 |  |  | 42.963 |  |  | 24.3563 |  |  | -30.6639 |  |  | -146.8379 |  |  | -334.9359 |  |  | -561.1649 |  |  | -704.4052 |  |  | -790.8101 |  |  | -982.5911
[13 empty] | C Non choked w/ reducers | 7 |  | 23.578 |  |  | 71.2208 |  |  | 1135.6818 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 19.4682 |  |  | 56.2152 |  |  | 179.6183 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 23.578 |  |  | 71.2208 |  |  | 1135.6818 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 18.578 | 132.4141 |  | 59.2208 | 368.1589 |  | 1112.6818 | 883.7232 |  | 5500 | 1687.3514 |  | 5500 | 2775.0718 |  | 5500 | 4131.7037 |  | 5500 | 5513.7746 |  | 5500 | 6727.8529 |  | 5500 | 7810.8283 |  | 5500 | 8889.4512
[13 empty] | Next iteration flow rate |  |  | 135.0624 | Abs Value of | Flow this | 371.8405 | Abs Value of | Flow this | 892.5604 | Abs Value of | Flow this | 1704.2249 | Abs Value of | Flow this | 2802.8225 | Abs Value of | Flow this | 4173.0207 | Abs Value of | Flow this | 5568.9124 | Abs Value of | Flow this | 6795.1314 | Abs Value of | Flow this | 7888.9366 | Abs Value of | Flow this | 8978.3457 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.3001 |  |  | 52.2466 |  |  | 30.0109 |  |  | -41.1717 |  |  | -208.3933 |  |  | -531.1994 |  |  | -990.4592 |  |  | -1502.4831 |  |  | -2044.9184 |  |  | -2665.4983
[13 empty] | P2 at this iteration flow rate |  |  | 24.78 |  |  | 25.5907 |  |  | 30.0378 |  |  | 44.2743 |  |  | 77.7187 |  |  | 142.2799 |  |  | 234.1318 |  |  | 336.5366 |  |  | 445.0237 |  |  | 569.1397
[13 empty] | Delta P at this iteration flow rate |  |  | 31.5201 |  |  | 26.6559 |  |  | -0.026911 |  |  | -85.4461 |  |  | -286.112 |  |  | -673.4793 |  |  | -1224.5911 |  |  | -1839.0197 |  |  | -2489.9421 |  |  | -3234.638
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.255 |  |  | 42.8868 |  |  | 23.9274 |  |  | -32.1575 |  |  | -150.608 |  |  | -342.3992 |  |  | -573.1008 |  |  | -719.1069 |  |  | -807.1533 |  |  | -1002.7682
[13 empty] | C Non choked w/ reducers | 7 |  | 24.0605 |  |  | 72.0818 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 19.8618 |  |  | 56.8277 |  |  | 183.0335 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 24.0605 |  |  | 72.0818 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 19.0605 | 135.0624 |  | 60.0818 | 371.8405 |  | 5500 | 892.5604 |  | 5500 | 1704.2249 |  | 5500 | 2802.8225 |  | 5500 | 4173.0207 |  | 5500 | 5568.9124 |  | 5500 | 6795.1314 |  | 5500 | 7888.9366 |  | 5500 | 8978.3457
[13 empty] | Next iteration flow rate |  |  | 137.7637 | Abs Value of | Flow this | 375.5589 | Abs Value of | Flow this | 901.486 | Abs Value of | Flow this | 1721.2671 | Abs Value of | Flow this | 2830.8507 | Abs Value of | Flow this | 4214.7509 | Abs Value of | Flow this | 5624.6015 | Abs Value of | Flow this | 6863.0827 | Abs Value of | Flow this | 7967.826 | Abs Value of | Flow this | 9068.1292 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.2752 |  |  | 52.1527 |  |  | 29.4701 |  |  | -43.1433 |  |  | -213.7261 |  |  | -543.0206 |  |  | -1011.5115 |  |  | -1533.827 |  |  | -2087.1653 |  |  | -2720.2188
[13 empty] | P2 at this iteration flow rate |  |  | 24.785 |  |  | 25.6095 |  |  | 30.146 |  |  | 44.6687 |  |  | 78.7852 |  |  | 144.6441 |  |  | 238.3423 |  |  | 342.8054 |  |  | 453.4731 |  |  | 580.0838
[13 empty] | Delta P at this iteration flow rate |  |  | 31.4902 |  |  | 26.5433 |  |  | -0.67587 |  |  | -87.812 |  |  | -292.5113 |  |  | -687.6647 |  |  | -1249.8538 |  |  | -1876.6324 |  |  | -2540.6383 |  |  | -3300.3026
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.2344 |  |  | 42.8091 |  |  | 23.4898 |  |  | -33.6811 |  |  | -154.4539 |  |  | -350.0125 |  |  | -585.2767 |  |  | -734.1041 |  |  | -823.8251 |  |  | -1023.3508
[13 empty] | C Non choked w/ reducers | 7 |  | 24.5533 |  |  | 72.9569 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 20.2635 |  |  | 57.4481 |  |  | 186.5778 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 24.5533 |  |  | 72.9569 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 19.5533 | 137.7637 |  | 60.9569 | 375.5589 |  | 5500 | 901.486 |  | 5500 | 1721.2671 |  | 5500 | 2830.8507 |  | 5500 | 4214.7509 |  | 5500 | 5624.6015 |  | 5500 | 6863.0827 |  | 5500 | 7967.826 |  | 5500 | 9068.1292
[13 empty] | Next iteration flow rate |  |  | 140.5189 | Abs Value of | Flow this | 379.3145 | Abs Value of | Flow this | 910.5008 | Abs Value of | Flow this | 1738.4798 | Abs Value of | Flow this | 2859.1592 | Abs Value of | Flow this | 4256.8985 | Abs Value of | Flow this | 5680.8475 | Abs Value of | Flow this | 6931.7135 | Abs Value of | Flow this | 8047.5042 | Abs Value of | Flow this | 9158.8105 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.2493 |  |  | 52.057 |  |  | 28.9184 |  |  | -45.1545 |  |  | -219.166 |  |  | -555.0793 |  |  | -1032.9869 |  |  | -1565.8009 |  |  | -2130.2613 |  |  | -2776.0393
[13 empty] | P2 at this iteration flow rate |  |  | 24.7901 |  |  | 25.6286 |  |  | 30.2563 |  |  | 45.0709 |  |  | 79.8732 |  |  | 147.0559 |  |  | 242.6374 |  |  | 349.2002 |  |  | 462.0923 |  |  | 591.2479
[13 empty] | Delta P at this iteration flow rate |  |  | 31.4591 |  |  | 26.4284 |  |  | -1.3379 |  |  | -90.2254 |  |  | -299.0392 |  |  | -702.1351 |  |  | -1275.6242 |  |  | -1915.0011 |  |  | -2592.3536 |  |  | -3367.2871
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.213 |  |  | 42.7299 |  |  | 23.0434 |  |  | -35.2354 |  |  | -158.3771 |  |  | -357.7789 |  |  | -597.6973 |  |  | -749.4027 |  |  | -840.8319 |  |  | -1044.3471
[13 empty] | C Non choked w/ reducers | 7 |  | 25.0568 |  |  | 73.8465 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 20.6736 |  |  | 58.0763 |  |  | 190.26 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 25.0568 |  |  | 73.8465 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 20.0568 | 140.5189 |  | 61.8465 | 379.3145 |  | 5500 | 910.5008 |  | 5500 | 1738.4798 |  | 5500 | 2859.1592 |  | 5500 | 4256.8985 |  | 5500 | 5680.8475 |  | 5500 | 6931.7135 |  | 5500 | 8047.5042 |  | 5500 | 9158.8105
[13 empty] | Next iteration flow rate |  |  | 143.3293 | Abs Value of | Flow this | 383.1077 | Abs Value of | Flow this | 919.6059 | Abs Value of | Flow this | 1755.8646 | Abs Value of | Flow this | 2887.7508 | Abs Value of | Flow this | 4299.4674 | Abs Value of | Flow this | 5737.656 | Abs Value of | Flow this | 7001.0307 | Abs Value of | Flow this | 8127.9793 | Abs Value of | Flow this | 9250.3986 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.2223 |  |  | 51.9593 |  |  | 28.3557 |  |  | -47.2061 |  |  | -224.7152 |  |  | -567.3804 |  |  | -1054.8939 |  |  | -1598.4175 |  |  | -2174.2236 |  |  | -2832.9817
[13 empty] | P2 at this iteration flow rate |  |  | 24.7955 |  |  | 25.6481 |  |  | 30.3689 |  |  | 45.4812 |  |  | 80.983 |  |  | 149.5161 |  |  | 247.0188 |  |  | 355.7235 |  |  | 470.8847 |  |  | 602.6363
[13 empty] | Delta P at this iteration flow rate |  |  | 31.4268 |  |  | 26.3112 |  |  | -2.0132 |  |  | -92.6874 |  |  | -305.6983 |  |  | -716.8965 |  |  | -1301.9127 |  |  | -1954.141 |  |  | -2645.1083 |  |  | -3435.618
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.1907 |  |  | 42.649 |  |  | 22.588 |  |  | -36.8208 |  |  | -162.3792 |  |  | -365.7013 |  |  | -610.3675 |  |  | -765.0088 |  |  | -858.1806 |  |  | -1065.7655
[13 empty] | C Non choked w/ reducers | 7 |  | 25.571 |  |  | 74.7509 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 21.0922 |  |  | 58.7127 |  |  | 194.0898 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 25.571 |  |  | 74.7509 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 20.571 | 143.3293 |  | 62.7509 | 383.1077 |  | 5500 | 919.6059 |  | 5500 | 1755.8646 |  | 5500 | 2887.7508 |  | 5500 | 4299.4674 |  | 5500 | 5737.656 |  | 5500 | 7001.0307 |  | 5500 | 8127.9793 |  | 5500 | 9250.3986
[13 empty] | Next iteration flow rate |  |  | 146.1959 | Abs Value of | Flow this | 386.9387 | Abs Value of | Flow this | 928.8019 | Abs Value of | Flow this | 1773.4232 | Abs Value of | Flow this | 2916.6283 | Abs Value of | Flow this | 4342.4621 | Abs Value of | Flow this | 5795.0325 | Abs Value of | Flow this | 7071.041 | Abs Value of | Flow this | 8209.259 | Abs Value of | Flow this | 9342.9026 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.1943 |  |  | 51.8597 |  |  | 27.7816 |  |  | -49.299 |  |  | -230.376 |  |  | -579.9287 |  |  | -1077.2413 |  |  | -1631.6897 |  |  | -2219.0695 |  |  | -2891.0686
[13 empty] | P2 at this iteration flow rate |  |  | 24.8011 |  |  | 25.6681 |  |  | 30.4837 |  |  | 45.8998 |  |  | 82.1152 |  |  | 152.0257 |  |  | 251.4883 |  |  | 362.3779 |  |  | 479.8539 |  |  | 614.2537
[13 empty] | Delta P at this iteration flow rate |  |  | 31.3932 |  |  | 26.1916 |  |  | -2.702 |  |  | -95.1988 |  |  | -312.4912 |  |  | -731.9545 |  |  | -1328.7296 |  |  | -1994.0677 |  |  | -2698.9234 |  |  | -3505.3223
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.1675 |  |  | 42.5665 |  |  | 22.1235 |  |  | -38.4382 |  |  | -166.4616 |  |  | -373.783 |  |  | -623.2925 |  |  | -780.9287 |  |  | -875.878 |  |  | -1087.6144
[13 empty] | C Non choked w/ reducers | 7 |  | 26.0964 |  |  | 75.6705 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 21.5194 |  |  | 59.3572 |  |  | 198.078 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 26.0964 |  |  | 75.6705 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 21.0964 | 146.1959 |  | 63.6705 | 386.9387 |  | 5500 | 928.8019 |  | 5500 | 1773.4232 |  | 5500 | 2916.6283 |  | 5500 | 4342.4621 |  | 5500 | 5795.0325 |  | 5500 | 7071.041 |  | 5500 | 8209.259 |  | 5500 | 9342.9026
[13 empty] | Next iteration flow rate |  |  | 149.1198 | Abs Value of | Flow this | 390.8081 | Abs Value of | Flow this | 938.0899 | Abs Value of | Flow this | 1791.1575 | Abs Value of | Flow this | 2945.7946 | Abs Value of | Flow this | 4385.8867 | Abs Value of | Flow this | 5852.9829 | Abs Value of | Flow this | 7141.7514 | Abs Value of | Flow this | 8291.3516 | Abs Value of | Flow this | 9436.3316 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.1652 |  |  | 51.7581 |  |  | 27.196 |  |  | -51.4339 |  |  | -236.1506 |  |  | -592.7293 |  |  | -1100.0379 |  |  | -1665.6307 |  |  | -2264.8168 |  |  | -2950.3231
[13 empty] | P2 at this iteration flow rate |  |  | 24.807 |  |  | 25.6884 |  |  | 30.6008 |  |  | 46.3268 |  |  | 83.2701 |  |  | 154.5859 |  |  | 256.0476 |  |  | 369.1661 |  |  | 489.0034 |  |  | 626.1046
[13 empty] | Delta P at this iteration flow rate |  |  | 31.3582 |  |  | 26.0697 |  |  | -3.4048 |  |  | -97.7607 |  |  | -319.4207 |  |  | -747.3152 |  |  | -1356.0854 |  |  | -2034.7969 |  |  | -2753.8201 |  |  | -3576.4277
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.1433 |  |  | 42.4824 |  |  | 21.6497 |  |  | -40.0881 |  |  | -170.6262 |  |  | -382.0272 |  |  | -636.4772 |  |  | -797.1685 |  |  | -893.9311 |  |  | -1109.9024
[13 empty] | C Non choked w/ reducers | 7 |  | 26.6332 |  |  | 76.6058 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 21.9556 |  |  | 60.0101 |  |  | 202.2362 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 26.6332 |  |  | 76.6058 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 21.6332 | 149.1198 |  | 64.6058 | 390.8081 |  | 5500 | 938.0899 |  | 5500 | 1791.1575 |  | 5500 | 2945.7946 |  | 5500 | 4385.8867 |  | 5500 | 5852.9829 |  | 5500 | 7141.7514 |  | 5500 | 8291.3516 |  | 5500 | 9436.3316
[13 empty] | Next iteration flow rate |  |  | 152.1022 | Abs Value of | Flow this | 394.7162 | Abs Value of | Flow this | 947.4708 | Abs Value of | Flow this | 1809.0691 | Abs Value of | Flow this | 2975.2525 | Abs Value of | Flow this | 4429.7456 | Abs Value of | Flow this | 5911.5127 | Abs Value of | Flow this | 7213.1689 | Abs Value of | Flow this | 8374.2652 | Abs Value of | Flow this | 9530.6949 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.1348 |  |  | 51.6544 |  |  | 26.5986 |  |  | -53.6117 |  |  | -242.0412 |  |  | -605.7872 |  |  | -1123.2926 |  |  | -1700.2539 |  |  | -2311.4836 |  |  | -3010.7686
[13 empty] | P2 at this iteration flow rate |  |  | 24.813 |  |  | 25.7091 |  |  | 30.7203 |  |  | 46.7623 |  |  | 84.4482 |  |  | 157.1974 |  |  | 260.6985 |  |  | 376.0908 |  |  | 498.3367 |  |  | 638.1937
[13 empty] | Delta P at this iteration flow rate |  |  | 31.3218 |  |  | 25.9453 |  |  | -4.1216 |  |  | -100.3741 |  |  | -326.4895 |  |  | -762.9846 |  |  | -1383.9912 |  |  | -2076.3447 |  |  | -2809.8203 |  |  | -3648.9623
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.1182 |  |  | 42.3966 |  |  | 21.1663 |  |  | -41.7711 |  |  | -174.8744 |  |  | -390.437 |  |  | -649.9269 |  |  | -813.7347 |  |  | -912.3471 |  |  | -1132.6384
[13 empty] | C Non choked w/ reducers | 7 |  | 27.1816 |  |  | 77.5571 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 22.4008 |  |  | 60.6716 |  |  | 206.5777 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 27.1816 |  |  | 77.5571 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 22.1816 | 152.1022 |  | 65.5571 | 394.7162 |  | 5500 | 947.4708 |  | 5500 | 1809.0691 |  | 5500 | 2975.2525 |  | 5500 | 4429.7456 |  | 5500 | 5911.5127 |  | 5500 | 7213.1689 |  | 5500 | 8374.2652 |  | 5500 | 9530.6949
[13 empty] | Next iteration flow rate |  |  | 155.1442 | Abs Value of | Flow this | 398.6634 | Abs Value of | Flow this | 956.9455 | Abs Value of | Flow this | 1827.1597 | Abs Value of | Flow this | 3005.0051 | Abs Value of | Flow this | 4474.0431 | Abs Value of | Flow this | 5970.6278 | Abs Value of | Flow this | 7285.3006 | Abs Value of | Flow this | 8458.0078 | Abs Value of | Flow this | 9626.0018 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.1033 |  |  | 51.5486 |  |  | 25.9893 |  |  | -55.8334 |  |  | -248.0503 |  |  | -619.1075 |  |  | -1147.0148 |  |  | -1735.573 |  |  | -2359.0885 |  |  | -3072.4291
[13 empty] | P2 at this iteration flow rate |  |  | 24.8193 |  |  | 25.7303 |  |  | 30.8421 |  |  | 47.2067 |  |  | 85.6501 |  |  | 159.8615 |  |  | 265.443 |  |  | 383.1546 |  |  | 507.8577 |  |  | 650.5258
[13 empty] | Delta P at this iteration flow rate |  |  | 31.2839 |  |  | 25.8183 |  |  | -4.8529 |  |  | -103.04 |  |  | -333.7003 |  |  | -778.969 |  |  | -1412.4578 |  |  | -2118.7276 |  |  | -2866.9461 |  |  | -3722.9549
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.092 |  |  | 42.309 |  |  | 20.6732 |  |  | -43.4879 |  |  | -179.2081 |  |  | -399.0159 |  |  | -663.647 |  |  | -830.6339 |  |  | -931.1332 |  |  | -1155.8314
[13 empty] | C Non choked w/ reducers | 7 |  | 27.7421 |  |  | 78.525 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 22.8553 |  |  | 61.3416 |  |  | 211.1171 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 27.7421 |  |  | 78.525 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 22.7421 | 155.1442 |  | 66.525 | 398.6634 |  | 5500 | 956.9455 |  | 5500 | 1827.1597 |  | 5500 | 3005.0051 |  | 5500 | 4474.0431 |  | 5500 | 5970.6278 |  | 5500 | 7285.3006 |  | 5500 | 8458.0078 |  | 5500 | 9626.0018
[13 empty] | Next iteration flow rate |  |  | 158.2471 | Abs Value of | Flow this | 402.65 | Abs Value of | Flow this | 966.515 | Abs Value of | Flow this | 1845.4313 | Abs Value of | Flow this | 3035.0551 | Abs Value of | Flow this | 4518.7835 | Abs Value of | Flow this | 6030.3341 | Abs Value of | Flow this | 7358.1536 | Abs Value of | Flow this | 8542.5879 | Abs Value of | Flow this | 9722.2619 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.0704 |  |  | 51.4407 |  |  | 25.3676 |  |  | -58.0996 |  |  | -254.1801 |  |  | -632.6956 |  |  | -1171.2139 |  |  | -1771.6021 |  |  | -2407.6501 |  |  | -3135.3289
[13 empty] | P2 at this iteration flow rate |  |  | 24.8259 |  |  | 25.7519 |  |  | 30.9665 |  |  | 47.6599 |  |  | 86.876 |  |  | 162.5791 |  |  | 270.2828 |  |  | 390.3604 |  |  | 517.57 |  |  | 663.1058
[13 empty] | Delta P at this iteration flow rate |  |  | 31.2445 |  |  | 25.6889 |  |  | -5.5988 |  |  | -105.7595 |  |  | -341.0561 |  |  | -795.2747 |  |  | -1441.4966 |  |  | -2161.9625 |  |  | -2925.2202 |  |  | -3798.4347
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.0649 |  |  | 42.2197 |  |  | 20.1702 |  |  | -45.2393 |  |  | -183.6288 |  |  | -407.7672 |  |  | -677.6428 |  |  | -847.8728 |  |  | -950.297 |  |  | -1179.4906
[13 empty] | C Non choked w/ reducers | 7 |  | 28.3147 |  |  | 79.5098 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 23.3192 |  |  | 62.0206 |  |  | 215.8705 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 28.3147 |  |  | 79.5098 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 23.3147 | 158.2471 |  | 67.5098 | 402.65 |  | 5500 | 966.515 |  | 5500 | 1845.4313 |  | 5500 | 3035.0551 |  | 5500 | 4518.7835 |  | 5500 | 6030.3341 |  | 5500 | 7358.1536 |  | 5500 | 8542.5879 |  | 5500 | 9722.2619
[13 empty] | Next iteration flow rate |  |  | 161.4121 | Abs Value of | Flow this | 406.6765 | Abs Value of | Flow this | 976.1801 | Abs Value of | Flow this | 1863.8857 | Abs Value of | Flow this | 3065.4057 | Abs Value of | Flow this | 4563.9713 | Abs Value of | Flow this | 6090.6374 | Abs Value of | Flow this | 7431.7351 | Abs Value of | Flow this | 8628.0138 | Abs Value of | Flow this | 9819.4845 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.0362 |  |  | 51.3307 |  |  | 24.7335 |  |  | -60.4114 |  |  | -260.4331 |  |  | -646.5568 |  |  | -1195.8993 |  |  | -1808.3553 |  |  | -2457.1879 |  |  | -3199.493
[13 empty] | P2 at this iteration flow rate |  |  | 24.8328 |  |  | 25.7739 |  |  | 31.0933 |  |  | 48.1223 |  |  | 88.1266 |  |  | 165.3514 |  |  | 275.2199 |  |  | 397.7111 |  |  | 527.4776 |  |  | 675.9386
[13 empty] | Delta P at this iteration flow rate |  |  | 31.2035 |  |  | 25.5568 |  |  | -6.3598 |  |  | -108.5337 |  |  | -348.5598 |  |  | -811.9082 |  |  | -1471.1191 |  |  | -2206.0663 |  |  | -2984.6655 |  |  | -3875.4316
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.0366 |  |  | 42.1286 |  |  | 19.6571 |  |  | -47.0259 |  |  | -188.1385 |  |  | -416.6944 |  |  | -691.92 |  |  | -865.4582 |  |  | -969.8459 |  |  | -1203.6254
[13 empty] | C Non choked w/ reducers | 7 |  | 28.9 |  |  | 80.5122 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 23.7929 |  |  | 62.7085 |  |  | 220.8565 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 28.9 |  |  | 80.5122 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 23.9 | 161.4121 |  | 68.5122 | 406.6765 |  | 5500 | 976.1801 |  | 5500 | 1863.8857 |  | 5500 | 3065.4057 |  | 5500 | 4563.9713 |  | 5500 | 6090.6374 |  | 5500 | 7431.7351 |  | 5500 | 8628.0138 |  | 5500 | 9819.4845
[13 empty] | Next iteration flow rate |  |  | 164.6403 | Abs Value of | Flow this | 410.7433 | Abs Value of | Flow this | 985.9419 | Abs Value of | Flow this | 1882.5245 | Abs Value of | Flow this | 3096.0597 | Abs Value of | Flow this | 4609.611 | Abs Value of | Flow this | 6151.5438 | Abs Value of | Flow this | 7506.0525 | Abs Value of | Flow this | 8714.2939 | Abs Value of | Flow this | 9917.6793 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 56.0007 |  |  | 51.2184 |  |  | 24.0866 |  |  | -62.7697 |  |  | -266.8118 |  |  | -660.6966 |  |  | -1221.0809 |  |  | -1845.8472 |  |  | -2507.7214 |  |  | -3264.9469
[13 empty] | P2 at this iteration flow rate |  |  | 24.8399 |  |  | 25.7963 |  |  | 31.2227 |  |  | 48.5939 |  |  | 89.4024 |  |  | 168.1793 |  |  | 280.2562 |  |  | 405.2094 |  |  | 537.5843 |  |  | 689.0294
[13 empty] | Delta P at this iteration flow rate |  |  | 31.1608 |  |  | 25.4221 |  |  | -7.136 |  |  | -111.3637 |  |  | -356.2142 |  |  | -828.8759 |  |  | -1501.337 |  |  | -2251.0567 |  |  | -3045.3057 |  |  | -3953.9762
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 46.0071 |  |  | 42.0357 |  |  | 19.1337 |  |  | -48.8483 |  |  | -192.7387 |  |  | -425.8011 |  |  | -706.4841 |  |  | -883.3971 |  |  | -989.7878 |  |  | -1228.2452
[13 empty] | C Non choked w/ reducers | 7 |  | 29.4982 |  |  | 81.5325 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 24.2766 |  |  | 63.4055 |  |  | 226.0955 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 29.4982 |  |  | 81.5325 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 24.4982 | 164.6403 |  | 69.5325 | 410.7433 |  | 5500 | 985.9419 |  | 5500 | 1882.5245 |  | 5500 | 3096.0597 |  | 5500 | 4609.611 |  | 5500 | 6151.5438 |  | 5500 | 7506.0525 |  | 5500 | 8714.2939 |  | 5500 | 9917.6793
[13 empty] | Next iteration flow rate |  |  | 167.9331 | Abs Value of | Flow this | 414.8507 | Abs Value of | Flow this | 995.8014 | Abs Value of | Flow this | 1901.3498 | Abs Value of | Flow this | 3127.0203 | Abs Value of | Flow this | 4655.7071 | Abs Value of | Flow this | 6213.0592 | Abs Value of | Flow this | 7581.113 | Abs Value of | Flow this | 8801.4368 | Abs Value of | Flow this | 10016.8561 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.9637 |  |  | 51.1039 |  |  | 23.4268 |  |  | -65.1754 |  |  | -273.3188 |  |  | -675.1206 |  |  | -1246.7686 |  |  | -1884.0928 |  |  | -2559.2706 |  |  | -3331.7163
[13 empty] | P2 at this iteration flow rate |  |  | 24.8473 |  |  | 25.8192 |  |  | 31.3546 |  |  | 49.0751 |  |  | 90.7038 |  |  | 171.0641 |  |  | 285.3937 |  |  | 412.8586 |  |  | 547.8941 |  |  | 702.3833
[13 empty] | Delta P at this iteration flow rate |  |  | 31.1165 |  |  | 25.2847 |  |  | -7.9279 |  |  | -114.2505 |  |  | -364.0225 |  |  | -846.1848 |  |  | -1532.1623 |  |  | -2296.9513 |  |  | -3107.1648 |  |  | -4034.0996
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.9765 |  |  | 41.9409 |  |  | 18.5998 |  |  | -50.7075 |  |  | -197.4314 |  |  | -435.0908 |  |  | -721.341 |  |  | -901.6965 |  |  | -1010.1305 |  |  | -1253.3599
[13 empty] | C Non choked w/ reducers | 7 |  | 30.1096 |  |  | 82.5713 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 24.7703 |  |  | 64.1119 |  |  | 231.611 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 30.1096 |  |  | 82.5713 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 25.1096 | 167.9331 |  | 70.5713 | 414.8507 |  | 5500 | 995.8014 |  | 5500 | 1901.3498 |  | 5500 | 3127.0203 |  | 5500 | 4655.7071 |  | 5500 | 6213.0592 |  | 5500 | 7581.113 |  | 5500 | 8801.4368 |  | 5500 | 10016.8561
[13 empty] | Next iteration flow rate |  |  | 171.2918 | Abs Value of | Flow this | 418.9992 | Abs Value of | Flow this | 1005.7594 | Abs Value of | Flow this | 1920.3633 | Abs Value of | Flow this | 3158.2905 | Abs Value of | Flow this | 4702.2642 | Abs Value of | Flow this | 6275.1898 | Abs Value of | Flow this | 7656.9241 | Abs Value of | Flow this | 8889.4512 | Abs Value of | Flow this | 10117.0247 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.9252 |  |  | 50.9871 |  |  | 22.7536 |  |  | -67.6295 |  |  | -279.9565 |  |  | -689.8346 |  |  | -1272.9727 |  |  | -1923.1071 |  |  | -2611.856 |  |  | -3399.8278
[13 empty] | P2 at this iteration flow rate |  |  | 24.855 |  |  | 25.8426 |  |  | 31.4893 |  |  | 49.5659 |  |  | 92.0313 |  |  | 174.0069 |  |  | 290.6345 |  |  | 420.6614 |  |  | 558.4112 |  |  | 716.0056
[13 empty] | Delta P at this iteration flow rate |  |  | 31.0703 |  |  | 25.1445 |  |  | -8.7356 |  |  | -117.1953 |  |  | -371.9878 |  |  | -863.8415 |  |  | -1563.6072 |  |  | -2343.7685 |  |  | -3170.2672 |  |  | -4115.8334
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.9446 |  |  | 41.8442 |  |  | 18.0551 |  |  | -52.6039 |  |  | -202.2185 |  |  | -444.5672 |  |  | -736.4965 |  |  | -920.3637 |  |  | -1030.8821 |  |  | -1278.9795
[13 empty] | C Non choked w/ reducers | 7 |  | 30.7346 |  |  | 83.6291 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 25.2745 |  |  | 64.8278 |  |  | 237.4293 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 30.7346 |  |  | 83.6291 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 25.7346 | 171.2918 |  | 71.6291 | 418.9992 |  | 5500 | 1005.7594 |  | 5500 | 1920.3633 |  | 5500 | 3158.2905 |  | 5500 | 4702.2642 |  | 5500 | 6275.1898 |  | 5500 | 7656.9241 |  | 5500 | 8889.4512 |  | 5500 | 10117.0247
[13 empty] | Next iteration flow rate |  |  | 174.7176 | Abs Value of | Flow this | 423.1892 | Abs Value of | Flow this | 1015.817 | Abs Value of | Flow this | 1939.5669 | Abs Value of | Flow this | 3189.8734 | Abs Value of | Flow this | 4749.2869 | Abs Value of | Flow this | 6337.9417 | Abs Value of | Flow this | 7733.4934 | Abs Value of | Flow this | 8978.3457 | Abs Value of | Flow this | 10218.1949 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.8852 |  |  | 50.8679 |  |  | 22.067 |  |  | -70.1328 |  |  | -286.7276 |  |  | -704.8443 |  |  | -1299.7034 |  |  | -1962.9055 |  |  | -2665.4983 |  |  | -3469.3084
[13 empty] | P2 at this iteration flow rate |  |  | 24.863 |  |  | 25.8664 |  |  | 31.6266 |  |  | 50.0666 |  |  | 93.3855 |  |  | 177.0089 |  |  | 295.9807 |  |  | 428.6211 |  |  | 569.1397 |  |  | 729.9017
[13 empty] | Delta P at this iteration flow rate |  |  | 31.0222 |  |  | 25.0015 |  |  | -9.5596 |  |  | -120.1994 |  |  | -380.1132 |  |  | -881.8531 |  |  | -1595.6841 |  |  | -2391.5266 |  |  | -3234.638 |  |  | -4199.21
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.9115 |  |  | 41.7455 |  |  | 17.4995 |  |  | -54.5385 |  |  | -207.1017 |  |  | -454.2341 |  |  | -751.9566 |  |  | -939.4062 |  |  | -1052.0508 |  |  | -1305.1139
[13 empty] | C Non choked w/ reducers | 7 |  | 31.3736 |  |  | 84.7067 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 25.7893 |  |  | 65.5534 |  |  | 243.5808 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 31.3736 |  |  | 84.7067 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 26.3736 | 174.7176 |  | 72.7067 | 423.1892 |  | 5500 | 1015.817 |  | 5500 | 1939.5669 |  | 5500 | 3189.8734 |  | 5500 | 4749.2869 |  | 5500 | 6337.9417 |  | 5500 | 7733.4934 |  | 5500 | 8978.3457 |  | 5500 | 10218.1949
[13 empty] | Next iteration flow rate |  |  | 178.212 | Abs Value of | Flow this | 427.4211 | Abs Value of | Flow this | 1025.9751 | Abs Value of | Flow this | 1958.9626 | Abs Value of | Flow this | 3221.7722 | Abs Value of | Flow this | 4796.7797 | Abs Value of | Flow this | 6401.3211 | Abs Value of | Flow this | 7810.8283 | Abs Value of | Flow this | 9068.1292 | Abs Value of | Flow this | 10320.3769 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.8435 |  |  | 50.7463 |  |  | 21.3665 |  |  | -72.6865 |  |  | -293.6349 |  |  | -720.1556 |  |  | -1326.9715 |  |  | -2003.5039 |  |  | -2720.2188 |  |  | -3540.1855
[13 empty] | P2 at this iteration flow rate |  |  | 24.8713 |  |  | 25.8907 |  |  | 31.7667 |  |  | 50.5773 |  |  | 94.767 |  |  | 180.0711 |  |  | 301.4343 |  |  | 436.7408 |  |  | 580.0838 |  |  | 744.0771
[13 empty] | Delta P at this iteration flow rate |  |  | 30.9723 |  |  | 24.8556 |  |  | -10.4002 |  |  | -123.2638 |  |  | -388.4019 |  |  | -900.2268 |  |  | -1628.4058 |  |  | -2440.2447 |  |  | -3300.3026 |  |  | -4284.2626
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.877 |  |  | 41.6449 |  |  | 16.9327 |  |  | -56.512 |  |  | -212.0831 |  |  | -464.0953 |  |  | -767.7275 |  |  | -958.8314 |  |  | -1073.645 |  |  | -1331.7737
[13 empty] | C Non choked w/ reducers | 7 |  | 32.0268 |  |  | 85.8044 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 26.315 |  |  | 66.2889 |  |  | 250.1002 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 32.0268 |  |  | 85.8044 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 27.0268 | 178.212 |  | 73.8044 | 427.4211 |  | 5500 | 1025.9751 |  | 5500 | 1958.9626 |  | 5500 | 3221.7722 |  | 5500 | 4796.7797 |  | 5500 | 6401.3211 |  | 5500 | 7810.8283 |  | 5500 | 9068.1292 |  | 5500 | 10320.3769
[13 empty] | Next iteration flow rate |  |  | 181.7762 | Abs Value of | Flow this | 431.6953 | Abs Value of | Flow this | 1036.2349 | Abs Value of | Flow this | 1978.5522 | Abs Value of | Flow this | 3253.9899 | Abs Value of | Flow this | 4844.7475 | Abs Value of | Flow this | 6465.3344 | Abs Value of | Flow this | 7888.9366 | Abs Value of | Flow this | 9158.8105 | Abs Value of | Flow this | 10423.5807 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.8002 |  |  | 50.6223 |  |  | 20.652 |  |  | -75.2915 |  |  | -300.681 |  |  | -735.7748 |  |  | -1354.7876 |  |  | -2044.9184 |  |  | -2776.0393 |  |  | -3612.4872
[13 empty] | P2 at this iteration flow rate |  |  | 24.88 |  |  | 25.9155 |  |  | 31.9096 |  |  | 51.0983 |  |  | 96.1762 |  |  | 183.195 |  |  | 306.9975 |  |  | 445.0237 |  |  | 591.2479 |  |  | 758.5374
[13 empty] | Delta P at this iteration flow rate |  |  | 30.9203 |  |  | 24.7068 |  |  | -11.2577 |  |  | -126.3898 |  |  | -396.8571 |  |  | -918.9698 |  |  | -1661.7851 |  |  | -2489.9421 |  |  | -3367.2871 |  |  | -4371.0247
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.8411 |  |  | 41.5422 |  |  | 16.3545 |  |  | -58.5251 |  |  | -217.1647 |  |  | -474.1547 |  |  | -783.8154 |  |  | -978.6471 |  |  | -1095.6732 |  |  | -1358.9693
[13 empty] | C Non choked w/ reducers | 7 |  | 32.6948 |  |  | 86.9231 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 26.8518 |  |  | 67.0345 |  |  | 257.0275 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 32.6948 |  |  | 86.9231 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 27.6948 | 181.7762 |  | 74.9231 | 431.6953 |  | 5500 | 1036.2349 |  | 5500 | 1978.5522 |  | 5500 | 3253.9899 |  | 5500 | 4844.7475 |  | 5500 | 6465.3344 |  | 5500 | 7888.9366 |  | 5500 | 9158.8105 |  | 5500 | 10423.5807
[13 empty] | Next iteration flow rate |  |  | 185.4117 | Abs Value of | Flow this | 436.0123 | Abs Value of | Flow this | 1046.5972 | Abs Value of | Flow this | 1998.3377 | Abs Value of | Flow this | 3286.5298 | Abs Value of | Flow this | 4893.195 | Abs Value of | Flow this | 6529.9877 | Abs Value of | Flow this | 7967.826 | Abs Value of | Flow this | 9250.3986 | Abs Value of | Flow this | 10527.8165 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.7551 |  |  | 50.4958 |  |  | 19.923 |  |  | -77.9489 |  |  | -307.8687 |  |  | -751.7079 |  |  | -1383.1629 |  |  | -2087.1653 |  |  | -2832.9817 |  |  | -3686.2422
[13 empty] | P2 at this iteration flow rate |  |  | 24.889 |  |  | 25.9408 |  |  | 32.0554 |  |  | 51.6298 |  |  | 97.6137 |  |  | 186.3816 |  |  | 312.6726 |  |  | 453.4731 |  |  | 602.6363 |  |  | 773.2884
[13 empty] | Delta P at this iteration flow rate |  |  | 30.8662 |  |  | 24.5549 |  |  | -12.1324 |  |  | -129.5787 |  |  | -405.4824 |  |  | -938.0895 |  |  | -1695.8354 |  |  | -2540.6383 |  |  | -3435.618 |  |  | -4459.5307
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.8038 |  |  | 41.4375 |  |  | 15.7647 |  |  | -60.5788 |  |  | -222.3484 |  |  | -484.4163 |  |  | -800.2266 |  |  | -998.861 |  |  | -1118.1442 |  |  | -1386.7116
[13 empty] | C Non choked w/ reducers | 7 |  | 33.3779 |  |  | 88.0633 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 27.4 |  |  | 67.7903 |  |  | 264.4093 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 33.3779 |  |  | 88.0633 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 28.3779 | 185.4117 |  | 76.0633 | 436.0123 |  | 5500 | 1046.5972 |  | 5500 | 1998.3377 |  | 5500 | 3286.5298 |  | 5500 | 4893.195 |  | 5500 | 6529.9877 |  | 5500 | 7967.826 |  | 5500 | 9250.3986 |  | 5500 | 10527.8165
[13 empty] | Next iteration flow rate |  |  | 189.12 | Abs Value of | Flow this | 440.3724 | Abs Value of | Flow this | 1057.0632 | Abs Value of | Flow this | 2018.3211 | Abs Value of | Flow this | 3319.3951 | Abs Value of | Flow this | 4942.127 | Abs Value of | Flow this | 6595.2876 | Abs Value of | Flow this | 8047.5042 | Abs Value of | Flow this | 9342.9026 | Abs Value of | Flow this | 10633.0946 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.7082 |  |  | 50.3667 |  |  | 19.1795 |  |  | -80.6597 |  |  | -315.2008 |  |  | -767.9612 |  |  | -1412.1085 |  |  | -2130.2613 |  |  | -2891.0686 |  |  | -3761.4797
[13 empty] | P2 at this iteration flow rate |  |  | 24.8984 |  |  | 25.9667 |  |  | 32.2041 |  |  | 52.1719 |  |  | 99.0802 |  |  | 189.6322 |  |  | 318.4617 |  |  | 462.0923 |  |  | 614.2537 |  |  | 788.3359
[13 empty] | Delta P at this iteration flow rate |  |  | 30.8099 |  |  | 24.4001 |  |  | -13.0246 |  |  | -132.8316 |  |  | -414.281 |  |  | -957.5935 |  |  | -1730.5701 |  |  | -2592.3536 |  |  | -3505.3223 |  |  | -4549.8157
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.7649 |  |  | 41.3306 |  |  | 15.1631 |  |  | -62.6736 |  |  | -227.6362 |  |  | -494.8842 |  |  | -816.9677 |  |  | -1019.4813 |  |  | -1141.0669 |  |  | -1415.0115
[13 empty] | C Non choked w/ reducers | 7 |  | 34.0766 |  |  | 89.2257 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 27.9598 |  |  | 68.5567 |  |  | 272.3001 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 34.0766 |  |  | 89.2257 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 29.0766 | 189.12 |  | 77.2257 | 440.3724 |  | 5500 | 1057.0632 |  | 5500 | 2018.3211 |  | 5500 | 3319.3951 |  | 5500 | 4942.127 |  | 5500 | 6595.2876 |  | 5500 | 8047.5042 |  | 5500 | 9342.9026 |  | 5500 | 10633.0946
[13 empty] | Next iteration flow rate |  |  | 192.9024 | Abs Value of | Flow this | 444.7761 | Abs Value of | Flow this | 1067.6338 | Abs Value of | Flow this | 2038.5043 | Abs Value of | Flow this | 3352.589 | Abs Value of | Flow this | 4991.5482 | Abs Value of | Flow this | 6661.2405 | Abs Value of | Flow this | 8127.9793 | Abs Value of | Flow this | 9436.3316 | Abs Value of | Flow this | 10739.4256 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.6594 |  |  | 50.2351 |  |  | 18.421 |  |  | -83.4249 |  |  | -322.6804 |  |  | -784.5413 |  |  | -1441.6358 |  |  | -2174.2236 |  |  | -2950.3231 |  |  | -3838.2295
[13 empty] | P2 at this iteration flow rate |  |  | 24.9081 |  |  | 25.993 |  |  | 32.3558 |  |  | 52.725 |  |  | 100.5761 |  |  | 192.9483 |  |  | 324.3672 |  |  | 470.8847 |  |  | 626.1046 |  |  | 803.6859
[13 empty] | Delta P at this iteration flow rate |  |  | 30.7513 |  |  | 24.2421 |  |  | -13.9348 |  |  | -136.1499 |  |  | -423.2565 |  |  | -977.4895 |  |  | -1766.003 |  |  | -2645.1083 |  |  | -3576.4277 |  |  | -4641.9154
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.7245 |  |  | 41.2217 |  |  | 14.5493 |  |  | -64.8106 |  |  | -233.0304 |  |  | -505.5625 |  |  | -834.0453 |  |  | -1040.516 |  |  | -1164.4503 |  |  | -1443.8802
[13 empty] | C Non choked w/ reducers | 7 |  | 34.7912 |  |  | 90.4111 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 28.5316 |  |  | 69.3337 |  |  | 280.7639 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 34.7912 |  |  | 90.4111 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 29.7912 | 192.9024 |  | 78.4111 | 444.7761 |  | 5500 | 1067.6338 |  | 5500 | 2038.5043 |  | 5500 | 3352.589 |  | 5500 | 4991.5482 |  | 5500 | 6661.2405 |  | 5500 | 8127.9793 |  | 5500 | 9436.3316 |  | 5500 | 10739.4256
[13 empty] | Next iteration flow rate |  |  | 196.7604 | Abs Value of | Flow this | 449.2239 | Abs Value of | Flow this | 1078.3102 | Abs Value of | Flow this | 2058.8893 | Abs Value of | Flow this | 3386.1149 | Abs Value of | Flow this | 5041.4637 | Abs Value of | Flow this | 6727.8529 | Abs Value of | Flow this | 8209.259 | Abs Value of | Flow this | 9530.6949 | Abs Value of | Flow this | 10846.8198 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.6087 |  |  | 50.1008 |  |  | 17.6472 |  |  | -86.2458 |  |  | -330.3103 |  |  | -801.4546 |  |  | -1471.7567 |  |  | -2219.0695 |  |  | -3010.7686 |  |  | -3916.5219
[13 empty] | P2 at this iteration flow rate |  |  | 24.9183 |  |  | 26.0198 |  |  | 32.5106 |  |  | 53.2892 |  |  | 102.1021 |  |  | 196.3309 |  |  | 330.3913 |  |  | 479.8539 |  |  | 638.1937 |  |  | 819.3444
[13 empty] | Delta P at this iteration flow rate |  |  | 30.6904 |  |  | 24.081 |  |  | -14.8633 |  |  | -139.535 |  |  | -432.4123 |  |  | -997.7855 |  |  | -1802.1481 |  |  | -2698.9234 |  |  | -3648.9623 |  |  | -4735.8663
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.6825 |  |  | 41.1105 |  |  | 13.9232 |  |  | -66.9906 |  |  | -238.533 |  |  | -516.4554 |  |  | -851.4661 |  |  | -1061.9735 |  |  | -1188.3037 |  |  | -1473.3292
[13 empty] | C Non choked w/ reducers | 7 |  | 35.5222 |  |  | 91.6203 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 29.1156 |  |  | 70.1216 |  |  | 289.8771 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 35.5222 |  |  | 91.6203 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 30.5222 | 196.7604 |  | 79.6203 | 449.2239 |  | 5500 | 1078.3102 |  | 5500 | 2058.8893 |  | 5500 | 3386.1149 |  | 5500 | 5041.4637 |  | 5500 | 6727.8529 |  | 5500 | 8209.259 |  | 5500 | 9530.6949 |  | 5500 | 10846.8198
[13 empty] | Next iteration flow rate |  |  | 200.6956 | Abs Value of | Flow this | 453.7161 | Abs Value of | Flow this | 1089.0933 | Abs Value of | Flow this | 2079.4782 | Abs Value of | Flow this | 3419.9761 | Abs Value of | Flow this | 5091.8783 | Abs Value of | Flow this | 6795.1314 | Abs Value of | Flow this | 8291.3516 | Abs Value of | Flow this | 9626.0018 | Abs Value of | Flow this | 10955.288 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.5558 |  |  | 49.9638 |  |  | 16.8579 |  |  | -89.1234 |  |  | -338.0935 |  |  | -818.7078 |  |  | -1502.4831 |  |  | -2264.8168 |  |  | -3072.4291 |  |  | -3996.388
[13 empty] | P2 at this iteration flow rate |  |  | 24.9288 |  |  | 26.0472 |  |  | 32.6684 |  |  | 53.8647 |  |  | 103.6587 |  |  | 199.7816 |  |  | 336.5366 |  |  | 489.0034 |  |  | 650.5258 |  |  | 835.3176
[13 empty] | Delta P at this iteration flow rate |  |  | 30.627 |  |  | 23.9166 |  |  | -15.8105 |  |  | -142.988 |  |  | -441.7522 |  |  | -1018.4894 |  |  | -1839.0197 |  |  | -2753.8201 |  |  | -3722.9549 |  |  | -4831.7056
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.6388 |  |  | 40.9971 |  |  | 13.2846 |  |  | -69.2144 |  |  | -244.1462 |  |  | -527.5672 |  |  | -869.2371 |  |  | -1083.8623 |  |  | -1212.6366 |  |  | -1503.3701
[13 empty] | C Non choked w/ reducers | 7 |  | 36.2701 |  |  | 92.8539 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 29.7122 |  |  | 70.9207 |  |  | 299.731 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 36.2701 |  |  | 92.8539 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 31.2701 | 200.6956 |  | 80.8539 | 453.7161 |  | 5500 | 1089.0933 |  | 5500 | 2079.4782 |  | 5500 | 3419.9761 |  | 5500 | 5091.8783 |  | 5500 | 6795.1314 |  | 5500 | 8291.3516 |  | 5500 | 9626.0018 |  | 5500 | 10955.288
[13 empty] | Next iteration flow rate |  |  | 204.7095 | Abs Value of | Flow this | 458.2533 | Abs Value of | Flow this | 1099.9842 | Abs Value of | Flow this | 2100.273 | Abs Value of | Flow this | 3454.1758 | Abs Value of | Flow this | 5142.7971 | Abs Value of | Flow this | 6863.0827 | Abs Value of | Flow this | 8374.2652 | Abs Value of | Flow this | 9722.2619 | Abs Value of | Flow this | 11064.8409 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.5009 |  |  | 49.8241 |  |  | 16.0527 |  |  | -92.0588 |  |  | -346.0332 |  |  | -836.3078 |  |  | -1533.827 |  |  | -2311.4836 |  |  | -3135.3289 |  |  | -4077.8594
[13 empty] | P2 at this iteration flow rate |  |  | 24.9398 |  |  | 26.0752 |  |  | 32.8295 |  |  | 54.4518 |  |  | 105.2466 |  |  | 203.3016 |  |  | 342.8054 |  |  | 498.3367 |  |  | 663.1058 |  |  | 851.6119
[13 empty] | Delta P at this iteration flow rate |  |  | 30.5611 |  |  | 23.7489 |  |  | -16.7767 |  |  | -146.5105 |  |  | -451.2799 |  |  | -1039.6094 |  |  | -1876.6324 |  |  | -2809.8203 |  |  | -3798.4347 |  |  | -4929.4713
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.5932 |  |  | 40.8814 |  |  | 12.6331 |  |  | -71.4828 |  |  | -249.8722 |  |  | -538.9024 |  |  | -887.3653 |  |  | -1106.1911 |  |  | -1237.4586 |  |  | -1534.0148
[13 empty] | C Non choked w/ reducers | 7 |  | 37.0354 |  |  | 94.113 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 30.3215 |  |  | 71.7312 |  |  | 310.4363 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 37.0354 |  |  | 94.113 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 32.0354 | 204.7095 |  | 82.113 | 458.2533 |  | 5500 | 1099.9842 |  | 5500 | 2100.273 |  | 5500 | 3454.1758 |  | 5500 | 5142.7971 |  | 5500 | 6863.0827 |  | 5500 | 8374.2652 |  | 5500 | 9722.2619 |  | 5500 | 11064.8409
[13 empty] | Next iteration flow rate |  |  | 208.8037 | Abs Value of | Flow this | 462.8358 | Abs Value of | Flow this | 1110.9841 | Abs Value of | Flow this | 2121.2757 | Abs Value of | Flow this | 3488.7176 | Abs Value of | Flow this | 5194.2251 | Abs Value of | Flow this | 6931.7135 | Abs Value of | Flow this | 8458.0078 | Abs Value of | Flow this | 9819.4845 | Abs Value of | Flow this | 11175.4893 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.4437 |  |  | 49.6815 |  |  | 15.2314 |  |  | -95.0532 |  |  | -354.1325 |  |  | -854.2616 |  |  | -1565.8009 |  |  | -2359.0885 |  |  | -3199.493 |  |  | -4160.9684
[13 empty] | P2 at this iteration flow rate |  |  | 24.9513 |  |  | 26.1037 |  |  | 32.9937 |  |  | 55.0506 |  |  | 106.8665 |  |  | 206.8923 |  |  | 349.2002 |  |  | 507.8577 |  |  | 675.9386 |  |  | 868.2337
[13 empty] | Delta P at this iteration flow rate |  |  | 30.4924 |  |  | 23.5778 |  |  | -17.7623 |  |  | -150.1038 |  |  | -460.999 |  |  | -1061.154 |  |  | -1915.0011 |  |  | -2866.9461 |  |  | -3875.4316 |  |  | -5029.2021
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.5459 |  |  | 40.7634 |  |  | 11.9685 |  |  | -73.7969 |  |  | -255.7133 |  |  | -550.4655 |  |  | -905.8579 |  |  | -1128.9687 |  |  | -1262.7794 |  |  | -1565.2755
[13 empty] | C Non choked w/ reducers | 7 |  | 37.8186 |  |  | 95.3983 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 30.944 |  |  | 72.5533 |  |  | 322.1284 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 37.8186 |  |  | 95.3983 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 32.8186 | 208.8037 |  | 83.3983 | 462.8358 |  | 5500 | 1110.9841 |  | 5500 | 2121.2757 |  | 5500 | 3488.7176 |  | 5500 | 5194.2251 |  | 5500 | 6931.7135 |  | 5500 | 8458.0078 |  | 5500 | 9819.4845 |  | 5500 | 11175.4893
[13 empty] | Next iteration flow rate |  |  | 212.9798 | Abs Value of | Flow this | 467.4642 | Abs Value of | Flow this | 1122.0939 | Abs Value of | Flow this | 2142.4885 | Abs Value of | Flow this | 3523.6048 | Abs Value of | Flow this | 5246.1673 | Abs Value of | Flow this | 7001.0307 | Abs Value of | Flow this | 8542.5879 | Abs Value of | Flow this | 9917.6793 | Abs Value of | Flow this | 11287.2442 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.3842 |  |  | 49.5361 |  |  | 14.3935 |  |  | -98.1077 |  |  | -362.3946 |  |  | -872.5763 |  |  | -1598.4175 |  |  | -2407.6501 |  |  | -3264.9469 |  |  | -4245.7479
[13 empty] | P2 at this iteration flow rate |  |  | 24.9632 |  |  | 26.1328 |  |  | 33.1613 |  |  | 55.6615 |  |  | 108.5189 |  |  | 210.5553 |  |  | 355.7235 |  |  | 517.57 |  |  | 689.0294 |  |  | 885.1896
[13 empty] | Delta P at this iteration flow rate |  |  | 30.4211 |  |  | 23.4033 |  |  | -18.7678 |  |  | -153.7693 |  |  | -470.9135 |  |  | -1083.1316 |  |  | -1954.141 |  |  | -2925.2202 |  |  | -3953.9762 |  |  | -5130.9375
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.4966 |  |  | 40.643 |  |  | 11.2905 |  |  | -76.1575 |  |  | -261.6718 |  |  | -562.2609 |  |  | -924.7222 |  |  | -1152.2041 |  |  | -1288.6093 |  |  | -1597.1645
[13 empty] | C Non choked w/ reducers | 7 |  | 38.6202 |  |  | 96.7108 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 31.58 |  |  | 73.3873 |  |  | 334.9755 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 38.6202 |  |  | 96.7108 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 33.6202 | 212.9798 |  | 84.7108 | 467.4642 |  | 5500 | 1122.0939 |  | 5500 | 2142.4885 |  | 5500 | 3523.6048 |  | 5500 | 5246.1673 |  | 5500 | 7001.0307 |  | 5500 | 8542.5879 |  | 5500 | 9917.6793 |  | 5500 | 11287.2442
[13 empty] | Next iteration flow rate |  |  | 217.2394 | Abs Value of | Flow this | 472.1388 | Abs Value of | Flow this | 1133.3148 | Abs Value of | Flow this | 2163.9134 | Abs Value of | Flow this | 3558.8408 | Abs Value of | Flow this | 5298.629 | Abs Value of | Flow this | 7071.041 | Abs Value of | Flow this | 8628.0138 | Abs Value of | Flow this | 10016.8561 | Abs Value of | Flow this | 11400.1166 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.3223 |  |  | 49.3878 |  |  | 13.5388 |  |  | -101.2237 |  |  | -370.8227 |  |  | -891.2591 |  |  | -1631.6897 |  |  | -2457.1879 |  |  | -3331.7163 |  |  | -4332.2314
[13 empty] | P2 at this iteration flow rate |  |  | 24.9755 |  |  | 26.1624 |  |  | 33.3322 |  |  | 56.2847 |  |  | 110.2045 |  |  | 214.2918 |  |  | 362.3779 |  |  | 527.4776 |  |  | 702.3833 |  |  | 902.4863
[13 empty] | Delta P at this iteration flow rate |  |  | 30.3468 |  |  | 23.2253 |  |  | -19.7934 |  |  | -157.5085 |  |  | -481.0273 |  |  | -1105.5509 |  |  | -1994.0677 |  |  | -2984.6655 |  |  | -4034.0996 |  |  | -5234.7177
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.4454 |  |  | 40.5202 |  |  | 10.5989 |  |  | -78.5655 |  |  | -267.75 |  |  | -574.2935 |  |  | -943.9657 |  |  | -1175.9065 |  |  | -1314.9583 |  |  | -1629.6945
[13 empty] | C Non choked w/ reducers | 7 |  | 39.4408 |  |  | 98.0515 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 32.2298 |  |  | 74.2334 |  |  | 349.1888 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 39.4408 |  |  | 98.0515 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 34.4408 | 217.2394 |  | 86.0515 | 472.1388 |  | 5500 | 1133.3148 |  | 5500 | 2163.9134 |  | 5500 | 3558.8408 |  | 5500 | 5298.629 |  | 5500 | 7071.041 |  | 5500 | 8628.0138 |  | 5500 | 10016.8561 |  | 5500 | 11400.1166
[13 empty] | Next iteration flow rate |  |  | 221.5842 | Abs Value of | Flow this | 476.8602 | Abs Value of | Flow this | 1144.648 | Abs Value of | Flow this | 2185.5525 | Abs Value of | Flow this | 3594.4292 | Abs Value of | Flow this | 5351.6153 | Abs Value of | Flow this | 7141.7514 | Abs Value of | Flow this | 8714.2939 | Abs Value of | Flow this | 10117.0247 | Abs Value of | Flow this | 11514.1178 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.2579 |  |  | 49.2365 |  |  | 12.6669 |  |  | -104.4023 |  |  | -379.4203 |  |  | -910.3174 |  |  | -1665.6307 |  |  | -2507.7214 |  |  | -3399.8278 |  |  | -4420.4533
[13 empty] | P2 at this iteration flow rate |  |  | 24.9884 |  |  | 26.1927 |  |  | 33.5066 |  |  | 56.9205 |  |  | 111.9241 |  |  | 218.1035 |  |  | 369.1661 |  |  | 537.5843 |  |  | 716.0056 |  |  | 920.1307
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2695 |  |  | 23.0437 |  |  | -20.8397 |  |  | -161.3228 |  |  | -491.3443 |  |  | -1128.4209 |  |  | -2034.7969 |  |  | -3045.3057 |  |  | -4115.8334 |  |  | -5340.584
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.3921 |  |  | 40.395 |  |  | 9.8934 |  |  | -81.0219 |  |  | -273.9505 |  |  | -586.5679 |  |  | -963.5959 |  |  | -1200.0854 |  |  | -1341.8369 |  |  | -1662.8783
[13 empty] | C Non choked w/ reducers | 7 |  | 40.2809 |  |  | 99.4215 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 32.8937 |  |  | 75.0919 |  |  | 365.0388 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 40.2809 |  |  | 99.4215 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 35.2809 | 221.5842 |  | 87.4215 | 476.8602 |  | 5500 | 1144.648 |  | 5500 | 2185.5525 |  | 5500 | 3594.4292 |  | 5500 | 5351.6153 |  | 5500 | 7141.7514 |  | 5500 | 8714.2939 |  | 5500 | 10117.0247 |  | 5500 | 11514.1178
[13 empty] | Next iteration flow rate |  |  | 226.0159 | Abs Value of | Flow this | 481.6288 | Abs Value of | Flow this | 1156.0945 | Abs Value of | Flow this | 2207.408 | Abs Value of | Flow this | 3630.3735 | Abs Value of | Flow this | 5405.1315 | Abs Value of | Flow this | 7213.1689 | Abs Value of | Flow this | 8801.4368 | Abs Value of | Flow this | 10218.1949 | Abs Value of | Flow this | 11629.259 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.1909 |  |  | 49.0821 |  |  | 11.7775 |  |  | -107.6448 |  |  | -388.1906 |  |  | -929.7588 |  |  | -1700.2539 |  |  | -2559.2706 |  |  | -3469.3084 |  |  | -4510.4484
[13 empty] | P2 at this iteration flow rate |  |  | 25.0018 |  |  | 26.2236 |  |  | 33.6845 |  |  | 57.569 |  |  | 113.6781 |  |  | 221.9918 |  |  | 376.0908 |  |  | 547.8941 |  |  | 729.9017 |  |  | 938.1297
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1891 |  |  | 22.8585 |  |  | -21.907 |  |  | -165.2138 |  |  | -501.8688 |  |  | -1151.7506 |  |  | -2076.3447 |  |  | -3107.1648 |  |  | -4199.21 |  |  | -5448.5781
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.3366 |  |  | 40.2672 |  |  | 9.1738 |  |  | -83.5277 |  |  | -280.2756 |  |  | -599.089 |  |  | -983.6207 |  |  | -1224.7503 |  |  | -1369.2558 |  |  | -1696.7292
[13 empty] | C Non choked w/ reducers | 7 |  | 41.1412 |  |  | 100.8217 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 33.5721 |  |  | 75.9631 |  |  | 382.8777 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 41.1412 |  |  | 100.8217 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 36.1412 | 226.0159 |  | 88.8217 | 481.6288 |  | 5500 | 1156.0945 |  | 5500 | 2207.408 |  | 5500 | 3630.3735 |  | 5500 | 5405.1315 |  | 5500 | 7213.1689 |  | 5500 | 8801.4368 |  | 5500 | 10218.1949 |  | 5500 | 11629.259
[13 empty] | Next iteration flow rate |  |  | 230.5362 | Abs Value of | Flow this | 486.4451 | Abs Value of | Flow this | 1167.6554 | Abs Value of | Flow this | 2229.4821 | Abs Value of | Flow this | 3666.6772 | Abs Value of | Flow this | 5459.1828 | Abs Value of | Flow this | 7285.3006 | Abs Value of | Flow this | 8889.4512 | Abs Value of | Flow this | 10320.3769 | Abs Value of | Flow this | 11745.5516 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.1212 |  |  | 48.9246 |  |  | 10.8702 |  |  | -110.9525 |  |  | -397.1373 |  |  | -949.591 |  |  | -1735.573 |  |  | -2611.856 |  |  | -3540.1855 |  |  | -4602.2524
[13 empty] | P2 at this iteration flow rate |  |  | 25.0158 |  |  | 26.2551 |  |  | 33.866 |  |  | 58.2305 |  |  | 115.4675 |  |  | 225.9582 |  |  | 383.1546 |  |  | 558.4112 |  |  | 744.0771 |  |  | 956.4905
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1055 |  |  | 22.6696 |  |  | -22.9957 |  |  | -169.183 |  |  | -512.6047 |  |  | -1175.5492 |  |  | -2118.7276 |  |  | -3170.2672 |  |  | -4284.2626 |  |  | -5558.7429
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.2789 |  |  | 40.1368 |  |  | 8.4396 |  |  | -86.0839 |  |  | -286.7278 |  |  | -611.8618 |  |  | -1004.0481 |  |  | -1249.9109 |  |  | -1397.2258 |  |  | -1731.2604
[13 empty] | C Non choked w/ reducers | 7 |  | 42.0223 |  |  | 102.2535 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 34.2653 |  |  | 76.8472 |  |  | 403.175 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 42.0223 |  |  | 102.2535 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 37.0223 | 230.5362 |  | 90.2535 | 486.4451 |  | 5500 | 1167.6554 |  | 5500 | 2229.4821 |  | 5500 | 3666.6772 |  | 5500 | 5459.1828 |  | 5500 | 7285.3006 |  | 5500 | 8889.4512 |  | 5500 | 10320.3769 |  | 5500 | 11745.5516
[13 empty] | Next iteration flow rate |  |  | 235.1469 | Abs Value of | Flow this | 491.3095 | Abs Value of | Flow this | 1179.332 | Abs Value of | Flow this | 2251.7769 | Abs Value of | Flow this | 3703.344 | Abs Value of | Flow this | 5513.7746 | Abs Value of | Flow this | 7358.1536 | Abs Value of | Flow this | 8978.3457 | Abs Value of | Flow this | 10423.5807 | Abs Value of | Flow this | 11863.0071 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.0487 |  |  | 48.764 |  |  | 9.9447 |  |  | -114.3267 |  |  | -406.2638 |  |  | -969.8218 |  |  | -1771.6021 |  |  | -2665.4983 |  |  | -3612.4872 |  |  | -4695.9017
[13 empty] | P2 at this iteration flow rate |  |  | 25.0303 |  |  | 26.2872 |  |  | 34.0511 |  |  | 58.9053 |  |  | 117.2928 |  |  | 230.0044 |  |  | 390.3604 |  |  | 569.1397 |  |  | 758.5374 |  |  | 975.2203
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0185 |  |  | 22.4768 |  |  | -24.1063 |  |  | -173.232 |  |  | -523.5565 |  |  | -1199.8262 |  |  | -2161.9625 |  |  | -3234.638 |  |  | -4371.0247 |  |  | -5671.1221
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.2188 |  |  | 40.0039 |  |  | 7.6907 |  |  | -88.6914 |  |  | -293.3097 |  |  | -624.8913 |  |  | -1024.886 |  |  | -1275.5773 |  |  | -1425.758 |  |  | -1766.4857
[13 empty] | C Non choked w/ reducers | 7 |  | 42.9248 |  |  | 103.7179 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 34.9738 |  |  | 77.7445 |  |  | 426.5723 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 42.9248 |  |  | 103.7179 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 37.9248 | 235.1469 |  | 91.7179 | 491.3095 |  | 5500 | 1179.332 |  | 5500 | 2251.7769 |  | 5500 | 3703.344 |  | 5500 | 5513.7746 |  | 5500 | 7358.1536 |  | 5500 | 8978.3457 |  | 5500 | 10423.5807 |  | 5500 | 11863.0071
[13 empty] | Next iteration flow rate |  |  | 239.8499 | Abs Value of | Flow this | 496.2226 | Abs Value of | Flow this | 1191.1253 | Abs Value of | Flow this | 2274.2947 | Abs Value of | Flow this | 3740.3775 | Abs Value of | Flow this | 5568.9124 | Abs Value of | Flow this | 7431.7351 | Abs Value of | Flow this | 9068.1292 | Abs Value of | Flow this | 10527.8165 | Abs Value of | Flow this | 11981.6372 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.9733 |  |  | 48.6001 |  |  | 9.0006 |  |  | -117.7686 |  |  | -415.5737 |  |  | -990.4592 |  |  | -1808.3553 |  |  | -2720.2188 |  |  | -3686.2422 |  |  | -4791.4334
[13 empty] | P2 at this iteration flow rate |  |  | 25.0453 |  |  | 26.32 |  |  | 34.2399 |  |  | 59.5937 |  |  | 119.1547 |  |  | 234.1318 |  |  | 397.7111 |  |  | 580.0838 |  |  | 773.2884 |  |  | 994.3267
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9279 |  |  | 22.2802 |  |  | -25.2393 |  |  | -177.3624 |  |  | -534.7284 |  |  | -1224.5911 |  |  | -2206.0663 |  |  | -3300.3026 |  |  | -4459.5307 |  |  | -5785.76
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.1564 |  |  | 39.8682 |  |  | 6.9268 |  |  | -91.3514 |  |  | -300.0239 |  |  | -638.1827 |  |  | -1046.1427 |  |  | -1301.7595 |  |  | -1454.8637 |  |  | -1802.4191
[13 empty] | C Non choked w/ reducers | 7 |  | 43.8495 |  |  | 105.2163 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 35.698 |  |  | 78.6555 |  |  | 453.9749 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 43.8495 |  |  | 105.2163 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 38.8495 | 239.8499 |  | 93.2163 | 496.2226 |  | 5500 | 1191.1253 |  | 5500 | 2274.2947 |  | 5500 | 3740.3775 |  | 5500 | 5568.9124 |  | 5500 | 7431.7351 |  | 5500 | 9068.1292 |  | 5500 | 10527.8165 |  | 5500 | 11981.6372
[13 empty] | Next iteration flow rate |  |  | 244.6468 | Abs Value of | Flow this | 501.1848 | Abs Value of | Flow this | 1203.0365 | Abs Value of | Flow this | 2297.0377 | Abs Value of | Flow this | 3777.7812 | Abs Value of | Flow this | 5624.6015 | Abs Value of | Flow this | 7506.0525 | Abs Value of | Flow this | 9158.8105 | Abs Value of | Flow this | 10633.0946 | Abs Value of | Flow this | 12101.4535 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.8948 |  |  | 48.433 |  |  | 8.0375 |  |  | -121.2798 |  |  | -425.0707 |  |  | -1011.5115 |  |  | -1845.8472 |  |  | -2776.0393 |  |  | -3761.4797 |  |  | -4888.8852
[13 empty] | P2 at this iteration flow rate |  |  | 25.061 |  |  | 26.3534 |  |  | 34.4325 |  |  | 60.296 |  |  | 121.0541 |  |  | 238.3423 |  |  | 405.2094 |  |  | 591.2479 |  |  | 788.3359 |  |  | 1013.817
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8338 |  |  | 22.0796 |  |  | -26.395 |  |  | -181.5758 |  |  | -546.1249 |  |  | -1249.8538 |  |  | -2251.0567 |  |  | -3367.2871 |  |  | -4549.8157 |  |  | -5902.7022
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.0914 |  |  | 39.7298 |  |  | 6.1475 |  |  | -94.0648 |  |  | -306.873 |  |  | -651.7413 |  |  | -1067.8267 |  |  | -1328.468 |  |  | -1484.5545 |  |  | -1839.0747
[13 empty] | C Non choked w/ reducers | 7 |  | 44.797 |  |  | 106.7501 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 36.4382 |  |  | 79.5802 |  |  | 486.71 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 44.797 |  |  | 106.7501 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 39.797 | 244.6468 |  | 94.7501 | 501.1848 |  | 5500 | 1203.0365 |  | 5500 | 2297.0377 |  | 5500 | 3777.7812 |  | 5500 | 5624.6015 |  | 5500 | 7506.0525 |  | 5500 | 9158.8105 |  | 5500 | 10633.0946 |  | 5500 | 12101.4535
[13 empty] | Next iteration flow rate |  |  | 249.5398 | Abs Value of | Flow this | 506.1967 | Abs Value of | Flow this | 1215.0669 | Abs Value of | Flow this | 2320.008 | Abs Value of | Flow this | 3815.559 | Abs Value of | Flow this | 5680.8475 | Abs Value of | Flow this | 7581.113 | Abs Value of | Flow this | 9250.3986 | Abs Value of | Flow this | 10739.4256 | Abs Value of | Flow this | 12222.4681 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.8131 |  |  | 48.2625 |  |  | 7.055 |  |  | -124.8615 |  |  | -434.7587 |  |  | -1032.9869 |  |  | -1884.0928 |  |  | -2832.9817 |  |  | -3838.2295 |  |  | -4988.2958
[13 empty] | P2 at this iteration flow rate |  |  | 25.0774 |  |  | 26.3875 |  |  | 34.629 |  |  | 61.0123 |  |  | 122.9917 |  |  | 242.6374 |  |  | 412.8586 |  |  | 602.6363 |  |  | 803.6859 |  |  | 1033.6992
[13 empty] | Delta P at this iteration flow rate |  |  | 29.7358 |  |  | 21.875 |  |  | -27.574 |  |  | -185.8739 |  |  | -557.7504 |  |  | -1275.6242 |  |  | -2296.9513 |  |  | -3435.618 |  |  | -4641.9154 |  |  | -6021.995
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 45.0238 |  |  | 39.5887 |  |  | 5.3525 |  |  | -96.8327 |  |  | -313.8598 |  |  | -665.5724 |  |  | -1089.9466 |  |  | -1355.7134 |  |  | -1514.842 |  |  | -1876.4671
[13 empty] | C Non choked w/ reducers | 7 |  | 45.7682 |  |  | 108.3206 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 37.1948 |  |  | 80.5192 |  |  | 526.8185 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 45.7682 |  |  | 108.3206 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 40.7682 | 249.5398 |  | 96.3206 | 506.1967 |  | 5500 | 1215.0669 |  | 5500 | 2320.008 |  | 5500 | 3815.559 |  | 5500 | 5680.8475 |  | 5500 | 7581.113 |  | 5500 | 9250.3986 |  | 5500 | 10739.4256 |  | 5500 | 12222.4681
[13 empty] | Next iteration flow rate |  |  | 254.5306 | Abs Value of | Flow this | 511.2587 | Abs Value of | Flow this | 1227.2176 | Abs Value of | Flow this | 2343.2081 | Abs Value of | Flow this | 3853.7146 | Abs Value of | Flow this | 5737.656 | Abs Value of | Flow this | 7656.9241 | Abs Value of | Flow this | 9342.9026 | Abs Value of | Flow this | 10846.8198 | Abs Value of | Flow this | 12344.6928 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.7282 |  |  | 48.0885 |  |  | 6.0528 |  |  | -128.5153 |  |  | -444.6413 |  |  | -1054.8939 |  |  | -1923.1071 |  |  | -2891.0686 |  |  | -3916.5219 |  |  | -5089.7046
[13 empty] | P2 at this iteration flow rate |  |  | 25.0944 |  |  | 26.4223 |  |  | 34.8294 |  |  | 61.7431 |  |  | 124.9683 |  |  | 247.0188 |  |  | 420.6614 |  |  | 614.2537 |  |  | 819.3444 |  |  | 1053.9809
[13 empty] | Delta P at this iteration flow rate |  |  | 29.6338 |  |  | 21.6662 |  |  | -28.7766 |  |  | -190.2583 |  |  | -569.6096 |  |  | -1301.9127 |  |  | -2343.7685 |  |  | -3505.3223 |  |  | -4735.8663 |  |  | -6143.6855
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.9534 |  |  | 39.4447 |  |  | 4.5416 |  |  | -99.6563 |  |  | -320.9871 |  |  | -679.6815 |  |  | -1112.5111 |  |  | -1383.5064 |  |  | -1545.7383 |  |  | -1914.611
[13 empty] | C Non choked w/ reducers | 7 |  | 46.7638 |  |  | 109.9296 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 37.9684 |  |  | 81.4727 |  |  | 577.6411 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 46.7638 |  |  | 109.9296 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 41.7638 | 254.5306 |  | 97.9296 | 511.2587 |  | 5500 | 1227.2176 |  | 5500 | 2343.2081 |  | 5500 | 3853.7146 |  | 5500 | 5737.656 |  | 5500 | 7656.9241 |  | 5500 | 9342.9026 |  | 5500 | 10846.8198 |  | 5500 | 12344.6928
[13 empty] | Next iteration flow rate |  |  | 259.6212 | Abs Value of | Flow this | 516.3712 | Abs Value of | Flow this | 1239.4898 | Abs Value of | Flow this | 2366.6402 | Abs Value of | Flow this | 3892.2518 | Abs Value of | Flow this | 5795.0325 | Abs Value of | Flow this | 7733.4934 | Abs Value of | Flow this | 9436.3316 | Abs Value of | Flow this | 10955.288 | Abs Value of | Flow this | 12468.1397 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.6398 |  |  | 47.9111 |  |  | 5.0305 |  |  | -132.2424 |  |  | -454.7226 |  |  | -1077.2413 |  |  | -1962.9055 |  |  | -2950.3231 |  |  | -3996.388 |  |  | -5193.1516
[13 empty] | P2 at this iteration flow rate |  |  | 25.112 |  |  | 26.4578 |  |  | 35.0339 |  |  | 62.4885 |  |  | 126.9845 |  |  | 251.4883 |  |  | 428.6211 |  |  | 626.1046 |  |  | 835.3176 |  |  | 1074.6703
[13 empty] | Delta P at this iteration flow rate |  |  | 29.5277 |  |  | 21.4533 |  |  | -30.0034 |  |  | -194.7309 |  |  | -581.7072 |  |  | -1328.7296 |  |  | -2391.5266 |  |  | -3576.4277 |  |  | -4831.7056 |  |  | -6267.822
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.8802 |  |  | 39.2978 |  |  | 3.7143 |  |  | -102.5367 |  |  | -328.2576 |  |  | -694.0742 |  |  | -1135.5291 |  |  | -1411.858 |  |  | -1577.2556 |  |  | -1953.5217
[13 empty] | C Non choked w/ reducers | 7 |  | 47.7847 |  |  | 111.5785 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 38.7593 |  |  | 82.4411 |  |  | 645.1223 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 47.7847 |  |  | 111.5785 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 42.7847 | 259.6212 |  | 99.5785 | 516.3712 |  | 5500 | 1239.4898 |  | 5500 | 2366.6402 |  | 5500 | 3892.2518 |  | 5500 | 5795.0325 |  | 5500 | 7733.4934 |  | 5500 | 9436.3316 |  | 5500 | 10955.288 |  | 5500 | 12468.1397
[13 empty] | Next iteration flow rate |  |  | 264.8136 | Abs Value of | Flow this | 521.535 | Abs Value of | Flow this | 1251.8847 | Abs Value of | Flow this | 2390.3066 | Abs Value of | Flow this | 3931.1743 | Abs Value of | Flow this | 5852.9829 | Abs Value of | Flow this | 7810.8283 | Abs Value of | Flow this | 9530.6949 | Abs Value of | Flow this | 11064.8409 | Abs Value of | Flow this | 12592.8211 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.5478 |  |  | 47.7301 |  |  | 3.9876 |  |  | -136.0445 |  |  | -465.0066 |  |  | -1100.0379 |  |  | -2003.5039 |  |  | -3010.7686 |  |  | -4077.8594 |  |  | -5298.678
[13 empty] | P2 at this iteration flow rate |  |  | 25.1304 |  |  | 26.494 |  |  | 35.2425 |  |  | 63.2489 |  |  | 129.0413 |  |  | 256.0476 |  |  | 436.7408 |  |  | 638.1937 |  |  | 851.6119 |  |  | 1095.7756
[13 empty] | Delta P at this iteration flow rate |  |  | 29.4174 |  |  | 21.2361 |  |  | -31.2549 |  |  | -199.2934 |  |  | -594.0479 |  |  | -1356.0854 |  |  | -2440.2447 |  |  | -3648.9623 |  |  | -4929.4713 |  |  | -6394.4536
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.8041 |  |  | 39.148 |  |  | 2.8705 |  |  | -105.4749 |  |  | -335.6742 |  |  | -708.7562 |  |  | -1159.0097 |  |  | -1440.7795 |  |  | -1609.4064 |  |  | -1993.2145
[13 empty] | C Non choked w/ reducers | 7 |  | 48.8317 |  |  | 113.2691 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 39.5681 |  |  | 83.4247 |  |  | 741.1865 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 48.8317 |  |  | 113.2691 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 43.8317 | 264.8136 |  | 101.2691 | 521.535 |  | 5500 | 1251.8847 |  | 5500 | 2390.3066 |  | 5500 | 3931.1743 |  | 5500 | 5852.9829 |  | 5500 | 7810.8283 |  | 5500 | 9530.6949 |  | 5500 | 11064.8409 |  | 5500 | 12592.8211
[13 empty] | Next iteration flow rate |  |  | 270.1099 | Abs Value of | Flow this | 526.7503 | Abs Value of | Flow this | 1264.4035 | Abs Value of | Flow this | 2414.2097 | Abs Value of | Flow this | 3970.486 | Abs Value of | Flow this | 5911.5127 | Abs Value of | Flow this | 7888.9366 | Abs Value of | Flow this | 9626.0018 | Abs Value of | Flow this | 11175.4893 | Abs Value of | Flow this | 12718.7493 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.4521 |  |  | 47.5455 |  |  | 2.9237 |  |  | -139.923 |  |  | -475.4972 |  |  | -1123.2926 |  |  | -2044.9184 |  |  | -3072.4291 |  |  | -4160.9684 |  |  | -5406.3254
[13 empty] | P2 at this iteration flow rate |  |  | 25.1496 |  |  | 26.5309 |  |  | 35.4553 |  |  | 64.0246 |  |  | 131.1394 |  |  | 260.6985 |  |  | 445.0237 |  |  | 650.5258 |  |  | 868.2337 |  |  | 1117.3051
[13 empty] | Delta P at this iteration flow rate |  |  | 29.3026 |  |  | 21.0146 |  |  | -32.5316 |  |  | -203.9477 |  |  | -606.6367 |  |  | -1383.9912 |  |  | -2489.9421 |  |  | -3722.9549 |  |  | -5029.2021 |  |  | -6523.6305
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.7248 |  |  | 38.9951 |  |  | 2.0096 |  |  | -108.4722 |  |  | -343.24 |  |  | -723.7332 |  |  | -1182.9624 |  |  | -1470.2823 |  |  | -1642.2034 |  |  | -2033.7051
[13 empty] | C Non choked w/ reducers | 7 |  | 49.9058 |  |  | 115.0033 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 40.3952 |  |  | 84.4239 |  |  | 894.6762 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 49.9058 |  |  | 115.0033 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 44.9058 | 270.1099 |  | 103.0033 | 526.7503 |  | 5500 | 1264.4035 |  | 5500 | 2414.2097 |  | 5500 | 3970.486 |  | 5500 | 5911.5127 |  | 5500 | 7888.9366 |  | 5500 | 9626.0018 |  | 5500 | 11175.4893 |  | 5500 | 12718.7493
[13 empty] | Next iteration flow rate |  |  | 275.5121 | Abs Value of | Flow this | 532.0178 | Abs Value of | Flow this | 1277.0475 | Abs Value of | Flow this | 2438.3518 | Abs Value of | Flow this | 4010.1909 | Abs Value of | Flow this | 5970.6278 | Abs Value of | Flow this | 7967.826 | Abs Value of | Flow this | 9722.2619 | Abs Value of | Flow this | 11287.2442 | Abs Value of | Flow this | 12845.9368 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.3526 |  |  | 47.3571 |  |  | 1.8385 |  |  | -143.8795 |  |  | -486.1987 |  |  | -1147.0148 |  |  | -2087.1653 |  |  | -3135.3289 |  |  | -4245.7479 |  |  | -5516.1366
[13 empty] | P2 at this iteration flow rate |  |  | 25.1695 |  |  | 26.5686 |  |  | 35.6723 |  |  | 64.8159 |  |  | 133.2797 |  |  | 265.443 |  |  | 453.4731 |  |  | 663.1058 |  |  | 885.1896 |  |  | 1139.2673
[13 empty] | Delta P at this iteration flow rate |  |  | 29.1831 |  |  | 20.7885 |  |  | -33.8339 |  |  | -208.6954 |  |  | -619.4785 |  |  | -1412.4578 |  |  | -2540.6383 |  |  | -3798.4347 |  |  | -5130.9375 |  |  | -6655.4039
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.6424 |  |  | 38.8392 |  |  | 1.1315 |  |  | -111.5298 |  |  | -350.9578 |  |  | -739.0114 |  |  | -1207.3965 |  |  | -1500.3781 |  |  | -1675.6597 |  |  | -2075.0095
[13 empty] | C Non choked w/ reducers | 7 |  | 51.008 |  |  | 116.7831 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 41.2411 |  |  | 85.4391 |  |  | 1204.2507 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 51.008 |  |  | 116.7831 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 46.008 | 275.5121 |  | 104.7831 | 532.0178 |  | 5500 | 1277.0475 |  | 5500 | 2438.3518 |  | 5500 | 4010.1909 |  | 5500 | 5970.6278 |  | 5500 | 7967.826 |  | 5500 | 9722.2619 |  | 5500 | 11287.2442 |  | 5500 | 12845.9368
[13 empty] | Next iteration flow rate |  |  | 281.0223 | Abs Value of | Flow this | 537.338 | Abs Value of | Flow this | 1289.818 | Abs Value of | Flow this | 2462.7353 | Abs Value of | Flow this | 4050.2928 | Abs Value of | Flow this | 6030.3341 | Abs Value of | Flow this | 8047.5042 | Abs Value of | Flow this | 9819.4845 | Abs Value of | Flow this | 11400.1166 | Abs Value of | Flow this | 12974.3962 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.249 |  |  | 47.165 |  |  | 0.73139 |  |  | -147.9155 |  |  | -497.1153 |  |  | -1171.2139 |  |  | -2130.2613 |  |  | -3199.493 |  |  | -4332.2314 |  |  | -5628.155
[13 empty] | P2 at this iteration flow rate |  |  | 25.1902 |  |  | 26.607 |  |  | 35.8937 |  |  | 65.6231 |  |  | 135.4631 |  |  | 270.2828 |  |  | 462.0923 |  |  | 675.9386 |  |  | 902.4863 |  |  | 1161.671
[13 empty] | Delta P at this iteration flow rate |  |  | 29.0588 |  |  | 20.558 |  |  | -35.1623 |  |  | -213.5386 |  |  | -632.5784 |  |  | -1441.4966 |  |  | -2592.3536 |  |  | -3875.4316 |  |  | -5234.7177 |  |  | -6789.826
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.5566 |  |  | 38.6801 |  |  | 0.23573 |  |  | -114.6488 |  |  | -358.8307 |  |  | -754.5966 |  |  | -1232.3217 |  |  | -1531.0789 |  |  | -1709.7884 |  |  | -2117.1442
[13 empty] | C Non choked w/ reducers | 7 |  | 52.1393 |  |  | 118.6105 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 42.1064 |  |  | 86.4707 |  |  | 2664.7583 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 52.1393 |  |  | 118.6105 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 47.1393 | 281.0223 |  | 106.6105 | 537.338 |  | 5500 | 1289.818 |  | 5500 | 2462.7353 |  | 5500 | 4050.2928 |  | 5500 | 6030.3341 |  | 5500 | 8047.5042 |  | 5500 | 9819.4845 |  | 5500 | 11400.1166 |  | 5500 | 12974.3962
[13 empty] | Next iteration flow rate |  |  | 286.6428 | Abs Value of | Flow this | 542.7114 | Abs Value of | Flow this | 1302.7162 | Abs Value of | Flow this | 2487.3626 | Abs Value of | Flow this | 4090.7957 | Abs Value of | Flow this | 6090.6374 | Abs Value of | Flow this | 8127.9793 | Abs Value of | Flow this | 9917.6793 | Abs Value of | Flow this | 11514.1178 | Abs Value of | Flow this | 13104.1401 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.1413 |  |  | 46.969 |  |  | -0.39792 |  |  | -152.0326 |  |  | -508.2514 |  |  | -1195.8993 |  |  | -2174.2236 |  |  | -3264.9469 |  |  | -4420.4533 |  |  | -5742.4249
[13 empty] | P2 at this iteration flow rate |  |  | 25.2117 |  |  | 26.6462 |  |  | 36.1196 |  |  | 66.4465 |  |  | 137.6903 |  |  | 275.2199 |  |  | 470.8847 |  |  | 689.0294 |  |  | 920.1307 |  |  | 1184.525
[13 empty] | Delta P at this iteration flow rate |  |  | 28.9295 |  |  | 20.3228 |  |  | -36.5175 |  |  | -218.4791 |  |  | -645.9416 |  |  | -1471.1191 |  |  | -2645.1083 |  |  | -3953.9762 |  |  | -5340.584 |  |  | -6926.9499
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.4674 |  |  | 38.5179 |  |  | -0.67805 |  |  | -117.8305 |  |  | -366.8618 |  |  | -770.4951 |  |  | -1257.7479 |  |  | -1562.3967 |  |  | -1744.6031 |  |  | -2160.1258
[13 empty] | C Non choked w/ reducers | 7 |  | 53.3008 |  |  | 120.4878 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 42.9916 |  |  | 87.5192 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 53.3008 |  |  | 120.4878 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 48.3008 | 286.6428 |  | 108.4878 | 542.7114 |  | 5500 | 1302.7162 |  | 5500 | 2487.3626 |  | 5500 | 4090.7957 |  | 5500 | 6090.6374 |  | 5500 | 8127.9793 |  | 5500 | 9917.6793 |  | 5500 | 11514.1178 |  | 5500 | 13104.1401
[13 empty] | Next iteration flow rate |  |  | 292.3756 | Abs Value of | Flow this | 548.1385 | Abs Value of | Flow this | 1315.7434 | Abs Value of | Flow this | 2512.2363 | Abs Value of | Flow this | 4131.7037 | Abs Value of | Flow this | 6151.5438 | Abs Value of | Flow this | 8209.259 | Abs Value of | Flow this | 10016.8561 | Abs Value of | Flow this | 11629.259 | Abs Value of | Flow this | 13235.1815 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.0292 |  |  | 46.769 |  |  | -1.5499 |  |  | -156.2325 |  |  | -519.6112 |  |  | -1221.0809 |  |  | -2219.0695 |  |  | -3331.7163 |  |  | -4510.4484 |  |  | -5858.9916
[13 empty] | P2 at this iteration flow rate |  |  | 25.2342 |  |  | 26.6862 |  |  | 36.35 |  |  | 67.2865 |  |  | 139.9622 |  |  | 280.2562 |  |  | 479.8539 |  |  | 702.3833 |  |  | 938.1297 |  |  | 1207.8383
[13 empty] | Delta P at this iteration flow rate |  |  | 28.795 |  |  | 20.0828 |  |  | -37.8999 |  |  | -223.519 |  |  | -659.5735 |  |  | -1501.337 |  |  | -2698.9234 |  |  | -4034.0996 |  |  | -5448.5781 |  |  | -7066.83
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.3746 |  |  | 38.3524 |  |  | -1.6102 |  |  | -121.0761 |  |  | -375.0544 |  |  | -786.7132 |  |  | -1283.6852 |  |  | -1594.344 |  |  | -1780.1176 |  |  | -2203.9713
[13 empty] | C Non choked w/ reducers | 7 |  | 54.4937 |  |  | 122.4175 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 43.8973 |  |  | 88.5849 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 54.4937 |  |  | 122.4175 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 49.4937 | 292.3756 |  | 110.4175 | 548.1385 |  | 5500 | 1315.7434 |  | 5500 | 2512.2363 |  | 5500 | 4131.7037 |  | 5500 | 6151.5438 |  | 5500 | 8209.259 |  | 5500 | 10016.8561 |  | 5500 | 11629.259 |  | 5500 | 13235.1815
[13 empty] | Next iteration flow rate |  |  | 298.2231 | Abs Value of | Flow this | 553.6199 | Abs Value of | Flow this | 1328.9008 | Abs Value of | Flow this | 2537.3586 | Abs Value of | Flow this | 4173.0207 | Abs Value of | Flow this | 6213.0592 | Abs Value of | Flow this | 8291.3516 | Abs Value of | Flow this | 10117.0247 | Abs Value of | Flow this | 11745.5516 | Abs Value of | Flow this | 13367.5333 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.9125 |  |  | 46.5651 |  |  | -2.7251 |  |  | -160.5168 |  |  | -531.1994 |  |  | -1246.7686 |  |  | -2264.8168 |  |  | -3399.8278 |  |  | -4602.2524 |  |  | -5977.9014
[13 empty] | P2 at this iteration flow rate |  |  | 25.2575 |  |  | 26.727 |  |  | 36.585 |  |  | 68.1434 |  |  | 142.2799 |  |  | 285.3937 |  |  | 489.0034 |  |  | 716.0056 |  |  | 956.4905 |  |  | 1231.6203
[13 empty] | Delta P at this iteration flow rate |  |  | 28.655 |  |  | 19.8381 |  |  | -39.3101 |  |  | -228.6601 |  |  | -673.4793 |  |  | -1532.1623 |  |  | -2753.8201 |  |  | -4115.8334 |  |  | -5558.7429 |  |  | -7209.5217
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.278 |  |  | 38.1835 |  |  | -2.5611 |  |  | -124.387 |  |  | -383.4117 |  |  | -803.2572 |  |  | -1310.1438 |  |  | -1626.9335 |  |  | -1816.3459 |  |  | -2248.6981
[13 empty] | C Non choked w/ reducers | 7 |  | 55.7191 |  |  | 124.402 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 44.824 |  |  | 89.6684 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 55.7191 |  |  | 124.402 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 50.7191 | 298.2231 |  | 112.402 | 553.6199 |  | 5500 | 1328.9008 |  | 5500 | 2537.3586 |  | 5500 | 4173.0207 |  | 5500 | 6213.0592 |  | 5500 | 8291.3516 |  | 5500 | 10117.0247 |  | 5500 | 11745.5516 |  | 5500 | 13367.5333
[13 empty] | Next iteration flow rate |  |  | 304.1876 | Abs Value of | Flow this | 559.1561 | Abs Value of | Flow this | 1342.1898 | Abs Value of | Flow this | 2562.7322 | Abs Value of | Flow this | 4214.7509 | Abs Value of | Flow this | 6275.1898 | Abs Value of | Flow this | 8374.2652 | Abs Value of | Flow this | 10218.1949 | Abs Value of | Flow this | 11863.0071 | Abs Value of | Flow this | 13501.2087 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.7912 |  |  | 46.357 |  |  | -3.9239 |  |  | -164.8872 |  |  | -543.0206 |  |  | -1272.9727 |  |  | -2311.4836 |  |  | -3469.3084 |  |  | -4695.9017 |  |  | -6099.2012
[13 empty] | P2 at this iteration flow rate |  |  | 25.2818 |  |  | 26.7686 |  |  | 36.8248 |  |  | 69.0174 |  |  | 144.6441 |  |  | 290.6345 |  |  | 498.3367 |  |  | 729.9017 |  |  | 975.2203 |  |  | 1255.8802
[13 empty] | Delta P at this iteration flow rate |  |  | 28.5094 |  |  | 19.5884 |  |  | -40.7487 |  |  | -233.9046 |  |  | -687.6647 |  |  | -1563.6072 |  |  | -2809.8203 |  |  | -4199.21 |  |  | -5671.1221 |  |  | -7355.0815
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.1775 |  |  | 38.0113 |  |  | -3.5311 |  |  | -127.7644 |  |  | -391.9369 |  |  | -820.1338 |  |  | -1337.1342 |  |  | -1660.178 |  |  | -1853.3025 |  |  | -2294.3239
[13 empty] | C Non choked w/ reducers | 7 |  | 56.9785 |  |  | 126.4442 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 45.7725 |  |  | 90.77 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 56.9785 |  |  | 126.4442 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 51.9785 | 304.1876 |  | 114.4442 | 559.1561 |  | 5500 | 1342.1898 |  | 5500 | 2562.7322 |  | 5500 | 4214.7509 |  | 5500 | 6275.1898 |  | 5500 | 8374.2652 |  | 5500 | 10218.1949 |  | 5500 | 11863.0071 |  | 5500 | 13501.2087
[13 empty] | Next iteration flow rate |  |  | 310.2714 | Abs Value of | Flow this | 564.7476 | Abs Value of | Flow this | 1355.6117 | Abs Value of | Flow this | 2588.3595 | Abs Value of | Flow this | 4256.8985 | Abs Value of | Flow this | 6337.9417 | Abs Value of | Flow this | 8458.0078 | Abs Value of | Flow this | 10320.3769 | Abs Value of | Flow this | 11981.6372 | Abs Value of | Flow this | 13636.2207 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.6649 |  |  | 46.1448 |  |  | -5.1468 |  |  | -169.3454 |  |  | -555.0793 |  |  | -1299.7034 |  |  | -2359.0885 |  |  | -3540.1855 |  |  | -4791.4334 |  |  | -6222.9392
[13 empty] | P2 at this iteration flow rate |  |  | 25.307 |  |  | 26.811 |  |  | 37.0694 |  |  | 69.9091 |  |  | 147.0559 |  |  | 295.9807 |  |  | 507.8577 |  |  | 744.0771 |  |  | 994.3267 |  |  | 1280.6278
[13 empty] | Delta P at this iteration flow rate |  |  | 28.3579 |  |  | 19.3337 |  |  | -42.2161 |  |  | -239.2545 |  |  | -702.1351 |  |  | -1595.6841 |  |  | -2866.9461 |  |  | -4284.2626 |  |  | -5785.76 |  |  | -7503.567
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 44.073 |  |  | 37.8356 |  |  | -4.5206 |  |  | -131.2098 |  |  | -400.6336 |  |  | -837.3495 |  |  | -1364.6671 |  |  | -1694.0907 |  |  | -1891.0018 |  |  | -2340.8668
[13 empty] | C Non choked w/ reducers | 7 |  | 58.2731 |  |  | 128.547 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 46.7433 |  |  | 91.8903 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 58.2731 |  |  | 128.547 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 53.2731 | 310.2714 |  | 116.547 | 564.7476 |  | 5500 | 1355.6117 |  | 5500 | 2588.3595 |  | 5500 | 4256.8985 |  | 5500 | 6337.9417 |  | 5500 | 8458.0078 |  | 5500 | 10320.3769 |  | 5500 | 11981.6372 |  | 5500 | 13636.2207
[13 empty] | Next iteration flow rate |  |  | 316.4768 | Abs Value of | Flow this | 570.3951 | Abs Value of | Flow this | 1369.1678 | Abs Value of | Flow this | 2614.2431 | Abs Value of | Flow this | 4299.4674 | Abs Value of | Flow this | 6401.3211 | Abs Value of | Flow this | 8542.5879 | Abs Value of | Flow this | 10423.5807 | Abs Value of | Flow this | 12101.4535 | Abs Value of | Flow this | 13772.583 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.5336 |  |  | 45.9283 |  |  | -6.3942 |  |  | -173.8933 |  |  | -567.3804 |  |  | -1326.9715 |  |  | -2407.6501 |  |  | -3612.4872 |  |  | -4888.8852 |  |  | -6349.1643
[13 empty] | P2 at this iteration flow rate |  |  | 25.3333 |  |  | 26.8543 |  |  | 37.3188 |  |  | 70.8187 |  |  | 149.5161 |  |  | 301.4343 |  |  | 517.57 |  |  | 758.5374 |  |  | 1013.817 |  |  | 1305.8729
[13 empty] | Delta P at this iteration flow rate |  |  | 28.2003 |  |  | 19.0739 |  |  | -43.7131 |  |  | -244.7119 |  |  | -716.8965 |  |  | -1628.4058 |  |  | -2925.2202 |  |  | -4371.0247 |  |  | -5902.7022 |  |  | -7655.0371
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 43.9642 |  |  | 37.6564 |  |  | -5.53 |  |  | -134.7243 |  |  | -409.505 |  |  | -854.9114 |  |  | -1392.7535 |  |  | -1728.6851 |  |  | -1929.4589 |  |  | -2388.3452
[13 empty] | C Non choked w/ reducers | 7 |  | 59.6044 |  |  | 130.7137 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 47.7371 |  |  | 93.0298 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 59.6044 |  |  | 130.7137 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 54.6044 | 316.4768 |  | 118.7137 | 570.3951 |  | 5500 | 1369.1678 |  | 5500 | 2614.2431 |  | 5500 | 4299.4674 |  | 5500 | 6401.3211 |  | 5500 | 8542.5879 |  | 5500 | 10423.5807 |  | 5500 | 12101.4535 |  | 5500 | 13772.583
[13 empty] | Next iteration flow rate |  |  | 322.8063 | Abs Value of | Flow this | 576.0991 | Abs Value of | Flow this | 1382.8595 | Abs Value of | Flow this | 2640.3856 | Abs Value of | Flow this | 4342.4621 | Abs Value of | Flow this | 6465.3344 | Abs Value of | Flow this | 8628.0138 | Abs Value of | Flow this | 10527.8165 | Abs Value of | Flow this | 12222.4681 | Abs Value of | Flow this | 13910.3088 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.3969 |  |  | 45.7074 |  |  | -7.6668 |  |  | -178.5326 |  |  | -579.9287 |  |  | -1354.7876 |  |  | -2457.1879 |  |  | -3686.2422 |  |  | -4988.2958 |  |  | -6477.9265
[13 empty] | P2 at this iteration flow rate |  |  | 25.3606 |  |  | 26.8985 |  |  | 37.5734 |  |  | 71.7465 |  |  | 152.0257 |  |  | 306.9975 |  |  | 527.4776 |  |  | 773.2884 |  |  | 1033.6992 |  |  | 1331.6253
[13 empty] | Delta P at this iteration flow rate |  |  | 28.0363 |  |  | 18.8089 |  |  | -45.2401 |  |  | -250.2791 |  |  | -731.9545 |  |  | -1661.7851 |  |  | -2984.6655 |  |  | -4459.5307 |  |  | -6021.995 |  |  | -7809.5518
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 43.8511 |  |  | 37.4735 |  |  | -6.5597 |  |  | -138.3095 |  |  | -418.5547 |  |  | -872.8262 |  |  | -1421.4044 |  |  | -1763.9748 |  |  | -1968.689 |  |  | -2436.7779
[13 empty] | C Non choked w/ reducers | 7 |  | 60.9741 |  |  | 132.9478 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 48.7546 |  |  | 94.1891 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 60.9741 |  |  | 132.9478 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 55.9741 | 322.8063 |  | 120.9478 | 576.0991 |  | 5500 | 1382.8595 |  | 5500 | 2640.3856 |  | 5500 | 4342.4621 |  | 5500 | 6465.3344 |  | 5500 | 8628.0138 |  | 5500 | 10527.8165 |  | 5500 | 12222.4681 |  | 5500 | 13910.3088
[13 empty] | Next iteration flow rate |  |  | 329.2624 | Abs Value of | Flow this | 581.86 | Abs Value of | Flow this | 1396.6881 | Abs Value of | Flow this | 2666.7894 | Abs Value of | Flow this | 4385.8867 | Abs Value of | Flow this | 6529.9877 | Abs Value of | Flow this | 8714.2939 | Abs Value of | Flow this | 10633.0946 | Abs Value of | Flow this | 12344.6928 | Abs Value of | Flow this | 14049.4119 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.2548 |  |  | 45.4821 |  |  | -8.9649 |  |  | -183.2651 |  |  | -592.7293 |  |  | -1383.1629 |  |  | -2507.7214 |  |  | -3761.4797 |  |  | -5089.7046 |  |  | -6609.2768
[13 empty] | P2 at this iteration flow rate |  |  | 25.389 |  |  | 26.9436 |  |  | 37.833 |  |  | 72.693 |  |  | 154.5859 |  |  | 312.6726 |  |  | 537.5843 |  |  | 788.3359 |  |  | 1053.9809 |  |  | 1357.8954
[13 empty] | Delta P at this iteration flow rate |  |  | 27.8657 |  |  | 18.5386 |  |  | -46.7979 |  |  | -255.9581 |  |  | -747.3152 |  |  | -1695.8354 |  |  | -3045.3057 |  |  | -4549.8157 |  |  | -6143.6855 |  |  | -7967.1722
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 43.7333 |  |  | 37.287 |  |  | -7.6101 |  |  | -141.9668 |  |  | -427.7863 |  |  | -891.1011 |  |  | -1450.6311 |  |  | -1799.9738 |  |  | -2008.7076 |  |  | -2486.1842
[13 empty] | C Non choked w/ reducers | 7 |  | 62.3836 |  |  | 135.2528 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 49.7966 |  |  | 95.3686 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 62.3836 |  |  | 135.2528 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 57.3836 | 329.2624 |  | 123.2528 | 581.86 |  | 5500 | 1396.6881 |  | 5500 | 2666.7894 |  | 5500 | 4385.8867 |  | 5500 | 6529.9877 |  | 5500 | 8714.2939 |  | 5500 | 10633.0946 |  | 5500 | 12344.6928 |  | 5500 | 14049.4119
[13 empty] | Next iteration flow rate |  |  | 335.8477 | Abs Value of | Flow this | 587.6786 | Abs Value of | Flow this | 1410.655 | Abs Value of | Flow this | 2693.4573 | Abs Value of | Flow this | 4429.7456 | Abs Value of | Flow this | 6595.2876 | Abs Value of | Flow this | 8801.4368 | Abs Value of | Flow this | 10739.4256 | Abs Value of | Flow this | 12468.1397 | Abs Value of | Flow this | 14189.906 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 53.1068 |  |  | 45.2523 |  |  | -10.2891 |  |  | -188.0927 |  |  | -605.7872 |  |  | -1412.1085 |  |  | -2559.2706 |  |  | -3838.2295 |  |  | -5193.1516 |  |  | -6743.2673
[13 empty] | P2 at this iteration flow rate |  |  | 25.4186 |  |  | 26.9895 |  |  | 38.0978 |  |  | 73.6585 |  |  | 157.1974 |  |  | 318.4617 |  |  | 547.8941 |  |  | 803.6859 |  |  | 1074.6703 |  |  | 1384.6935
[13 empty] | Delta P at this iteration flow rate |  |  | 27.6882 |  |  | 18.2628 |  |  | -48.3869 |  |  | -261.7513 |  |  | -762.9846 |  |  | -1730.5701 |  |  | -3107.1648 |  |  | -4641.9154 |  |  | -6267.822 |  |  | -8127.9608
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 43.6109 |  |  | 37.0968 |  |  | -8.6815 |  |  | -145.6976 |  |  | -437.2035 |  |  | -909.7433 |  |  | -1480.4454 |  |  | -1836.6965 |  |  | -2049.5306 |  |  | -2536.5834
[13 empty] | C Non choked w/ reducers | 7 |  | 63.835 |  |  | 137.6329 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 50.8638 |  |  | 96.5689 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 63.835 |  |  | 137.6329 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 58.835 | 335.8477 |  | 125.6329 | 587.6786 |  | 5500 | 1410.655 |  | 5500 | 2693.4573 |  | 5500 | 4429.7456 |  | 5500 | 6595.2876 |  | 5500 | 8801.4368 |  | 5500 | 10739.4256 |  | 5500 | 12468.1397 |  | 5500 | 14189.906
[13 empty] | Next iteration flow rate |  |  | 342.5647 | Abs Value of | Flow this | 593.5554 | Abs Value of | Flow this | 1424.7615 | Abs Value of | Flow this | 2720.3919 | Abs Value of | Flow this | 4474.0431 | Abs Value of | Flow this | 6661.2405 | Abs Value of | Flow this | 8889.4512 | Abs Value of | Flow this | 10846.8198 | Abs Value of | Flow this | 12592.8211 | Abs Value of | Flow this | 14331.8051 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 52.9529 |  |  | 45.0179 |  |  | -11.6399 |  |  | -193.0174 |  |  | -619.1075 |  |  | -1441.6358 |  |  | -2611.856 |  |  | -3916.5219 |  |  | -5298.678 |  |  | -6879.951
[13 empty] | P2 at this iteration flow rate |  |  | 25.4494 |  |  | 27.0364 |  |  | 38.368 |  |  | 74.6435 |  |  | 159.8615 |  |  | 324.3672 |  |  | 558.4112 |  |  | 819.3444 |  |  | 1095.7756 |  |  | 1412.0302
[13 empty] | Delta P at this iteration flow rate |  |  | 27.5035 |  |  | 17.9814 |  |  | -50.0079 |  |  | -267.6609 |  |  | -778.969 |  |  | -1766.003 |  |  | -3170.2672 |  |  | -4735.8663 |  |  | -6394.4536 |  |  | -8291.9812
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 43.4834 |  |  | 36.9027 |  |  | -9.7746 |  |  | -149.5034 |  |  | -446.8099 |  |  | -928.7603 |  |  | -1510.8589 |  |  | -1874.1572 |  |  | -2091.1741 |  |  | -2587.9958
[13 empty] | C Non choked w/ reducers | 7 |  | 65.3299 |  |  | 140.0925 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 51.957 |  |  | 97.7908 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 65.3299 |  |  | 140.0925 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 60.3299 | 342.5647 |  | 128.0925 | 593.5554 |  | 5500 | 1424.7615 |  | 5500 | 2720.3919 |  | 5500 | 4474.0431 |  | 5500 | 6661.2405 |  | 5500 | 8889.4512 |  | 5500 | 10846.8198 |  | 5500 | 12592.8211 |  | 5500 | 14331.8051
[13 empty] | Next iteration flow rate |  |  | 349.4159 | Abs Value of | Flow this | 599.491 | Abs Value of | Flow this | 1439.0091 | Abs Value of | Flow this | 2747.5958 | Abs Value of | Flow this | 4518.7835 | Abs Value of | Flow this | 6727.8529 | Abs Value of | Flow this | 8978.3457 | Abs Value of | Flow this | 10955.288 | Abs Value of | Flow this | 12718.7493 | Abs Value of | Flow this | 14475.1231 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 52.7928 |  |  | 44.7787 |  |  | -13.0179 |  |  | -198.0411 |  |  | -632.6956 |  |  | -1471.7567 |  |  | -2665.4983 |  |  | -3996.388 |  |  | -5406.3254 |  |  | -7019.382
[13 empty] | P2 at this iteration flow rate |  |  | 25.4814 |  |  | 27.0843 |  |  | 38.6436 |  |  | 75.6482 |  |  | 162.5791 |  |  | 330.3913 |  |  | 569.1397 |  |  | 835.3176 |  |  | 1117.3051 |  |  | 1439.9164
[13 empty] | Delta P at this iteration flow rate |  |  | 27.3114 |  |  | 17.6945 |  |  | -51.6615 |  |  | -273.6893 |  |  | -795.2747 |  |  | -1802.1481 |  |  | -3234.638 |  |  | -4831.7056 |  |  | -6523.6305 |  |  | -8459.2984
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 43.3508 |  |  | 36.7047 |  |  | -10.8896 |  |  | -153.3857 |  |  | -456.6095 |  |  | -948.1594 |  |  | -1541.8837 |  |  | -1912.3709 |  |  | -2133.6547 |  |  | -2640.4415
[13 empty] | C Non choked w/ reducers | 7 |  | 66.8705 |  |  | 142.6362 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 53.0771 |  |  | 99.0347 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 66.8705 |  |  | 142.6362 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 61.8705 | 349.4159 |  | 130.6362 | 599.491 |  | 5500 | 1439.0091 |  | 5500 | 2747.5958 |  | 5500 | 4518.7835 |  | 5500 | 6727.8529 |  | 5500 | 8978.3457 |  | 5500 | 10955.288 |  | 5500 | 12718.7493 |  | 5500 | 14475.1231
[13 empty] | Next iteration flow rate |  |  | 356.4043 | Abs Value of | Flow this | 605.4859 | Abs Value of | Flow this | 1453.3992 | Abs Value of | Flow this | 2775.0718 | Abs Value of | Flow this | 4563.9713 | Abs Value of | Flow this | 6795.1314 | Abs Value of | Flow this | 9068.1292 | Abs Value of | Flow this | 11064.8409 | Abs Value of | Flow this | 12845.9368 | Abs Value of | Flow this | 14619.8743 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 52.6262 |  |  | 44.5347 |  |  | -14.4236 |  |  | -203.1657 |  |  | -646.5568 |  |  | -1502.4831 |  |  | -2720.2188 |  |  | -4077.8594 |  |  | -5516.1366 |  |  | -7161.6156
[13 empty] | P2 at this iteration flow rate |  |  | 25.5148 |  |  | 27.1331 |  |  | 38.9247 |  |  | 76.6731 |  |  | 165.3514 |  |  | 336.5366 |  |  | 580.0838 |  |  | 851.6119 |  |  | 1139.2673 |  |  | 1468.3631
[13 empty] | Delta P at this iteration flow rate |  |  | 27.1115 |  |  | 17.4017 |  |  | -53.3483 |  |  | -279.8388 |  |  | -811.9082 |  |  | -1839.0197 |  |  | -3300.3026 |  |  | -4929.4713 |  |  | -6655.4039 |  |  | -8629.9787
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 43.2129 |  |  | 36.5028 |  |  | -12.027 |  |  | -157.346 |  |  | -466.606 |  |  | -967.9485 |  |  | -1573.5321 |  |  | -1951.3527 |  |  | -2176.9891 |  |  | -2693.9413
[13 empty] | C Non choked w/ reducers | 7 |  | 68.4589 |  |  | 145.2693 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 54.225 |  |  | 100.3014 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 68.4589 |  |  | 145.2693 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 63.4589 | 356.4043 |  | 133.2693 | 605.4859 |  | 5500 | 1453.3992 |  | 5500 | 2775.0718 |  | 5500 | 4563.9713 |  | 5500 | 6795.1314 |  | 5500 | 9068.1292 |  | 5500 | 11064.8409 |  | 5500 | 12845.9368 |  | 5500 | 14619.8743
[13 empty] | Next iteration flow rate |  |  | 363.5323 | Abs Value of | Flow this | 611.5408 | Abs Value of | Flow this | 1467.9332 | Abs Value of | Flow this | 2802.8225 | Abs Value of | Flow this | 4609.611 | Abs Value of | Flow this | 6863.0827 | Abs Value of | Flow this | 9158.8105 | Abs Value of | Flow this | 11175.4893 | Abs Value of | Flow this | 12974.3962 | Abs Value of | Flow this | 14766.0731 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 52.4529 |  |  | 44.2859 |  |  | -15.8575 |  |  | -208.3933 |  |  | -660.6966 |  |  | -1533.827 |  |  | -2776.0393 |  |  | -4160.9684 |  |  | -5628.155 |  |  | -7306.7081
[13 empty] | P2 at this iteration flow rate |  |  | 25.5494 |  |  | 27.1828 |  |  | 39.2115 |  |  | 77.7187 |  |  | 168.1793 |  |  | 342.8054 |  |  | 591.2479 |  |  | 868.2337 |  |  | 1161.671 |  |  | 1497.3816
[13 empty] | Delta P at this iteration flow rate |  |  | 26.9035 |  |  | 17.1031 |  |  | -55.069 |  |  | -286.112 |  |  | -828.8759 |  |  | -1876.6324 |  |  | -3367.2871 |  |  | -5029.2021 |  |  | -6789.826 |  |  | -8804.0897
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 43.0694 |  |  | 36.2967 |  |  | -13.1872 |  |  | -161.3859 |  |  | -476.8034 |  |  | -988.1354 |  |  | -1605.8166 |  |  | -1991.118 |  |  | -2221.1946 |  |  | -2748.5165
[13 empty] | C Non choked w/ reducers | 7 |  | 70.0974 |  |  | 147.9974 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 55.4016 |  |  | 101.5915 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 70.0974 |  |  | 147.9974 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 65.0974 | 363.5323 |  | 135.9974 | 611.5408 |  | 5500 | 1467.9332 |  | 5500 | 2802.8225 |  | 5500 | 4609.611 |  | 5500 | 6863.0827 |  | 5500 | 9158.8105 |  | 5500 | 11175.4893 |  | 5500 | 12974.3962 |  | 5500 | 14766.0731
[13 empty] | Next iteration flow rate |  |  | 370.803 | Abs Value of | Flow this | 617.6562 | Abs Value of | Flow this | 1482.6125 | Abs Value of | Flow this | 2830.8507 | Abs Value of | Flow this | 4655.7071 | Abs Value of | Flow this | 6931.7135 | Abs Value of | Flow this | 9250.3986 | Abs Value of | Flow this | 11287.2442 | Abs Value of | Flow this | 13104.1401 | Abs Value of | Flow this | 14913.7338 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 52.2726 |  |  | 44.032 |  |  | -17.3203 |  |  | -213.7261 |  |  | -675.1206 |  |  | -1565.8009 |  |  | -2832.9817 |  |  | -4245.7479 |  |  | -5742.4249 |  |  | -7454.717
[13 empty] | P2 at this iteration flow rate |  |  | 25.5855 |  |  | 27.2336 |  |  | 39.5041 |  |  | 78.7852 |  |  | 171.0641 |  |  | 349.2002 |  |  | 602.6363 |  |  | 885.1896 |  |  | 1184.525 |  |  | 1526.9834
[13 empty] | Delta P at this iteration flow rate |  |  | 26.6871 |  |  | 16.7984 |  |  | -56.8243 |  |  | -292.5113 |  |  | -846.1848 |  |  | -1915.0011 |  |  | -3435.618 |  |  | -5130.9375 |  |  | -6926.9499 |  |  | -8981.7003
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 42.9201 |  |  | 36.0866 |  |  | -14.3708 |  |  | -165.507 |  |  | -487.2059 |  |  | -1008.728 |  |  | -1638.7501 |  |  | -2031.6827 |  |  | -2266.2886 |  |  | -2804.1887
[13 empty] | C Non choked w/ reducers | 7 |  | 71.7886 |  |  | 150.8267 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 56.6078 |  |  | 102.9057 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 71.7886 |  |  | 150.8267 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 66.7886 | 370.803 |  | 138.8267 | 617.6562 |  | 5500 | 1482.6125 |  | 5500 | 2830.8507 |  | 5500 | 4655.7071 |  | 5500 | 6931.7135 |  | 5500 | 9250.3986 |  | 5500 | 11287.2442 |  | 5500 | 13104.1401 |  | 5500 | 14913.7338
[13 empty] | Next iteration flow rate |  |  | 378.2191 | Abs Value of | Flow this | 623.8327 | Abs Value of | Flow this | 1497.4387 | Abs Value of | Flow this | 2859.1592 | Abs Value of | Flow this | 4702.2642 | Abs Value of | Flow this | 7001.0307 | Abs Value of | Flow this | 9342.9026 | Abs Value of | Flow this | 11400.1166 | Abs Value of | Flow this | 13235.1815 | Abs Value of | Flow this | 15062.8711 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 52.085 |  |  | 43.773 |  |  | -18.8124 |  |  | -219.166 |  |  | -689.8346 |  |  | -1598.4175 |  |  | -2891.0686 |  |  | -4332.2314 |  |  | -5858.9916 |  |  | -7605.7008
[13 empty] | P2 at this iteration flow rate |  |  | 25.623 |  |  | 27.2854 |  |  | 39.8025 |  |  | 79.8732 |  |  | 174.0069 |  |  | 355.7235 |  |  | 614.2537 |  |  | 902.4863 |  |  | 1207.8383 |  |  | 1557.1802
[13 empty] | Delta P at this iteration flow rate |  |  | 26.462 |  |  | 16.4876 |  |  | -58.6149 |  |  | -299.0392 |  |  | -863.8415 |  |  | -1954.141 |  |  | -3505.3223 |  |  | -5234.7177 |  |  | -7066.83 |  |  | -9162.8809
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 42.7647 |  |  | 35.8722 |  |  | -15.5782 |  |  | -169.7109 |  |  | -497.8174 |  |  | -1029.7346 |  |  | -1672.3455 |  |  | -2073.0626 |  |  | -2312.2889 |  |  | -2860.9799
[13 empty] | C Non choked w/ reducers | 7 |  | 73.5352 |  |  | 153.7639 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 57.8448 |  |  | 104.2449 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 73.5352 |  |  | 153.7639 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 68.5352 | 378.2191 |  | 141.7639 | 623.8327 |  | 5500 | 1497.4387 |  | 5500 | 2859.1592 |  | 5500 | 4702.2642 |  | 5500 | 7001.0307 |  | 5500 | 9342.9026 |  | 5500 | 11400.1166 |  | 5500 | 13235.1815 |  | 5500 | 15062.8711
[13 empty] | Next iteration flow rate |  |  | 385.7834 | Abs Value of | Flow this | 630.071 | Abs Value of | Flow this | 1512.4131 | Abs Value of | Flow this | 2887.7508 | Abs Value of | Flow this | 4749.2869 | Abs Value of | Flow this | 7071.041 | Abs Value of | Flow this | 9436.3316 | Abs Value of | Flow this | 11514.1178 | Abs Value of | Flow this | 13367.5333 | Abs Value of | Flow this | 15213.4999 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 51.8898 |  |  | 43.5089 |  |  | -20.3346 |  |  | -224.7152 |  |  | -704.8443 |  |  | -1631.6897 |  |  | -2950.3231 |  |  | -4420.4533 |  |  | -5977.9014 |  |  | -7759.7194
[13 empty] | P2 at this iteration flow rate |  |  | 25.662 |  |  | 27.3382 |  |  | 40.1069 |  |  | 80.983 |  |  | 177.0089 |  |  | 362.3779 |  |  | 626.1046 |  |  | 920.1307 |  |  | 1231.6203 |  |  | 1587.9839
[13 empty] | Delta P at this iteration flow rate |  |  | 26.2278 |  |  | 16.1706 |  |  | -60.4415 |  |  | -305.6983 |  |  | -881.8531 |  |  | -1994.0677 |  |  | -3576.4277 |  |  | -5340.584 |  |  | -7209.5217 |  |  | -9347.7033
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 42.6031 |  |  | 35.6535 |  |  | -16.8099 |  |  | -173.9994 |  |  | -508.6422 |  |  | -1051.1633 |  |  | -1706.6162 |  |  | -2115.2743 |  |  | -2359.2139 |  |  | -2918.9125
[13 empty] | C Non choked w/ reducers | 7 |  | 75.3401 |  |  | 156.8165 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 59.1135 |  |  | 105.6098 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 75.3401 |  |  | 156.8165 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 70.3401 | 385.7834 |  | 144.8165 | 630.071 |  | 5500 | 1512.4131 |  | 5500 | 2887.7508 |  | 5500 | 4749.2869 |  | 5500 | 7071.041 |  | 5500 | 9436.3316 |  | 5500 | 11514.1178 |  | 5500 | 13367.5333 |  | 5500 | 15213.4999
[13 empty] | Next iteration flow rate |  |  | 393.4991 | Abs Value of | Flow this | 636.3718 | Abs Value of | Flow this | 1527.5372 | Abs Value of | Flow this | 2916.6283 | Abs Value of | Flow this | 4796.7797 | Abs Value of | Flow this | 7141.7514 | Abs Value of | Flow this | 9530.6949 | Abs Value of | Flow this | 11629.259 | Abs Value of | Flow this | 13501.2087 | Abs Value of | Flow this | 15365.6349 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 51.6868 |  |  | 43.2394 |  |  | -21.8873 |  |  | -230.376 |  |  | -720.1556 |  |  | -1665.6307 |  |  | -3010.7686 |  |  | -4510.4484 |  |  | -6099.2012 |  |  | -7916.8338
[13 empty] | P2 at this iteration flow rate |  |  | 25.7026 |  |  | 27.3921 |  |  | 40.4175 |  |  | 82.1152 |  |  | 180.0711 |  |  | 369.1661 |  |  | 638.1937 |  |  | 938.1297 |  |  | 1255.8802 |  |  | 1619.4068
[13 empty] | Delta P at this iteration flow rate |  |  | 25.9841 |  |  | 15.8473 |  |  | -62.3048 |  |  | -312.4912 |  |  | -900.2268 |  |  | -2034.7969 |  |  | -3648.9623 |  |  | -5448.5781 |  |  | -7355.0815 |  |  | -9536.2405
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 42.435 |  |  | 35.4304 |  |  | -18.0663 |  |  | -178.374 |  |  | -519.6845 |  |  | -1073.0228 |  |  | -1741.5757 |  |  | -2158.3345 |  |  | -2407.0821 |  |  | -2978.0097
[13 empty] | C Non choked w/ reducers | 7 |  | 77.2064 |  |  | 159.9925 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 60.4151 |  |  | 107.0011 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 77.2064 |  |  | 159.9925 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 72.2064 | 393.4991 |  | 147.9925 | 636.3718 |  | 5500 | 1527.5372 |  | 5500 | 2916.6283 |  | 5500 | 4796.7797 |  | 5500 | 7141.7514 |  | 5500 | 9530.6949 |  | 5500 | 11629.259 |  | 5500 | 13501.2087 |  | 5500 | 15365.6349
[13 empty] | Next iteration flow rate |  |  | 401.3691 | Abs Value of | Flow this | 642.7355 | Abs Value of | Flow this | 1542.8126 | Abs Value of | Flow this | 2945.7946 | Abs Value of | Flow this | 4844.7475 | Abs Value of | Flow this | 7213.1689 | Abs Value of | Flow this | 9626.0018 | Abs Value of | Flow this | 11745.5516 | Abs Value of | Flow this | 13636.2207 | Abs Value of | Flow this | 15519.2912 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 51.4755 |  |  | 42.9645 |  |  | -23.4712 |  |  | -236.1506 |  |  | -735.7748 |  |  | -1700.2539 |  |  | -3072.4291 |  |  | -4602.2524 |  |  | -6222.9392 |  |  | -8077.1061
[13 empty] | P2 at this iteration flow rate |  |  | 25.7449 |  |  | 27.4471 |  |  | 40.7342 |  |  | 83.2701 |  |  | 183.195 |  |  | 376.0908 |  |  | 650.5258 |  |  | 956.4905 |  |  | 1280.6278 |  |  | 1651.4612
[13 empty] | Delta P at this iteration flow rate |  |  | 25.7306 |  |  | 15.5174 |  |  | -64.2055 |  |  | -319.4207 |  |  | -918.9698 |  |  | -2076.3447 |  |  | -3722.9549 |  |  | -5558.7429 |  |  | -7503.567 |  |  | -9728.5674
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 42.26 |  |  | 35.2029 |  |  | -19.3479 |  |  | -182.8366 |  |  | -530.9489 |  |  | -1095.3217 |  |  | -1777.2379 |  |  | -2202.2602 |  |  | -2455.9124 |  |  | -3038.2946
[13 empty] | C Non choked w/ reducers | 7 |  | 79.1375 |  |  | 163.301 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 61.7508 |  |  | 108.4199 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 79.1375 |  |  | 163.301 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 74.1375 | 401.3691 |  | 151.301 | 642.7355 |  | 5500 | 1542.8126 |  | 5500 | 2945.7946 |  | 5500 | 4844.7475 |  | 5500 | 7213.1689 |  | 5500 | 9626.0018 |  | 5500 | 11745.5516 |  | 5500 | 13636.2207 |  | 5500 | 15519.2912
[13 empty] | Next iteration flow rate |  |  | 409.3965 | Abs Value of | Flow this | 649.1628 | Abs Value of | Flow this | 1558.2407 | Abs Value of | Flow this | 2975.2525 | Abs Value of | Flow this | 4893.195 | Abs Value of | Flow this | 7285.3006 | Abs Value of | Flow this | 9722.2619 | Abs Value of | Flow this | 11863.0071 | Abs Value of | Flow this | 13772.583 | Abs Value of | Flow this | 15674.4841 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 51.2557 |  |  | 42.684 |  |  | -25.087 |  |  | -242.0412 |  |  | -751.7079 |  |  | -1735.573 |  |  | -3135.3289 |  |  | -4695.9017 |  |  | -6349.1643 |  |  | -8240.6
[13 empty] | P2 at this iteration flow rate |  |  | 25.7889 |  |  | 27.5032 |  |  | 41.0574 |  |  | 84.4482 |  |  | 186.3816 |  |  | 383.1546 |  |  | 663.1058 |  |  | 975.2203 |  |  | 1305.8729 |  |  | 1684.16
[13 empty] | Delta P at this iteration flow rate |  |  | 25.4669 |  |  | 15.1809 |  |  | -66.1444 |  |  | -326.4895 |  |  | -938.0895 |  |  | -2118.7276 |  |  | -3798.4347 |  |  | -5671.1221 |  |  | -7655.0371 |  |  | -9924.76
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 42.078 |  |  | 34.9707 |  |  | -20.6553 |  |  | -187.3889 |  |  | -542.4396 |  |  | -1118.0687 |  |  | -1813.6169 |  |  | -2247.0688 |  |  | -2505.7242 |  |  | -3099.7913
[13 empty] | C Non choked w/ reducers | 7 |  | 81.1372 |  |  | 166.7521 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 63.1219 |  |  | 109.867 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 81.1372 |  |  | 166.7521 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 76.1372 | 409.3965 |  | 154.7521 | 649.1628 |  | 5500 | 1558.2407 |  | 5500 | 2975.2525 |  | 5500 | 4893.195 |  | 5500 | 7285.3006 |  | 5500 | 9722.2619 |  | 5500 | 11863.0071 |  | 5500 | 13772.583 |  | 5500 | 15674.4841
[13 empty] | Next iteration flow rate |  |  | 417.5844 | Abs Value of | Flow this | 655.6545 | Abs Value of | Flow this | 1573.8231 | Abs Value of | Flow this | 3005.0051 | Abs Value of | Flow this | 4942.127 | Abs Value of | Flow this | 7358.1536 | Abs Value of | Flow this | 9819.4845 | Abs Value of | Flow this | 11981.6372 | Abs Value of | Flow this | 13910.3088 | Abs Value of | Flow this | 15831.229 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 51.027 |  |  | 42.398 |  |  | -26.7353 |  |  | -248.0503 |  |  | -767.9612 |  |  | -1771.6021 |  |  | -3199.493 |  |  | -4791.4334 |  |  | -6477.9265 |  |  | -8407.3801
[13 empty] | P2 at this iteration flow rate |  |  | 25.8346 |  |  | 27.5604 |  |  | 41.3871 |  |  | 85.6501 |  |  | 189.6322 |  |  | 390.3604 |  |  | 675.9386 |  |  | 994.3267 |  |  | 1331.6253 |  |  | 1717.516
[13 empty] | Delta P at this iteration flow rate |  |  | 25.1924 |  |  | 14.8376 |  |  | -68.1224 |  |  | -333.7003 |  |  | -957.5935 |  |  | -2161.9625 |  |  | -3875.4316 |  |  | -5785.76 |  |  | -7809.5518 |  |  | -10124.8961
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 41.8887 |  |  | 34.7339 |  |  | -21.989 |  |  | -192.0326 |  |  | -554.1613 |  |  | -1141.273 |  |  | -1850.7272 |  |  | -2292.778 |  |  | -2556.5372 |  |  | -3162.5241
[13 empty] | C Non choked w/ reducers | 7 |  | 83.2095 |  |  | 170.3567 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 64.5297 |  |  | 111.3433 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 83.2095 |  |  | 170.3567 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 78.2095 | 417.5844 |  | 158.3567 | 655.6545 |  | 5500 | 1573.8231 |  | 5500 | 3005.0051 |  | 5500 | 4942.127 |  | 5500 | 7358.1536 |  | 5500 | 9819.4845 |  | 5500 | 11981.6372 |  | 5500 | 13910.3088 |  | 5500 | 15831.229
[13 empty] | Next iteration flow rate |  |  | 425.9361 | Abs Value of | Flow this | 662.211 | Abs Value of | Flow this | 1589.5613 | Abs Value of | Flow this | 3035.0551 | Abs Value of | Flow this | 4991.5482 | Abs Value of | Flow this | 7431.7351 | Abs Value of | Flow this | 9917.6793 | Abs Value of | Flow this | 12101.4535 | Abs Value of | Flow this | 14049.4119 | Abs Value of | Flow this | 15989.5412 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 50.7891 |  |  | 42.1062 |  |  | -28.4167 |  |  | -254.1801 |  |  | -784.5413 |  |  | -1808.3553 |  |  | -3264.9469 |  |  | -4888.8852 |  |  | -6609.2768 |  |  | -8577.5124
[13 empty] | P2 at this iteration flow rate |  |  | 25.8822 |  |  | 27.6188 |  |  | 41.7233 |  |  | 86.876 |  |  | 192.9483 |  |  | 397.7111 |  |  | 689.0294 |  |  | 1013.817 |  |  | 1357.8954 |  |  | 1751.5425
[13 empty] | Delta P at this iteration flow rate |  |  | 24.9069 |  |  | 14.4874 |  |  | -70.14 |  |  | -341.0561 |  |  | -977.4895 |  |  | -2206.0663 |  |  | -3953.9762 |  |  | -5902.7022 |  |  | -7967.1722 |  |  | -10329.0549
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 41.6917 |  |  | 34.4923 |  |  | -23.3495 |  |  | -196.7697 |  |  | -566.1186 |  |  | -1164.9437 |  |  | -1888.5833 |  |  | -2339.406 |  |  | -2608.3716 |  |  | -3226.5179
[13 empty] | C Non choked w/ reducers | 7 |  | 85.3587 |  |  | 174.1273 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 65.9756 |  |  | 112.8498 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 85.3587 |  |  | 174.1273 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 80.3587 | 425.9361 |  | 162.1273 | 662.211 |  | 5500 | 1589.5613 |  | 5500 | 3035.0551 |  | 5500 | 4991.5482 |  | 5500 | 7431.7351 |  | 5500 | 9917.6793 |  | 5500 | 12101.4535 |  | 5500 | 14049.4119 |  | 5500 | 15989.5412
[13 empty] | Next iteration flow rate |  |  | 434.4548 | Abs Value of | Flow this | 668.8331 | Abs Value of | Flow this | 1605.4569 | Abs Value of | Flow this | 3065.4057 | Abs Value of | Flow this | 5041.4637 | Abs Value of | Flow this | 7506.0525 | Abs Value of | Flow this | 10016.8561 | Abs Value of | Flow this | 12222.4681 | Abs Value of | Flow this | 14189.906 | Abs Value of | Flow this | 16149.4367 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 50.5416 |  |  | 41.8085 |  |  | -30.1319 |  |  | -260.4331 |  |  | -801.4546 |  |  | -1845.8472 |  |  | -3331.7163 |  |  | -4988.2958 |  |  | -6743.2673 |  |  | -8751.0644
[13 empty] | P2 at this iteration flow rate |  |  | 25.9317 |  |  | 27.6783 |  |  | 42.0664 |  |  | 88.1266 |  |  | 196.3309 |  |  | 405.2094 |  |  | 702.3833 |  |  | 1033.6992 |  |  | 1384.6935 |  |  | 1786.2529
[13 empty] | Delta P at this iteration flow rate |  |  | 24.6099 |  |  | 14.1302 |  |  | -72.1983 |  |  | -348.5598 |  |  | -997.7855 |  |  | -2251.0567 |  |  | -4034.0996 |  |  | -6021.995 |  |  | -8127.9608 |  |  | -10537.3173
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 41.4867 |  |  | 34.2459 |  |  | -24.7374 |  |  | -201.6021 |  |  | -578.3163 |  |  | -1189.0902 |  |  | -1927.2004 |  |  | -2386.9712 |  |  | -2661.2478 |  |  | -3291.7978
[13 empty] | C Non choked w/ reducers | 7 |  | 87.5898 |  |  | 178.0777 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 67.4612 |  |  | 114.3877 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 87.5898 |  |  | 178.0777 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 82.5898 | 434.4548 |  | 166.0777 | 668.8331 |  | 5500 | 1605.4569 |  | 5500 | 3065.4057 |  | 5500 | 5041.4637 |  | 5500 | 7506.0525 |  | 5500 | 10016.8561 |  | 5500 | 12222.4681 |  | 5500 | 14189.906 |  | 5500 | 16149.4367
[13 empty] | Next iteration flow rate |  |  | 443.1439 | Abs Value of | Flow this | 675.5214 | Abs Value of | Flow this | 1621.5115 | Abs Value of | Flow this | 3096.0597 | Abs Value of | Flow this | 5091.8783 | Abs Value of | Flow this | 7581.113 | Abs Value of | Flow this | 10117.0247 | Abs Value of | Flow this | 12344.6928 | Abs Value of | Flow this | 14331.8051 | Abs Value of | Flow this | 16310.931 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 50.284 |  |  | 41.5048 |  |  | -31.8815 |  |  | -266.8118 |  |  | -818.7078 |  |  | -1884.0928 |  |  | -3399.8278 |  |  | -5089.7046 |  |  | -6879.951 |  |  | -8928.1048
[13 empty] | P2 at this iteration flow rate |  |  | 25.9832 |  |  | 27.739 |  |  | 42.4163 |  |  | 89.4024 |  |  | 199.7816 |  |  | 412.8586 |  |  | 716.0056 |  |  | 1053.9809 |  |  | 1412.0302 |  |  | 1821.661
[13 empty] | Delta P at this iteration flow rate |  |  | 24.3009 |  |  | 13.7658 |  |  | -74.2979 |  |  | -356.2142 |  |  | -1018.4894 |  |  | -2296.9513 |  |  | -4115.8334 |  |  | -6143.6855 |  |  | -8291.9812 |  |  | -10749.7658
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 41.2734 |  |  | 33.9945 |  |  | -26.1531 |  |  | -206.5315 |  |  | -590.7591 |  |  | -1213.722 |  |  | -1966.5937 |  |  | -2435.4924 |  |  | -2715.1869 |  |  | -3358.39
[13 empty] | C Non choked w/ reducers | 7 |  | 89.9078 |  |  | 182.2235 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 68.9879 |  |  | 115.9579 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 89.9078 |  |  | 182.2235 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 84.9078 | 443.1439 |  | 170.2235 | 675.5214 |  | 5500 | 1621.5115 |  | 5500 | 3096.0597 |  | 5500 | 5091.8783 |  | 5500 | 7581.113 |  | 5500 | 10117.0247 |  | 5500 | 12344.6928 |  | 5500 | 14331.8051 |  | 5500 | 16310.931
[13 empty] | Next iteration flow rate |  |  | 452.0068 | Abs Value of | Flow this | 682.2767 | Abs Value of | Flow this | 1637.7266 | Abs Value of | Flow this | 3127.0203 | Abs Value of | Flow this | 5142.7971 | Abs Value of | Flow this | 7656.9241 | Abs Value of | Flow this | 10218.1949 | Abs Value of | Flow this | 12468.1397 | Abs Value of | Flow this | 14475.1231 | Abs Value of | Flow this | 16474.0403 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 50.0161 |  |  | 41.1951 |  |  | -33.6664 |  |  | -273.3188 |  |  | -836.3078 |  |  | -1923.1071 |  |  | -3469.3084 |  |  | -5193.1516 |  |  | -7019.382 |  |  | -9108.7037
[13 empty] | P2 at this iteration flow rate |  |  | 26.0368 |  |  | 27.801 |  |  | 42.7733 |  |  | 90.7038 |  |  | 203.3016 |  |  | 420.6614 |  |  | 729.9017 |  |  | 1074.6703 |  |  | 1439.9164 |  |  | 1857.7807
[13 empty] | Delta P at this iteration flow rate |  |  | 23.9793 |  |  | 13.3941 |  |  | -76.4397 |  |  | -364.0225 |  |  | -1039.6094 |  |  | -2343.7685 |  |  | -4199.21 |  |  | -6267.822 |  |  | -8459.2984 |  |  | -10966.4845
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 41.0516 |  |  | 33.7381 |  |  | -27.5973 |  |  | -211.5601 |  |  | -603.452 |  |  | -1238.8489 |  |  | -2006.7787 |  |  | -2484.989 |  |  | -2770.2101 |  |  | -3426.3206
[13 empty] | C Non choked w/ reducers | 7 |  | 92.3188 |  |  | 186.5821 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 70.5576 |  |  | 117.5617 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 92.3188 |  |  | 186.5821 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 87.3188 | 452.0068 |  | 174.5821 | 682.2767 |  | 5500 | 1637.7266 |  | 5500 | 3127.0203 |  | 5500 | 5142.7971 |  | 5500 | 7656.9241 |  | 5500 | 10218.1949 |  | 5500 | 12468.1397 |  | 5500 | 14475.1231 |  | 5500 | 16474.0403
[13 empty] | Next iteration flow rate |  |  | 461.0469 | Abs Value of | Flow this | 689.0994 | Abs Value of | Flow this | 1654.1039 | Abs Value of | Flow this | 3158.2905 | Abs Value of | Flow this | 5194.2251 | Abs Value of | Flow this | 7733.4934 | Abs Value of | Flow this | 10320.3769 | Abs Value of | Flow this | 12592.8211 | Abs Value of | Flow this | 14619.8743 | Abs Value of | Flow this | 16638.7807 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 49.7373 |  |  | 40.8791 |  |  | -35.4871 |  |  | -279.9565 |  |  | -854.2616 |  |  | -1962.9055 |  |  | -3540.1855 |  |  | -5298.678 |  |  | -7161.6156 |  |  | -9292.9327
[13 empty] | P2 at this iteration flow rate |  |  | 26.0925 |  |  | 27.8642 |  |  | 43.1374 |  |  | 92.0313 |  |  | 206.8923 |  |  | 428.6211 |  |  | 744.0771 |  |  | 1095.7756 |  |  | 1468.3631 |  |  | 1894.6265
[13 empty] | Delta P at this iteration flow rate |  |  | 23.6448 |  |  | 13.0149 |  |  | -78.6245 |  |  | -371.9878 |  |  | -1061.154 |  |  | -2391.5266 |  |  | -4284.2626 |  |  | -6394.4536 |  |  | -8629.9787 |  |  | -11187.5593
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 40.8207 |  |  | 33.4765 |  |  | -29.0706 |  |  | -216.6897 |  |  | -616.4001 |  |  | -1264.4808 |  |  | -2047.7715 |  |  | -2535.4804 |  |  | -2826.3393 |  |  | -3495.6166
[13 empty] | C Non choked w/ reducers | 7 |  | 94.8289 |  |  | 191.1735 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 72.1719 |  |  | 119.2004 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 94.8289 |  |  | 191.1735 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 89.8289 | 461.0469 |  | 179.1735 | 689.0994 |  | 5500 | 1654.1039 |  | 5500 | 3158.2905 |  | 5500 | 5194.2251 |  | 5500 | 7733.4934 |  | 5500 | 10320.3769 |  | 5500 | 12592.8211 |  | 5500 | 14619.8743 |  | 5500 | 16638.7807
[13 empty] | Next iteration flow rate |  |  | 470.2679 | Abs Value of | Flow this | 695.9904 | Abs Value of | Flow this | 1670.6449 | Abs Value of | Flow this | 3189.8734 | Abs Value of | Flow this | 5246.1673 | Abs Value of | Flow this | 7810.8283 | Abs Value of | Flow this | 10423.5807 | Abs Value of | Flow this | 12718.7493 | Abs Value of | Flow this | 14766.0731 | Abs Value of | Flow this | 16805.1685 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 49.4473 |  |  | 40.5567 |  |  | -37.3444 |  |  | -286.7276 |  |  | -872.5763 |  |  | -2003.5039 |  |  | -3612.4872 |  |  | -5406.3254 |  |  | -7306.7081 |  |  | -9480.8647
[13 empty] | P2 at this iteration flow rate |  |  | 26.1505 |  |  | 27.9287 |  |  | 43.5089 |  |  | 93.3855 |  |  | 210.5553 |  |  | 436.7408 |  |  | 758.5374 |  |  | 1117.3051 |  |  | 1497.3816 |  |  | 1932.2129
[13 empty] | Delta P at this iteration flow rate |  |  | 23.2968 |  |  | 12.6281 |  |  | -80.8533 |  |  | -380.1132 |  |  | -1083.1316 |  |  | -2440.2447 |  |  | -4371.0247 |  |  | -6523.6305 |  |  | -8804.0897 |  |  | -11413.0776
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 40.5806 |  |  | 33.2096 |  |  | -30.5734 |  |  | -221.9224 |  |  | -629.6084 |  |  | -1290.628 |  |  | -2089.5883 |  |  | -2586.9867 |  |  | -2883.5967 |  |  | -3566.3055
[13 empty] | C Non choked w/ reducers | 7 |  | 97.4453 |  |  | 196.0201 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 73.8329 |  |  | 120.8751 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 97.4453 |  |  | 196.0201 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 92.4453 | 470.2679 |  | 184.0201 | 695.9904 |  | 5500 | 1670.6449 |  | 5500 | 3189.8734 |  | 5500 | 5246.1673 |  | 5500 | 7810.8283 |  | 5500 | 10423.5807 |  | 5500 | 12718.7493 |  | 5500 | 14766.0731 |  | 5500 | 16805.1685
[13 empty] | Next iteration flow rate |  |  | 479.6732 | Abs Value of | Flow this | 702.9503 | Abs Value of | Flow this | 1687.3514 | Abs Value of | Flow this | 3221.7722 | Abs Value of | Flow this | 5298.629 | Abs Value of | Flow this | 7888.9366 | Abs Value of | Flow this | 10527.8165 | Abs Value of | Flow this | 12845.9368 | Abs Value of | Flow this | 14913.7338 | Abs Value of | Flow this | 16973.2202 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 49.1456 |  |  | 40.2279 |  |  | -39.239 |  |  | -293.6349 |  |  | -891.2591 |  |  | -2044.9184 |  |  | -3686.2422 |  |  | -5516.1366 |  |  | -7454.717 |  |  | -9672.5741
[13 empty] | P2 at this iteration flow rate |  |  | 26.2109 |  |  | 27.9944 |  |  | 43.8878 |  |  | 94.767 |  |  | 214.2918 |  |  | 445.0237 |  |  | 773.2884 |  |  | 1139.2673 |  |  | 1526.9834 |  |  | 1970.5548
[13 empty] | Delta P at this iteration flow rate |  |  | 22.9347 |  |  | 12.2335 |  |  | -83.1268 |  |  | -388.4019 |  |  | -1105.5509 |  |  | -2489.9421 |  |  | -4459.5307 |  |  | -6655.4039 |  |  | -8981.7003 |  |  | -11643.1289
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 40.3307 |  |  | 32.9374 |  |  | -32.1065 |  |  | -227.2603 |  |  | -643.0822 |  |  | -1317.3007 |  |  | -2132.2455 |  |  | -2639.5283 |  |  | -2942.005 |  |  | -3638.4152
[13 empty] | C Non choked w/ reducers | 7 |  | 100.1757 |  |  | 201.1479 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 75.5424 |  |  | 122.5873 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 100.1757 |  |  | 201.1479 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 95.1757 | 479.6732 |  | 189.1479 | 702.9503 |  | 5500 | 1687.3514 |  | 5500 | 3221.7722 |  | 5500 | 5298.629 |  | 5500 | 7888.9366 |  | 5500 | 10527.8165 |  | 5500 | 12845.9368 |  | 5500 | 14913.7338 |  | 5500 | 16973.2202
[13 empty] | Next iteration flow rate |  |  | 489.2667 | Abs Value of | Flow this | 709.9798 | Abs Value of | Flow this | 1704.2249 | Abs Value of | Flow this | 3253.9899 | Abs Value of | Flow this | 5351.6153 | Abs Value of | Flow this | 7967.826 | Abs Value of | Flow this | 10633.0946 | Abs Value of | Flow this | 12974.3962 | Abs Value of | Flow this | 15062.8711 | Abs Value of | Flow this | 17142.9524 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 48.8316 |  |  | 39.8925 |  |  | -41.1717 |  |  | -300.681 |  |  | -910.3174 |  |  | -2087.1653 |  |  | -3761.4797 |  |  | -5628.155 |  |  | -7605.7008 |  |  | -9868.1368
[13 empty] | P2 at this iteration flow rate |  |  | 26.2737 |  |  | 28.0615 |  |  | 44.2743 |  |  | 96.1762 |  |  | 218.1035 |  |  | 453.4731 |  |  | 788.3359 |  |  | 1161.671 |  |  | 1557.1802 |  |  | 2009.6674
[13 empty] | Delta P at this iteration flow rate |  |  | 22.558 |  |  | 11.8309 |  |  | -85.4461 |  |  | -396.8571 |  |  | -1128.4209 |  |  | -2540.6383 |  |  | -4549.8157 |  |  | -6789.826 |  |  | -9162.8809 |  |  | -11877.8042
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 40.0708 |  |  | 32.6598 |  |  | -33.6703 |  |  | -232.7055 |  |  | -656.8268 |  |  | -1344.5096 |  |  | -2175.7602 |  |  | -2693.126 |  |  | -3001.5872 |  |  | -3711.9743
[13 empty] | C Non choked w/ reducers | 7 |  | 103.0289 |  |  | 206.5865 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 77.3028 |  |  | 124.3384 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 103.0289 |  |  | 206.5865 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 98.0289 | 489.2667 |  | 194.5865 | 709.9798 |  | 5500 | 1704.2249 |  | 5500 | 3253.9899 |  | 5500 | 5351.6153 |  | 5500 | 7967.826 |  | 5500 | 10633.0946 |  | 5500 | 12974.3962 |  | 5500 | 15062.8711 |  | 5500 | 17142.9524
[13 empty] | Next iteration flow rate |  |  | 499.052 | Abs Value of | Flow this | 717.0796 | Abs Value of | Flow this | 1721.2671 | Abs Value of | Flow this | 3286.5298 | Abs Value of | Flow this | 5405.1315 | Abs Value of | Flow this | 8047.5042 | Abs Value of | Flow this | 10739.4256 | Abs Value of | Flow this | 13104.1401 | Abs Value of | Flow this | 15213.4999 | Abs Value of | Flow this | 17314.382 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 48.505 |  |  | 39.5503 |  |  | -43.1433 |  |  | -307.8687 |  |  | -929.7588 |  |  | -2130.2613 |  |  | -3838.2295 |  |  | -5742.4249 |  |  | -7759.7194 |  |  | -10067.6304
[13 empty] | P2 at this iteration flow rate |  |  | 26.339 |  |  | 28.1299 |  |  | 44.6687 |  |  | 97.6137 |  |  | 221.9918 |  |  | 462.0923 |  |  | 803.6859 |  |  | 1184.525 |  |  | 1587.9839 |  |  | 2049.5661
[13 empty] | Delta P at this iteration flow rate |  |  | 22.166 |  |  | 11.4203 |  |  | -87.812 |  |  | -405.4824 |  |  | -1151.7506 |  |  | -2592.3536 |  |  | -4641.9154 |  |  | -6926.9499 |  |  | -9347.7033 |  |  | -12117.1965
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 39.8003 |  |  | 32.3765 |  |  | -35.2656 |  |  | -238.2601 |  |  | -670.8477 |  |  | -1372.2653 |  |  | -2220.1495 |  |  | -2747.8009 |  |  | -3062.3671 |  |  | -3787.012
[13 empty] | C Non choked w/ reducers | 7 |  | 106.0145 |  |  | 212.3702 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 79.1163 |  |  | 126.1299 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 106.0145 |  |  | 212.3702 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 101.0145 | 499.052 |  | 200.3702 | 717.0796 |  | 5500 | 1721.2671 |  | 5500 | 3286.5298 |  | 5500 | 5405.1315 |  | 5500 | 8047.5042 |  | 5500 | 10739.4256 |  | 5500 | 13104.1401 |  | 5500 | 15213.4999 |  | 5500 | 17314.382
[13 empty] | Next iteration flow rate |  |  | 509.0331 | Abs Value of | Flow this | 724.2504 | Abs Value of | Flow this | 1738.4798 | Abs Value of | Flow this | 3319.3951 | Abs Value of | Flow this | 5459.1828 | Abs Value of | Flow this | 8127.9793 | Abs Value of | Flow this | 10846.8198 | Abs Value of | Flow this | 13235.1815 | Abs Value of | Flow this | 15365.6349 | Abs Value of | Flow this | 17487.5258 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 48.1652 |  |  | 39.2012 |  |  | -45.1545 |  |  | -315.2008 |  |  | -949.591 |  |  | -2174.2236 |  |  | -3916.5219 |  |  | -5858.9916 |  |  | -7916.8338 |  |  | -10271.1338
[13 empty] | P2 at this iteration flow rate |  |  | 26.407 |  |  | 28.1998 |  |  | 45.0709 |  |  | 99.0802 |  |  | 225.9582 |  |  | 470.8847 |  |  | 819.3444 |  |  | 1207.8383 |  |  | 1619.4068 |  |  | 2090.2668
[13 empty] | Delta P at this iteration flow rate |  |  | 21.7583 |  |  | 11.0015 |  |  | -90.2254 |  |  | -414.281 |  |  | -1175.5492 |  |  | -2645.1083 |  |  | -4735.8663 |  |  | -7066.83 |  |  | -9536.2405 |  |  | -12361.4005
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 39.5189 |  |  | 32.0875 |  |  | -36.893 |  |  | -243.9264 |  |  | -685.1504 |  |  | -1400.579 |  |  | -2265.4311 |  |  | -2803.5749 |  |  | -3124.3686 |  |  | -3863.5579
[13 empty] | C Non choked w/ reducers | 7 |  | 109.1434 |  |  | 218.539 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 80.9854 |  |  | 127.9635 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 109.1434 |  |  | 218.539 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 104.1434 | 509.0331 |  | 206.539 | 724.2504 |  | 5500 | 1738.4798 |  | 5500 | 3319.3951 |  | 5500 | 5459.1828 |  | 5500 | 8127.9793 |  | 5500 | 10846.8198 |  | 5500 | 13235.1815 |  | 5500 | 15365.6349 |  | 5500 | 17487.5258
[13 empty] | Next iteration flow rate |  |  | 519.2137 | Abs Value of | Flow this | 731.4929 | Abs Value of | Flow this | 1755.8646 | Abs Value of | Flow this | 3352.589 | Abs Value of | Flow this | 5513.7746 | Abs Value of | Flow this | 8209.259 | Abs Value of | Flow this | 10955.288 | Abs Value of | Flow this | 13367.5333 | Abs Value of | Flow this | 15519.2912 | Abs Value of | Flow this | 17662.401 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 47.8117 |  |  | 38.8452 |  |  | -47.2061 |  |  | -322.6804 |  |  | -969.8218 |  |  | -2219.0695 |  |  | -3996.388 |  |  | -5977.9014 |  |  | -8077.1061 |  |  | -10478.7276
[13 empty] | P2 at this iteration flow rate |  |  | 26.4777 |  |  | 28.271 |  |  | 45.4812 |  |  | 100.5761 |  |  | 230.0044 |  |  | 479.8539 |  |  | 835.3176 |  |  | 1231.6203 |  |  | 1651.4612 |  |  | 2131.7855
[13 empty] | Delta P at this iteration flow rate |  |  | 21.334 |  |  | 10.5742 |  |  | -92.6874 |  |  | -423.2565 |  |  | -1199.8262 |  |  | -2698.9234 |  |  | -4831.7056 |  |  | -7209.5217 |  |  | -9728.5674 |  |  | -12610.5131
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 39.2262 |  |  | 31.7928 |  |  | -38.5531 |  |  | -249.7066 |  |  | -699.7406 |  |  | -1429.4617 |  |  | -2311.6228 |  |  | -2860.4699 |  |  | -3187.6164 |  |  | -3941.6424
[13 empty] | C Non choked w/ reducers | 7 |  | 112.4277 |  |  | 225.1398 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 82.9128 |  |  | 129.8409 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 112.4277 |  |  | 225.1398 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 107.4277 | 519.2137 |  | 213.1398 | 731.4929 |  | 5500 | 1755.8646 |  | 5500 | 3352.589 |  | 5500 | 5513.7746 |  | 5500 | 8209.259 |  | 5500 | 10955.288 |  | 5500 | 13367.5333 |  | 5500 | 15519.2912 |  | 5500 | 17662.401
[13 empty] | Next iteration flow rate |  |  | 529.598 | Abs Value of | Flow this | 738.8079 | Abs Value of | Flow this | 1773.4232 | Abs Value of | Flow this | 3386.1149 | Abs Value of | Flow this | 5568.9124 | Abs Value of | Flow this | 8291.3516 | Abs Value of | Flow this | 11064.8409 | Abs Value of | Flow this | 13501.2087 | Abs Value of | Flow this | 15674.4841 | Abs Value of | Flow this | 17839.025 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 47.4439 |  |  | 38.4819 |  |  | -49.299 |  |  | -330.3103 |  |  | -990.4592 |  |  | -2264.8168 |  |  | -4077.8594 |  |  | -6099.2012 |  |  | -8240.6 |  |  | -10690.494
[13 empty] | P2 at this iteration flow rate |  |  | 26.5512 |  |  | 28.3436 |  |  | 45.8998 |  |  | 102.1021 |  |  | 234.1318 |  |  | 489.0034 |  |  | 851.6119 |  |  | 1255.8802 |  |  | 1684.16 |  |  | 2174.1388
[13 empty] | Delta P at this iteration flow rate |  |  | 20.8926 |  |  | 10.1383 |  |  | -95.1988 |  |  | -432.4123 |  |  | -1224.5911 |  |  | -2753.8201 |  |  | -4929.4713 |  |  | -7355.0815 |  |  | -9924.76 |  |  | -12864.6328
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 38.9216 |  |  | 31.4921 |  |  | -40.2465 |  |  | -255.6029 |  |  | -714.6241 |  |  | -1458.925 |  |  | -2358.743 |  |  | -2918.5085 |  |  | -3252.1355 |  |  | -4021.2964
[13 empty] | C Non choked w/ reducers | 7 |  | 115.8812 |  |  | 232.2278 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 84.9013 |  |  | 131.7639 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 115.8812 |  |  | 232.2278 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 110.8812 | 529.598 |  | 220.2278 | 738.8079 |  | 5500 | 1773.4232 |  | 5500 | 3386.1149 |  | 5500 | 5568.9124 |  | 5500 | 8291.3516 |  | 5500 | 11064.8409 |  | 5500 | 13501.2087 |  | 5500 | 15674.4841 |  | 5500 | 17839.025
[13 empty] | Next iteration flow rate |  |  | 540.1899 | Abs Value of | Flow this | 746.1959 | Abs Value of | Flow this | 1791.1575 | Abs Value of | Flow this | 3419.9761 | Abs Value of | Flow this | 5624.6015 | Abs Value of | Flow this | 8374.2652 | Abs Value of | Flow this | 11175.4893 | Abs Value of | Flow this | 13636.2207 | Abs Value of | Flow this | 15831.229 | Abs Value of | Flow this | 18017.4153 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 47.0612 |  |  | 38.1114 |  |  | -51.4339 |  |  | -338.0935 |  |  | -1011.5115 |  |  | -2311.4836 |  |  | -4160.9684 |  |  | -6222.9392 |  |  | -8407.3801 |  |  | -10906.517
[13 empty] | P2 at this iteration flow rate |  |  | 26.6278 |  |  | 28.4177 |  |  | 46.3268 |  |  | 103.6587 |  |  | 238.3423 |  |  | 498.3367 |  |  | 868.2337 |  |  | 1280.6278 |  |  | 1717.516 |  |  | 2217.3434
[13 empty] | Delta P at this iteration flow rate |  |  | 20.4334 |  |  | 9.6937 |  |  | -97.7607 |  |  | -441.7522 |  |  | -1249.8538 |  |  | -2809.8203 |  |  | -5029.2021 |  |  | -7503.567 |  |  | -10124.8961 |  |  | -13123.8603
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 38.6047 |  |  | 31.1853 |  |  | -41.974 |  |  | -261.6178 |  |  | -729.8067 |  |  | -1488.9805 |  |  | -2406.8102 |  |  | -2977.7136 |  |  | -3317.9514 |  |  | -4102.5515
[13 empty] | C Non choked w/ reducers | 7 |  | 119.5197 |  |  | 239.869 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 86.954 |  |  | 133.7344 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 119.5197 |  |  | 239.869 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 114.5197 | 540.1899 |  | 227.869 | 746.1959 |  | 5500 | 1791.1575 |  | 5500 | 3419.9761 |  | 5500 | 5624.6015 |  | 5500 | 8374.2652 |  | 5500 | 11175.4893 |  | 5500 | 13636.2207 |  | 5500 | 15831.229 |  | 5500 | 18017.4153
[13 empty] | Next iteration flow rate |  |  | 550.9937 | Abs Value of | Flow this | 753.6579 | Abs Value of | Flow this | 1809.0691 | Abs Value of | Flow this | 3454.1758 | Abs Value of | Flow this | 5680.8475 | Abs Value of | Flow this | 8458.0078 | Abs Value of | Flow this | 11287.2442 | Abs Value of | Flow this | 13772.583 | Abs Value of | Flow this | 15989.5412 | Abs Value of | Flow this | 18197.5895 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 46.663 |  |  | 37.7334 |  |  | -53.6117 |  |  | -346.0332 |  |  | -1032.9869 |  |  | -2359.0885 |  |  | -4245.7479 |  |  | -6349.1643 |  |  | -8577.5124 |  |  | -11126.882
[13 empty] | P2 at this iteration flow rate |  |  | 26.7074 |  |  | 28.4933 |  |  | 46.7623 |  |  | 105.2466 |  |  | 242.6374 |  |  | 507.8577 |  |  | 885.1896 |  |  | 1305.8729 |  |  | 1751.5425 |  |  | 2261.4164
[13 empty] | Delta P at this iteration flow rate |  |  | 19.9557 |  |  | 9.2401 |  |  | -100.3741 |  |  | -451.2799 |  |  | -1275.6242 |  |  | -2866.9461 |  |  | -5130.9375 |  |  | -7655.0371 |  |  | -10329.0549 |  |  | -13388.2984
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 38.2751 |  |  | 30.8725 |  |  | -43.7362 |  |  | -267.7536 |  |  | -745.2945 |  |  | -1519.6401 |  |  | -2455.8437 |  |  | -3038.1088 |  |  | -3385.0902 |  |  | -4185.4397
[13 empty] | C Non choked w/ reducers | 7 |  | 123.3608 |  |  | 248.1426 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 89.0743 |  |  | 135.7545 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 123.3608 |  |  | 248.1426 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 118.3608 | 550.9937 |  | 236.1426 | 753.6579 |  | 5500 | 1809.0691 |  | 5500 | 3454.1758 |  | 5500 | 5680.8475 |  | 5500 | 8458.0078 |  | 5500 | 11287.2442 |  | 5500 | 13772.583 |  | 5500 | 15989.5412 |  | 5500 | 18197.5895
[13 empty] | Next iteration flow rate |  |  | 562.0136 | Abs Value of | Flow this | 761.1945 | Abs Value of | Flow this | 1827.1597 | Abs Value of | Flow this | 3488.7176 | Abs Value of | Flow this | 5737.656 | Abs Value of | Flow this | 8542.5879 | Abs Value of | Flow this | 11400.1166 | Abs Value of | Flow this | 13910.3088 | Abs Value of | Flow this | 16149.4367 | Abs Value of | Flow this | 18379.5653 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 46.2488 |  |  | 37.3479 |  |  | -55.8334 |  |  | -354.1325 |  |  | -1054.8939 |  |  | -2407.6501 |  |  | -4332.2314 |  |  | -6477.9265 |  |  | -8751.0644 |  |  | -11351.6763
[13 empty] | P2 at this iteration flow rate |  |  | 26.7902 |  |  | 28.5704 |  |  | 47.2067 |  |  | 106.8665 |  |  | 247.0188 |  |  | 517.57 |  |  | 902.4863 |  |  | 1331.6253 |  |  | 1786.2529 |  |  | 2306.3753
[13 empty] | Delta P at this iteration flow rate |  |  | 19.4586 |  |  | 8.7774 |  |  | -103.04 |  |  | -460.999 |  |  | -1301.9127 |  |  | -2925.2202 |  |  | -5234.7177 |  |  | -7809.5518 |  |  | -10537.3173 |  |  | -13658.0516
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 37.9321 |  |  | 30.5533 |  |  | -45.5338 |  |  | -274.0127 |  |  | -761.0936 |  |  | -1550.9159 |  |  | -2505.8627 |  |  | -3099.718 |  |  | -3453.5784 |  |  | -4269.9941
[13 empty] | C Non choked w/ reducers | 7 |  | 127.425 |  |  | 257.1448 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 91.2656 |  |  | 137.8264 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 127.425 |  |  | 257.1448 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 122.425 | 562.0136 |  | 245.1448 | 761.1945 |  | 5500 | 1827.1597 |  | 5500 | 3488.7176 |  | 5500 | 5737.656 |  | 5500 | 8542.5879 |  | 5500 | 11400.1166 |  | 5500 | 13910.3088 |  | 5500 | 16149.4367 |  | 5500 | 18379.5653
[13 empty] | Next iteration flow rate |  |  | 573.2539 | Abs Value of | Flow this | 768.8064 | Abs Value of | Flow this | 1845.4313 | Abs Value of | Flow this | 3523.6048 | Abs Value of | Flow this | 5795.0325 | Abs Value of | Flow this | 8628.0138 | Abs Value of | Flow this | 11514.1178 | Abs Value of | Flow this | 14049.4119 | Abs Value of | Flow this | 16310.931 | Abs Value of | Flow this | 18563.361 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 45.8179 |  |  | 36.9545 |  |  | -58.0996 |  |  | -362.3946 |  |  | -1077.2413 |  |  | -2457.1879 |  |  | -4420.4533 |  |  | -6609.2768 |  |  | -8928.1048 |  |  | -11580.989
[13 empty] | P2 at this iteration flow rate |  |  | 26.8764 |  |  | 28.6491 |  |  | 47.6599 |  |  | 108.5189 |  |  | 251.4883 |  |  | 527.4776 |  |  | 920.1307 |  |  | 1357.8954 |  |  | 1821.661 |  |  | 2352.2378
[13 empty] | Delta P at this iteration flow rate |  |  | 18.9414 |  |  | 8.3054 |  |  | -105.7595 |  |  | -470.9135 |  |  | -1328.7296 |  |  | -2984.6655 |  |  | -5340.584 |  |  | -7967.1722 |  |  | -10749.7658 |  |  | -13933.2268
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 37.5752 |  |  | 30.2277 |  |  | -47.3676 |  |  | -280.3976 |  |  | -777.2102 |  |  | -1582.8204 |  |  | -2556.887 |  |  | -3162.5654 |  |  | -3523.4433 |  |  | -4356.2479
[13 empty] | C Non choked w/ reducers | 7 |  | 131.7359 |  |  | 266.9939 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 93.5319 |  |  | 139.9524 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 131.7359 |  |  | 266.9939 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 126.7359 | 573.2539 |  | 254.9939 | 768.8064 |  | 5500 | 1845.4313 |  | 5500 | 3523.6048 |  | 5500 | 5795.0325 |  | 5500 | 8628.0138 |  | 5500 | 11514.1178 |  | 5500 | 14049.4119 |  | 5500 | 16310.931 |  | 5500 | 18563.361
[13 empty] | Next iteration flow rate |  |  | 584.719 | Abs Value of | Flow this | 776.4945 | Abs Value of | Flow this | 1863.8857 | Abs Value of | Flow this | 3558.8408 | Abs Value of | Flow this | 5852.9829 | Abs Value of | Flow this | 8714.2939 | Abs Value of | Flow this | 11629.259 | Abs Value of | Flow this | 14189.906 | Abs Value of | Flow this | 16474.0403 | Abs Value of | Flow this | 18748.9946 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 45.3695 |  |  | 36.5533 |  |  | -60.4114 |  |  | -370.8227 |  |  | -1100.0379 |  |  | -2507.7214 |  |  | -4510.4484 |  |  | -6743.2673 |  |  | -9108.7037 |  |  | -11814.9109
[13 empty] | P2 at this iteration flow rate |  |  | 26.9661 |  |  | 28.7293 |  |  | 48.1223 |  |  | 110.2045 |  |  | 256.0476 |  |  | 537.5843 |  |  | 938.1297 |  |  | 1384.6935 |  |  | 1857.7807 |  |  | 2399.0222
[13 empty] | Delta P at this iteration flow rate |  |  | 18.4034 |  |  | 7.824 |  |  | -108.5337 |  |  | -481.0273 |  |  | -1356.0854 |  |  | -3045.3057 |  |  | -5448.5781 |  |  | -8127.9608 |  |  | -10966.4845 |  |  | -14213.9331
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 37.2039 |  |  | 29.8955 |  |  | -49.2382 |  |  | -286.9108 |  |  | -793.6508 |  |  | -1615.3662 |  |  | -2608.937 |  |  | -3226.6762 |  |  | -3594.7125 |  |  | -4444.2355
[13 empty] | C Non choked w/ reducers | 7 |  | 136.3207 |  |  | 277.8373 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 95.8774 |  |  | 142.135 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 136.3207 |  |  | 277.8373 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 131.3207 | 584.719 |  | 265.8373 | 776.4945 |  | 5500 | 1863.8857 |  | 5500 | 3558.8408 |  | 5500 | 5852.9829 |  | 5500 | 8714.2939 |  | 5500 | 11629.259 |  | 5500 | 14189.906 |  | 5500 | 16474.0403 |  | 5500 | 18748.9946
[13 empty] | Next iteration flow rate |  |  | 596.4133 | Abs Value of | Flow this | 784.2594 | Abs Value of | Flow this | 1882.5245 | Abs Value of | Flow this | 3594.4292 | Abs Value of | Flow this | 5911.5127 | Abs Value of | Flow this | 8801.4368 | Abs Value of | Flow this | 11745.5516 | Abs Value of | Flow this | 14331.8051 | Abs Value of | Flow this | 16638.7807 | Abs Value of | Flow this | 18936.4846 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 44.903 |  |  | 36.144 |  |  | -62.7697 |  |  | -379.4203 |  |  | -1123.2926 |  |  | -2559.2706 |  |  | -4602.2524 |  |  | -6879.951 |  |  | -9292.9327 |  |  | -12053.5346
[13 empty] | P2 at this iteration flow rate |  |  | 27.0594 |  |  | 28.8112 |  |  | 48.5939 |  |  | 111.9241 |  |  | 260.6985 |  |  | 547.8941 |  |  | 956.4905 |  |  | 1412.0302 |  |  | 1894.6265 |  |  | 2446.7469
[13 empty] | Delta P at this iteration flow rate |  |  | 17.8436 |  |  | 7.3328 |  |  | -111.3637 |  |  | -491.3443 |  |  | -1383.9912 |  |  | -3107.1648 |  |  | -5558.7429 |  |  | -8291.9812 |  |  | -11187.5593 |  |  | -14500.2816
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 36.8177 |  |  | 29.5567 |  |  | -51.1464 |  |  | -293.555 |  |  | -810.4219 |  |  | -1648.5662 |  |  | -2662.0332 |  |  | -3292.0755 |  |  | -3667.4142 |  |  | -4533.9916
[13 empty] | C Non choked w/ reducers | 7 |  | 141.2113 |  |  | 289.8612 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 98.3066 |  |  | 144.3768 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 141.2113 |  |  | 289.8612 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 136.2113 | 596.4133 |  | 277.8612 | 784.2594 |  | 5500 | 1882.5245 |  | 5500 | 3594.4292 |  | 5500 | 5911.5127 |  | 5500 | 8801.4368 |  | 5500 | 11745.5516 |  | 5500 | 14331.8051 |  | 5500 | 16638.7807 |  | 5500 | 18936.4846
[13 empty] | Next iteration flow rate |  |  | 608.3416 | Abs Value of | Flow this | 792.102 | Abs Value of | Flow this | 1901.3498 | Abs Value of | Flow this | 3630.3735 | Abs Value of | Flow this | 5970.6278 | Abs Value of | Flow this | 8889.4512 | Abs Value of | Flow this | 11863.0071 | Abs Value of | Flow this | 14475.1231 | Abs Value of | Flow this | 16805.1685 | Abs Value of | Flow this | 19125.8494 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 44.4177 |  |  | 35.7265 |  |  | -65.1754 |  |  | -388.1906 |  |  | -1147.0148 |  |  | -2611.856 |  |  | -4695.9017 |  |  | -7019.382 |  |  | -9480.8647 |  |  | -12296.9547
[13 empty] | P2 at this iteration flow rate |  |  | 27.1565 |  |  | 28.8947 |  |  | 49.0751 |  |  | 113.6781 |  |  | 265.443 |  |  | 558.4112 |  |  | 975.2203 |  |  | 1439.9164 |  |  | 1932.2129 |  |  | 2495.4309
[13 empty] | Delta P at this iteration flow rate |  |  | 17.2612 |  |  | 6.8318 |  |  | -114.2505 |  |  | -501.8688 |  |  | -1412.4578 |  |  | -3170.2672 |  |  | -5671.1221 |  |  | -8459.2984 |  |  | -11413.0776 |  |  | -14792.3856
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 36.4158 |  |  | 29.2111 |  |  | -53.093 |  |  | -300.3327 |  |  | -827.53 |  |  | -1682.4335 |  |  | -2716.1966 |  |  | -3358.7894 |  |  | -3741.5772 |  |  | -4625.5518
[13 empty] | C Non choked w/ reducers | 7 |  | 146.4453 |  |  | 303.305 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 100.8245 |  |  | 146.6808 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 146.4453 |  |  | 303.305 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 141.4453 | 608.3416 |  | 291.305 | 792.102 |  | 5500 | 1901.3498 |  | 5500 | 3630.3735 |  | 5500 | 5970.6278 |  | 5500 | 8889.4512 |  | 5500 | 11863.0071 |  | 5500 | 14475.1231 |  | 5500 | 16805.1685 |  | 5500 | 19125.8494
[13 empty] | Next iteration flow rate |  |  | 620.5084 | Abs Value of | Flow this | 800.023 | Abs Value of | Flow this | 1920.3633 | Abs Value of | Flow this | 3666.6772 | Abs Value of | Flow this | 6030.3341 | Abs Value of | Flow this | 8978.3457 | Abs Value of | Flow this | 11981.6372 | Abs Value of | Flow this | 14619.8743 | Abs Value of | Flow this | 16973.2202 | Abs Value of | Flow this | 19317.1079 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 43.9127 |  |  | 35.3006 |  |  | -67.6295 |  |  | -397.1373 |  |  | -1171.2139 |  |  | -2665.4983 |  |  | -4791.4334 |  |  | -7161.6156 |  |  | -9672.5741 |  |  | -12545.2675
[13 empty] | P2 at this iteration flow rate |  |  | 27.2575 |  |  | 28.9799 |  |  | 49.5659 |  |  | 115.4675 |  |  | 270.2828 |  |  | 569.1397 |  |  | 994.3267 |  |  | 1468.3631 |  |  | 1970.5548 |  |  | 2545.0935
[13 empty] | Delta P at this iteration flow rate |  |  | 16.6553 |  |  | 6.3207 |  |  | -117.1953 |  |  | -512.6047 |  |  | -1441.4966 |  |  | -3234.638 |  |  | -5785.76 |  |  | -8629.9787 |  |  | -11643.1289 |  |  | -15090.361
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 35.9977 |  |  | 28.8585 |  |  | -55.0787 |  |  | -307.2467 |  |  | -844.982 |  |  | -1716.9815 |  |  | -2771.4487 |  |  | -3426.8442 |  |  | -3817.2309 |  |  | -4718.9524
[13 empty] | C Non choked w/ reducers | 7 |  | 152.0671 |  |  | 318.4826 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 103.4366 |  |  | 149.0498 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 152.0671 |  |  | 318.4826 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 147.0671 | 620.5084 |  | 306.4826 | 800.023 |  | 5500 | 1920.3633 |  | 5500 | 3666.6772 |  | 5500 | 6030.3341 |  | 5500 | 8978.3457 |  | 5500 | 11981.6372 |  | 5500 | 14619.8743 |  | 5500 | 16973.2202 |  | 5500 | 19317.1079
[13 empty] | Next iteration flow rate |  |  | 632.9186 | Abs Value of | Flow this | 808.0233 | Abs Value of | Flow this | 1939.5669 | Abs Value of | Flow this | 3703.344 | Abs Value of | Flow this | 6090.6374 | Abs Value of | Flow this | 9068.1292 | Abs Value of | Flow this | 12101.4535 | Abs Value of | Flow this | 14766.0731 | Abs Value of | Flow this | 17142.9524 | Abs Value of | Flow this | 19510.279 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 43.3874 |  |  | 34.8661 |  |  | -70.1328 |  |  | -406.2638 |  |  | -1195.8993 |  |  | -2720.2188 |  |  | -4888.8852 |  |  | -7306.7081 |  |  | -9868.1368 |  |  | -12798.5714
[13 empty] | P2 at this iteration flow rate |  |  | 27.3625 |  |  | 29.0668 |  |  | 50.0666 |  |  | 117.2928 |  |  | 275.2199 |  |  | 580.0838 |  |  | 1013.817 |  |  | 1497.3816 |  |  | 2009.6674 |  |  | 2595.7543
[13 empty] | Delta P at this iteration flow rate |  |  | 16.0249 |  |  | 5.7993 |  |  | -120.1994 |  |  | -523.5565 |  |  | -1471.1191 |  |  | -3300.3026 |  |  | -5902.7022 |  |  | -8804.0897 |  |  | -11877.8042 |  |  | -15394.3257
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 35.5627 |  |  | 28.4988 |  |  | -57.1043 |  |  | -314.2996 |  |  | -862.7849 |  |  | -1752.2239 |  |  | -2827.8114 |  |  | -3496.2669 |  |  | -3894.4052 |  |  | -4814.2303
[13 empty] | C Non choked w/ reducers | 7 |  | 158.1299 |  |  | 335.8155 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 106.1486 |  |  | 151.4873 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 158.1299 |  |  | 335.8155 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 153.1299 | 632.9186 |  | 323.8155 | 808.0233 |  | 5500 | 1939.5669 |  | 5500 | 3703.344 |  | 5500 | 6090.6374 |  | 5500 | 9068.1292 |  | 5500 | 12101.4535 |  | 5500 | 14766.0731 |  | 5500 | 17142.9524 |  | 5500 | 19510.279
[13 empty] | Next iteration flow rate |  |  | 645.577 | Abs Value of | Flow this | 816.1035 | Abs Value of | Flow this | 1958.9626 | Abs Value of | Flow this | 3740.3775 | Abs Value of | Flow this | 6151.5438 | Abs Value of | Flow this | 9158.8105 | Abs Value of | Flow this | 12222.4681 | Abs Value of | Flow this | 14913.7338 | Abs Value of | Flow this | 17314.382 | Abs Value of | Flow this | 19705.3818 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 42.8408 |  |  | 34.4229 |  |  | -72.6865 |  |  | -415.5737 |  |  | -1221.0809 |  |  | -2776.0393 |  |  | -4988.2958 |  |  | -7454.717 |  |  | -10067.6304 |  |  | -13056.9667
[13 empty] | P2 at this iteration flow rate |  |  | 27.4718 |  |  | 29.1554 |  |  | 50.5773 |  |  | 119.1547 |  |  | 280.2562 |  |  | 591.2479 |  |  | 1033.6992 |  |  | 1526.9834 |  |  | 2049.5661 |  |  | 2647.4333
[13 empty] | Delta P at this iteration flow rate |  |  | 15.369 |  |  | 5.2675 |  |  | -123.2638 |  |  | -534.7284 |  |  | -1501.337 |  |  | -3367.2871 |  |  | -6021.995 |  |  | -8981.7003 |  |  | -12117.1965 |  |  | -15704.4
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 35.1101 |  |  | 28.1319 |  |  | -59.1706 |  |  | -321.4943 |  |  | -880.9455 |  |  | -1788.1747 |  |  | -2885.3069 |  |  | -3567.085 |  |  | -3973.1307 |  |  | -4911.4233
[13 empty] | C Non choked w/ reducers | 7 |  | 164.6981 |  |  | 355.8848 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 108.9672 |  |  | 153.9967 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 164.6981 |  |  | 355.8848 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 159.6981 | 645.577 |  | 343.8848 | 816.1035 |  | 5500 | 1958.9626 |  | 5500 | 3740.3775 |  | 5500 | 6151.5438 |  | 5500 | 9158.8105 |  | 5500 | 12222.4681 |  | 5500 | 14913.7338 |  | 5500 | 17314.382 |  | 5500 | 19705.3818
[13 empty] | Next iteration flow rate |  |  | 658.4885 | Abs Value of | Flow this | 824.2645 | Abs Value of | Flow this | 1978.5522 | Abs Value of | Flow this | 3777.7812 | Abs Value of | Flow this | 6213.0592 | Abs Value of | Flow this | 9250.3986 | Abs Value of | Flow this | 12344.6928 | Abs Value of | Flow this | 15062.8711 | Abs Value of | Flow this | 17487.5258 | Abs Value of | Flow this | 19902.4356 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 42.2722 |  |  | 33.9708 |  |  | -75.2915 |  |  | -425.0707 |  |  | -1246.7686 |  |  | -2832.9817 |  |  | -5089.7046 |  |  | -7605.7008 |  |  | -10271.1338 |  |  | -13320.5557
[13 empty] | P2 at this iteration flow rate |  |  | 27.5856 |  |  | 29.2458 |  |  | 51.0983 |  |  | 121.0541 |  |  | 285.3937 |  |  | 602.6363 |  |  | 1053.9809 |  |  | 1557.1802 |  |  | 2090.2668 |  |  | 2700.1511
[13 empty] | Delta P at this iteration flow rate |  |  | 14.6866 |  |  | 4.7249 |  |  | -126.3898 |  |  | -546.1249 |  |  | -1532.1623 |  |  | -3435.618 |  |  | -6143.6855 |  |  | -9162.8809 |  |  | -12361.4005 |  |  | -16020.7069
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 34.6392 |  |  | 27.7576 |  |  | -61.2785 |  |  | -328.8335 |  |  | -899.4712 |  |  | -1824.8481 |  |  | -2943.9581 |  |  | -3639.3266 |  |  | -4053.4386 |  |  | -5010.5699
[13 empty] | C Non choked w/ reducers | 7 |  | 171.8504 |  |  | 379.5194 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 111.8994 |  |  | 156.5817 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 171.8504 |  |  | 379.5194 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 166.8504 | 658.4885 |  | 367.5194 | 824.2645 |  | 5500 | 1978.5522 |  | 5500 | 3777.7812 |  | 5500 | 6213.0592 |  | 5500 | 9250.3986 |  | 5500 | 12344.6928 |  | 5500 | 15062.8711 |  | 5500 | 17487.5258 |  | 5500 | 19902.4356
[13 empty] | Next iteration flow rate |  |  | 671.6583 | Abs Value of | Flow this | 832.5072 | Abs Value of | Flow this | 1998.3377 | Abs Value of | Flow this | 3815.559 | Abs Value of | Flow this | 6275.1898 | Abs Value of | Flow this | 9342.9026 | Abs Value of | Flow this | 12468.1397 | Abs Value of | Flow this | 15213.4999 | Abs Value of | Flow this | 17662.401 | Abs Value of | Flow this | 20101.4599 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 41.6806 |  |  | 33.5096 |  |  | -77.9489 |  |  | -434.7587 |  |  | -1272.9727 |  |  | -2891.0686 |  |  | -5193.1516 |  |  | -7759.7194 |  |  | -10478.7276 |  |  | -13589.4429
[13 empty] | P2 at this iteration flow rate |  |  | 27.7039 |  |  | 29.3381 |  |  | 51.6298 |  |  | 122.9917 |  |  | 290.6345 |  |  | 614.2537 |  |  | 1074.6703 |  |  | 1587.9839 |  |  | 2131.7855 |  |  | 2753.9286
[13 empty] | Delta P at this iteration flow rate |  |  | 13.9767 |  |  | 4.1715 |  |  | -129.5787 |  |  | -557.7504 |  |  | -1563.6072 |  |  | -3505.3223 |  |  | -6267.822 |  |  | -9347.7033 |  |  | -12610.5131 |  |  | -16343.3715
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 34.1493 |  |  | 27.3758 |  |  | -63.4287 |  |  | -336.3204 |  |  | -918.3692 |  |  | -1862.2587 |  |  | -3003.7882 |  |  | -3713.0202 |  |  | -4135.3607 |  |  | -5111.7094
[13 empty] | C Non choked w/ reducers | 7 |  | 179.6841 |  |  | 407.9505 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 114.9531 |  |  | 159.2465 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 179.6841 |  |  | 407.9505 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 174.6841 | 671.6583 |  | 395.9505 | 832.5072 |  | 5500 | 1998.3377 |  | 5500 | 3815.559 |  | 5500 | 6275.1898 |  | 5500 | 9342.9026 |  | 5500 | 12468.1397 |  | 5500 | 15213.4999 |  | 5500 | 17662.401 |  | 5500 | 20101.4599
[13 empty] | Next iteration flow rate |  |  | 685.0915 | Abs Value of | Flow this | 840.8323 | Abs Value of | Flow this | 2018.3211 | Abs Value of | Flow this | 3853.7146 | Abs Value of | Flow this | 6337.9417 | Abs Value of | Flow this | 9436.3316 | Abs Value of | Flow this | 12592.8211 | Abs Value of | Flow this | 15365.6349 | Abs Value of | Flow this | 17839.025 | Abs Value of | Flow this | 20302.4745 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 41.0651 |  |  | 33.0391 |  |  | -80.6597 |  |  | -444.6413 |  |  | -1299.7034 |  |  | -2950.3231 |  |  | -5298.678 |  |  | -7916.8338 |  |  | -10690.494 |  |  | -13863.7347
[13 empty] | P2 at this iteration flow rate |  |  | 27.827 |  |  | 29.4322 |  |  | 52.1719 |  |  | 124.9683 |  |  | 295.9807 |  |  | 626.1046 |  |  | 1095.7756 |  |  | 1619.4068 |  |  | 2174.1388 |  |  | 2808.7869
[13 empty] | Delta P at this iteration flow rate |  |  | 13.2381 |  |  | 3.6069 |  |  | -132.8316 |  |  | -569.6096 |  |  | -1595.6841 |  |  | -3576.4277 |  |  | -6394.4536 |  |  | -9536.2405 |  |  | -12864.6328 |  |  | -16672.5217
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 33.6396 |  |  | 26.9864 |  |  | -65.6221 |  |  | -343.9577 |  |  | -937.6471 |  |  | -1900.4212 |  |  | -3064.8209 |  |  | -3788.195 |  |  | -4218.9294 |  |  | -5214.8817
[13 empty] | C Non choked w/ reducers | 7 |  | 188.3213 |  |  | 443.1042 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 118.1371 |  |  | 161.9954 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 188.3213 |  |  | 443.1042 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 183.3213 | 685.0915 |  | 431.1042 | 840.8323 |  | 5500 | 2018.3211 |  | 5500 | 3853.7146 |  | 5500 | 6337.9417 |  | 5500 | 9436.3316 |  | 5500 | 12592.8211 |  | 5500 | 15365.6349 |  | 5500 | 17839.025 |  | 5500 | 20302.4745
[13 empty] | Next iteration flow rate |  |  | 698.7933 | Abs Value of | Flow this | 849.2406 | Abs Value of | Flow this | 2038.5043 | Abs Value of | Flow this | 3892.2518 | Abs Value of | Flow this | 6401.3211 | Abs Value of | Flow this | 9530.6949 | Abs Value of | Flow this | 12718.7493 | Abs Value of | Flow this | 15519.2912 | Abs Value of | Flow this | 18017.4153 | Abs Value of | Flow this | 20505.4993 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 40.4247 |  |  | 32.5592 |  |  | -83.4249 |  |  | -454.7226 |  |  | -1326.9715 |  |  | -3010.7686 |  |  | -5406.3254 |  |  | -8077.1061 |  |  | -10906.517 |  |  | -14143.5398
[13 empty] | P2 at this iteration flow rate |  |  | 27.9551 |  |  | 29.5282 |  |  | 52.725 |  |  | 126.9845 |  |  | 301.4343 |  |  | 638.1937 |  |  | 1117.3051 |  |  | 1651.4612 |  |  | 2217.3434 |  |  | 2864.748
[13 empty] | Delta P at this iteration flow rate |  |  | 12.4696 |  |  | 3.031 |  |  | -136.1499 |  |  | -581.7072 |  |  | -1628.4058 |  |  | -3648.9623 |  |  | -6523.6305 |  |  | -9728.5674 |  |  | -13123.8603 |  |  | -17008.2878
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 33.1094 |  |  | 26.5891 |  |  | -67.8597 |  |  | -351.7485 |  |  | -957.3125 |  |  | -1939.3507 |  |  | -3127.0803 |  |  | -3864.8809 |  |  | -4304.1778 |  |  | -5320.1278
[13 empty] | C Non choked w/ reducers | 7 |  | 197.9181 |  |  | 488.2047 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 121.461 |  |  | 164.8332 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 197.9181 |  |  | 488.2047 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 192.9181 | 698.7933 |  | 476.2047 | 849.2406 |  | 5500 | 2038.5043 |  | 5500 | 3892.2518 |  | 5500 | 6401.3211 |  | 5500 | 9530.6949 |  | 5500 | 12718.7493 |  | 5500 | 15519.2912 |  | 5500 | 18017.4153 |  | 5500 | 20505.4993
[13 empty] | Next iteration flow rate |  |  | 712.7692 | Abs Value of | Flow this | 857.733 | Abs Value of | Flow this | 2058.8893 | Abs Value of | Flow this | 3931.1743 | Abs Value of | Flow this | 6465.3344 | Abs Value of | Flow this | 9626.0018 | Abs Value of | Flow this | 12845.9368 | Abs Value of | Flow this | 15674.4841 | Abs Value of | Flow this | 18197.5895 | Abs Value of | Flow this | 20710.5543 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 39.7584 |  |  | 32.0696 |  |  | -86.2458 |  |  | -465.0066 |  |  | -1354.7876 |  |  | -3072.4291 |  |  | -5516.1366 |  |  | -8240.6 |  |  | -11126.882 |  |  | -14428.969
[13 empty] | P2 at this iteration flow rate |  |  | 28.0883 |  |  | 29.6261 |  |  | 53.2892 |  |  | 129.0413 |  |  | 306.9975 |  |  | 650.5258 |  |  | 1139.2673 |  |  | 1684.16 |  |  | 2261.4164 |  |  | 2921.8338
[13 empty] | Delta P at this iteration flow rate |  |  | 11.6701 |  |  | 2.4435 |  |  | -139.535 |  |  | -594.0479 |  |  | -1661.7851 |  |  | -3722.9549 |  |  | -6655.4039 |  |  | -9924.76 |  |  | -13388.2984 |  |  | -17350.8028
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 32.5577 |  |  | 26.1838 |  |  | -70.1422 |  |  | -359.6959 |  |  | -977.3731 |  |  | -1979.0628 |  |  | -3190.5912 |  |  | -3943.1081 |  |  | -4391.1398 |  |  | -5427.4894
[13 empty] | C Non choked w/ reducers | 7 |  | 208.6771 |  |  | 549.1726 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 124.9355 |  |  | 167.7651 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 208.6771 |  |  | 549.1726 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 203.6771 | 712.7692 |  | 537.1726 | 857.733 |  | 5500 | 2058.8893 |  | 5500 | 3931.1743 |  | 5500 | 6465.3344 |  | 5500 | 9626.0018 |  | 5500 | 12845.9368 |  | 5500 | 15674.4841 |  | 5500 | 18197.5895 |  | 5500 | 20710.5543
[13 empty] | Next iteration flow rate |  |  | 727.0245 | Abs Value of | Flow this | 866.3103 | Abs Value of | Flow this | 2079.4782 | Abs Value of | Flow this | 3970.486 | Abs Value of | Flow this | 6529.9877 | Abs Value of | Flow this | 9722.2619 | Abs Value of | Flow this | 12974.3962 | Abs Value of | Flow this | 15831.229 | Abs Value of | Flow this | 18379.5653 | Abs Value of | Flow this | 20917.6598 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 39.0653 |  |  | 31.5702 |  |  | -89.1234 |  |  | -475.4972 |  |  | -1383.1629 |  |  | -3135.3289 |  |  | -5628.155 |  |  | -8407.3801 |  |  | -11351.6763 |  |  | -14720.1353
[13 empty] | P2 at this iteration flow rate |  |  | 28.2269 |  |  | 29.726 |  |  | 53.8647 |  |  | 131.1394 |  |  | 312.6726 |  |  | 663.1058 |  |  | 1161.671 |  |  | 1717.516 |  |  | 2306.3753 |  |  | 2980.0671
[13 empty] | Delta P at this iteration flow rate |  |  | 10.8383 |  |  | 1.8442 |  |  | -142.988 |  |  | -606.6367 |  |  | -1695.8354 |  |  | -3798.4347 |  |  | -6789.826 |  |  | -10124.8961 |  |  | -13658.0516 |  |  | -17700.2023
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 31.9837 |  |  | 25.7704 |  |  | -72.4706 |  |  | -367.803 |  |  | -997.837 |  |  | -2019.573 |  |  | -3255.3786 |  |  | -4022.9078 |  |  | -4479.8497 |  |  | -5537.0089
[13 empty] | C Non choked w/ reducers | 7 |  | 220.8675 |  |  | 638.4565 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 128.5726 |  |  | 170.7965 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 220.8675 |  |  | 638.4565 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 215.8675 | 727.0245 |  | 626.4565 | 866.3103 |  | 5500 | 2079.4782 |  | 5500 | 3970.486 |  | 5500 | 6529.9877 |  | 5500 | 9722.2619 |  | 5500 | 12974.3962 |  | 5500 | 15831.229 |  | 5500 | 18379.5653 |  | 5500 | 20917.6598
[13 empty] | Next iteration flow rate |  |  | 741.565 | Abs Value of | Flow this | 874.9734 | Abs Value of | Flow this | 2100.273 | Abs Value of | Flow this | 4010.1909 | Abs Value of | Flow this | 6595.2876 | Abs Value of | Flow this | 9819.4845 | Abs Value of | Flow this | 13104.1401 | Abs Value of | Flow this | 15989.5412 | Abs Value of | Flow this | 18563.361 | Abs Value of | Flow this | 21126.8364 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 38.3441 |  |  | 31.0607 |  |  | -92.0588 |  |  | -486.1987 |  |  | -1412.1085 |  |  | -3199.493 |  |  | -5742.4249 |  |  | -8577.5124 |  |  | -11580.989 |  |  | -15017.154
[13 empty] | P2 at this iteration flow rate |  |  | 28.3712 |  |  | 29.8279 |  |  | 54.4518 |  |  | 133.2797 |  |  | 318.4617 |  |  | 675.9386 |  |  | 1184.525 |  |  | 1751.5425 |  |  | 2352.2378 |  |  | 3039.4708
[13 empty] | Delta P at this iteration flow rate |  |  | 9.9729 |  |  | 1.2329 |  |  | -146.5105 |  |  | -619.4785 |  |  | -1730.5701 |  |  | -3875.4316 |  |  | -6926.9499 |  |  | -10329.0549 |  |  | -13933.2268 |  |  | -18056.6248
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 31.3865 |  |  | 25.3486 |  |  | -74.8457 |  |  | -376.0731 |  |  | -1018.7122 |  |  | -2060.8975 |  |  | -3321.4683 |  |  | -4104.3114 |  |  | -4570.3426 |  |  | -5648.7298
[13 empty] | C Non choked w/ reducers | 7 |  | 234.8562 |  |  | 788.6761 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 132.3857 |  |  | 173.9335 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 234.8562 |  |  | 788.6761 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 229.8562 | 741.565 |  | 776.6761 | 874.9734 |  | 5500 | 2100.273 |  | 5500 | 4010.1909 |  | 5500 | 6595.2876 |  | 5500 | 9819.4845 |  | 5500 | 13104.1401 |  | 5500 | 15989.5412 |  | 5500 | 18563.361 |  | 5500 | 21126.8364
[13 empty] | Next iteration flow rate |  |  | 756.3963 | Abs Value of | Flow this | 883.7232 | Abs Value of | Flow this | 2121.2757 | Abs Value of | Flow this | 4050.2928 | Abs Value of | Flow this | 6661.2405 | Abs Value of | Flow this | 9917.6793 | Abs Value of | Flow this | 13235.1815 | Abs Value of | Flow this | 16149.4367 | Abs Value of | Flow this | 18748.9946 | Abs Value of | Flow this | 21338.1048 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 37.5938 |  |  | 30.541 |  |  | -95.0532 |  |  | -497.1153 |  |  | -1441.6358 |  |  | -3264.9469 |  |  | -5858.9916 |  |  | -8751.0644 |  |  | -11814.9109 |  |  | -15320.1428
[13 empty] | P2 at this iteration flow rate |  |  | 28.5212 |  |  | 29.9318 |  |  | 55.0506 |  |  | 135.4631 |  |  | 324.3672 |  |  | 689.0294 |  |  | 1207.8383 |  |  | 1786.2529 |  |  | 2399.0222 |  |  | 3100.0686
[13 empty] | Delta P at this iteration flow rate |  |  | 9.0725 |  |  | 0.60926 |  |  | -150.1038 |  |  | -632.5784 |  |  | -1766.003 |  |  | -3953.9762 |  |  | -7066.83 |  |  | -10537.3173 |  |  | -14213.9331 |  |  | -18420.2114
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 30.7652 |  |  | 24.9184 |  |  | -77.2687 |  |  | -384.5094 |  |  | -1040.007 |  |  | -2103.0527 |  |  | -3388.8863 |  |  | -4187.3512 |  |  | -4662.6545 |  |  | -5762.6962
[13 empty] | C Non choked w/ reducers | 7 |  | 251.159 |  |  | 1133.1359 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 136.3901 |  |  | 177.1829 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 251.159 |  |  | 1133.1359 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 246.159 | 756.3963 |  | 1121.1359 | 883.7232 |  | 5500 | 2121.2757 |  | 5500 | 4050.2928 |  | 5500 | 6661.2405 |  | 5500 | 9917.6793 |  | 5500 | 13235.1815 |  | 5500 | 16149.4367 |  | 5500 | 18748.9946 |  | 5500 | 21338.1048
[13 empty] | Next iteration flow rate |  |  | 771.5243 | Abs Value of | Flow this | 892.5604 | Abs Value of | Flow this | 2142.4885 | Abs Value of | Flow this | 4090.7957 | Abs Value of | Flow this | 6727.8529 | Abs Value of | Flow this | 10016.8561 | Abs Value of | Flow this | 13367.5333 | Abs Value of | Flow this | 16310.931 | Abs Value of | Flow this | 18936.4846 | Abs Value of | Flow this | 21551.4858 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 36.8131 |  |  | 30.0109 |  |  | -98.1077 |  |  | -508.2514 |  |  | -1471.7567 |  |  | -3331.7163 |  |  | -5977.9014 |  |  | -8928.1048 |  |  | -12053.5346 |  |  | -15629.2217
[13 empty] | P2 at this iteration flow rate |  |  | 28.6774 |  |  | 30.0378 |  |  | 55.6615 |  |  | 137.6903 |  |  | 330.3913 |  |  | 702.3833 |  |  | 1231.6203 |  |  | 1821.661 |  |  | 2446.7469 |  |  | 3161.8843
[13 empty] | Delta P at this iteration flow rate |  |  | 8.1358 |  |  | -0.026911 |  |  | -153.7693 |  |  | -645.9416 |  |  | -1802.1481 |  |  | -4034.0996 |  |  | -7209.5217 |  |  | -10749.7658 |  |  | -14500.2816 |  |  | -18791.106
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 30.1188 |  |  | 24.4795 |  |  | -79.7403 |  |  | -393.1153 |  |  | -1061.7298 |  |  | -2146.0551 |  |  | -3457.6595 |  |  | -4272.0601 |  |  | -4756.8218 |  |  | -5878.9534
[13 empty] | C Non choked w/ reducers | 7 |  | 270.5288 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 140.6028 |  |  | 180.5517 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 270.5288 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 265.5288 | 771.5243 |  | 5500 | 892.5604 |  | 5500 | 2142.4885 |  | 5500 | 4090.7957 |  | 5500 | 6727.8529 |  | 5500 | 10016.8561 |  | 5500 | 13367.5333 |  | 5500 | 16310.931 |  | 5500 | 18936.4846 |  | 5500 | 21551.4858
[13 empty] | Next iteration flow rate |  |  | 786.9547 | Abs Value of | Flow this | 901.486 | Abs Value of | Flow this | 2163.9134 | Abs Value of | Flow this | 4131.7037 | Abs Value of | Flow this | 6795.1314 | Abs Value of | Flow this | 10117.0247 | Abs Value of | Flow this | 13501.2087 | Abs Value of | Flow this | 16474.0403 | Abs Value of | Flow this | 19125.8494 | Abs Value of | Flow this | 21767.0007 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 36.001 |  |  | 29.4701 |  |  | -101.2237 |  |  | -519.6112 |  |  | -1502.4831 |  |  | -3399.8278 |  |  | -6099.2012 |  |  | -9108.7037 |  |  | -12296.9547 |  |  | -15944.5131
[13 empty] | P2 at this iteration flow rate |  |  | 28.8398 |  |  | 30.146 |  |  | 56.2847 |  |  | 139.9622 |  |  | 336.5366 |  |  | 716.0056 |  |  | 1255.8802 |  |  | 1857.7807 |  |  | 2495.4309 |  |  | 3224.9426
[13 empty] | Delta P at this iteration flow rate |  |  | 7.1612 |  |  | -0.67587 |  |  | -157.5085 |  |  | -659.5735 |  |  | -1839.0197 |  |  | -4115.8334 |  |  | -7355.0815 |  |  | -10966.4845 |  |  | -14792.3856 |  |  | -19169.4557
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 29.4463 |  |  | 24.0319 |  |  | -82.2616 |  |  | -401.8942 |  |  | -1083.8892 |  |  | -2189.922 |  |  | -3527.815 |  |  | -4358.4716 |  |  | -4852.8819 |  |  | -5997.5473
[13 empty] | C Non choked w/ reducers | 7 |  | 294.1175 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 145.0433 |  |  | 184.048 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 294.1175 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 289.1175 | 786.9547 |  | 5500 | 901.486 |  | 5500 | 2163.9134 |  | 5500 | 4131.7037 |  | 5500 | 6795.1314 |  | 5500 | 10117.0247 |  | 5500 | 13501.2087 |  | 5500 | 16474.0403 |  | 5500 | 19125.8494 |  | 5500 | 21767.0007
[13 empty] | Next iteration flow rate |  |  | 802.6938 | Abs Value of | Flow this | 910.5008 | Abs Value of | Flow this | 2185.5525 | Abs Value of | Flow this | 4173.0207 | Abs Value of | Flow this | 6863.0827 | Abs Value of | Flow this | 10218.1949 | Abs Value of | Flow this | 13636.2207 | Abs Value of | Flow this | 16638.7807 | Abs Value of | Flow this | 19317.1079 | Abs Value of | Flow this | 21984.6707 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 35.156 |  |  | 28.9184 |  |  | -104.4023 |  |  | -531.1994 |  |  | -1533.827 |  |  | -3469.3084 |  |  | -6222.9392 |  |  | -9292.9327 |  |  | -12545.2675 |  |  | -16266.1418
[13 empty] | P2 at this iteration flow rate |  |  | 29.0088 |  |  | 30.2563 |  |  | 56.9205 |  |  | 142.2799 |  |  | 342.8054 |  |  | 729.9017 |  |  | 1280.6278 |  |  | 1894.6265 |  |  | 2545.0935 |  |  | 3289.2684
[13 empty] | Delta P at this iteration flow rate |  |  | 6.1472 |  |  | -1.3379 |  |  | -161.3228 |  |  | -673.4793 |  |  | -1876.6324 |  |  | -4199.21 |  |  | -7503.567 |  |  | -11187.5593 |  |  | -15090.361 |  |  | -19555.4102
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 28.7466 |  |  | 23.5752 |  |  | -84.8336 |  |  | -410.8495 |  |  | -1106.4941 |  |  | -2234.6705 |  |  | -3599.3806 |  |  | -4446.62 |  |  | -4950.8728 |  |  | -6118.525
[13 empty] | C Non choked w/ reducers | 7 |  | 323.798 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 149.7338 |  |  | 187.6803 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 323.798 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 318.798 | 802.6938 |  | 5500 | 910.5008 |  | 5500 | 2185.5525 |  | 5500 | 4173.0207 |  | 5500 | 6863.0827 |  | 5500 | 10218.1949 |  | 5500 | 13636.2207 |  | 5500 | 16638.7807 |  | 5500 | 19317.1079 |  | 5500 | 21984.6707
[13 empty] | Next iteration flow rate |  |  | 818.7477 | Abs Value of | Flow this | 919.6059 | Abs Value of | Flow this | 2207.408 | Abs Value of | Flow this | 4214.7509 | Abs Value of | Flow this | 6931.7135 | Abs Value of | Flow this | 10320.3769 | Abs Value of | Flow this | 13772.583 | Abs Value of | Flow this | 16805.1685 | Abs Value of | Flow this | 19510.279 | Abs Value of | Flow this | 22204.5174 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 34.2769 |  |  | 28.3557 |  |  | -107.6448 |  |  | -543.0206 |  |  | -1565.8009 |  |  | -3540.1855 |  |  | -6349.1643 |  |  | -9480.8647 |  |  | -12798.5714 |  |  | -16594.2353
[13 empty] | P2 at this iteration flow rate |  |  | 29.1846 |  |  | 30.3689 |  |  | 57.569 |  |  | 144.6441 |  |  | 349.2002 |  |  | 744.0771 |  |  | 1305.8729 |  |  | 1932.2129 |  |  | 2595.7543 |  |  | 3354.8871
[13 empty] | Delta P at this iteration flow rate |  |  | 5.0923 |  |  | -2.0132 |  |  | -165.2138 |  |  | -687.6647 |  |  | -1915.0011 |  |  | -4284.2626 |  |  | -7655.0371 |  |  | -11413.0776 |  |  | -15394.3257 |  |  | -19949.1223
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 28.0187 |  |  | 23.1093 |  |  | -87.4573 |  |  | -419.9848 |  |  | -1129.5533 |  |  | -2280.3185 |  |  | -3672.3847 |  |  | -4536.5403 |  |  | -5050.8333 |  |  | -6241.9344
[13 empty] | C Non choked w/ reducers | 7 |  | 362.8751 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 154.6998 |  |  | 191.4582 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 362.8751 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 357.8751 | 818.7477 |  | 5500 | 919.6059 |  | 5500 | 2207.408 |  | 5500 | 4214.7509 |  | 5500 | 6931.7135 |  | 5500 | 10320.3769 |  | 5500 | 13772.583 |  | 5500 | 16805.1685 |  | 5500 | 19510.279 |  | 5500 | 22204.5174
[13 empty] | Next iteration flow rate |  |  | 835.1227 | Abs Value of | Flow this | 928.8019 | Abs Value of | Flow this | 2229.4821 | Abs Value of | Flow this | 4256.8985 | Abs Value of | Flow this | 7001.0307 | Abs Value of | Flow this | 10423.5807 | Abs Value of | Flow this | 13910.3088 | Abs Value of | Flow this | 16973.2202 | Abs Value of | Flow this | 19705.3818 | Abs Value of | Flow this | 22426.5626 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 33.3623 |  |  | 27.7816 |  |  | -110.9525 |  |  | -555.0793 |  |  | -1598.4175 |  |  | -3612.4872 |  |  | -6477.9265 |  |  | -9672.5741 |  |  | -13056.9667 |  |  | -16928.9234
[13 empty] | P2 at this iteration flow rate |  |  | 29.3675 |  |  | 30.4837 |  |  | 58.2305 |  |  | 147.0559 |  |  | 355.7235 |  |  | 758.5374 |  |  | 1331.6253 |  |  | 1970.5548 |  |  | 2647.4333 |  |  | 3421.8247
[13 empty] | Delta P at this iteration flow rate |  |  | 3.9947 |  |  | -2.702 |  |  | -169.183 |  |  | -702.1351 |  |  | -1954.141 |  |  | -4371.0247 |  |  | -7809.5518 |  |  | -11643.1289 |  |  | -15704.4 |  |  | -20350.7481
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 27.2613 |  |  | 22.6341 |  |  | -90.1337 |  |  | -429.3038 |  |  | -1153.076 |  |  | -2326.884 |  |  | -3746.8562 |  |  | -4628.2679 |  |  | -5152.803 |  |  | -6367.8242
[13 empty] | C Non choked w/ reducers | 7 |  | 417.8975 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 159.9706 |  |  | 195.3922 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 417.8975 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 412.8975 | 835.1227 |  | 5500 | 928.8019 |  | 5500 | 2229.4821 |  | 5500 | 4256.8985 |  | 5500 | 7001.0307 |  | 5500 | 10423.5807 |  | 5500 | 13910.3088 |  | 5500 | 16973.2202 |  | 5500 | 19705.3818 |  | 5500 | 22426.5626
[13 empty] | Next iteration flow rate |  |  | 851.8251 | Abs Value of | Flow this | 938.0899 | Abs Value of | Flow this | 2251.7769 | Abs Value of | Flow this | 4299.4674 | Abs Value of | Flow this | 7071.041 | Abs Value of | Flow this | 10527.8165 | Abs Value of | Flow this | 14049.4119 | Abs Value of | Flow this | 17142.9524 | Abs Value of | Flow this | 19902.4356 | Abs Value of | Flow this | 22650.8282 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 32.4107 |  |  | 27.196 |  |  | -114.3267 |  |  | -567.3804 |  |  | -1631.6897 |  |  | -3686.2422 |  |  | -6609.2768 |  |  | -9868.1368 |  |  | -13320.5557 |  |  | -17270.3388
[13 empty] | P2 at this iteration flow rate |  |  | 29.5579 |  |  | 30.6008 |  |  | 58.9053 |  |  | 149.5161 |  |  | 362.3779 |  |  | 773.2884 |  |  | 1357.8954 |  |  | 2009.6674 |  |  | 2700.1511 |  |  | 3490.1078
[13 empty] | Delta P at this iteration flow rate |  |  | 2.8528 |  |  | -3.4048 |  |  | -173.232 |  |  | -716.8965 |  |  | -1994.0677 |  |  | -4459.5307 |  |  | -7967.1722 |  |  | -11877.8042 |  |  | -16020.7069 |  |  | -20760.4465
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 26.4734 |  |  | 22.1493 |  |  | -92.8639 |  |  | -438.8101 |  |  | -1177.0715 |  |  | -2374.3854 |  |  | -3822.8245 |  |  | -4721.8392 |  |  | -5256.8223 |  |  | -6496.2445
[13 empty] | C Non choked w/ reducers | 7 |  | 504.3998 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 165.5806 |  |  | 199.4941 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 504.3998 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 499.3998 | 851.8251 |  | 5500 | 938.0899 |  | 5500 | 2251.7769 |  | 5500 | 4299.4674 |  | 5500 | 7071.041 |  | 5500 | 10527.8165 |  | 5500 | 14049.4119 |  | 5500 | 17142.9524 |  | 5500 | 19902.4356 |  | 5500 | 22650.8282
[13 empty] | Next iteration flow rate |  |  | 868.8616 | Abs Value of | Flow this | 947.4708 | Abs Value of | Flow this | 2274.2947 | Abs Value of | Flow this | 4342.4621 | Abs Value of | Flow this | 7141.7514 | Abs Value of | Flow this | 10633.0946 | Abs Value of | Flow this | 14189.906 | Abs Value of | Flow this | 17314.382 | Abs Value of | Flow this | 20101.4599 | Abs Value of | Flow this | 22877.3365 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 31.4207 |  |  | 26.5986 |  |  | -117.7686 |  |  | -579.9287 |  |  | -1665.6307 |  |  | -3761.4797 |  |  | -6743.2673 |  |  | -10067.6304 |  |  | -13589.4429 |  |  | -17618.6166
[13 empty] | P2 at this iteration flow rate |  |  | 29.7559 |  |  | 30.7203 |  |  | 59.5937 |  |  | 152.0257 |  |  | 369.1661 |  |  | 788.3359 |  |  | 1384.6935 |  |  | 2049.5661 |  |  | 2753.9286 |  |  | 3559.7633
[13 empty] | Delta P at this iteration flow rate |  |  | 1.6648 |  |  | -4.1216 |  |  | -177.3624 |  |  | -731.9545 |  |  | -2034.7969 |  |  | -4549.8157 |  |  | -8127.9608 |  |  | -12117.1965 |  |  | -16343.3715 |  |  | -21178.3799
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 25.6536 |  |  | 21.6548 |  |  | -95.649 |  |  | -448.5074 |  |  | -1201.5493 |  |  | -2422.8417 |  |  | -3900.3198 |  |  | -4817.2913 |  |  | -5362.9324 |  |  | -6627.246
[13 empty] | C Non choked w/ reducers | 7 |  | 673.4887 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 171.5695 |  |  | 203.7767 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 673.4887 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 668.4887 | 868.8616 |  | 5500 | 947.4708 |  | 5500 | 2274.2947 |  | 5500 | 4342.4621 |  | 5500 | 7141.7514 |  | 5500 | 10633.0946 |  | 5500 | 14189.906 |  | 5500 | 17314.382 |  | 5500 | 20101.4599 |  | 5500 | 22877.3365
[13 empty] | Next iteration flow rate |  |  | 886.2389 | Abs Value of | Flow this | 956.9455 | Abs Value of | Flow this | 2297.0377 | Abs Value of | Flow this | 4385.8867 | Abs Value of | Flow this | 7213.1689 | Abs Value of | Flow this | 10739.4256 | Abs Value of | Flow this | 14331.8051 | Abs Value of | Flow this | 17487.5258 | Abs Value of | Flow this | 20302.4745 | Abs Value of | Flow this | 23106.1098 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 30.3907 |  |  | 25.9893 |  |  | -121.2798 |  |  | -592.7293 |  |  | -1700.2539 |  |  | -3838.2295 |  |  | -6879.951 |  |  | -10271.1338 |  |  | -13863.7347 |  |  | -17973.8948
[13 empty] | P2 at this iteration flow rate |  |  | 29.9619 |  |  | 30.8421 |  |  | 60.296 |  |  | 154.5859 |  |  | 376.0908 |  |  | 803.6859 |  |  | 1412.0302 |  |  | 2090.2668 |  |  | 2808.7869 |  |  | 3630.819
[13 empty] | Delta P at this iteration flow rate |  |  | 0.4288 |  |  | -4.8529 |  |  | -181.5758 |  |  | -747.3152 |  |  | -2076.3447 |  |  | -4641.9154 |  |  | -8291.9812 |  |  | -12361.4005 |  |  | -16672.5217 |  |  | -21604.7138
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 24.8007 |  |  | 21.1503 |  |  | -98.4901 |  |  | -458.3997 |  |  | -1226.5191 |  |  | -2472.2719 |  |  | -3979.3728 |  |  | -4914.662 |  |  | -5471.1753 |  |  | -6760.8806
[13 empty] | C Non choked w/ reducers | 7 |  | 1353.587 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 177.9846 |  |  | 208.2545 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | 1353.587 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 1348.587 | 886.2389 |  | 5500 | 956.9455 |  | 5500 | 2297.0377 |  | 5500 | 4385.8867 |  | 5500 | 7213.1689 |  | 5500 | 10739.4256 |  | 5500 | 14331.8051 |  | 5500 | 17487.5258 |  | 5500 | 20302.4745 |  | 5500 | 23106.1098
[13 empty] | Next iteration flow rate |  |  | 903.9636 | Abs Value of | Flow this | 966.515 | Abs Value of | Flow this | 2320.008 | Abs Value of | Flow this | 4429.7456 | Abs Value of | Flow this | 7285.3006 | Abs Value of | Flow this | 10846.8198 | Abs Value of | Flow this | 14475.1231 | Abs Value of | Flow this | 17662.401 | Abs Value of | Flow this | 20505.4993 | Abs Value of | Flow this | 23337.1709 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 29.319 |  |  | 25.3676 |  |  | -124.8615 |  |  | -605.7872 |  |  | -1735.573 |  |  | -3916.5219 |  |  | -7019.382 |  |  | -10478.7276 |  |  | -14143.5398 |  |  | -18336.3141
[13 empty] | P2 at this iteration flow rate |  |  | 30.1762 |  |  | 30.9665 |  |  | 61.0123 |  |  | 157.1974 |  |  | 383.1546 |  |  | 819.3444 |  |  | 1439.9164 |  |  | 2131.7855 |  |  | 2864.748 |  |  | 3703.3028
[13 empty] | Delta P at this iteration flow rate |  |  | -0.85715 |  |  | -5.5988 |  |  | -185.8739 |  |  | -762.9846 |  |  | -2118.7276 |  |  | -4735.8663 |  |  | -8459.2984 |  |  | -12610.5131 |  |  | -17008.2878 |  |  | -22039.6169
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 23.9133 |  |  | 20.6357 |  |  | -101.3882 |  |  | -468.4907 |  |  | -1251.9908 |  |  | -2522.6957 |  |  | -4060.0147 |  |  | -5013.9899 |  |  | -5581.5939 |  |  | -6897.2013
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 184.882 |  |  | 212.9435 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 903.9636 |  | 5500 | 966.515 |  | 5500 | 2320.008 |  | 5500 | 4429.7456 |  | 5500 | 7285.3006 |  | 5500 | 10846.8198 |  | 5500 | 14475.1231 |  | 5500 | 17662.401 |  | 5500 | 20505.4993 |  | 5500 | 23337.1709
[13 empty] | Next iteration flow rate |  |  | 922.0429 | Abs Value of | Flow this | 976.1801 | Abs Value of | Flow this | 2343.2081 | Abs Value of | Flow this | 4474.0431 | Abs Value of | Flow this | 7358.1536 | Abs Value of | Flow this | 10955.288 | Abs Value of | Flow this | 14619.8743 | Abs Value of | Flow this | 17839.025 | Abs Value of | Flow this | 20710.5543 | Abs Value of | Flow this | 23570.5427 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 28.2041 |  |  | 24.7335 |  |  | -128.5153 |  |  | -619.1075 |  |  | -1771.6021 |  |  | -3996.388 |  |  | -7161.6156 |  |  | -10690.494 |  |  | -14428.969 |  |  | -18706.018
[13 empty] | P2 at this iteration flow rate |  |  | 30.3992 |  |  | 31.0933 |  |  | 61.7431 |  |  | 159.8615 |  |  | 390.3604 |  |  | 835.3176 |  |  | 1468.3631 |  |  | 2174.1388 |  |  | 2921.8338 |  |  | 3777.2436
[13 empty] | Delta P at this iteration flow rate |  |  | -2.1951 |  |  | -6.3598 |  |  | -190.2583 |  |  | -778.969 |  |  | -2161.9625 |  |  | -4831.7056 |  |  | -8629.9787 |  |  | -12864.6328 |  |  | -17350.8028 |  |  | -22483.2616
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 22.9901 |  |  | 20.1108 |  |  | -104.3447 |  |  | -478.7847 |  |  | -1277.9745 |  |  | -2574.1329 |  |  | -4142.2776 |  |  | -5115.3142 |  |  | -5694.2319 |  |  | -7036.262
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 192.3288 |  |  | 217.8619 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 922.0429 |  | 5500 | 976.1801 |  | 5500 | 2343.2081 |  | 5500 | 4474.0431 |  | 5500 | 7358.1536 |  | 5500 | 10955.288 |  | 5500 | 14619.8743 |  | 5500 | 17839.025 |  | 5500 | 20710.5543 |  | 5500 | 23570.5427
[13 empty] | Next iteration flow rate |  |  | 940.4838 | Abs Value of | Flow this | 985.9419 | Abs Value of | Flow this | 2366.6402 | Abs Value of | Flow this | 4518.7835 | Abs Value of | Flow this | 7431.7351 | Abs Value of | Flow this | 11064.8409 | Abs Value of | Flow this | 14766.0731 | Abs Value of | Flow this | 18017.4153 | Abs Value of | Flow this | 20917.6598 | Abs Value of | Flow this | 23806.2481 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 27.0441 |  |  | 24.0866 |  |  | -132.2424 |  |  | -632.6956 |  |  | -1808.3553 |  |  | -4077.8594 |  |  | -7306.7081 |  |  | -10906.517 |  |  | -14720.1353 |  |  | -19083.153
[13 empty] | P2 at this iteration flow rate |  |  | 30.6312 |  |  | 31.2227 |  |  | 62.4885 |  |  | 162.5791 |  |  | 397.7111 |  |  | 851.6119 |  |  | 1497.3816 |  |  | 2217.3434 |  |  | 2980.0671 |  |  | 3852.6706
[13 empty] | Delta P at this iteration flow rate |  |  | -3.587 |  |  | -7.136 |  |  | -194.7309 |  |  | -795.2747 |  |  | -2206.0663 |  |  | -4929.4713 |  |  | -8804.0897 |  |  | -13123.8603 |  |  | -17700.2023 |  |  | -22935.8236
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 22.0296 |  |  | 19.5753 |  |  | -107.3605 |  |  | -489.2855 |  |  | -1304.4804 |  |  | -2626.6041 |  |  | -4226.1939 |  |  | -5218.6752 |  |  | -5809.1339 |  |  | -7178.1179
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 200.4064 |  |  | 223.0299 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 940.4838 |  | 5500 | 985.9419 |  | 5500 | 2366.6402 |  | 5500 | 4518.7835 |  | 5500 | 7431.7351 |  | 5500 | 11064.8409 |  | 5500 | 14766.0731 |  | 5500 | 18017.4153 |  | 5500 | 20917.6598 |  | 5500 | 23806.2481
[13 empty] | Next iteration flow rate |  |  | 959.2934 | Abs Value of | Flow this | 995.8014 | Abs Value of | Flow this | 2390.3066 | Abs Value of | Flow this | 4563.9713 | Abs Value of | Flow this | 7506.0525 | Abs Value of | Flow this | 11175.4893 | Abs Value of | Flow this | 14913.7338 | Abs Value of | Flow this | 18197.5895 | Abs Value of | Flow this | 21126.8364 | Abs Value of | Flow this | 24044.3106 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 25.8373 |  |  | 23.4268 |  |  | -136.0445 |  |  | -646.5568 |  |  | -1845.8472 |  |  | -4160.9684 |  |  | -7454.717 |  |  | -11126.882 |  |  | -15017.154 |  |  | -19467.8684
[13 empty] | P2 at this iteration flow rate |  |  | 30.8725 |  |  | 31.3546 |  |  | 63.2489 |  |  | 165.3514 |  |  | 405.2094 |  |  | 868.2337 |  |  | 1526.9834 |  |  | 2261.4164 |  |  | 3039.4708 |  |  | 3929.6137
[13 empty] | Delta P at this iteration flow rate |  |  | -5.0352 |  |  | -7.9279 |  |  | -199.2934 |  |  | -811.9082 |  |  | -2251.0567 |  |  | -5029.2021 |  |  | -8981.7003 |  |  | -13388.2984 |  |  | -18056.6248 |  |  | -23397.4821
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 21.0303 |  |  | 19.029 |  |  | -110.437 |  |  | -499.9974 |  |  | -1331.5191 |  |  | -2680.1299 |  |  | -4311.7969 |  |  | -5324.1137 |  |  | -5926.3455 |  |  | -7322.825
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 209.2149 |  |  | 228.4705 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 959.2934 |  | 5500 | 995.8014 |  | 5500 | 2390.3066 |  | 5500 | 4563.9713 |  | 5500 | 7506.0525 |  | 5500 | 11175.4893 |  | 5500 | 14913.7338 |  | 5500 | 18197.5895 |  | 5500 | 21126.8364 |  | 5500 | 24044.3106
[13 empty] | Next iteration flow rate |  |  | 978.4793 | Abs Value of | Flow this | 1005.7594 | Abs Value of | Flow this | 2414.2097 | Abs Value of | Flow this | 4609.611 | Abs Value of | Flow this | 7581.113 | Abs Value of | Flow this | 11287.2442 | Abs Value of | Flow this | 15062.8711 | Abs Value of | Flow this | 18379.5653 | Abs Value of | Flow this | 21338.1048 | Abs Value of | Flow this | 24284.7537 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 24.5817 |  |  | 22.7536 |  |  | -139.923 |  |  | -660.6966 |  |  | -1884.0928 |  |  | -4245.7479 |  |  | -7605.7008 |  |  | -11351.6763 |  |  | -15320.1428 |  |  | -19860.3166
[13 empty] | P2 at this iteration flow rate |  |  | 31.1237 |  |  | 31.4893 |  |  | 64.0246 |  |  | 168.1793 |  |  | 412.8586 |  |  | 885.1896 |  |  | 1557.1802 |  |  | 2306.3753 |  |  | 3100.0686 |  |  | 4008.1033
[13 empty] | Delta P at this iteration flow rate |  |  | -6.5419 |  |  | -8.7356 |  |  | -203.9477 |  |  | -828.8759 |  |  | -2296.9513 |  |  | -5130.9375 |  |  | -9162.8809 |  |  | -13658.0516 |  |  | -18420.2114 |  |  | -23868.4199
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 19.9906 |  |  | 18.4718 |  |  | -113.5753 |  |  | -510.9246 |  |  | -1359.1014 |  |  | -2734.7317 |  |  | -4399.1206 |  |  | -5431.6715 |  |  | -6045.913 |  |  | -7470.4408
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 218.8782 |  |  | 234.21 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 978.4793 |  | 5500 | 1005.7594 |  | 5500 | 2414.2097 |  | 5500 | 4609.611 |  | 5500 | 7581.113 |  | 5500 | 11287.2442 |  | 5500 | 15062.8711 |  | 5500 | 18379.5653 |  | 5500 | 21338.1048 |  | 5500 | 24284.7537
[13 empty] | Next iteration flow rate |  |  | 998.0489 | Abs Value of | Flow this | 1015.817 | Abs Value of | Flow this | 2438.3518 | Abs Value of | Flow this | 4655.7071 | Abs Value of | Flow this | 7656.9241 | Abs Value of | Flow this | 11400.1166 | Abs Value of | Flow this | 15213.4999 | Abs Value of | Flow this | 18563.361 | Abs Value of | Flow this | 21551.4858 | Abs Value of | Flow this | 24527.6012 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 23.2754 |  |  | 22.067 |  |  | -143.8795 |  |  | -675.1206 |  |  | -1923.1071 |  |  | -4332.2314 |  |  | -7759.7194 |  |  | -11580.989 |  |  | -15629.2217 |  |  | -20260.6529
[13 empty] | P2 at this iteration flow rate |  |  | 31.3849 |  |  | 31.6266 |  |  | 64.8159 |  |  | 171.0641 |  |  | 420.6614 |  |  | 902.4863 |  |  | 1587.9839 |  |  | 2352.2378 |  |  | 3161.8843 |  |  | 4088.1706
[13 empty] | Delta P at this iteration flow rate |  |  | -8.1095 |  |  | -9.5596 |  |  | -208.6954 |  |  | -846.1848 |  |  | -2343.7685 |  |  | -5234.7177 |  |  | -9347.7033 |  |  | -13933.2268 |  |  | -18791.106 |  |  | -24348.8235
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 18.9089 |  |  | 17.9033 |  |  | -116.7767 |  |  | -522.0714 |  |  | -1387.238 |  |  | -2790.4309 |  |  | -4488.1995 |  |  | -5541.3913 |  |  | -6167.8838 |  |  | -7621.0236
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 229.5527 |  |  | 240.2781 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 998.0489 |  | 5500 | 1015.817 |  | 5500 | 2438.3518 |  | 5500 | 4655.7071 |  | 5500 | 7656.9241 |  | 5500 | 11400.1166 |  | 5500 | 15213.4999 |  | 5500 | 18563.361 |  | 5500 | 21551.4858 |  | 5500 | 24527.6012
[13 empty] | Next iteration flow rate |  |  | 1018.0099 | Abs Value of | Flow this | 1025.9751 | Abs Value of | Flow this | 2462.7353 | Abs Value of | Flow this | 4702.2642 | Abs Value of | Flow this | 7733.4934 | Abs Value of | Flow this | 11514.1178 | Abs Value of | Flow this | 15365.6349 | Abs Value of | Flow this | 18748.9946 | Abs Value of | Flow this | 21767.0007 | Abs Value of | Flow this | 24772.8772 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 21.9163 |  |  | 21.3665 |  |  | -147.9155 |  |  | -689.8346 |  |  | -1962.9055 |  |  | -4420.4533 |  |  | -7916.8338 |  |  | -11814.9109 |  |  | -15944.5131 |  |  | -20669.0361
[13 empty] | P2 at this iteration flow rate |  |  | 31.6567 |  |  | 31.7667 |  |  | 65.6231 |  |  | 174.0069 |  |  | 428.6211 |  |  | 920.1307 |  |  | 1619.4068 |  |  | 2399.0222 |  |  | 3224.9426 |  |  | 4169.8472
[13 empty] | Delta P at this iteration flow rate |  |  | -9.7404 |  |  | -10.4002 |  |  | -213.5386 |  |  | -863.8415 |  |  | -2391.5266 |  |  | -5340.584 |  |  | -9536.2405 |  |  | -14213.9331 |  |  | -19169.4557 |  |  | -24838.8833
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 17.7835 |  |  | 17.3235 |  |  | -120.0424 |  |  | -533.4423 |  |  | -1415.9401 |  |  | -2847.2496 |  |  | -4579.0688 |  |  | -5653.3164 |  |  | -6292.3063 |  |  | -7774.6332
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 241.4388 |  |  | 246.7091 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1018.0099 |  | 5500 | 1025.9751 |  | 5500 | 2462.7353 |  | 5500 | 4702.2642 |  | 5500 | 7733.4934 |  | 5500 | 11514.1178 |  | 5500 | 15365.6349 |  | 5500 | 18748.9946 |  | 5500 | 21767.0007 |  | 5500 | 24772.8772
[13 empty] | Next iteration flow rate |  |  | 1038.3701 | Abs Value of | Flow this | 1036.2349 | Abs Value of | Flow this | 2487.3626 | Abs Value of | Flow this | 4749.2869 | Abs Value of | Flow this | 7810.8283 | Abs Value of | Flow this | 11629.259 | Abs Value of | Flow this | 15519.2912 | Abs Value of | Flow this | 18936.4846 | Abs Value of | Flow this | 21984.6707 | Abs Value of | Flow this | 25020.606 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 20.5023 |  |  | 20.652 |  |  | -152.0326 |  |  | -704.8443 |  |  | -2003.5039 |  |  | -4510.4484 |  |  | -8077.1061 |  |  | -12053.5346 |  |  | -16266.1418 |  |  | -21085.6277
[13 empty] | P2 at this iteration flow rate |  |  | 31.9395 |  |  | 31.9096 |  |  | 66.4465 |  |  | 177.0089 |  |  | 436.7408 |  |  | 938.1297 |  |  | 1651.4612 |  |  | 2446.7469 |  |  | 3289.2684 |  |  | 4253.1655
[13 empty] | Delta P at this iteration flow rate |  |  | -11.4372 |  |  | -11.2577 |  |  | -218.4791 |  |  | -881.8531 |  |  | -2440.2447 |  |  | -5448.5781 |  |  | -9728.5674 |  |  | -14500.2816 |  |  | -19555.4102 |  |  | -25338.7933
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 16.6126 |  |  | 16.7319 |  |  | -123.3738 |  |  | -545.0418 |  |  | -1445.2192 |  |  | -2905.2104 |  |  | -4671.7646 |  |  | -5767.4912 |  |  | -6419.2296 |  |  | -7931.3303
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 254.7983 |  |  | 253.5424 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1038.3701 |  | 5500 | 1036.2349 |  | 5500 | 2487.3626 |  | 5500 | 4749.2869 |  | 5500 | 7810.8283 |  | 5500 | 11629.259 |  | 5500 | 15519.2912 |  | 5500 | 18936.4846 |  | 5500 | 21984.6707 |  | 5500 | 25020.606
[13 empty] | Next iteration flow rate |  |  | 1059.1375 | Abs Value of | Flow this | 1046.5972 | Abs Value of | Flow this | 2512.2363 | Abs Value of | Flow this | 4796.7797 | Abs Value of | Flow this | 7888.9366 | Abs Value of | Flow this | 11745.5516 | Abs Value of | Flow this | 15674.4841 | Abs Value of | Flow this | 19125.8494 | Abs Value of | Flow this | 22204.5174 | Abs Value of | Flow this | 25270.812 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 19.0312 |  |  | 19.923 |  |  | -156.2325 |  |  | -720.1556 |  |  | -2044.9184 |  |  | -4602.2524 |  |  | -8240.6 |  |  | -12296.9547 |  |  | -16594.2353 |  |  | -21510.5929
[13 empty] | P2 at this iteration flow rate |  |  | 32.2338 |  |  | 32.0554 |  |  | 67.2865 |  |  | 180.0711 |  |  | 445.0237 |  |  | 956.4905 |  |  | 1684.16 |  |  | 2495.4309 |  |  | 3354.8871 |  |  | 4338.1586
[13 empty] | Delta P at this iteration flow rate |  |  | -13.2025 |  |  | -12.1324 |  |  | -223.519 |  |  | -900.2268 |  |  | -2489.9421 |  |  | -5558.7429 |  |  | -9924.76 |  |  | -14792.3856 |  |  | -19949.1223 |  |  | -25848.7514
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 15.3945 |  |  | 16.1285 |  |  | -126.7722 |  |  | -556.8744 |  |  | -1475.0868 |  |  | -2964.3363 |  |  | -4766.3236 |  |  | -5883.9609 |  |  | -6548.7041 |  |  | -8091.177
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 269.9812 |  |  | 260.8242 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1059.1375 |  | 5500 | 1046.5972 |  | 5500 | 2512.2363 |  | 5500 | 4796.7797 |  | 5500 | 7888.9366 |  | 5500 | 11745.5516 |  | 5500 | 15674.4841 |  | 5500 | 19125.8494 |  | 5500 | 22204.5174 |  | 5500 | 25270.812
[13 empty] | Next iteration flow rate |  |  | 1080.3202 | Abs Value of | Flow this | 1057.0632 | Abs Value of | Flow this | 2537.3586 | Abs Value of | Flow this | 4844.7475 | Abs Value of | Flow this | 7967.826 | Abs Value of | Flow this | 11863.0071 | Abs Value of | Flow this | 15831.229 | Abs Value of | Flow this | 19317.1079 | Abs Value of | Flow this | 22426.5626 | Abs Value of | Flow this | 25523.5202 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 17.5007 |  |  | 19.1795 |  |  | -160.5168 |  |  | -735.7748 |  |  | -2087.1653 |  |  | -4695.9017 |  |  | -8407.3801 |  |  | -12545.2675 |  |  | -16928.9234 |  |  | -21944.0998
[13 empty] | P2 at this iteration flow rate |  |  | 32.5399 |  |  | 32.2041 |  |  | 68.1434 |  |  | 183.195 |  |  | 453.4731 |  |  | 975.2203 |  |  | 1717.516 |  |  | 2545.0935 |  |  | 3421.8247 |  |  | 4424.86
[13 empty] | Delta P at this iteration flow rate |  |  | -15.0392 |  |  | -13.0246 |  |  | -228.6601 |  |  | -918.9698 |  |  | -2540.6383 |  |  | -5671.1221 |  |  | -10124.8961 |  |  | -15090.361 |  |  | -20350.7481 |  |  | -26368.9597
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 14.1271 |  |  | 15.513 |  |  | -130.2388 |  |  | -568.9448 |  |  | -1505.5547 |  |  | -3024.6505 |  |  | -4862.7833 |  |  | -6002.7717 |  |  | -6680.781 |  |  | -8254.2366
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 287.4681 |  |  | 268.6079 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1080.3202 |  | 5500 | 1057.0632 |  | 5500 | 2537.3586 |  | 5500 | 4844.7475 |  | 5500 | 7967.826 |  | 5500 | 11863.0071 |  | 5500 | 15831.229 |  | 5500 | 19317.1079 |  | 5500 | 22426.5626 |  | 5500 | 25523.5202
[13 empty] | Next iteration flow rate |  |  | 1101.9266 | Abs Value of | Flow this | 1067.6338 | Abs Value of | Flow this | 2562.7322 | Abs Value of | Flow this | 4893.195 | Abs Value of | Flow this | 8047.5042 | Abs Value of | Flow this | 11981.6372 | Abs Value of | Flow this | 15989.5412 | Abs Value of | Flow this | 19510.279 | Abs Value of | Flow this | 22650.8282 | Abs Value of | Flow this | 25778.7554 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 15.9083 |  |  | 18.421 |  |  | -164.8872 |  |  | -751.7079 |  |  | -2130.2613 |  |  | -4791.4334 |  |  | -8577.5124 |  |  | -12798.5714 |  |  | -17270.3388 |  |  | -22386.3202
[13 empty] | P2 at this iteration flow rate |  |  | 32.8583 |  |  | 32.3558 |  |  | 69.0174 |  |  | 186.3816 |  |  | 462.0923 |  |  | 994.3267 |  |  | 1751.5425 |  |  | 2595.7543 |  |  | 3490.1078 |  |  | 4513.304
[13 empty] | Delta P at this iteration flow rate |  |  | -16.95 |  |  | -13.9348 |  |  | -233.9046 |  |  | -938.0895 |  |  | -2592.3536 |  |  | -5785.76 |  |  | -10329.0549 |  |  | -15394.3257 |  |  | -20760.4465 |  |  | -26899.6243
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 12.8085 |  |  | 14.8851 |  |  | -133.7751 |  |  | -581.2578 |  |  | -1536.635 |  |  | -3086.1771 |  |  | -4961.1818 |  |  | -6123.9705 |  |  | -6815.5127 |  |  | -8420.5738
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 307.9405 |  |  | 276.957 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1101.9266 |  | 5500 | 1067.6338 |  | 5500 | 2562.7322 |  | 5500 | 4893.195 |  | 5500 | 8047.5042 |  | 5500 | 11981.6372 |  | 5500 | 15989.5412 |  | 5500 | 19510.279 |  | 5500 | 22650.8282 |  | 5500 | 25778.7554
[13 empty] | Next iteration flow rate |  |  | 1123.9652 | Abs Value of | Flow this | 1078.3102 | Abs Value of | Flow this | 2588.3595 | Abs Value of | Flow this | 4942.127 | Abs Value of | Flow this | 8127.9793 | Abs Value of | Flow this | 12101.4535 | Abs Value of | Flow this | 16149.4367 | Abs Value of | Flow this | 19705.3818 | Abs Value of | Flow this | 22877.3365 | Abs Value of | Flow this | 26036.5429 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 14.2516 |  |  | 17.6472 |  |  | -169.3454 |  |  | -767.9612 |  |  | -2174.2236 |  |  | -4888.8852 |  |  | -8751.0644 |  |  | -13056.9667 |  |  | -17618.6166 |  |  | -22837.4293
[13 empty] | P2 at this iteration flow rate |  |  | 33.1897 |  |  | 32.5106 |  |  | 69.9091 |  |  | 189.6322 |  |  | 470.8847 |  |  | 1013.817 |  |  | 1786.2529 |  |  | 2647.4333 |  |  | 3559.7633 |  |  | 4603.5259
[13 empty] | Delta P at this iteration flow rate |  |  | -18.9381 |  |  | -14.8633 |  |  | -239.2545 |  |  | -957.5935 |  |  | -2645.1083 |  |  | -5902.7022 |  |  | -10537.3173 |  |  | -15704.4 |  |  | -21178.3799 |  |  | -27440.9551
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 11.4367 |  |  | 14.2445 |  |  | -137.3825 |  |  | -593.8184 |  |  | -1568.34 |  |  | -3148.9404 |  |  | -5061.5581 |  |  | -6247.6055 |  |  | -6952.9524 |  |  | -8590.2543
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 332.4043 |  |  | 285.9467 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1123.9652 |  | 5500 | 1078.3102 |  | 5500 | 2588.3595 |  | 5500 | 4942.127 |  | 5500 | 8127.9793 |  | 5500 | 12101.4535 |  | 5500 | 16149.4367 |  | 5500 | 19705.3818 |  | 5500 | 22877.3365 |  | 5500 | 26036.5429
[13 empty] | Next iteration flow rate |  |  | 1146.4445 | Abs Value of | Flow this | 1089.0933 | Abs Value of | Flow this | 2614.2431 | Abs Value of | Flow this | 4991.5482 | Abs Value of | Flow this | 8209.259 | Abs Value of | Flow this | 12222.4681 | Abs Value of | Flow this | 16310.931 | Abs Value of | Flow this | 19902.4356 | Abs Value of | Flow this | 23106.1098 | Abs Value of | Flow this | 26296.9084 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 12.5279 |  |  | 16.8579 |  |  | -173.8933 |  |  | -784.5413 |  |  | -2219.0695 |  |  | -4988.2958 |  |  | -8928.1048 |  |  | -13320.5557 |  |  | -17973.8948 |  |  | -23297.6056
[13 empty] | P2 at this iteration flow rate |  |  | 33.5344 |  |  | 32.6684 |  |  | 70.8187 |  |  | 192.9483 |  |  | 479.8539 |  |  | 1033.6992 |  |  | 1821.661 |  |  | 2700.1511 |  |  | 3630.819 |  |  | 4695.5611
[13 empty] | Delta P at this iteration flow rate |  |  | -21.0065 |  |  | -15.8105 |  |  | -244.7119 |  |  | -977.4895 |  |  | -2698.9234 |  |  | -6021.995 |  |  | -10749.7658 |  |  | -16020.7069 |  |  | -21604.7138 |  |  | -27993.1667
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 10.0094 |  |  | 13.5911 |  |  | -141.0624 |  |  | -606.6314 |  |  | -1600.6823 |  |  | -3212.9652 |  |  | -5163.9519 |  |  | -6373.7255 |  |  | -7093.1547 |  |  | -8763.3454
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 362.4204 |  |  | 295.667 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1146.4445 |  | 5500 | 1089.0933 |  | 5500 | 2614.2431 |  | 5500 | 4991.5482 |  | 5500 | 8209.259 |  | 5500 | 12222.4681 |  | 5500 | 16310.931 |  | 5500 | 19902.4356 |  | 5500 | 23106.1098 |  | 5500 | 26296.9084
[13 empty] | Next iteration flow rate |  |  | 1169.3734 | Abs Value of | Flow this | 1099.9842 | Abs Value of | Flow this | 2640.3856 | Abs Value of | Flow this | 5041.4637 | Abs Value of | Flow this | 8291.3516 | Abs Value of | Flow this | 12344.6928 | Abs Value of | Flow this | 16474.0403 | Abs Value of | Flow this | 20101.4599 | Abs Value of | Flow this | 23337.1709 | Abs Value of | Flow this | 26559.8774 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 10.7346 |  |  | 16.0527 |  |  | -178.5326 |  |  | -801.4546 |  |  | -2264.8168 |  |  | -5089.7046 |  |  | -9108.7037 |  |  | -13589.4429 |  |  | -18336.3141 |  |  | -23767.0315
[13 empty] | P2 at this iteration flow rate |  |  | 33.8931 |  |  | 32.8295 |  |  | 71.7465 |  |  | 196.3309 |  |  | 489.0034 |  |  | 1053.9809 |  |  | 1857.7807 |  |  | 2753.9286 |  |  | 3703.3028 |  |  | 4789.4463
[13 empty] | Delta P at this iteration flow rate |  |  | -23.1584 |  |  | -16.7767 |  |  | -250.2791 |  |  | -997.7855 |  |  | -2753.8201 |  |  | -6143.6855 |  |  | -10966.4845 |  |  | -16343.3715 |  |  | -22039.6169 |  |  | -28556.4778
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 8.5245 |  |  | 12.9246 |  |  | -144.8163 |  |  | -619.7019 |  |  | -1633.6747 |  |  | -3278.2769 |  |  | -5268.4039 |  |  | -6502.3805 |  |  | -7236.1751 |  |  | -8939.9156
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 400.5744 |  |  | 306.2271 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1169.3734 |  | 5500 | 1099.9842 |  | 5500 | 2640.3856 |  | 5500 | 5041.4637 |  | 5500 | 8291.3516 |  | 5500 | 12344.6928 |  | 5500 | 16474.0403 |  | 5500 | 20101.4599 |  | 5500 | 23337.1709 |  | 5500 | 26559.8774
[13 empty] | Next iteration flow rate |  |  | 1192.7608 | Abs Value of | Flow this | 1110.9841 | Abs Value of | Flow this | 2666.7894 | Abs Value of | Flow this | 5091.8783 | Abs Value of | Flow this | 8374.2652 | Abs Value of | Flow this | 12468.1397 | Abs Value of | Flow this | 16638.7807 | Abs Value of | Flow this | 20302.4745 | Abs Value of | Flow this | 23570.5427 | Abs Value of | Flow this | 26825.4762 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 8.8689 |  |  | 15.2314 |  |  | -183.2651 |  |  | -818.7078 |  |  | -2311.4836 |  |  | -5193.1516 |  |  | -9292.9327 |  |  | -13863.7347 |  |  | -18706.018 |  |  | -24245.8928
[13 empty] | P2 at this iteration flow rate |  |  | 34.2662 |  |  | 32.9937 |  |  | 72.693 |  |  | 199.7816 |  |  | 498.3367 |  |  | 1074.6703 |  |  | 1894.6265 |  |  | 2808.7869 |  |  | 3777.2436 |  |  | 4885.2186
[13 empty] | Delta P at this iteration flow rate |  |  | -25.3973 |  |  | -17.7623 |  |  | -255.9581 |  |  | -1018.4894 |  |  | -2809.8203 |  |  | -6267.822 |  |  | -11187.5593 |  |  | -16672.5217 |  |  | -22483.2616 |  |  | -29131.1114
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 6.9795 |  |  | 12.2447 |  |  | -148.6457 |  |  | -633.0352 |  |  | -1667.3302 |  |  | -3344.9013 |  |  | -5374.9554 |  |  | -6633.6215 |  |  | -7382.0702 |  |  | -9120.0349
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 451.5476 |  |  | 317.7607 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1192.7608 |  | 5500 | 1110.9841 |  | 5500 | 2666.7894 |  | 5500 | 5091.8783 |  | 5500 | 8374.2652 |  | 5500 | 12468.1397 |  | 5500 | 16638.7807 |  | 5500 | 20302.4745 |  | 5500 | 23570.5427 |  | 5500 | 26825.4762
[13 empty] | Next iteration flow rate |  |  | 1216.616 | Abs Value of | Flow this | 1122.0939 | Abs Value of | Flow this | 2693.4573 | Abs Value of | Flow this | 5142.7971 | Abs Value of | Flow this | 8458.0078 | Abs Value of | Flow this | 12592.8211 | Abs Value of | Flow this | 16805.1685 | Abs Value of | Flow this | 20505.4993 | Abs Value of | Flow this | 23806.2481 | Abs Value of | Flow this | 27093.731 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 6.9278 |  |  | 14.3935 |  |  | -188.0927 |  |  | -836.3078 |  |  | -2359.0885 |  |  | -5298.678 |  |  | -9480.8647 |  |  | -14143.5398 |  |  | -19083.153 |  |  | -24734.3793
[13 empty] | P2 at this iteration flow rate |  |  | 34.6544 |  |  | 33.1613 |  |  | 73.6585 |  |  | 203.3016 |  |  | 507.8577 |  |  | 1095.7756 |  |  | 1932.2129 |  |  | 2864.748 |  |  | 3852.6706 |  |  | 4982.9159
[13 empty] | Delta P at this iteration flow rate |  |  | -27.7266 |  |  | -18.7678 |  |  | -261.7513 |  |  | -1039.6094 |  |  | -2866.9461 |  |  | -6394.4536 |  |  | -11413.0776 |  |  | -17008.2878 |  |  | -22935.8236 |  |  | -29717.2952
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 5.3722 |  |  | 11.5511 |  |  | -152.552 |  |  | -646.6365 |  |  | -1701.6622 |  |  | -3412.8649 |  |  | -5483.6485 |  |  | -6767.5004 |  |  | -7530.8978 |  |  | -9303.7746
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 524.9779 |  |  | 330.4335 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1216.616 |  | 5500 | 1122.0939 |  | 5500 | 2693.4573 |  | 5500 | 5142.7971 |  | 5500 | 8458.0078 |  | 5500 | 12592.8211 |  | 5500 | 16805.1685 |  | 5500 | 20505.4993 |  | 5500 | 23806.2481 |  | 5500 | 27093.731
[13 empty] | Next iteration flow rate |  |  | 1240.9484 | Abs Value of | Flow this | 1133.3148 | Abs Value of | Flow this | 2720.3919 | Abs Value of | Flow this | 5194.2251 | Abs Value of | Flow this | 8542.5879 | Abs Value of | Flow this | 12718.7493 | Abs Value of | Flow this | 16973.2202 | Abs Value of | Flow this | 20710.5543 | Abs Value of | Flow this | 24044.3106 | Abs Value of | Flow this | 27364.6683 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 4.9083 |  |  | 13.5388 |  |  | -193.0174 |  |  | -854.2616 |  |  | -2407.6501 |  |  | -5406.3254 |  |  | -9672.5741 |  |  | -14428.969 |  |  | -19467.8684 |  |  | -25232.6843
[13 empty] | P2 at this iteration flow rate |  |  | 35.0583 |  |  | 33.3322 |  |  | 74.6435 |  |  | 206.8923 |  |  | 517.57 |  |  | 1117.3051 |  |  | 1970.5548 |  |  | 2921.8338 |  |  | 3929.6137 |  |  | 5082.5769
[13 empty] | Delta P at this iteration flow rate |  |  | -30.1501 |  |  | -19.7934 |  |  | -267.6609 |  |  | -1061.154 |  |  | -2925.2202 |  |  | -6523.6305 |  |  | -11643.1289 |  |  | -17350.8028 |  |  | -23397.4821 |  |  | -30315.2612
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 3.6999 |  |  | 10.8435 |  |  | -156.5368 |  |  | -660.5111 |  |  | -1736.6843 |  |  | -3482.1946 |  |  | -5594.5264 |  |  | -6904.0704 |  |  | -7682.7168 |  |  | -9491.2074
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 645.2395 |  |  | 344.4541 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1240.9484 |  | 5500 | 1133.3148 |  | 5500 | 2720.3919 |  | 5500 | 5194.2251 |  | 5500 | 8542.5879 |  | 5500 | 12718.7493 |  | 5500 | 16973.2202 |  | 5500 | 20710.5543 |  | 5500 | 24044.3106 |  | 5500 | 27364.6683
[13 empty] | Next iteration flow rate |  |  | 1265.7673 | Abs Value of | Flow this | 1144.648 | Abs Value of | Flow this | 2747.5958 | Abs Value of | Flow this | 5246.1673 | Abs Value of | Flow this | 8628.0138 | Abs Value of | Flow this | 12845.9368 | Abs Value of | Flow this | 17142.9524 | Abs Value of | Flow this | 20917.6598 | Abs Value of | Flow this | 24284.7537 | Abs Value of | Flow this | 27638.315 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 2.8072 |  |  | 12.6669 |  |  | -198.0411 |  |  | -872.5763 |  |  | -2457.1879 |  |  | -5516.1366 |  |  | -9868.1368 |  |  | -14720.1353 |  |  | -19860.3166 |  |  | -25741.0053
[13 empty] | P2 at this iteration flow rate |  |  | 35.4786 |  |  | 33.5066 |  |  | 75.6482 |  |  | 210.5553 |  |  | 527.4776 |  |  | 1139.2673 |  |  | 2009.6674 |  |  | 2980.0671 |  |  | 4008.1033 |  |  | 5184.2411
[13 empty] | Delta P at this iteration flow rate |  |  | -32.6714 |  |  | -20.8397 |  |  | -273.6893 |  |  | -1083.1316 |  |  | -2984.6655 |  |  | -6655.4039 |  |  | -11877.8042 |  |  | -17700.2023 |  |  | -23868.4199 |  |  | -30925.2464
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 1.9601 |  |  | 10.1217 |  |  | -160.6017 |  |  | -674.6646 |  |  | -1772.4104 |  |  | -3552.9178 |  |  | -5707.6329 |  |  | -7043.3853 |  |  | -7837.5874 |  |  | -9682.4077
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 904.2318 |  |  | 360.0892 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1265.7673 |  | 5500 | 1144.648 |  | 5500 | 2747.5958 |  | 5500 | 5246.1673 |  | 5500 | 8628.0138 |  | 5500 | 12845.9368 |  | 5500 | 17142.9524 |  | 5500 | 20917.6598 |  | 5500 | 24284.7537 |  | 5500 | 27638.315
[13 empty] | Next iteration flow rate |  |  | 1291.0827 | Abs Value of | Flow this | 1156.0945 | Abs Value of | Flow this | 2775.0718 | Abs Value of | Flow this | 5298.629 | Abs Value of | Flow this | 8714.2939 | Abs Value of | Flow this | 12974.3962 | Abs Value of | Flow this | 17314.382 | Abs Value of | Flow this | 21126.8364 | Abs Value of | Flow this | 24527.6012 | Abs Value of | Flow this | 27914.6981 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 0.62116 |  |  | 11.7775 |  |  | -203.1657 |  |  | -891.2591 |  |  | -2507.7214 |  |  | -5628.155 |  |  | -10067.6304 |  |  | -15017.154 |  |  | -20260.6529 |  |  | -26259.5435
[13 empty] | P2 at this iteration flow rate |  |  | 35.9158 |  |  | 33.6845 |  |  | 76.6731 |  |  | 214.2918 |  |  | 537.5843 |  |  | 1161.671 |  |  | 2049.5661 |  |  | 3039.4708 |  |  | 4088.1706 |  |  | 5287.9487
[13 empty] | Delta P at this iteration flow rate |  |  | -35.2946 |  |  | -21.907 |  |  | -279.8388 |  |  | -1105.5509 |  |  | -3045.3057 |  |  | -6789.826 |  |  | -12117.1965 |  |  | -18056.6248 |  |  | -24348.8235 |  |  | -31547.4922
[13 empty] | Choked pressure drop w/ reducers | 3 |  | 0.14996 |  |  | 9.3855 |  |  | -164.7483 |  |  | -689.1026 |  |  | -1808.8545 |  |  | -3625.0626 |  |  | -5823.0129 |  |  | -7185.5005 |  |  | -7995.5709 |  |  | -9877.4511
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | 3334.4771 |  |  | 377.6863 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1291.0827 |  | 5500 | 1156.0945 |  | 5500 | 2775.0718 |  | 5500 | 5298.629 |  | 5500 | 8714.2939 |  | 5500 | 12974.3962 |  | 5500 | 17314.382 |  | 5500 | 21126.8364 |  | 5500 | 24527.6012 |  | 5500 | 27914.6981
[13 empty] | Next iteration flow rate |  |  | 1316.9043 | Abs Value of | Flow this | 1167.6554 | Abs Value of | Flow this | 2802.8225 | Abs Value of | Flow this | 5351.6153 | Abs Value of | Flow this | 8801.4368 | Abs Value of | Flow this | 13104.1401 | Abs Value of | Flow this | 17487.5258 | Abs Value of | Flow this | 21338.1048 | Abs Value of | Flow this | 24772.8772 | Abs Value of | Flow this | 28193.8451 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -1.6532 |  |  | 10.8702 |  |  | -208.3933 |  |  | -910.3174 |  |  | -2559.2706 |  |  | -5742.4249 |  |  | -10271.1338 |  |  | -15320.1428 |  |  | -20669.0361 |  |  | -26788.5044
[13 empty] | P2 at this iteration flow rate |  |  | 36.3706 |  |  | 33.866 |  |  | 77.7187 |  |  | 218.1035 |  |  | 547.8941 |  |  | 1184.525 |  |  | 2090.2668 |  |  | 3100.0686 |  |  | 4169.8472 |  |  | 5393.7409
[13 empty] | Delta P at this iteration flow rate |  |  | -38.0238 |  |  | -22.9957 |  |  | -286.112 |  |  | -1128.4209 |  |  | -3107.1648 |  |  | -6926.9499 |  |  | -12361.4005 |  |  | -18420.2114 |  |  | -24838.8833 |  |  | -32182.2452
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -1.7333 |  |  | 8.6344 |  |  | -168.9783 |  |  | -703.8309 |  |  | -1846.0311 |  |  | -3698.6574 |  |  | -5940.712 |  |  | -7330.4722 |  |  | -8156.7298 |  |  | -10076.4148
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 397.7083 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1316.9043 |  | 5500 | 1167.6554 |  | 5500 | 2802.8225 |  | 5500 | 5351.6153 |  | 5500 | 8801.4368 |  | 5500 | 13104.1401 |  | 5500 | 17487.5258 |  | 5500 | 21338.1048 |  | 5500 | 24772.8772 |  | 5500 | 28193.8451
[13 empty] | Next iteration flow rate |  |  | 1343.2424 | Abs Value of | Flow this | 1179.332 | Abs Value of | Flow this | 2830.8507 | Abs Value of | Flow this | 5405.1315 | Abs Value of | Flow this | 8889.4512 | Abs Value of | Flow this | 13235.1815 | Abs Value of | Flow this | 17662.401 | Abs Value of | Flow this | 21551.4858 | Abs Value of | Flow this | 25020.606 | Abs Value of | Flow this | 28475.7835 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -4.0194 |  |  | 9.9447 |  |  | -213.7261 |  |  | -929.7588 |  |  | -2611.856 |  |  | -5858.9916 |  |  | -10478.7276 |  |  | -15629.2217 |  |  | -21085.6277 |  |  | -27328.0973
[13 empty] | P2 at this iteration flow rate |  |  | 36.8439 |  |  | 34.0511 |  |  | 78.7852 |  |  | 221.9918 |  |  | 558.4112 |  |  | 1207.8383 |  |  | 2131.7855 |  |  | 3161.8843 |  |  | 4253.1655 |  |  | 5501.6595
[13 empty] | Delta P at this iteration flow rate |  |  | -40.8632 |  |  | -24.1063 |  |  | -292.5113 |  |  | -1151.7506 |  |  | -3170.2672 |  |  | -7066.83 |  |  | -12610.5131 |  |  | -18791.106 |  |  | -25338.7933 |  |  | -32829.7568
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -3.6926 |  |  | 7.8682 |  |  | -173.2933 |  |  | -718.8551 |  |  | -1883.955 |  |  | -3773.7315 |  |  | -6060.7768 |  |  | -7478.3579 |  |  | -8321.128 |  |  | -10279.3778
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 420.7883 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1343.2424 |  | 5500 | 1179.332 |  | 5500 | 2830.8507 |  | 5500 | 5405.1315 |  | 5500 | 8889.4512 |  | 5500 | 13235.1815 |  | 5500 | 17662.401 |  | 5500 | 21551.4858 |  | 5500 | 25020.606 |  | 5500 | 28475.7835
[13 empty] | Next iteration flow rate |  |  | 1370.1073 | Abs Value of | Flow this | 1191.1253 | Abs Value of | Flow this | 2859.1592 | Abs Value of | Flow this | 5459.1828 | Abs Value of | Flow this | 8978.3457 | Abs Value of | Flow this | 13367.5333 | Abs Value of | Flow this | 17839.025 | Abs Value of | Flow this | 21767.0007 | Abs Value of | Flow this | 25270.812 | Abs Value of | Flow this | 28760.5414 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -6.4812 |  |  | 9.0006 |  |  | -219.166 |  |  | -949.591 |  |  | -2665.4983 |  |  | -5977.9014 |  |  | -10690.494 |  |  | -15944.5131 |  |  | -21510.5929 |  |  | -27878.5361
[13 empty] | P2 at this iteration flow rate |  |  | 37.3362 |  |  | 34.2399 |  |  | 79.8732 |  |  | 225.9582 |  |  | 569.1397 |  |  | 1231.6203 |  |  | 2174.1388 |  |  | 3224.9426 |  |  | 4338.1586 |  |  | 5611.7472
[13 empty] | Delta P at this iteration flow rate |  |  | -43.8174 |  |  | -25.2393 |  |  | -299.0392 |  |  | -1175.5492 |  |  | -3234.638 |  |  | -7209.5217 |  |  | -12864.6328 |  |  | -19169.4557 |  |  | -25848.7514 |  |  | -33490.2833
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -5.7311 |  |  | 7.0866 |  |  | -177.695 |  |  | -734.1814 |  |  | -1922.6412 |  |  | -3850.3147 |  |  | -6183.255 |  |  | -7629.216 |  |  | -8488.8307 |  |  | -10486.4202
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 447.8194 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1370.1073 |  | 5500 | 1191.1253 |  | 5500 | 2859.1592 |  | 5500 | 5459.1828 |  | 5500 | 8978.3457 |  | 5500 | 13367.5333 |  | 5500 | 17839.025 |  | 5500 | 21767.0007 |  | 5500 | 25270.812 |  | 5500 | 28760.5414
[13 empty] | Next iteration flow rate |  |  | 1397.5094 | Abs Value of | Flow this | 1203.0365 | Abs Value of | Flow this | 2887.7508 | Abs Value of | Flow this | 5513.7746 | Abs Value of | Flow this | 9068.1292 | Abs Value of | Flow this | 13501.2087 | Abs Value of | Flow this | 18017.4153 | Abs Value of | Flow this | 21984.6707 | Abs Value of | Flow this | 25523.5202 | Abs Value of | Flow this | 29048.1468 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -9.0424 |  |  | 8.0375 |  |  | -224.7152 |  |  | -969.8218 |  |  | -2720.2188 |  |  | -6099.2012 |  |  | -10906.517 |  |  | -16266.1418 |  |  | -21944.0998 |  |  | -28440.0387
[13 empty] | P2 at this iteration flow rate |  |  | 37.8485 |  |  | 34.4325 |  |  | 80.983 |  |  | 230.0044 |  |  | 580.0838 |  |  | 1255.8802 |  |  | 2217.3434 |  |  | 3289.2684 |  |  | 4424.86 |  |  | 5724.0477
[13 empty] | Delta P at this iteration flow rate |  |  | -46.8909 |  |  | -26.395 |  |  | -305.6983 |  |  | -1199.8262 |  |  | -3300.3026 |  |  | -7355.0815 |  |  | -13123.8603 |  |  | -19555.4102 |  |  | -26368.9597 |  |  | -34164.0864
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -7.852 |  |  | 6.2894 |  |  | -182.1852 |  |  | -749.8157 |  |  | -1962.1049 |  |  | -3928.4371 |  |  | -6308.1949 |  |  | -7783.1064 |  |  | -8659.9041 |  |  | -10697.6243
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 480.1106 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1397.5094 |  | 5500 | 1203.0365 |  | 5500 | 2887.7508 |  | 5500 | 5513.7746 |  | 5500 | 9068.1292 |  | 5500 | 13501.2087 |  | 5500 | 18017.4153 |  | 5500 | 21984.6707 |  | 5500 | 25523.5202 |  | 5500 | 29048.1468
[13 empty] | Next iteration flow rate |  |  | 1425.4596 | Abs Value of | Flow this | 1215.0669 | Abs Value of | Flow this | 2916.6283 | Abs Value of | Flow this | 5568.9124 | Abs Value of | Flow this | 9158.8105 | Abs Value of | Flow this | 13636.2207 | Abs Value of | Flow this | 18197.5895 | Abs Value of | Flow this | 22204.5174 | Abs Value of | Flow this | 25778.7554 | Abs Value of | Flow this | 29338.6283 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -11.7071 |  |  | 7.055 |  |  | -230.376 |  |  | -990.4592 |  |  | -2776.0393 |  |  | -6222.9392 |  |  | -11126.882 |  |  | -16594.2353 |  |  | -22386.3202 |  |  | -29012.8275
[13 empty] | P2 at this iteration flow rate |  |  | 38.3814 |  |  | 34.629 |  |  | 82.1152 |  |  | 234.1318 |  |  | 591.2479 |  |  | 1280.6278 |  |  | 2261.4164 |  |  | 3354.8871 |  |  | 4513.304 |  |  | 5838.6055
[13 empty] | Delta P at this iteration flow rate |  |  | -50.0886 |  |  | -27.574 |  |  | -312.4912 |  |  | -1224.5911 |  |  | -3367.2871 |  |  | -7503.567 |  |  | -13388.2984 |  |  | -19949.1223 |  |  | -26899.6243 |  |  | -34851.433
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -10.0585 |  |  | 5.4761 |  |  | -186.7656 |  |  | -765.7642 |  |  | -2002.3619 |  |  | -4008.1298 |  |  | -6435.6462 |  |  | -7940.09 |  |  | -8834.4162 |  |  | -10913.0735
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 519.6754 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1425.4596 |  | 5500 | 1215.0669 |  | 5500 | 2916.6283 |  | 5500 | 5568.9124 |  | 5500 | 9158.8105 |  | 5500 | 13636.2207 |  | 5500 | 18197.5895 |  | 5500 | 22204.5174 |  | 5500 | 25778.7554 |  | 5500 | 29338.6283
[13 empty] | Next iteration flow rate |  |  | 1453.9688 | Abs Value of | Flow this | 1227.2176 | Abs Value of | Flow this | 2945.7946 | Abs Value of | Flow this | 5624.6015 | Abs Value of | Flow this | 9250.3986 | Abs Value of | Flow this | 13772.583 | Abs Value of | Flow this | 18379.5653 | Abs Value of | Flow this | 22426.5626 | Abs Value of | Flow this | 26036.5429 | Abs Value of | Flow this | 29632.0145 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -14.4795 |  |  | 6.0528 |  |  | -236.1506 |  |  | -1011.5115 |  |  | -2832.9817 |  |  | -6349.1643 |  |  | -11351.6763 |  |  | -16928.9234 |  |  | -22837.4293 |  |  | -29597.1293
[13 empty] | P2 at this iteration flow rate |  |  | 38.9359 |  |  | 34.8294 |  |  | 83.2701 |  |  | 238.3423 |  |  | 602.6363 |  |  | 1305.8729 |  |  | 2306.3753 |  |  | 3421.8247 |  |  | 4603.5259 |  |  | 5955.4659
[13 empty] | Delta P at this iteration flow rate |  |  | -53.4154 |  |  | -28.7766 |  |  | -319.4207 |  |  | -1249.8538 |  |  | -3435.618 |  |  | -7655.0371 |  |  | -13658.0516 |  |  | -20350.7481 |  |  | -27440.9551 |  |  | -35552.5952
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -12.3542 |  |  | 4.6464 |  |  | -191.4382 |  |  | -782.0333 |  |  | -2043.4281 |  |  | -4089.4243 |  |  | -6565.6592 |  |  | -8100.2289 |  |  | -9012.4359 |  |  | -11132.8532
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 569.8088 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1453.9688 |  | 5500 | 1227.2176 |  | 5500 | 2945.7946 |  | 5500 | 5624.6015 |  | 5500 | 9250.3986 |  | 5500 | 13772.583 |  | 5500 | 18379.5653 |  | 5500 | 22426.5626 |  | 5500 | 26036.5429 |  | 5500 | 29632.0145
[13 empty] | Next iteration flow rate |  |  | 1483.0482 | Abs Value of | Flow this | 1239.4898 | Abs Value of | Flow this | 2975.2525 | Abs Value of | Flow this | 5680.8475 | Abs Value of | Flow this | 9342.9026 | Abs Value of | Flow this | 13910.3088 | Abs Value of | Flow this | 18563.361 | Abs Value of | Flow this | 22650.8282 | Abs Value of | Flow this | 26296.9084 | Abs Value of | Flow this | 29928.3347 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -17.3639 |  |  | 5.0305 |  |  | -242.0412 |  |  | -1032.9869 |  |  | -2891.0686 |  |  | -6477.9265 |  |  | -11580.989 |  |  | -17270.3388 |  |  | -23297.6056 |  |  | -30193.1756
[13 empty] | P2 at this iteration flow rate |  |  | 39.5128 |  |  | 35.0339 |  |  | 84.4482 |  |  | 242.6374 |  |  | 614.2537 |  |  | 1331.6253 |  |  | 2352.2378 |  |  | 3490.1078 |  |  | 4695.5611 |  |  | 6074.6751
[13 empty] | Delta P at this iteration flow rate |  |  | -56.8767 |  |  | -30.0034 |  |  | -326.4895 |  |  | -1275.6242 |  |  | -3505.3223 |  |  | -7809.5518 |  |  | -13933.2268 |  |  | -20760.4465 |  |  | -27993.1667 |  |  | -36267.8508
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -14.7426 |  |  | 3.8001 |  |  | -196.2046 |  |  | -798.6295 |  |  | -2085.3196 |  |  | -4172.3528 |  |  | -6698.2855 |  |  | -8263.5867 |  |  | -9194.0338 |  |  | -11357.0506
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 636.375 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1483.0482 |  | 5500 | 1239.4898 |  | 5500 | 2975.2525 |  | 5500 | 5680.8475 |  | 5500 | 9342.9026 |  | 5500 | 13910.3088 |  | 5500 | 18563.361 |  | 5500 | 22650.8282 |  | 5500 | 26296.9084 |  | 5500 | 29928.3347
[13 empty] | Next iteration flow rate |  |  | 1512.7091 | Abs Value of | Flow this | 1251.8847 | Abs Value of | Flow this | 3005.0051 | Abs Value of | Flow this | 5737.656 | Abs Value of | Flow this | 9436.3316 | Abs Value of | Flow this | 14049.4119 | Abs Value of | Flow this | 18748.9946 | Abs Value of | Flow this | 22877.3365 | Abs Value of | Flow this | 26559.8774 | Abs Value of | Flow this | 30227.618 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -20.3648 |  |  | 3.9876 |  |  | -248.0503 |  |  | -1054.8939 |  |  | -2950.3231 |  |  | -6609.2768 |  |  | -11814.9109 |  |  | -17618.6166 |  |  | -23767.0315 |  |  | -30801.2025
[13 empty] | P2 at this iteration flow rate |  |  | 40.113 |  |  | 35.2425 |  |  | 85.6501 |  |  | 247.0188 |  |  | 626.1046 |  |  | 1357.8954 |  |  | 2399.0222 |  |  | 3559.7633 |  |  | 4789.4463 |  |  | 6196.2805
[13 empty] | Delta P at this iteration flow rate |  |  | -60.4778 |  |  | -31.2549 |  |  | -333.7003 |  |  | -1301.9127 |  |  | -3576.4277 |  |  | -7967.1722 |  |  | -14213.9331 |  |  | -21178.3799 |  |  | -28556.4778 |  |  | -36997.483
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -17.2275 |  |  | 2.9367 |  |  | -201.0668 |  |  | -815.5592 |  |  | -2128.0532 |  |  | -4256.9482 |  |  | -6833.5776 |  |  | -8430.2279 |  |  | -9379.2819 |  |  | -11585.7543
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 731.1367 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1512.7091 |  | 5500 | 1251.8847 |  | 5500 | 3005.0051 |  | 5500 | 5737.656 |  | 5500 | 9436.3316 |  | 5500 | 14049.4119 |  | 5500 | 18748.9946 |  | 5500 | 22877.3365 |  | 5500 | 26559.8774 |  | 5500 | 30227.618
[13 empty] | Next iteration flow rate |  |  | 1542.9633 | Abs Value of | Flow this | 1264.4035 | Abs Value of | Flow this | 3035.0551 | Abs Value of | Flow this | 5795.0325 | Abs Value of | Flow this | 9530.6949 | Abs Value of | Flow this | 14189.906 | Abs Value of | Flow this | 18936.4846 | Abs Value of | Flow this | 23106.1098 | Abs Value of | Flow this | 26825.4762 | Abs Value of | Flow this | 30529.8942 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -23.487 |  |  | 2.9237 |  |  | -254.1801 |  |  | -1077.2413 |  |  | -3010.7686 |  |  | -6743.2673 |  |  | -12053.5346 |  |  | -17973.8948 |  |  | -24245.8928 |  |  | -31421.4507
[13 empty] | P2 at this iteration flow rate |  |  | 40.7374 |  |  | 35.4553 |  |  | 86.876 |  |  | 251.4883 |  |  | 638.1937 |  |  | 1384.6935 |  |  | 2446.7469 |  |  | 3630.819 |  |  | 4885.2186 |  |  | 6320.3301
[13 empty] | Delta P at this iteration flow rate |  |  | -64.2243 |  |  | -32.5316 |  |  | -341.0561 |  |  | -1328.7296 |  |  | -3648.9623 |  |  | -8127.9608 |  |  | -14500.2816 |  |  | -21604.7138 |  |  | -29131.1114 |  |  | -37741.7808
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -19.8128 |  |  | 2.056 |  |  | -206.0268 |  |  | -832.8292 |  |  | -2171.6458 |  |  | -4343.2439 |  |  | -6971.5891 |  |  | -8600.2186 |  |  | -9568.2534 |  |  | -11819.0549
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 882.5453 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1542.9633 |  | 5500 | 1264.4035 |  | 5500 | 3035.0551 |  | 5500 | 5795.0325 |  | 5500 | 9530.6949 |  | 5500 | 14189.906 |  | 5500 | 18936.4846 |  | 5500 | 23106.1098 |  | 5500 | 26825.4762 |  | 5500 | 30529.8942
[13 empty] | Next iteration flow rate |  |  | 1573.8226 | Abs Value of | Flow this | 1277.0475 | Abs Value of | Flow this | 3065.4057 | Abs Value of | Flow this | 5852.9829 | Abs Value of | Flow this | 9626.0018 | Abs Value of | Flow this | 14331.8051 | Abs Value of | Flow this | 19125.8494 | Abs Value of | Flow this | 23337.1709 | Abs Value of | Flow this | 27093.731 | Abs Value of | Flow this | 30835.1932 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -26.7352 |  |  | 1.8385 |  |  | -260.4331 |  |  | -1100.0379 |  |  | -3072.4291 |  |  | -6879.951 |  |  | -12296.9547 |  |  | -18336.3141 |  |  | -24734.3793 |  |  | -32054.1658
[13 empty] | P2 at this iteration flow rate |  |  | 41.387 |  |  | 35.6723 |  |  | 88.1266 |  |  | 256.0476 |  |  | 650.5258 |  |  | 1412.0302 |  |  | 2495.4309 |  |  | 3703.3028 |  |  | 4982.9159 |  |  | 6446.8732
[13 empty] | Delta P at this iteration flow rate |  |  | -68.1223 |  |  | -33.8339 |  |  | -348.5598 |  |  | -1356.0854 |  |  | -3722.9549 |  |  | -8291.9812 |  |  | -14792.3856 |  |  | -22039.6169 |  |  | -29717.2952 |  |  | -38501.039
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -22.5026 |  |  | 1.1576 |  |  | -211.0865 |  |  | -850.4463 |  |  | -2216.1145 |  |  | -4431.2742 |  |  | -7112.3745 |  |  | -8773.6262 |  |  | -9761.0233 |  |  | -12057.0449
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 1187.9222 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1573.8226 |  | 5500 | 1277.0475 |  | 5500 | 3065.4057 |  | 5500 | 5852.9829 |  | 5500 | 9626.0018 |  | 5500 | 14331.8051 |  | 5500 | 19125.8494 |  | 5500 | 23337.1709 |  | 5500 | 27093.731 |  | 5500 | 30835.1932
[13 empty] | Next iteration flow rate |  |  | 1605.299 | Abs Value of | Flow this | 1289.818 | Abs Value of | Flow this | 3096.0597 | Abs Value of | Flow this | 5911.5127 | Abs Value of | Flow this | 9722.2619 | Abs Value of | Flow this | 14475.1231 | Abs Value of | Flow this | 19317.1079 | Abs Value of | Flow this | 23570.5427 | Abs Value of | Flow this | 27364.6683 | Abs Value of | Flow this | 31143.5451 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -30.1148 |  |  | 0.73139 |  |  | -266.8118 |  |  | -1123.2926 |  |  | -3135.3289 |  |  | -7019.382 |  |  | -12545.2675 |  |  | -18706.018 |  |  | -25232.6843 |  |  | -32699.5986
[13 empty] | P2 at this iteration flow rate |  |  | 42.063 |  |  | 35.8937 |  |  | 89.4024 |  |  | 260.6985 |  |  | 663.1058 |  |  | 1439.9164 |  |  | 2545.0935 |  |  | 3777.2436 |  |  | 5082.5769 |  |  | 6575.9597
[13 empty] | Delta P at this iteration flow rate |  |  | -72.1777 |  |  | -35.1623 |  |  | -356.2142 |  |  | -1383.9912 |  |  | -3798.4347 |  |  | -8459.2984 |  |  | -15090.361 |  |  | -22483.2616 |  |  | -30315.2612 |  |  | -39275.5583
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -25.301 |  |  | 0.24117 |  |  | -216.2478 |  |  | -868.4175 |  |  | -2261.4771 |  |  | -4521.074 |  |  | -7255.9898 |  |  | -8950.5192 |  |  | -9957.6678 |  |  | -12299.8185
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | 2628.6267 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1605.299 |  | 5500 | 1289.818 |  | 5500 | 3096.0597 |  | 5500 | 5911.5127 |  | 5500 | 9722.2619 |  | 5500 | 14475.1231 |  | 5500 | 19317.1079 |  | 5500 | 23570.5427 |  | 5500 | 27364.6683 |  | 5500 | 31143.5451
[13 empty] | Next iteration flow rate |  |  | 1637.405 | Abs Value of | Flow this | 1302.7162 | Abs Value of | Flow this | 3127.0203 | Abs Value of | Flow this | 5970.6278 | Abs Value of | Flow this | 9819.4845 | Abs Value of | Flow this | 14619.8743 | Abs Value of | Flow this | 19510.279 | Abs Value of | Flow this | 23806.2481 | Abs Value of | Flow this | 27638.315 | Abs Value of | Flow this | 31454.9805 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -33.6308 |  |  | -0.39792 |  |  | -273.3188 |  |  | -1147.0148 |  |  | -3199.493 |  |  | -7161.6156 |  |  | -12798.5714 |  |  | -19083.153 |  |  | -25741.0053 |  |  | -33358.0045
[13 empty] | P2 at this iteration flow rate |  |  | 42.7662 |  |  | 36.1196 |  |  | 90.7038 |  |  | 265.443 |  |  | 675.9386 |  |  | 1468.3631 |  |  | 2595.7543 |  |  | 3852.6706 |  |  | 5184.2411 |  |  | 6707.6409
[13 empty] | Delta P at this iteration flow rate |  |  | -76.397 |  |  | -36.5175 |  |  | -364.0225 |  |  | -1412.4578 |  |  | -3875.4316 |  |  | -8629.9787 |  |  | -15394.3257 |  |  | -22935.8236 |  |  | -30925.2464 |  |  | -40065.6454
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -28.2125 |  |  | -0.6937 |  |  | -221.5129 |  |  | -886.75 |  |  | -2307.7514 |  |  | -4612.6786 |  |  | -7402.4917 |  |  | -9130.9678 |  |  | -10158.2649 |  |  | -12547.4718
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1637.405 |  | 5500 | 1302.7162 |  | 5500 | 3127.0203 |  | 5500 | 5970.6278 |  | 5500 | 9819.4845 |  | 5500 | 14619.8743 |  | 5500 | 19510.279 |  | 5500 | 23806.2481 |  | 5500 | 27638.315 |  | 5500 | 31454.9805
[13 empty] | Next iteration flow rate |  |  | 1670.1531 | Abs Value of | Flow this | 1315.7434 | Abs Value of | Flow this | 3158.2905 | Abs Value of | Flow this | 6030.3341 | Abs Value of | Flow this | 9917.6793 | Abs Value of | Flow this | 14766.0731 | Abs Value of | Flow this | 19705.3818 | Abs Value of | Flow this | 24044.3106 | Abs Value of | Flow this | 27914.6981 | Abs Value of | Flow this | 31769.5303 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -37.2889 |  |  | -1.5499 |  |  | -279.9565 |  |  | -1171.2139 |  |  | -3264.9469 |  |  | -7306.7081 |  |  | -13056.9667 |  |  | -19467.8684 |  |  | -26259.5435 |  |  | -34029.6444
[13 empty] | P2 at this iteration flow rate |  |  | 43.4978 |  |  | 36.35 |  |  | 92.0313 |  |  | 270.2828 |  |  | 689.0294 |  |  | 1497.3816 |  |  | 2647.4333 |  |  | 3929.6137 |  |  | 5287.9487 |  |  | 6841.9689
[13 empty] | Delta P at this iteration flow rate |  |  | -80.7867 |  |  | -37.8999 |  |  | -371.9878 |  |  | -1441.4966 |  |  | -3953.9762 |  |  | -8804.0897 |  |  | -15704.4 |  |  | -23397.4821 |  |  | -31547.4922 |  |  | -40871.6133
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -31.2416 |  |  | -1.6474 |  |  | -226.8839 |  |  | -905.4509 |  |  | -2354.9559 |  |  | -4706.1246 |  |  | -7551.9384 |  |  | -9315.0434 |  |  | -10362.894 |  |  | -12800.103
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1670.1531 |  | 5500 | 1315.7434 |  | 5500 | 3158.2905 |  | 5500 | 6030.3341 |  | 5500 | 9917.6793 |  | 5500 | 14766.0731 |  | 5500 | 19705.3818 |  | 5500 | 24044.3106 |  | 5500 | 27914.6981 |  | 5500 | 31769.5303
[13 empty] | Next iteration flow rate |  |  | 1703.5562 | Abs Value of | Flow this | 1328.9008 | Abs Value of | Flow this | 3189.8734 | Abs Value of | Flow this | 6090.6374 | Abs Value of | Flow this | 10016.8561 | Abs Value of | Flow this | 14913.7338 | Abs Value of | Flow this | 19902.4356 | Abs Value of | Flow this | 24284.7537 | Abs Value of | Flow this | 28193.8451 | Abs Value of | Flow this | 32087.2257 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -41.0948 |  |  | -2.7251 |  |  | -286.7276 |  |  | -1195.8993 |  |  | -3331.7163 |  |  | -7454.717 |  |  | -13320.5557 |  |  | -19860.3166 |  |  | -26788.5044 |  |  | -34714.7843
[13 empty] | P2 at this iteration flow rate |  |  | 44.259 |  |  | 36.585 |  |  | 93.3855 |  |  | 275.2199 |  |  | 702.3833 |  |  | 1526.9834 |  |  | 2700.1511 |  |  | 4008.1033 |  |  | 5393.7409 |  |  | 6978.9969
[13 empty] | Delta P at this iteration flow rate |  |  | -85.3537 |  |  | -39.3101 |  |  | -380.1132 |  |  | -1471.1191 |  |  | -4034.0996 |  |  | -8981.7003 |  |  | -16020.7069 |  |  | -23868.4199 |  |  | -32182.2452 |  |  | -41693.7812
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -34.393 |  |  | -2.6202 |  |  | -232.3628 |  |  | -924.5277 |  |  | -2403.1092 |  |  | -4801.4488 |  |  | -7704.3889 |  |  | -9502.8189 |  |  | -10571.6361 |  |  | -13057.8121
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1703.5562 |  | 5500 | 1328.9008 |  | 5500 | 3189.8734 |  | 5500 | 6090.6374 |  | 5500 | 10016.8561 |  | 5500 | 14913.7338 |  | 5500 | 19902.4356 |  | 5500 | 24284.7537 |  | 5500 | 28193.8451 |  | 5500 | 32087.2257
[13 empty] | Next iteration flow rate |  |  | 1737.6273 | Abs Value of | Flow this | 1342.1898 | Abs Value of | Flow this | 3221.7722 | Abs Value of | Flow this | 6151.5438 | Abs Value of | Flow this | 10117.0247 | Abs Value of | Flow this | 15062.8711 | Abs Value of | Flow this | 20101.4599 | Abs Value of | Flow this | 24527.6012 | Abs Value of | Flow this | 28475.7835 | Abs Value of | Flow this | 32408.0979 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -45.0544 |  |  | -3.9239 |  |  | -293.6349 |  |  | -1221.0809 |  |  | -3399.8278 |  |  | -7605.7008 |  |  | -13589.4429 |  |  | -20260.6529 |  |  | -27328.0973 |  |  | -35413.6955
[13 empty] | P2 at this iteration flow rate |  |  | 45.0509 |  |  | 36.8248 |  |  | 94.767 |  |  | 280.2562 |  |  | 716.0056 |  |  | 1557.1802 |  |  | 2753.9286 |  |  | 4088.1706 |  |  | 5501.6595 |  |  | 7118.7791
[13 empty] | Delta P at this iteration flow rate |  |  | -90.1053 |  |  | -40.7487 |  |  | -388.4019 |  |  | -1501.337 |  |  | -4115.8334 |  |  | -9162.8809 |  |  | -16343.3715 |  |  | -24348.8235 |  |  | -32829.7568 |  |  | -42532.4746
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -37.6718 |  |  | -3.6126 |  |  | -237.9518 |  |  | -943.988 |  |  | -2452.2304 |  |  | -4898.689 |  |  | -7859.9036 |  |  | -9694.3687 |  |  | -10784.574 |  |  | -13320.7011
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1737.6273 |  | 5500 | 1342.1898 |  | 5500 | 3221.7722 |  | 5500 | 6151.5438 |  | 5500 | 10117.0247 |  | 5500 | 15062.8711 |  | 5500 | 20101.4599 |  | 5500 | 24527.6012 |  | 5500 | 28475.7835 |  | 5500 | 32408.0979
[13 empty] | Next iteration flow rate |  |  | 1772.3798 | Abs Value of | Flow this | 1355.6117 | Abs Value of | Flow this | 3253.9899 | Abs Value of | Flow this | 6213.0592 | Abs Value of | Flow this | 10218.1949 | Abs Value of | Flow this | 15213.4999 | Abs Value of | Flow this | 20302.4745 | Abs Value of | Flow this | 24772.8772 | Abs Value of | Flow this | 28760.5414 | Abs Value of | Flow this | 32732.1789 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -49.174 |  |  | -5.1468 |  |  | -300.681 |  |  | -1246.7686 |  |  | -3469.3084 |  |  | -7759.7194 |  |  | -13863.7347 |  |  | -20669.0361 |  |  | -27878.5361 |  |  | -36126.6548
[13 empty] | P2 at this iteration flow rate |  |  | 45.8748 |  |  | 37.0694 |  |  | 96.1762 |  |  | 285.3937 |  |  | 729.9017 |  |  | 1587.9839 |  |  | 2808.7869 |  |  | 4169.8472 |  |  | 5611.7472 |  |  | 7261.371
[13 empty] | Delta P at this iteration flow rate |  |  | -95.0488 |  |  | -42.2161 |  |  | -396.8571 |  |  | -1532.1623 |  |  | -4199.21 |  |  | -9347.7033 |  |  | -16672.5217 |  |  | -24838.8833 |  |  | -33490.2833 |  |  | -43388.0257
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -41.0831 |  |  | -4.6249 |  |  | -243.6531 |  |  | -963.8394 |  |  | -2502.3389 |  |  | -4997.8837 |  |  | -8018.5442 |  |  | -9889.7687 |  |  | -11001.7919 |  |  | -13588.8741
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1772.3798 |  | 5500 | 1355.6117 |  | 5500 | 3253.9899 |  | 5500 | 6213.0592 |  | 5500 | 10218.1949 |  | 5500 | 15213.4999 |  | 5500 | 20302.4745 |  | 5500 | 24772.8772 |  | 5500 | 28760.5414 |  | 5500 | 32732.1789
[13 empty] | Next iteration flow rate |  |  | 1807.8274 | Abs Value of | Flow this | 1369.1678 | Abs Value of | Flow this | 3286.5298 | Abs Value of | Flow this | 6275.1898 | Abs Value of | Flow this | 10320.3769 | Abs Value of | Flow this | 15365.6349 | Abs Value of | Flow this | 20505.4993 | Abs Value of | Flow this | 25020.606 | Abs Value of | Flow this | 29048.1468 | Abs Value of | Flow this | 33059.5007 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -53.4601 |  |  | -6.3942 |  |  | -307.8687 |  |  | -1272.9727 |  |  | -3540.1855 |  |  | -7916.8338 |  |  | -14143.5398 |  |  | -21085.6277 |  |  | -28440.0387 |  |  | -36853.9445
[13 empty] | P2 at this iteration flow rate |  |  | 46.732 |  |  | 37.3188 |  |  | 97.6137 |  |  | 290.6345 |  |  | 744.0771 |  |  | 1619.4068 |  |  | 2864.748 |  |  | 4253.1655 |  |  | 5724.0477 |  |  | 7406.8289
[13 empty] | Delta P at this iteration flow rate |  |  | -100.1921 |  |  | -43.7131 |  |  | -405.4824 |  |  | -1563.6072 |  |  | -4284.2626 |  |  | -9536.2405 |  |  | -17008.2878 |  |  | -25338.7933 |  |  | -34164.0864 |  |  | -44260.7735
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -44.6321 |  |  | -5.6576 |  |  | -249.4691 |  |  | -984.0898 |  |  | -2553.4545 |  |  | -5099.0723 |  |  | -8180.3735 |  |  | -10089.0962 |  |  | -11223.3759 |  |  | -13862.4375
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1807.8274 |  | 5500 | 1369.1678 |  | 5500 | 3286.5298 |  | 5500 | 6275.1898 |  | 5500 | 10320.3769 |  | 5500 | 15365.6349 |  | 5500 | 20505.4993 |  | 5500 | 25020.606 |  | 5500 | 29048.1468 |  | 5500 | 33059.5007
[13 empty] | Next iteration flow rate |  |  | 1843.984 | Abs Value of | Flow this | 1382.8595 | Abs Value of | Flow this | 3319.3951 | Abs Value of | Flow this | 6337.9417 | Abs Value of | Flow this | 10423.5807 | Abs Value of | Flow this | 15519.2912 | Abs Value of | Flow this | 20710.5543 | Abs Value of | Flow this | 25270.812 | Abs Value of | Flow this | 29338.6283 | Abs Value of | Flow this | 33390.0957 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -57.9193 |  |  | -7.6668 |  |  | -315.2008 |  |  | -1299.7034 |  |  | -3612.4872 |  |  | -8077.1061 |  |  | -14428.969 |  |  | -21510.5929 |  |  | -29012.8275 |  |  | -37595.8528
[13 empty] | P2 at this iteration flow rate |  |  | 47.6239 |  |  | 37.5734 |  |  | 99.0802 |  |  | 295.9807 |  |  | 758.5374 |  |  | 1651.4612 |  |  | 2921.8338 |  |  | 4338.1586 |  |  | 5838.6055 |  |  | 7555.2106
[13 empty] | Delta P at this iteration flow rate |  |  | -105.5431 |  |  | -45.2401 |  |  | -414.281 |  |  | -1595.6841 |  |  | -4371.0247 |  |  | -9728.5674 |  |  | -17350.8028 |  |  | -25848.7514 |  |  | -34851.433 |  |  | -45151.0634
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -48.3246 |  |  | -6.7111 |  |  | -255.402 |  |  | -1004.7473 |  |  | -2605.5977 |  |  | -5202.2948 |  |  | -8345.4556 |  |  | -10292.4302 |  |  | -11449.4137 |  |  | -14141.4995
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1843.984 |  | 5500 | 1382.8595 |  | 5500 | 3319.3951 |  | 5500 | 6337.9417 |  | 5500 | 10423.5807 |  | 5500 | 15519.2912 |  | 5500 | 20710.5543 |  | 5500 | 25270.812 |  | 5500 | 29338.6283 |  | 5500 | 33390.0957
[13 empty] | Next iteration flow rate |  |  | 1880.8637 | Abs Value of | Flow this | 1396.6881 | Abs Value of | Flow this | 3352.589 | Abs Value of | Flow this | 6401.3211 | Abs Value of | Flow this | 10527.8165 | Abs Value of | Flow this | 15674.4841 | Abs Value of | Flow this | 20917.6598 | Abs Value of | Flow this | 25523.5202 | Abs Value of | Flow this | 29632.0145 | Abs Value of | Flow this | 33723.9966 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -62.5586 |  |  | -8.9649 |  |  | -322.6804 |  |  | -1326.9715 |  |  | -3686.2422 |  |  | -8240.6 |  |  | -14720.1353 |  |  | -21944.0998 |  |  | -29597.1293 |  |  | -38352.6735
[13 empty] | P2 at this iteration flow rate |  |  | 48.5517 |  |  | 37.833 |  |  | 100.5761 |  |  | 301.4343 |  |  | 773.2884 |  |  | 1684.16 |  |  | 2980.0671 |  |  | 4424.86 |  |  | 5955.4659 |  |  | 7706.5747
[13 empty] | Delta P at this iteration flow rate |  |  | -111.1104 |  |  | -46.7979 |  |  | -423.2565 |  |  | -1628.4058 |  |  | -4459.5307 |  |  | -9924.76 |  |  | -17700.2023 |  |  | -26368.9597 |  |  | -35552.5952 |  |  | -46059.2482
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -52.1662 |  |  | -7.7857 |  |  | -261.4541 |  |  | -1025.8199 |  |  | -2658.7888 |  |  | -5307.592 |  |  | -8513.8558 |  |  | -10499.8511 |  |  | -11679.9949 |  |  | -14426.1706
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1880.8637 |  | 5500 | 1396.6881 |  | 5500 | 3352.589 |  | 5500 | 6401.3211 |  | 5500 | 10527.8165 |  | 5500 | 15674.4841 |  | 5500 | 20917.6598 |  | 5500 | 25523.5202 |  | 5500 | 29632.0145 |  | 5500 | 33723.9966
[13 empty] | Next iteration flow rate |  |  | 1918.4809 | Abs Value of | Flow this | 1410.655 | Abs Value of | Flow this | 3386.1149 | Abs Value of | Flow this | 6465.3344 | Abs Value of | Flow this | 10633.0946 | Abs Value of | Flow this | 15831.229 | Abs Value of | Flow this | 21126.8364 | Abs Value of | Flow this | 25778.7554 | Abs Value of | Flow this | 29928.3347 | Abs Value of | Flow this | 34061.2366 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -67.3854 |  |  | -10.2891 |  |  | -330.3103 |  |  | -1354.7876 |  |  | -3761.4797 |  |  | -8407.3801 |  |  | -15017.154 |  |  | -22386.3202 |  |  | -30193.1756 |  |  | -39124.7063
[13 empty] | P2 at this iteration flow rate |  |  | 49.5171 |  |  | 38.0978 |  |  | 102.1021 |  |  | 306.9975 |  |  | 788.3359 |  |  | 1717.516 |  |  | 3039.4708 |  |  | 4513.304 |  |  | 6074.6751 |  |  | 7860.9813
[13 empty] | Delta P at this iteration flow rate |  |  | -116.9025 |  |  | -48.3869 |  |  | -432.4123 |  |  | -1661.7851 |  |  | -4549.8157 |  |  | -10124.8961 |  |  | -18056.6248 |  |  | -26899.6243 |  |  | -36267.8508 |  |  | -46985.6875
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -56.1631 |  |  | -8.8819 |  |  | -267.6278 |  |  | -1047.3162 |  |  | -2713.0492 |  |  | -5415.0057 |  |  | -8685.6408 |  |  | -10711.4413 |  |  | -11915.2108 |  |  | -14716.5636
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1918.4809 |  | 5500 | 1410.655 |  | 5500 | 3386.1149 |  | 5500 | 6465.3344 |  | 5500 | 10633.0946 |  | 5500 | 15831.229 |  | 5500 | 21126.8364 |  | 5500 | 25778.7554 |  | 5500 | 29928.3347 |  | 5500 | 34061.2366
[13 empty] | Next iteration flow rate |  |  | 1956.8506 | Abs Value of | Flow this | 1424.7615 | Abs Value of | Flow this | 3419.9761 | Abs Value of | Flow this | 6529.9877 | Abs Value of | Flow this | 10739.4256 | Abs Value of | Flow this | 15989.5412 | Abs Value of | Flow this | 21338.1048 | Abs Value of | Flow this | 26036.5429 | Abs Value of | Flow this | 30227.618 | Abs Value of | Flow this | 34401.849 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -72.4072 |  |  | -11.6399 |  |  | -338.0935 |  |  | -1383.1629 |  |  | -3838.2295 |  |  | -8577.5124 |  |  | -15320.1428 |  |  | -22837.4293 |  |  | -30801.2025 |  |  | -39912.2569
[13 empty] | P2 at this iteration flow rate |  |  | 50.5214 |  |  | 38.368 |  |  | 103.6587 |  |  | 312.6726 |  |  | 803.6859 |  |  | 1751.5425 |  |  | 3100.0686 |  |  | 4603.5259 |  |  | 6196.2805 |  |  | 8018.4914
[13 empty] | Delta P at this iteration flow rate |  |  | -122.9286 |  |  | -50.0079 |  |  | -441.7522 |  |  | -1695.8354 |  |  | -4641.9154 |  |  | -10329.0549 |  |  | -18420.2114 |  |  | -27440.9551 |  |  | -36997.483 |  |  | -47930.7482
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -60.3214 |  |  | -10.0001 |  |  | -273.9257 |  |  | -1069.2445 |  |  | -2768.4001 |  |  | -5524.5784 |  |  | -8860.8787 |  |  | -10927.2844 |  |  | -12155.1545 |  |  | -15012.7935
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1956.8506 |  | 5500 | 1424.7615 |  | 5500 | 3419.9761 |  | 5500 | 6529.9877 |  | 5500 | 10739.4256 |  | 5500 | 15989.5412 |  | 5500 | 21338.1048 |  | 5500 | 26036.5429 |  | 5500 | 30227.618 |  | 5500 | 34401.849
[13 empty] | Next iteration flow rate |  |  | 1995.9876 | Abs Value of | Flow this | 1439.0091 | Abs Value of | Flow this | 3454.1758 | Abs Value of | Flow this | 6595.2876 | Abs Value of | Flow this | 10846.8198 | Abs Value of | Flow this | 16149.4367 | Abs Value of | Flow this | 21551.4858 | Abs Value of | Flow this | 26296.9084 | Abs Value of | Flow this | 30529.8942 | Abs Value of | Flow this | 34745.8675 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -77.6319 |  |  | -13.0179 |  |  | -346.0332 |  |  | -1412.1085 |  |  | -3916.5219 |  |  | -8751.0644 |  |  | -15629.2217 |  |  | -23297.6056 |  |  | -31421.4507 |  |  | -40715.6372
[13 empty] | P2 at this iteration flow rate |  |  | 51.5664 |  |  | 38.6436 |  |  | 105.2466 |  |  | 318.4617 |  |  | 819.3444 |  |  | 1786.2529 |  |  | 3161.8843 |  |  | 4695.5611 |  |  | 6320.3301 |  |  | 8179.1674
[13 empty] | Delta P at this iteration flow rate |  |  | -129.1982 |  |  | -51.6615 |  |  | -451.2799 |  |  | -1730.5701 |  |  | -4735.8663 |  |  | -10537.3173 |  |  | -18791.106 |  |  | -27993.1667 |  |  | -37741.7808 |  |  | -48894.8047
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -64.6476 |  |  | -11.1409 |  |  | -280.3501 |  |  | -1091.6136 |  |  | -2824.8636 |  |  | -5636.3535 |  |  | -9039.6389 |  |  | -11147.466 |  |  | -12399.921 |  |  | -15314.9776
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 1995.9876 |  | 5500 | 1439.0091 |  | 5500 | 3454.1758 |  | 5500 | 6595.2876 |  | 5500 | 10846.8198 |  | 5500 | 16149.4367 |  | 5500 | 21551.4858 |  | 5500 | 26296.9084 |  | 5500 | 30529.8942 |  | 5500 | 34745.8675
[13 empty] | Next iteration flow rate |  |  | 2035.9073 | Abs Value of | Flow this | 1453.3992 | Abs Value of | Flow this | 3488.7176 | Abs Value of | Flow this | 6661.2405 | Abs Value of | Flow this | 10955.288 | Abs Value of | Flow this | 16310.931 | Abs Value of | Flow this | 21767.0007 | Abs Value of | Flow this | 26559.8774 | Abs Value of | Flow this | 30835.1932 | Abs Value of | Flow this | 35093.3261 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -83.0676 |  |  | -14.4236 |  |  | -354.1325 |  |  | -1441.6358 |  |  | -3996.388 |  |  | -8928.1048 |  |  | -15944.5131 |  |  | -23767.0315 |  |  | -32054.1658 |  |  | -41535.1656
[13 empty] | P2 at this iteration flow rate |  |  | 52.6535 |  |  | 38.9247 |  |  | 106.8665 |  |  | 324.3672 |  |  | 835.3176 |  |  | 1821.661 |  |  | 3224.9426 |  |  | 4789.4463 |  |  | 6446.8732 |  |  | 8343.0731
[13 empty] | Delta P at this iteration flow rate |  |  | -135.7211 |  |  | -53.3483 |  |  | -460.999 |  |  | -1766.003 |  |  | -4831.7056 |  |  | -10749.7658 |  |  | -19169.4557 |  |  | -28556.4778 |  |  | -38501.039 |  |  | -49878.2387
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -69.1487 |  |  | -12.3045 |  |  | -286.9037 |  |  | -1114.4323 |  |  | -2882.4621 |  |  | -5750.3753 |  |  | -9221.9922 |  |  | -11372.0732 |  |  | -12649.6074 |  |  | -15623.2357
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2035.9073 |  | 5500 | 1453.3992 |  | 5500 | 3488.7176 |  | 5500 | 6661.2405 |  | 5500 | 10955.288 |  | 5500 | 16310.931 |  | 5500 | 21767.0007 |  | 5500 | 26559.8774 |  | 5500 | 30835.1932 |  | 5500 | 35093.3261
[13 empty] | Next iteration flow rate |  |  | 2076.6255 | Abs Value of | Flow this | 1467.9332 | Abs Value of | Flow this | 3523.6048 | Abs Value of | Flow this | 6727.8529 | Abs Value of | Flow this | 11064.8409 | Abs Value of | Flow this | 16474.0403 | Abs Value of | Flow this | 21984.6707 | Abs Value of | Flow this | 26825.4762 | Abs Value of | Flow this | 31143.5451 | Abs Value of | Flow this | 35444.2594 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -88.7229 |  |  | -15.8575 |  |  | -362.3946 |  |  | -1471.7567 |  |  | -4077.8594 |  |  | -9108.7037 |  |  | -16266.1418 |  |  | -24245.8928 |  |  | -32699.5986 |  |  | -42371.1664
[13 empty] | P2 at this iteration flow rate |  |  | 53.7846 |  |  | 39.2115 |  |  | 108.5189 |  |  | 330.3913 |  |  | 851.6119 |  |  | 1857.7807 |  |  | 3289.2684 |  |  | 4885.2186 |  |  | 6575.9597 |  |  | 8510.2733
[13 empty] | Delta P at this iteration flow rate |  |  | -142.5075 |  |  | -55.069 |  |  | -470.9135 |  |  | -1802.1481 |  |  | -4929.4713 |  |  | -10966.4845 |  |  | -19555.4102 |  |  | -29131.1114 |  |  | -39275.5583 |  |  | -50881.4397
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -73.8316 |  |  | -13.4916 |  |  | -293.5889 |  |  | -1137.7096 |  |  | -2941.2182 |  |  | -5866.689 |  |  | -9408.0108 |  |  | -11601.195 |  |  | -12904.3125 |  |  | -15937.6897
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2076.6255 |  | 5500 | 1467.9332 |  | 5500 | 3523.6048 |  | 5500 | 6727.8529 |  | 5500 | 11064.8409 |  | 5500 | 16474.0403 |  | 5500 | 21984.6707 |  | 5500 | 26825.4762 |  | 5500 | 31143.5451 |  | 5500 | 35444.2594
[13 empty] | Next iteration flow rate |  |  | 2118.158 | Abs Value of | Flow this | 1482.6125 | Abs Value of | Flow this | 3558.8408 | Abs Value of | Flow this | 6795.1314 | Abs Value of | Flow this | 11175.4893 | Abs Value of | Flow this | 16638.7807 | Abs Value of | Flow this | 22204.5174 | Abs Value of | Flow this | 27093.731 | Abs Value of | Flow this | 31454.9805 | Abs Value of | Flow this | 35798.702 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -94.6068 |  |  | -17.3203 |  |  | -370.8227 |  |  | -1502.4831 |  |  | -4160.9684 |  |  | -9292.9327 |  |  | -16594.2353 |  |  | -24734.3793 |  |  | -33358.0045 |  |  | -43223.9709
[13 empty] | P2 at this iteration flow rate |  |  | 54.9614 |  |  | 39.5041 |  |  | 110.2045 |  |  | 336.5366 |  |  | 868.2337 |  |  | 1894.6265 |  |  | 3354.8871 |  |  | 4982.9159 |  |  | 6707.6409 |  |  | 8680.8342
[13 empty] | Delta P at this iteration flow rate |  |  | -149.5681 |  |  | -56.8243 |  |  | -481.0273 |  |  | -1839.0197 |  |  | -5029.2021 |  |  | -11187.5593 |  |  | -19949.1223 |  |  | -29717.2952 |  |  | -40065.6454 |  |  | -51904.805
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -78.7038 |  |  | -14.7025 |  |  | -300.4086 |  |  | -1161.4548 |  |  | -3001.1554 |  |  | -5985.3405 |  |  | -9597.7684 |  |  | -11834.9222 |  |  | -13164.1372 |  |  | -16258.4643
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2118.158 |  | 5500 | 1482.6125 |  | 5500 | 3558.8408 |  | 5500 | 6795.1314 |  | 5500 | 11175.4893 |  | 5500 | 16638.7807 |  | 5500 | 22204.5174 |  | 5500 | 27093.731 |  | 5500 | 31454.9805 |  | 5500 | 35798.702
[13 empty] | Next iteration flow rate |  |  | 2160.5211 | Abs Value of | Flow this | 1497.4387 | Abs Value of | Flow this | 3594.4292 | Abs Value of | Flow this | 6863.0827 | Abs Value of | Flow this | 11287.2442 | Abs Value of | Flow this | 16805.1685 | Abs Value of | Flow this | 22426.5626 | Abs Value of | Flow this | 27364.6683 | Abs Value of | Flow this | 31769.5303 | Abs Value of | Flow this | 36156.689 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -100.7283 |  |  | -18.8124 |  |  | -379.4203 |  |  | -1533.827 |  |  | -4245.7479 |  |  | -9480.8647 |  |  | -16928.9234 |  |  | -25232.6843 |  |  | -34029.6444 |  |  | -44093.9167
[13 empty] | P2 at this iteration flow rate |  |  | 56.1857 |  |  | 39.8025 |  |  | 111.9241 |  |  | 342.8054 |  |  | 885.1896 |  |  | 1932.2129 |  |  | 3421.8247 |  |  | 5082.5769 |  |  | 6841.9689 |  |  | 8854.8233
[13 empty] | Delta P at this iteration flow rate |  |  | -156.9139 |  |  | -58.6149 |  |  | -491.3443 |  |  | -1876.6324 |  |  | -5130.9375 |  |  | -11413.0776 |  |  | -20350.7481 |  |  | -30315.2612 |  |  | -40871.6133 |  |  | -52948.74
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -83.7727 |  |  | -15.9377 |  |  | -307.3653 |  |  | -1185.6773 |  |  | -3062.2973 |  |  | -6106.377 |  |  | -9791.34 |  |  | -12073.3473 |  |  | -13429.1843 |  |  | -16585.6864
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2160.5211 |  | 5500 | 1497.4387 |  | 5500 | 3594.4292 |  | 5500 | 6863.0827 |  | 5500 | 11287.2442 |  | 5500 | 16805.1685 |  | 5500 | 22426.5626 |  | 5500 | 27364.6683 |  | 5500 | 31769.5303 |  | 5500 | 36156.689
[13 empty] | Next iteration flow rate |  |  | 2203.7316 | Abs Value of | Flow this | 1512.4131 | Abs Value of | Flow this | 3630.3735 | Abs Value of | Flow this | 6931.7135 | Abs Value of | Flow this | 11400.1166 | Abs Value of | Flow this | 16973.2202 | Abs Value of | Flow this | 22650.8282 | Abs Value of | Flow this | 27638.315 | Abs Value of | Flow this | 32087.2257 | Abs Value of | Flow this | 36518.2559 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -107.0971 |  |  | -20.3346 |  |  | -388.1906 |  |  | -1565.8009 |  |  | -4332.2314 |  |  | -9672.5741 |  |  | -17270.3388 |  |  | -25741.0053 |  |  | -34714.7843 |  |  | -44981.3484
[13 empty] | P2 at this iteration flow rate |  |  | 57.4594 |  |  | 40.1069 |  |  | 113.6781 |  |  | 349.2002 |  |  | 902.4863 |  |  | 1970.5548 |  |  | 3490.1078 |  |  | 5184.2411 |  |  | 6978.9969 |  |  | 9032.3097
[13 empty] | Delta P at this iteration flow rate |  |  | -164.5565 |  |  | -60.4415 |  |  | -501.8688 |  |  | -1915.0011 |  |  | -5234.7177 |  |  | -11643.1289 |  |  | -20760.4465 |  |  | -30925.2464 |  |  | -41693.7812 |  |  | -54013.6581
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -89.0464 |  |  | -17.1978 |  |  | -314.4619 |  |  | -1210.3867 |  |  | -3124.6681 |  |  | -6229.8462 |  |  | -9988.8025 |  |  | -12316.5647 |  |  | -13699.5588 |  |  | -16919.4856
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2203.7316 |  | 5500 | 1512.4131 |  | 5500 | 3630.3735 |  | 5500 | 6931.7135 |  | 5500 | 11400.1166 |  | 5500 | 16973.2202 |  | 5500 | 22650.8282 |  | 5500 | 27638.315 |  | 5500 | 32087.2257 |  | 5500 | 36518.2559
[13 empty] | Next iteration flow rate |  |  | 2247.8062 | Abs Value of | Flow this | 1527.5372 | Abs Value of | Flow this | 3666.6772 | Abs Value of | Flow this | 7001.0307 | Abs Value of | Flow this | 11514.1178 | Abs Value of | Flow this | 17142.9524 | Abs Value of | Flow this | 22877.3365 | Abs Value of | Flow this | 27914.6981 | Abs Value of | Flow this | 32408.0979 | Abs Value of | Flow this | 36883.4385 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -113.7233 |  |  | -21.8873 |  |  | -397.1373 |  |  | -1598.4175 |  |  | -4420.4533 |  |  | -9868.1368 |  |  | -17618.6166 |  |  | -26259.5435 |  |  | -35413.6955 |  |  | -45886.6176
[13 empty] | P2 at this iteration flow rate |  |  | 58.7847 |  |  | 40.4175 |  |  | 115.4675 |  |  | 355.7235 |  |  | 920.1307 |  |  | 2009.6674 |  |  | 3559.7633 |  |  | 5287.9487 |  |  | 7118.7791 |  |  | 9213.3635
[13 empty] | Delta P at this iteration flow rate |  |  | -172.5079 |  |  | -62.3048 |  |  | -512.6047 |  |  | -1954.141 |  |  | -5340.584 |  |  | -11877.8042 |  |  | -21178.3799 |  |  | -31547.4922 |  |  | -42532.4746 |  |  | -55099.9811
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -94.5332 |  |  | -18.4832 |  |  | -321.7011 |  |  | -1235.5927 |  |  | -3188.2926 |  |  | -6355.7972 |  |  | -10190.234 |  |  | -12564.6708 |  |  | -13975.368 |  |  | -17259.9943
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2247.8062 |  | 5500 | 1527.5372 |  | 5500 | 3666.6772 |  | 5500 | 7001.0307 |  | 5500 | 11514.1178 |  | 5500 | 17142.9524 |  | 5500 | 22877.3365 |  | 5500 | 27914.6981 |  | 5500 | 32408.0979 |  | 5500 | 36883.4385
[13 empty] | Next iteration flow rate |  |  | 2292.7623 | Abs Value of | Flow this | 1542.8126 | Abs Value of | Flow this | 3703.344 | Abs Value of | Flow this | 7071.041 | Abs Value of | Flow this | 11629.259 | Abs Value of | Flow this | 17314.382 | Abs Value of | Flow this | 23106.1098 | Abs Value of | Flow this | 28193.8451 | Abs Value of | Flow this | 32732.1789 | Abs Value of | Flow this | 37252.2728 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -120.6171 |  |  | -23.4712 |  |  | -406.2638 |  |  | -1631.6897 |  |  | -4510.4484 |  |  | -10067.6304 |  |  | -17973.8948 |  |  | -26788.5044 |  |  | -36126.6548 |  |  | -46810.0826
[13 empty] | P2 at this iteration flow rate |  |  | 60.1634 |  |  | 40.7342 |  |  | 117.2928 |  |  | 362.3779 |  |  | 938.1297 |  |  | 2049.5661 |  |  | 3630.819 |  |  | 5393.7409 |  |  | 7261.371 |  |  | 9398.0565
[13 empty] | Delta P at this iteration flow rate |  |  | -180.7805 |  |  | -64.2055 |  |  | -523.5565 |  |  | -1994.0677 |  |  | -5448.5781 |  |  | -12117.1965 |  |  | -21604.7138 |  |  | -32182.2452 |  |  | -43388.0257 |  |  | -56208.1391
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -100.2417 |  |  | -19.7944 |  |  | -329.0858 |  |  | -1261.3054 |  |  | -3253.196 |  |  | -6484.2799 |  |  | -10395.7142 |  |  | -12817.7638 |  |  | -14256.7208 |  |  | -17607.3472
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2292.7623 |  | 5500 | 1542.8126 |  | 5500 | 3703.344 |  | 5500 | 7071.041 |  | 5500 | 11629.259 |  | 5500 | 17314.382 |  | 5500 | 23106.1098 |  | 5500 | 28193.8451 |  | 5500 | 32732.1789 |  | 5500 | 37252.2728
[13 empty] | Next iteration flow rate |  |  | 2338.6176 | Abs Value of | Flow this | 1558.2407 | Abs Value of | Flow this | 3740.3775 | Abs Value of | Flow this | 7141.7514 | Abs Value of | Flow this | 11745.5516 | Abs Value of | Flow this | 17487.5258 | Abs Value of | Flow this | 23337.1709 | Abs Value of | Flow this | 28475.7835 | Abs Value of | Flow this | 33059.5007 | Abs Value of | Flow this | 37624.7956 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -127.7894 |  |  | -25.087 |  |  | -415.5737 |  |  | -1665.6307 |  |  | -4602.2524 |  |  | -10271.1338 |  |  | -18336.3141 |  |  | -27328.0973 |  |  | -36853.9445 |  |  | -47752.1093
[13 empty] | P2 at this iteration flow rate |  |  | 61.5979 |  |  | 41.0574 |  |  | 119.1547 |  |  | 369.1661 |  |  | 956.4905 |  |  | 2090.2668 |  |  | 3703.3028 |  |  | 5501.6595 |  |  | 7406.8289 |  |  | 9586.4619
[13 empty] | Delta P at this iteration flow rate |  |  | -189.3873 |  |  | -66.1444 |  |  | -534.7284 |  |  | -2034.7969 |  |  | -5558.7429 |  |  | -12361.4005 |  |  | -22039.6169 |  |  | -32829.7568 |  |  | -44260.7735 |  |  | -57338.5711
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -106.1807 |  |  | -21.132 |  |  | -336.619 |  |  | -1287.5349 |  |  | -3319.4039 |  |  | -6615.345 |  |  | -10605.3246 |  |  | -13075.944 |  |  | -14543.7289 |  |  | -17961.6818
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2338.6176 |  | 5500 | 1558.2407 |  | 5500 | 3740.3775 |  | 5500 | 7141.7514 |  | 5500 | 11745.5516 |  | 5500 | 17487.5258 |  | 5500 | 23337.1709 |  | 5500 | 28475.7835 |  | 5500 | 33059.5007 |  | 5500 | 37624.7956
[13 empty] | Next iteration flow rate |  |  | 2385.3899 | Abs Value of | Flow this | 1573.8231 | Abs Value of | Flow this | 3777.7812 | Abs Value of | Flow this | 7213.1689 | Abs Value of | Flow this | 11863.0071 | Abs Value of | Flow this | 17662.401 | Abs Value of | Flow this | 23570.5427 | Abs Value of | Flow this | 28760.5414 | Abs Value of | Flow this | 33390.0957 | Abs Value of | Flow this | 38001.0435 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -135.2515 |  |  | -26.7353 |  |  | -425.0707 |  |  | -1700.2539 |  |  | -4695.9017 |  |  | -10478.7276 |  |  | -18706.018 |  |  | -27878.5361 |  |  | -37595.8528 |  |  | -48713.0707
[13 empty] | P2 at this iteration flow rate |  |  | 63.0903 |  |  | 41.3871 |  |  | 121.0541 |  |  | 376.0908 |  |  | 975.2203 |  |  | 2131.7855 |  |  | 3777.2436 |  |  | 5611.7472 |  |  | 7555.2106 |  |  | 9778.6541
[13 empty] | Delta P at this iteration flow rate |  |  | -198.3418 |  |  | -68.1224 |  |  | -546.1249 |  |  | -2076.3447 |  |  | -5671.1221 |  |  | -12610.5131 |  |  | -22483.2616 |  |  | -33490.2833 |  |  | -45151.0634 |  |  | -58491.7248
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -112.3598 |  |  | -22.4965 |  |  | -344.3036 |  |  | -1314.2916 |  |  | -3386.9426 |  |  | -6749.0445 |  |  | -10819.1482 |  |  | -13339.3136 |  |  | -14836.5058 |  |  | -18323.1386
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2385.3899 |  | 5500 | 1573.8231 |  | 5500 | 3777.7812 |  | 5500 | 7213.1689 |  | 5500 | 11863.0071 |  | 5500 | 17662.401 |  | 5500 | 23570.5427 |  | 5500 | 28760.5414 |  | 5500 | 33390.0957 |  | 5500 | 38001.0435
[13 empty] | Next iteration flow rate |  |  | 2433.0977 | Abs Value of | Flow this | 1589.5613 | Abs Value of | Flow this | 3815.559 | Abs Value of | Flow this | 7285.3006 | Abs Value of | Flow this | 11981.6372 | Abs Value of | Flow this | 17839.025 | Abs Value of | Flow this | 23806.2481 | Abs Value of | Flow this | 29048.1468 | Abs Value of | Flow this | 33723.9966 | Abs Value of | Flow this | 38381.054 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -143.0151 |  |  | -28.4167 |  |  | -434.7587 |  |  | -1735.573 |  |  | -4791.4334 |  |  | -10690.494 |  |  | -19083.153 |  |  | -28440.0387 |  |  | -38352.6735 |  |  | -49693.3474
[13 empty] | P2 at this iteration flow rate |  |  | 64.643 |  |  | 41.7233 |  |  | 122.9917 |  |  | 383.1546 |  |  | 994.3267 |  |  | 2174.1388 |  |  | 3852.6706 |  |  | 5724.0477 |  |  | 7706.5747 |  |  | 9974.7095
[13 empty] | Delta P at this iteration flow rate |  |  | -207.6581 |  |  | -70.14 |  |  | -557.7504 |  |  | -2118.7276 |  |  | -5785.76 |  |  | -12864.6328 |  |  | -22935.8236 |  |  | -34164.0864 |  |  | -46059.2482 |  |  | -59668.0569
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -118.7884 |  |  | -23.8884 |  |  | -352.1426 |  |  | -1341.5861 |  |  | -3455.8388 |  |  | -6885.4314 |  |  | -11037.2696 |  |  | -13607.977 |  |  | -15135.1675 |  |  | -18691.8607
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2433.0977 |  | 5500 | 1589.5613 |  | 5500 | 3815.559 |  | 5500 | 7285.3006 |  | 5500 | 11981.6372 |  | 5500 | 17839.025 |  | 5500 | 23806.2481 |  | 5500 | 29048.1468 |  | 5500 | 33723.9966 |  | 5500 | 38381.054
[13 empty] | Next iteration flow rate |  |  | 2481.7597 | Abs Value of | Flow this | 1605.4569 | Abs Value of | Flow this | 3853.7146 | Abs Value of | Flow this | 7358.1536 | Abs Value of | Flow this | 12101.4535 | Abs Value of | Flow this | 18017.4153 | Abs Value of | Flow this | 24044.3106 | Abs Value of | Flow this | 29338.6283 | Abs Value of | Flow this | 34061.2366 | Abs Value of | Flow this | 38764.8645 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -151.0923 |  |  | -30.1319 |  |  | -444.6413 |  |  | -1771.6021 |  |  | -4888.8852 |  |  | -10906.517 |  |  | -19467.8684 |  |  | -29012.8275 |  |  | -39124.7063 |  |  | -50693.3277
[13 empty] | P2 at this iteration flow rate |  |  | 66.2585 |  |  | 42.0664 |  |  | 124.9683 |  |  | 390.3604 |  |  | 1013.817 |  |  | 2217.3434 |  |  | 3929.6137 |  |  | 5838.6055 |  |  | 7860.9813 |  |  | 10174.7055
[13 empty] | Delta P at this iteration flow rate |  |  | -217.3508 |  |  | -72.1983 |  |  | -569.6096 |  |  | -2161.9625 |  |  | -5902.7022 |  |  | -13123.8603 |  |  | -23397.4821 |  |  | -34851.433 |  |  | -46985.6875 |  |  | -60868.0332
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -125.4768 |  |  | -25.3083 |  |  | -360.1392 |  |  | -1369.4292 |  |  | -3526.1198 |  |  | -7024.5597 |  |  | -11259.7753 |  |  | -13882.0405 |  |  | -15439.8324 |  |  | -19067.9941
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2481.7597 |  | 5500 | 1605.4569 |  | 5500 | 3853.7146 |  | 5500 | 7358.1536 |  | 5500 | 12101.4535 |  | 5500 | 18017.4153 |  | 5500 | 24044.3106 |  | 5500 | 29338.6283 |  | 5500 | 34061.2366 |  | 5500 | 38764.8645
[13 empty] | Next iteration flow rate |  |  | 2531.3949 | Abs Value of | Flow this | 1621.5115 | Abs Value of | Flow this | 3892.2518 | Abs Value of | Flow this | 7431.7351 | Abs Value of | Flow this | 12222.4681 | Abs Value of | Flow this | 18197.5895 | Abs Value of | Flow this | 24284.7537 | Abs Value of | Flow this | 29632.0145 | Abs Value of | Flow this | 34401.849 | Abs Value of | Flow this | 39152.5132 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -159.4959 |  |  | -31.8815 |  |  | -454.7226 |  |  | -1808.3553 |  |  | -4988.2958 |  |  | -11126.882 |  |  | -19860.3166 |  |  | -29597.1293 |  |  | -39912.2569 |  |  | -51713.4076
[13 empty] | P2 at this iteration flow rate |  |  | 67.9392 |  |  | 42.4163 |  |  | 126.9845 |  |  | 397.7111 |  |  | 1033.6992 |  |  | 2261.4164 |  |  | 4008.1033 |  |  | 5955.4659 |  |  | 8018.4914 |  |  | 10378.7215
[13 empty] | Delta P at this iteration flow rate |  |  | -227.4351 |  |  | -74.2979 |  |  | -581.7072 |  |  | -2206.0663 |  |  | -6021.995 |  |  | -13388.2984 |  |  | -23868.4199 |  |  | -35552.5952 |  |  | -47930.7482 |  |  | -62092.1291
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -132.4353 |  |  | -26.7567 |  |  | -368.2965 |  |  | -1397.832 |  |  | -3597.8135 |  |  | -7166.4844 |  |  | -11486.7533 |  |  | -14161.6126 |  |  | -15750.621 |  |  | -19451.6877
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2531.3949 |  | 5500 | 1621.5115 |  | 5500 | 3892.2518 |  | 5500 | 7431.7351 |  | 5500 | 12222.4681 |  | 5500 | 18197.5895 |  | 5500 | 24284.7537 |  | 5500 | 29632.0145 |  | 5500 | 34401.849 |  | 5500 | 39152.5132
[13 empty] | Next iteration flow rate |  |  | 2582.0228 | Abs Value of | Flow this | 1637.7266 | Abs Value of | Flow this | 3931.1743 | Abs Value of | Flow this | 7506.0525 | Abs Value of | Flow this | 12344.6928 | Abs Value of | Flow this | 18379.5653 | Abs Value of | Flow this | 24527.6012 | Abs Value of | Flow this | 29928.3347 | Abs Value of | Flow this | 34745.8675 | Abs Value of | Flow this | 39544.0383 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -168.2389 |  |  | -33.6664 |  |  | -465.0066 |  |  | -1845.8472 |  |  | -5089.7046 |  |  | -11351.6763 |  |  | -20260.6529 |  |  | -30193.1756 |  |  | -40715.6372 |  |  | -52753.9911
[13 empty] | P2 at this iteration flow rate |  |  | 69.6878 |  |  | 42.7733 |  |  | 129.0413 |  |  | 405.2094 |  |  | 1053.9809 |  |  | 2306.3753 |  |  | 4088.1706 |  |  | 6074.6751 |  |  | 8179.1674 |  |  | 10586.8382
[13 empty] | Delta P at this iteration flow rate |  |  | -237.9267 |  |  | -76.4397 |  |  | -594.0479 |  |  | -2251.0567 |  |  | -6143.6855 |  |  | -13658.0516 |  |  | -24348.8235 |  |  | -36267.8508 |  |  | -48894.8047 |  |  | -63340.8293
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -139.6751 |  |  | -28.2342 |  |  | -376.6178 |  |  | -1426.8057 |  |  | -3670.9482 |  |  | -7311.2619 |  |  | -11718.2936 |  |  | -14446.8042 |  |  | -16067.6564 |  |  | -19843.0936
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2582.0228 |  | 5500 | 1637.7266 |  | 5500 | 3931.1743 |  | 5500 | 7506.0525 |  | 5500 | 12344.6928 |  | 5500 | 18379.5653 |  | 5500 | 24527.6012 |  | 5500 | 29928.3347 |  | 5500 | 34745.8675 |  | 5500 | 39544.0383
[13 empty] | Next iteration flow rate |  |  | 2633.6632 | Abs Value of | Flow this | 1654.1039 | Abs Value of | Flow this | 3970.486 | Abs Value of | Flow this | 7581.113 | Abs Value of | Flow this | 12468.1397 | Abs Value of | Flow this | 18563.361 | Abs Value of | Flow this | 24772.8772 | Abs Value of | Flow this | 30227.618 | Abs Value of | Flow this | 35093.3261 | Abs Value of | Flow this | 39939.4787 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -177.3352 |  |  | -35.4871 |  |  | -475.4972 |  |  | -1884.0928 |  |  | -5193.1516 |  |  | -11580.989 |  |  | -20669.0361 |  |  | -30801.2025 |  |  | -41535.1656 |  |  | -53815.4903
[13 empty] | P2 at this iteration flow rate |  |  | 71.507 |  |  | 43.1374 |  |  | 131.1394 |  |  | 412.8586 |  |  | 1074.6703 |  |  | 2352.2378 |  |  | 4169.8472 |  |  | 6196.2805 |  |  | 8343.0731 |  |  | 10799.1381
[13 empty] | Delta P at this iteration flow rate |  |  | -248.8422 |  |  | -78.6245 |  |  | -606.6367 |  |  | -2296.9513 |  |  | -6267.822 |  |  | -13933.2268 |  |  | -24838.8833 |  |  | -36997.483 |  |  | -49878.2387 |  |  | -64614.6284
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -147.2072 |  |  | -29.7415 |  |  | -385.1063 |  |  | -1456.3617 |  |  | -3745.5529 |  |  | -7458.9493 |  |  | -11954.4878 |  |  | -14737.7281 |  |  | -16391.0643 |  |  | -20242.3668
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2633.6632 |  | 5500 | 1654.1039 |  | 5500 | 3970.486 |  | 5500 | 7581.113 |  | 5500 | 12468.1397 |  | 5500 | 18563.361 |  | 5500 | 24772.8772 |  | 5500 | 30227.618 |  | 5500 | 35093.3261 |  | 5500 | 39939.4787
[13 empty] | Next iteration flow rate |  |  | 2686.3365 | Abs Value of | Flow this | 1670.6449 | Abs Value of | Flow this | 4010.1909 | Abs Value of | Flow this | 7656.9241 | Abs Value of | Flow this | 12592.8211 | Abs Value of | Flow this | 18748.9946 | Abs Value of | Flow this | 25020.606 | Abs Value of | Flow this | 30529.8942 | Abs Value of | Flow this | 35444.2594 | Abs Value of | Flow this | 40338.8735 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -186.7989 |  |  | -37.3444 |  |  | -486.1987 |  |  | -1923.1071 |  |  | -5298.678 |  |  | -11814.9109 |  |  | -21085.6277 |  |  | -31421.4507 |  |  | -42371.1664 |  |  | -54898.3257
[13 empty] | P2 at this iteration flow rate |  |  | 73.3998 |  |  | 43.5089 |  |  | 133.2797 |  |  | 420.6614 |  |  | 1095.7756 |  |  | 2399.0222 |  |  | 4253.1655 |  |  | 6320.3301 |  |  | 8510.2733 |  |  | 11015.7051
[13 empty] | Delta P at this iteration flow rate |  |  | -260.1987 |  |  | -80.8533 |  |  | -619.4785 |  |  | -2343.7685 |  |  | -6394.4536 |  |  | -14213.9331 |  |  | -25338.7933 |  |  | -37741.7808 |  |  | -50881.4397 |  |  | -65914.0309
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -155.0437 |  |  | -31.279 |  |  | -393.7655 |  |  | -1486.5119 |  |  | -3821.6572 |  |  | -7609.6053 |  |  | -12195.4296 |  |  | -15034.4996 |  |  | -16720.9726 |  |  | -20649.6654
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2686.3365 |  | 5500 | 1670.6449 |  | 5500 | 4010.1909 |  | 5500 | 7656.9241 |  | 5500 | 12592.8211 |  | 5500 | 18748.9946 |  | 5500 | 25020.606 |  | 5500 | 30529.8942 |  | 5500 | 35444.2594 |  | 5500 | 40338.8735
[13 empty] | Next iteration flow rate |  |  | 2740.0632 | Abs Value of | Flow this | 1687.3514 | Abs Value of | Flow this | 4050.2928 | Abs Value of | Flow this | 7733.4934 | Abs Value of | Flow this | 12718.7493 | Abs Value of | Flow this | 18936.4846 | Abs Value of | Flow this | 25270.812 | Abs Value of | Flow this | 30835.1932 | Abs Value of | Flow this | 35798.702 | Abs Value of | Flow this | 40742.2622 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -196.645 |  |  | -39.239 |  |  | -497.1153 |  |  | -1962.9055 |  |  | -5406.3254 |  |  | -12053.5346 |  |  | -21510.5929 |  |  | -32054.1658 |  |  | -43223.9709 |  |  | -56002.9261
[13 empty] | P2 at this iteration flow rate |  |  | 75.369 |  |  | 43.8878 |  |  | 135.4631 |  |  | 428.6211 |  |  | 1117.3051 |  |  | 2446.7469 |  |  | 4338.1586 |  |  | 6446.8732 |  |  | 8680.8342 |  |  | 11236.6252
[13 empty] | Delta P at this iteration flow rate |  |  | -272.014 |  |  | -83.1268 |  |  | -632.5784 |  |  | -2391.5266 |  |  | -6523.6305 |  |  | -14500.2816 |  |  | -25848.7514 |  |  | -38501.039 |  |  | -51904.805 |  |  | -67239.5513
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -163.1968 |  |  | -32.8474 |  |  | -402.5987 |  |  | -1517.268 |  |  | -3899.2912 |  |  | -7763.2895 |  |  | -12441.2143 |  |  | -15337.2362 |  |  | -17057.5121 |  |  | -21065.1506
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2740.0632 |  | 5500 | 1687.3514 |  | 5500 | 4050.2928 |  | 5500 | 7733.4934 |  | 5500 | 12718.7493 |  | 5500 | 18936.4846 |  | 5500 | 25270.812 |  | 5500 | 30835.1932 |  | 5500 | 35798.702 |  | 5500 | 40742.2622
[13 empty] | Next iteration flow rate |  |  | 2794.8645 | Abs Value of | Flow this | 1704.2249 | Abs Value of | Flow this | 4090.7957 | Abs Value of | Flow this | 7810.8283 | Abs Value of | Flow this | 12845.9368 | Abs Value of | Flow this | 19125.8494 | Abs Value of | Flow this | 25523.5202 | Abs Value of | Flow this | 31143.5451 | Abs Value of | Flow this | 36156.689 | Abs Value of | Flow this | 41149.6848 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -206.8889 |  |  | -41.1717 |  |  | -508.2514 |  |  | -2003.5039 |  |  | -5516.1366 |  |  | -12296.9547 |  |  | -21944.0998 |  |  | -32699.5986 |  |  | -44093.9167 |  |  | -57129.7289
[13 empty] | P2 at this iteration flow rate |  |  | 77.4178 |  |  | 44.2743 |  |  | 137.6903 |  |  | 436.7408 |  |  | 1139.2673 |  |  | 2495.4309 |  |  | 4424.86 |  |  | 6575.9597 |  |  | 8854.8233 |  |  | 11461.9858
[13 empty] | Delta P at this iteration flow rate |  |  | -284.3067 |  |  | -85.4461 |  |  | -645.9416 |  |  | -2440.2447 |  |  | -6655.4039 |  |  | -14792.3856 |  |  | -26368.9597 |  |  | -39275.5583 |  |  | -52948.74 |  |  | -68591.7147
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -171.6793 |  |  | -34.4474 |  |  | -411.6095 |  |  | -1548.6424 |  |  | -3978.4856 |  |  | -7920.0627 |  |  | -12691.9392 |  |  | -15646.0578 |  |  | -17400.8161 |  |  | -21488.9871
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2794.8645 |  | 5500 | 1704.2249 |  | 5500 | 4090.7957 |  | 5500 | 7810.8283 |  | 5500 | 12845.9368 |  | 5500 | 19125.8494 |  | 5500 | 25523.5202 |  | 5500 | 31143.5451 |  | 5500 | 36156.689 |  | 5500 | 41149.6848
[13 empty] | Next iteration flow rate |  |  | 2850.7618 | Abs Value of | Flow this | 1721.2671 | Abs Value of | Flow this | 4131.7037 | Abs Value of | Flow this | 7888.9366 | Abs Value of | Flow this | 12974.3962 | Abs Value of | Flow this | 19317.1079 | Abs Value of | Flow this | 25778.7554 | Abs Value of | Flow this | 31454.9805 | Abs Value of | Flow this | 36518.2559 | Abs Value of | Flow this | 41561.1817 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -217.5466 |  |  | -43.1433 |  |  | -519.6112 |  |  | -2044.9184 |  |  | -5628.155 |  |  | -12545.2675 |  |  | -22386.3202 |  |  | -33358.0045 |  |  | -44981.3484 |  |  | -58279.1805
[13 empty] | P2 at this iteration flow rate |  |  | 79.5493 |  |  | 44.6687 |  |  | 139.9622 |  |  | 445.0237 |  |  | 1161.671 |  |  | 2545.0935 |  |  | 4513.304 |  |  | 6707.6409 |  |  | 9032.3097 |  |  | 11691.8761
[13 empty] | Delta P at this iteration flow rate |  |  | -297.096 |  |  | -87.812 |  |  | -659.5735 |  |  | -2489.9421 |  |  | -6789.826 |  |  | -15090.361 |  |  | -26899.6243 |  |  | -40065.6454 |  |  | -54013.6581 |  |  | -69971.0566
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -180.5044 |  |  | -36.0795 |  |  | -420.8014 |  |  | -1580.6473 |  |  | -4059.2718 |  |  | -8079.9871 |  |  | -12947.7037 |  |  | -15961.0867 |  |  | -17751.0205 |  |  | -21921.3427
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2850.7618 |  | 5500 | 1721.2671 |  | 5500 | 4131.7037 |  | 5500 | 7888.9366 |  | 5500 | 12974.3962 |  | 5500 | 19317.1079 |  | 5500 | 25778.7554 |  | 5500 | 31454.9805 |  | 5500 | 36518.2559 |  | 5500 | 41561.1817
[13 empty] | Next iteration flow rate |  |  | 2907.777 | Abs Value of | Flow this | 1738.4798 | Abs Value of | Flow this | 4173.0207 | Abs Value of | Flow this | 7967.826 | Abs Value of | Flow this | 13104.1401 | Abs Value of | Flow this | 19510.279 | Abs Value of | Flow this | 26036.5429 | Abs Value of | Flow this | 31769.5303 | Abs Value of | Flow this | 36883.4385 | Abs Value of | Flow this | 41976.7935 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -228.6349 |  |  | -45.1545 |  |  | -531.1994 |  |  | -2087.1653 |  |  | -5742.4249 |  |  | -12798.5714 |  |  | -22837.4293 |  |  | -34029.6444 |  |  | -45886.6176 |  |  | -59451.736
[13 empty] | P2 at this iteration flow rate |  |  | 81.767 |  |  | 45.0709 |  |  | 142.2799 |  |  | 453.4731 |  |  | 1184.525 |  |  | 2595.7543 |  |  | 4603.5259 |  |  | 6841.9689 |  |  | 9213.3635 |  |  | 11926.3872
[13 empty] | Delta P at this iteration flow rate |  |  | -310.4019 |  |  | -90.2254 |  |  | -673.4793 |  |  | -2540.6383 |  |  | -6926.9499 |  |  | -15394.3257 |  |  | -27440.9551 |  |  | -40871.6133 |  |  | -55099.9811 |  |  | -71378.1232
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -189.6861 |  |  | -37.7444 |  |  | -430.178 |  |  | -1613.2956 |  |  | -4141.6819 |  |  | -8243.1259 |  |  | -13208.6091 |  |  | -16282.4477 |  |  | -18108.264 |  |  | -22362.3887
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2907.777 |  | 5500 | 1738.4798 |  | 5500 | 4173.0207 |  | 5500 | 7967.826 |  | 5500 | 13104.1401 |  | 5500 | 19510.279 |  | 5500 | 26036.5429 |  | 5500 | 31769.5303 |  | 5500 | 36883.4385 |  | 5500 | 41976.7935
[13 empty] | Next iteration flow rate |  |  | 2965.9325 | Abs Value of | Flow this | 1755.8646 | Abs Value of | Flow this | 4214.7509 | Abs Value of | Flow this | 8047.5042 | Abs Value of | Flow this | 13235.1815 | Abs Value of | Flow this | 19705.3818 | Abs Value of | Flow this | 26296.9084 | Abs Value of | Flow this | 32087.2257 | Abs Value of | Flow this | 37252.2728 | Abs Value of | Flow this | 42396.5614 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -240.1712 |  |  | -47.2061 |  |  | -543.0206 |  |  | -2130.2613 |  |  | -5858.9916 |  |  | -13056.9667 |  |  | -23297.6056 |  |  | -34714.7843 |  |  | -46810.0826 |  |  | -60647.8599
[13 empty] | P2 at this iteration flow rate |  |  | 84.0742 |  |  | 45.4812 |  |  | 144.6441 |  |  | 462.0923 |  |  | 1207.8383 |  |  | 2647.4333 |  |  | 4695.5611 |  |  | 6978.9969 |  |  | 9398.0565 |  |  | 12165.612
[13 empty] | Delta P at this iteration flow rate |  |  | -324.2454 |  |  | -92.6874 |  |  | -687.6647 |  |  | -2592.3536 |  |  | -7066.83 |  |  | -15704.4 |  |  | -27993.1667 |  |  | -41693.7812 |  |  | -56208.1391 |  |  | -72813.4719
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -199.2387 |  |  | -39.4428 |  |  | -439.7431 |  |  | -1646.6001 |  |  | -4225.7484 |  |  | -8409.5438 |  |  | -13474.7587 |  |  | -16610.268 |  |  | -18472.688 |  |  | -22812.2997
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 2965.9325 |  | 5500 | 1755.8646 |  | 5500 | 4214.7509 |  | 5500 | 8047.5042 |  | 5500 | 13235.1815 |  | 5500 | 19705.3818 |  | 5500 | 26296.9084 |  | 5500 | 32087.2257 |  | 5500 | 37252.2728 |  | 5500 | 42396.5614
[13 empty] | Next iteration flow rate |  |  | 3025.2512 | Abs Value of | Flow this | 1773.4232 | Abs Value of | Flow this | 4256.8985 | Abs Value of | Flow this | 8127.9793 | Abs Value of | Flow this | 13367.5333 | Abs Value of | Flow this | 19902.4356 | Abs Value of | Flow this | 26559.8774 | Abs Value of | Flow this | 32408.0979 | Abs Value of | Flow this | 37624.7956 | Abs Value of | Flow this | 42820.527 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -252.1735 |  |  | -49.299 |  |  | -555.0793 |  |  | -2174.2236 |  |  | -5977.9014 |  |  | -13320.5557 |  |  | -23767.0315 |  |  | -35413.6955 |  |  | -47752.1093 |  |  | -61868.0259
[13 empty] | P2 at this iteration flow rate |  |  | 86.4747 |  |  | 45.8998 |  |  | 147.0559 |  |  | 470.8847 |  |  | 1231.6203 |  |  | 2700.1511 |  |  | 4789.4463 |  |  | 7118.7791 |  |  | 9586.4619 |  |  | 12409.6452
[13 empty] | Delta P at this iteration flow rate |  |  | -338.6482 |  |  | -95.1988 |  |  | -702.1351 |  |  | -2645.1083 |  |  | -7209.5217 |  |  | -16020.7069 |  |  | -28556.4778 |  |  | -42532.4746 |  |  | -57338.5711 |  |  | -74277.6711
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -209.1773 |  |  | -41.1753 |  |  | -449.5005 |  |  | -1680.574 |  |  | -4311.5046 |  |  | -8579.3068 |  |  | -13746.2579 |  |  | -16944.6775 |  |  | -18844.437 |  |  | -23271.2539
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 3025.2512 |  | 5500 | 1773.4232 |  | 5500 | 4256.8985 |  | 5500 | 8127.9793 |  | 5500 | 13367.5333 |  | 5500 | 19902.4356 |  | 5500 | 26559.8774 |  | 5500 | 32408.0979 |  | 5500 | 37624.7956 |  | 5500 | 42820.527
[13 empty] | Next iteration flow rate |  |  | 3085.7562 | Abs Value of | Flow this | 1791.1575 | Abs Value of | Flow this | 4299.4674 | Abs Value of | Flow this | 8209.259 | Abs Value of | Flow this | 13501.2087 | Abs Value of | Flow this | 20101.4599 | Abs Value of | Flow this | 26825.4762 | Abs Value of | Flow this | 32732.1789 | Abs Value of | Flow this | 38001.0435 | Abs Value of | Flow this | 43248.7323 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -264.6607 |  |  | -51.4339 |  |  | -567.3804 |  |  | -2219.0695 |  |  | -6099.2012 |  |  | -13589.4429 |  |  | -24245.8928 |  |  | -36126.6548 |  |  | -48713.0707 |  |  | -63112.7173
[13 empty] | P2 at this iteration flow rate |  |  | 88.9721 |  |  | 46.3268 |  |  | 149.5161 |  |  | 479.8539 |  |  | 1255.8802 |  |  | 2753.9286 |  |  | 4885.2186 |  |  | 7261.371 |  |  | 9778.6541 |  |  | 12658.5835
[13 empty] | Delta P at this iteration flow rate |  |  | -353.6329 |  |  | -97.7607 |  |  | -716.8965 |  |  | -2698.9234 |  |  | -7355.0815 |  |  | -16343.3715 |  |  | -29131.1114 |  |  | -43388.0257 |  |  | -58491.7248 |  |  | -75771.3007
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -219.5174 |  |  | -42.9427 |  |  | -459.4539 |  |  | -1715.2308 |  |  | -4398.9845 |  |  | -8752.4819 |  |  | -14023.2142 |  |  | -17285.8087 |  |  | -19223.6582 |  |  | -23739.4331
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 3085.7562 |  | 5500 | 1791.1575 |  | 5500 | 4299.4674 |  | 5500 | 8209.259 |  | 5500 | 13501.2087 |  | 5500 | 20101.4599 |  | 5500 | 26825.4762 |  | 5500 | 32732.1789 |  | 5500 | 38001.0435 |  | 5500 | 43248.7323
[13 empty] | Next iteration flow rate |  |  | 3147.4713 | Abs Value of | Flow this | 1809.0691 | Abs Value of | Flow this | 4342.4621 | Abs Value of | Flow this | 8291.3516 | Abs Value of | Flow this | 13636.2207 | Abs Value of | Flow this | 20302.4745 | Abs Value of | Flow this | 27093.731 | Abs Value of | Flow this | 33059.5007 | Abs Value of | Flow this | 38381.054 | Abs Value of | Flow this | 43681.2196 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -277.6524 |  |  | -53.6117 |  |  | -579.9287 |  |  | -2264.8168 |  |  | -6222.9392 |  |  | -13863.7347 |  |  | -24734.3793 |  |  | -36853.9445 |  |  | -49693.3474 |  |  | -64382.4269
[13 empty] | P2 at this iteration flow rate |  |  | 91.5705 |  |  | 46.7623 |  |  | 152.0257 |  |  | 489.0034 |  |  | 1280.6278 |  |  | 2808.7869 |  |  | 4982.9159 |  |  | 7406.8289 |  |  | 9974.7095 |  |  | 12912.5254
[13 empty] | Delta P at this iteration flow rate |  |  | -369.2229 |  |  | -100.3741 |  |  | -731.9545 |  |  | -2753.8201 |  |  | -7503.567 |  |  | -16672.5217 |  |  | -29717.2952 |  |  | -44260.7735 |  |  | -59668.0569 |  |  | -77294.9523
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -230.2752 |  |  | -44.7455 |  |  | -469.6075 |  |  | -1750.5842 |  |  | -4488.2227 |  |  | -8929.1379 |  |  | -14305.7374 |  |  | -17633.7966 |  |  | -19610.5017 |  |  | -24217.0227
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 3147.4713 |  | 5500 | 1809.0691 |  | 5500 | 4342.4621 |  | 5500 | 8291.3516 |  | 5500 | 13636.2207 |  | 5500 | 20302.4745 |  | 5500 | 27093.731 |  | 5500 | 33059.5007 |  | 5500 | 38381.054 |  | 5500 | 43681.2196
[13 empty] | Next iteration flow rate |  |  | 3210.4208 | Abs Value of | Flow this | 1827.1597 | Abs Value of | Flow this | 4385.8867 | Abs Value of | Flow this | 8374.2652 | Abs Value of | Flow this | 13772.583 | Abs Value of | Flow this | 20505.4993 | Abs Value of | Flow this | 27364.6683 | Abs Value of | Flow this | 33390.0957 | Abs Value of | Flow this | 38764.8645 | Abs Value of | Flow this | 44118.0318 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -291.169 |  |  | -55.8334 |  |  | -592.7293 |  |  | -2311.4836 |  |  | -6349.1643 |  |  | -14143.5398 |  |  | -25232.6843 |  |  | -37595.8528 |  |  | -50693.3277 |  |  | -65677.6577
[13 empty] | P2 at this iteration flow rate |  |  | 94.2738 |  |  | 47.2067 |  |  | 154.5859 |  |  | 498.3367 |  |  | 1305.8729 |  |  | 2864.748 |  |  | 5082.5769 |  |  | 7555.2106 |  |  | 10174.7055 |  |  | 13171.5715
[13 empty] | Delta P at this iteration flow rate |  |  | -385.4428 |  |  | -103.04 |  |  | -747.3152 |  |  | -2809.8203 |  |  | -7655.0371 |  |  | -17008.2878 |  |  | -30315.2612 |  |  | -45151.0634 |  |  | -60868.0332 |  |  | -78849.2292
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -241.4676 |  |  | -46.5846 |  |  | -479.9651 |  |  | -1786.6482 |  |  | -4579.2547 |  |  | -9109.3447 |  |  | -14593.9392 |  |  | -17988.7791 |  |  | -20005.1207 |  |  | -24704.2118
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 3210.4208 |  | 5500 | 1827.1597 |  | 5500 | 4385.8867 |  | 5500 | 8374.2652 |  | 5500 | 13772.583 |  | 5500 | 20505.4993 |  | 5500 | 27364.6683 |  | 5500 | 33390.0957 |  | 5500 | 38764.8645 |  | 5500 | 44118.0318
[13 empty] | Next iteration flow rate |  |  | 3274.6292 | Abs Value of | Flow this | 1845.4313 | Abs Value of | Flow this | 4429.7456 | Abs Value of | Flow this | 8458.0078 | Abs Value of | Flow this | 13910.3088 | Abs Value of | Flow this | 20710.5543 | Abs Value of | Flow this | 27638.315 | Abs Value of | Flow this | 33723.9966 | Abs Value of | Flow this | 39152.5132 | Abs Value of | Flow this | 44559.2121 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -305.2317 |  |  | -58.0996 |  |  | -605.7872 |  |  | -2359.0885 |  |  | -6477.9265 |  |  | -14428.969 |  |  | -25741.0053 |  |  | -38352.6735 |  |  | -51713.4076 |  |  | -66998.9226
[13 empty] | P2 at this iteration flow rate |  |  | 97.0863 |  |  | 47.6599 |  |  | 157.1974 |  |  | 507.8577 |  |  | 1331.6253 |  |  | 2921.8338 |  |  | 5184.2411 |  |  | 7706.5747 |  |  | 10378.7215 |  |  | 13435.8245
[13 empty] | Delta P at this iteration flow rate |  |  | -402.318 |  |  | -105.7595 |  |  | -762.9846 |  |  | -2866.9461 |  |  | -7809.5518 |  |  | -17350.8028 |  |  | -30925.2464 |  |  | -46059.2482 |  |  | -62092.1291 |  |  | -80434.7471
[13 empty] | Choked pressure drop w/ reducers | 3 |  | -253.1122 |  |  | -48.4607 |  |  | -490.5309 |  |  | -1823.4371 |  |  | -4672.1164 |  |  | -9293.1736 |  |  | -14887.9339 |  |  | -18350.8967 |  |  | -20407.6716 |  |  | -25201.1935
[13 empty] | C Non choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 7 |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_h - Selected C |  |  |  | 5500 | 3274.6292 |  | 5500 | 1845.4313 |  | 5500 | 4429.7456 |  | 5500 | 8458.0078 |  | 5500 | 13910.3088 |  | 5500 | 20710.5543 |  | 5500 | 27638.315 |  | 5500 | 33723.9966 |  | 5500 | 39152.5132 |  | 5500 | 44559.2121

## Installed Gain
Neles RE
3 inch
PV123
Qmax = maximum
[8 empty] | design flow = | 550
Qmin = minimum
[8 empty] | design flow = | 80
[8 empty] | Flow units are | gpm
Installed gain is based on installed flow as graphed above.
1.0 on the relative flow axis represents the maximum specified
design flow, Qmax, for the system being evaluated.
This makes it possible to compare valves of different sizes
and types when they are installed in the same system.
Graph Data
Valve relative travel, h | 0 | 0.05 | 0.1 | 0.15 | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.55 | 0.6 | 0.65 | 0.7 | 0.75 | 0.8 | 0.85 | 0.9 | 0.95 | 1
Relative flow Q/Qmax | 0 | 0.025688 | 0.051376 | 0.087349 | 0.12332 | 0.17939 | 0.23547 | 0.31136 | 0.38726 | 0.48191 | 0.57657 | 0.673 | 0.76943 | 0.85415 | 0.93886 | 1.0144 | 1.09 | 1.1652 | 1.2405 | 1.2986 | 1.3567 | 0.14545 | 0.14545 | 1 | 1
Gain = Delta Q / Delta h |  | 0.51376 | 0.61661 | 0.71946 | 0.92045 | 1.1214 | 1.3197 | 1.5179 | 1.7055 | 1.8931 | 1.9109 | 1.9286 | 1.8114 | 1.6942 | 1.6027 | 1.5113 | 1.5082 | 1.5052 | 1.3337 | 1.1622
Qmin vertical line | [21 empty] | 0 | 4
Qmax vertical line | [23 empty] | 0 | 4
Delta Q |  | 0.051376 | 0.061661 | 0.071946 | 0.092045 | 0.11214 | 0.13197 | 0.15179 | 0.17055 | 0.18931 | 0.19109 | 0.19286 | 0.18114 | 0.16942 | 0.16027 | 0.15113 | 0.15082 | 0.15052 | 0.13337 | 0.11622
Delta h |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
`
Qmax

## Typical FL
Intermediate calculations
Typical FL values based on the Cv reported on Line 15 of the Valve Sizing tab | [6 empty] | For initial calculations (before
for TURBULENT FLOW and the valve size entered in D12 of the Valve Sizing tab. | [6 empty] | the Cv is known), consider using |  | DESCRIPTION OF VARIABLE | NAME OF VARIABLE | FORMULA
[7 empty] | the FL values listed below. |  | CALCULATED IN COLUMN "O" | CALCULATED IN COLUMN "O"
| Flow | 80 | 213 | 423 | 550 |  | Minimum | Maximum
| Valve type | Liquid pressure recovery factor. FL |  |  |  |  | Flow | Flow | Valve Cv/Valve size squared (Turbulent flow) | Cv_over_d_Sq_T | 1.5732 | 4.3304 | 9.8418 | 15.063
| Globe, 4 port cage | 0.94 | 0.92299 | 0.91307 | 0.90419 |  | 0.94 | 0.92 | The value of "Cv_over_d_Sq_T" is taken from the Valve Sizing tab (S, T, U, V 628)
where Kv has been converted to Cv if the worksheet has been
| Globe, Parabolic plug | 0.91014 | 0.87907 | 0.84833 | 0.82421 |  | 0.93 | 0.88 | configured for Kv and valve size in mm has been converted
to inch if the worksheet has been configured for mm.
| Rotary eccentric plug | 0.90136 | 0.85373 | 0.7946 | 0.76 |  | 0.89 | 0.78
[9 empty] | Valve Cv/Valve size squared (NonTurbulent flow) | Cv_over_d_Sq_NT | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Segment ball | 0.92317 | 0.89366 | 0.83469 | 0.77883 |  | 0.93 | 0.72
The value of "Cv_over_d_Sq_NT" is calculated from the Non-turb flow coef. on
| Butterfly | 0.85651 | 0.82772 | 0.77063 | 0.71711 |  | 0.85 | 0.58 | Line 26 of the Valve Sizing tab converted to Cv if the worksheet has been configured
for Kv and Valve size in D12 of the Valve Sizing tab is converted to inch
| Full ball | 0.89869 | 0.87666 | 0.83424 | 0.79594 |  | 0.91 | 0.67 | if the worksheet has been configured for valve size in mm.
Typical FL values based on the Cv reported on Line 26 of the Valve Sizing tab
for NON-TURBULENT FLOW and the valve size entered in D12 of the Valve Sizing tab.
| Flow | 80 | 213 | 423 | 550
| Valve type | Liquid pressure recovery factor. FL
| Globe, 4 port cage |  |  |  |  | `
Globe, Parabolic plug
Rotary eccentric plug
Segment ball
Butterfly
Full ball

## Mass to Volumetric Flow
This tab calculates Volumetric Flow for use on the Valve Sizing tab from the Mass flow entered in the blue fields on this tab and the specific gravity entered on the Valve Sizing tab.
Intermediate Calculations
Conversion from Pounds per hour to Gallons per minute (gpm) |  |  | Case 1 | Case 2 | Case 3 | Case 4
Density based on Specific Gravity on the Valve Sizing Tab
| Pounds per hour (lbm/h) | lb_h | 40015 | 106540 | 211575 | 275099 | lbm/ft3 | RHO_lb | 62.372 | 62.372 | 62.372 | 62.372
| Gallons per minutte (gpm) |  | 80.0018 | 213.0048 | 423.0007 | 550.0039 | kg/m3 | RHO_kg | 999.1 | 999.1 | 999.1 | 999.1
Conversion from Kilograms per hour to cubic meters per hour (m3/h)
| Kilograms per hour (kg/h) | kg_h | 18152 | 48329 | 95977 | 124793
| Cubic meters per hour (m3/h) |  | 18.1684 | 48.3725 | 96.0635 | 124.9054
Data input
Final results